## ABB - 600V - TYPE A
Issued: 2006-11-07
Last Revised: 2009-09-22
ID Number | Combination Type | Component Type | Component Manufactuer | Component Catalog Desgination | Component Ratings |  |  |  | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in.) | Conditions of Acceptability | Combination UL File Reference
[5 empty] | kA | Max Amps | Volts | Poles
ABB3600A01.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 600 | 3 | 200 | 600 | 3 | 0.75 | 1.3 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 3 | 600 | -
|  | MC | ABB France | A9 | 5 | 9 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU1.8 | 5 | 1.3 - 1.8 | 600 | 3
ABB3600A01.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 600 | 3 | 200 | 600 | 3 | 0.75 | 1.3 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 3 | 600 | -
|  | MC | ABB France | A9 | 5 | 9 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU1.8-20 | 5 | 1.3 - 1.8 | 600 | 3
ABB3600A02.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 600 | 3 | 200 | 600 | 3 | 1 | 1.7 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 6 | 600 | -
|  | MC | ABB France | A9 | 5 | 9 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU2.4 | 5 | 1.7 - 2.4 | 600 | 3
ABB3600A02.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 600 | 3 | 200 | 600 | 3 | 1 | 1.7 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 6 | 600 | -
|  | MC | ABB France | A9 | 5 | 9 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU2.4-20 | 5 | 1.7 - 2.4 | 600 | 3
ABB3600A03.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 600 | 3 | 200 | 600 | 3 | 1.5 | 2.4 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 6 | 600 | -
|  | MC | ABB France | A9 | 5 | 9 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU3.1 | 5 | 2.2 - 3.1 | 600 | 3
ABB3600A03.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 600 | 3 | 200 | 600 | 3 | 1.5 | 2.4 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 6 | 600 | -
|  | MC | ABB France | A9 | 5 | 9 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU3.1-20 | 5 | 2.2 - 3.1 | 600 | 3
ABB3600A04.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 600 | 3 | 200 | 600 | 3 | 2 | 2.7 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 10 | 600 | -
|  | MC | ABB France | A9 | 5 | 9 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU3.1 | 5 | 2.2 - 3.1 | 600 | 3
ABB3600A04.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 600 | 3 | 200 | 600 | 3 | 2 | 2.7 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 10 | 600 | -
|  | MC | ABB France | A9 | 5 | 9 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU3.1-20 | 5 | 2.2 - 3.1 | 600 | 3
ABB3600A05.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 600 | 3 | 200 | 600 | 3 | 3 | 3.9 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 15 | 600 | -
|  | MC | ABB France | A9 | 5 | 9 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU5.0 | 5 | 3.5 - 5.0 | 600 | 3
ABB3600A05.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 600 | 3 | 200 | 600 | 3 | 3 | 3.9 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 15 | 600 | -
|  | MC | ABB France | A9 | 5 | 9 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU5.0-20 | 5 | 3.5 - 5.0 | 600 | 3
ABB3600A06.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 600 | 3 | 200 | 600 | 3 | 5 | 6.1 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 20 | 600 | -
|  | MC | ABB France | A9 | 5 | 9 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU8.5 | 5 | 6.0 - 8.5 | 600 | 3
ABB3600A06.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 600 | 3 | 200 | 600 | 3 | 5 | 6.1 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 20 | 600 | -
|  | MC | ABB France | A9 | 5 | 9 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU8.5-20 | 5 | 6.0 - 8.5 | 600 | 3
ABB3600A07.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 600 | 3 | 200 | 600 | 3 | 7.5 | 9 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 600 | -
|  | MC | ABB France | A9 | 5 | 9 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU11 | 5 | 7.5 - 11 | 600 | 3
ABB3600A07.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 600 | 3 | 200 | 600 | 3 | 7.5 | 9 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 600 | -
|  | MC | ABB France | A9 | 5 | 9 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU11-20 | 5 | 7.5 - 11 | 600 | 3
ABB3600A08.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 600 | 3 | 200 | 600 | 3 | 10 | 11 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 600 | -
|  | MC | ABB France | A12 | 5 | 11 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU14 | 5 | 10 - 14 | 600 | 3
ABB3600A08.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 600 | 3 | 200 | 600 | 3 | 10 | 11 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 600 | -
|  | MC | ABB France | A12 | 5 | 11 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU14-20 | 5 | 10 - 14 | 600 | 3
ABB3600A09.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 600 | 3 | 200 | 600 | 3 | 15 | 17 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 600 | -
|  | MC | ABB France | A16 | 5 | 17 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU19 | 5 | 13 - 19 | 600 | 3
ABB3600A09.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 600 | 3 | 200 | 600 | 3 | 15 | 17 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 600 | -
|  | MC | ABB France | A16 | 5 | 17 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU19-20 | 5 | 13 - 19 | 600 | 3
ABB3600A10.01 | A | FDS | ABB Oy | OS60J12 | 200 | 60 | 600 | 3 | 200 | 600 | 3 | 20 | 22 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 60 | 600 | -
|  | MC | ABB France | A26 | 5 | 28 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU25 | 5 | 18 - 25 | 600 | 3
ABB3600A10.02 | A | FDS | ABB Oy | OS60J12 | 200 | 60 | 600 | 3 | 200 | 600 | 3 | 20 | 22 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 60 | 600 | -
|  | MC | ABB France | A26 | 5 | 28 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU25-20 | 5 | 18 - 25 | 600 | 3
ABB3600A11.01 | A | FDS | ABB Oy | OS60J12 | 200 | 60 | 600 | 3 | 200 | 600 | 3 | 25 | 27 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 60 | 600 | -
|  | MC | ABB France | A30 | 5 | 34 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU32 | 5 | 24 - 32 | 600 | 3
ABB3600A11.02 | A | FDS | ABB Oy | OS60J12 | 200 | 60 | 600 | 3 | 200 | 600 | 3 | 25 | 27 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 60 | 600 | -
|  | MC | ABB France | A30 | 5 | 34 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU32-20 | 5 | 24 - 32 | 600 | 3
ABB3600A12.01 | A | FDS | ABB Oy | OS100J03 | 200 | 100 | 600 | 3 | 200 | 600 | 3 | 30 | 32 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 100 | 600 | -
|  | MC | ABB France | A40 | 5 | 42 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA42DU42 | 5 | 29 - 42 | 600 | 3
ABB3600A12.02 | A | FDS | ABB Oy | OS100J03 | 200 | 100 | 600 | 3 | 200 | 600 | 3 | 30 | 32 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 100 | 600 | -
|  | MC | ABB France | A40 | 5 | 42 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA42DU42-20 | 5 | 29 - 42 | 600 | 3
ABB3600A13.01 | A | FDS | ABB Oy | OS100J03 | 200 | 100 | 600 | 3 | 200 | 600 | 3 | 40 | 41 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 100 | 600 | -
|  | MC | ABB France | A50 | 5 | 54 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA75DU52 | 5 | 36 - 52 | 600 | 3
ABB3600A13.02 | A | FDS | ABB Oy | OS100J03 | 200 | 100 | 600 | 3 | 200 | 600 | 3 | 40 | 41 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 100 | 600 | -
|  | MC | ABB France | A50 | 5 | 54 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA75DU52-20 | 5 | 36 - 52 | 600 | 3
ABB3600A14.01 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 600 | -
|  | MC | ABB France | A63 | 10 | 65 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA75DU63 | 5 | 45 - 63 | 600 | 3
ABB3600A14.02 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 600 | -
|  | MC | ABB France | A63 | 10 | 65 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA75DU63-20 | 5 | 45 - 63 | 600 | 3
ABB3600A15.01 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 600 | -
|  | MC | ABB France | A75 | 10 | 80 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA75DU80 | 5 | 60 - 80 | 600 | 3
ABB3600A15.02 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 600 | -
|  | MC | ABB France | A75 | 10 | 80 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA75DU80-20 | 5 | 60 - 80 | 600 | 3
ABB3600A16.01 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4800 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 600 | -
|  | MC | ABB AB,CEWE-Control | A110 | 10 | 110 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA110DU90 | 5 | 65 - 90 | 600 | 3
ABB3600A17.01 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4800 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 600 | -
|  | MC | ABB AB,CEWE-Control | A110 | 10 | 110 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA110DU110 | 5 | 80 - 110 | 600 | 3
ABB3600A18.01 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 4800 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 600 | -
|  | MC | ABB France | A145 | 10 | 130 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA200DU135 | 5 | 100 - 135 | 600 | 3
ABB3600A19.01 | A | FDS | ABB Oy | OS400J03 | 200 | 400 | 600 | 3 | 200 | 600 | 3 | 150 | 144 | 9000 | 1, 6 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 350 | 600 | -
|  | MC | ABB AB,CEWE-Control | A210 | 18 | 192 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA450DU185 | 5 | 130 - 185 | 600 | 3
ABB3600A20.01 | A | FDS | ABB Oy | OS400J03 | 200 | 400 | 600 | 3 | 200 | 600 | 3 | 200 | 192 | 9000 | 1, 6 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 400 | 600 | -
|  | MC | ABB AB,CEWE-Control | A260 | 18 | 248 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA450DU235 | 5 | 165 - 235 | 600 | 3
ABB3600A21.01 | A | FDS | ABB Oy | OS600J03 | 200 | 600 | 600 | 3 | 200 | 600 | 3 | 250 | 242 | 9000 | 1, 6 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 600 | 600 | -
|  | MC | ABB AB,CEWE-Control | A300 | 18 | 302 | 600 | 3
|  | OLR | ABB Stotz-kontakt | TA450DU310 | 5 | 220 - 310 | 600 | 3
Conditions of Acceptability:
|  | 1 | All of the specified individual components of the combination motor controller have been installed in an enclosure having
a specified internal volume in cubic inches. Additional testing of the combination motor controller is not required when
installed in an enclosure having the same or larger volume.
|  | 2 | When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from
the overcurrent protective devices and other components shall not be installed in this area.
|  | 3 | When specified, the overload relay heater table number shall be provided with the equipment.
|  | 4 | Unless otherwise specified, all connections between components are made with insulated wire having at least an ampacity of
100 percent of the rated motor current and connected to the terminals supplied with the individual components.
|  | 5 | The need for cautionary markings applicable to high fault short circuit current ratings, Type D a combination motor
controllers shall be considered in the end-product application.
|  | 6 | The TA450 overload relay requires the use of a mounting kit if mounted to the contactor. See the manufactures specifications.

## ABB-480V-Type A
Issued: 2009-09-22
Last Revised: 2009-09-22
ID Number | Combination Type | Component Type | Component Manufactuer | Component Catalog Desgination | Component Ratings |  |  |  | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in.) | Conditions of Acceptability | Combination UL File Reference
[5 empty] | kA | Max Amps | Volts | Poles
ABB3480A01.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 480 | 3 | 200 | 480 | 3 | 0.5 | 1.1 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 3 | 480 | -
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU1.4 | 5 | 1.0 - 1.4 | 480 | 3
ABB3480A01.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 480 | 3 | 200 | 480 | 3 | 0.5 | 1.1 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 3 | 480 | -
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU1.4-20 | 5 | 1.0 - 1.4 | 480 | 3
ABB3480A02.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 480 | 3 | 200 | 480 | 3 | 0.75 | 1.6 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 6 | 480 | -
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU1.8 | 5 | 1.3 - 1.8 | 480 | 3
ABB3480A02.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 480 | 3 | 200 | 480 | 3 | 0.75 | 1.6 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 6 | 480 | -
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU1.8-20 | 5 | 1.3 - 1.8 | 480 | 3
ABB3480A03.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 480 | 3 | 200 | 480 | 3 | 1 | 2.1 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 6 | 480 | -
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU2.4 | 5 | 1.7 - 2.4 | 480 | 3
ABB3480A03.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 480 | 3 | 200 | 480 | 3 | 1 | 2.1 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 6 | 480 | -
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU2.4-20 | 5 | 1.7 - 2.4 | 480 | 3
ABB3480A04.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 480 | 3 | 200 | 480 | 3 | 1.5 | 3 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 10 | 480 | -
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU4.0 | 5 | 2.8 - 4.0 | 480 | 3
ABB3480A04.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 480 | 3 | 200 | 480 | 3 | 1.5 | 3 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 10 | 480 | -
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU4.0-20 | 5 | 2.8 - 4.0 | 480 | 3
ABB3480A05.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 480 | 3 | 200 | 480 | 3 | 2 | 3.4 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 10 | 480 | -
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU4.0 | 5 | 2.8 - 4.0 | 480 | 3
ABB3480A05.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 480 | 3 | 200 | 480 | 3 | 2 | 3.4 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 10 | 480 | -
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU4.0-20 | 5 | 2.8 - 4.0 | 480 | 3
ABB3480A06.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 480 | 3 | 200 | 480 | 3 | 3 | 4.8 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 15 | 480 | -
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU6.5 | 5 | 4.5 - 6.5 | 480 | 3
ABB3480A06.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 480 | 3 | 200 | 480 | 3 | 3 | 4.8 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 15 | 480 | -
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU6.5-20 | 5 | 4.5 - 6.5 | 480 | 3
ABB3480A07.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 480 | 3 | 200 | 480 | 3 | 5 | 7.6 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 480 | -
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11 | 5 | 7.5 - 11 | 480 | 3
ABB3480A07.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 480 | 3 | 200 | 480 | 3 | 5 | 7.6 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 480 | -
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11-20 | 5 | 7.5 - 11 | 480 | 3
ABB3480A08.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 480 | 3 | 200 | 480 | 3 | 7.5 | 11 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 480 | -
|  | MC | ABB France | A12 | 5 | 11 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14 | 5 | 10 - 14.0 | 480 | 3
ABB3480A08.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 480 | 3 | 200 | 480 | 3 | 7.5 | 11 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 480 | -
|  | MC | ABB France | A12 | 5 | 11 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14-20 | 5 | 10 - 14.0 | 480 | 3
ABB3480A09.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 480 | 3 | 200 | 480 | 3 | 10 | 14 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 480 | -
|  | MC | ABB France | A16 | 5 | 17 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19 | 5 | 13 - 19 | 480 | 3
ABB3480A09.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 480 | 3 | 200 | 480 | 3 | 10 | 14 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 480 | -
|  | MC | ABB France | A16 | 5 | 17 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19-20 | 5 | 13 - 19 | 480 | 3
ABB3480A10.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 480 | 3 | 200 | 480 | 3 | 15 | 21 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 480 | -
|  | MC | ABB France | A26 | 5 | 28 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU25 | 5 | 18 - 25 | 480 | 3
ABB3480A10.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 480 | 3 | 200 | 480 | 3 | 15 | 21 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 480 | -
|  | MC | ABB France | A26 | 5 | 28 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU25-20 | 5 | 18 - 25 | 480 | 3
ABB3480A11.01 | A | FDS | ABB Oy | OS60J12 | 200 | 60 | 480 | 3 | 200 | 480 | 3 | 20 | 27 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 60 | 480 | -
|  | MC | ABB France | A26 | 5 | 28 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32 | 5 | 24 - 32 | 480 | 3
ABB3480A11.02 | A | FDS | ABB Oy | OS60J12 | 200 | 60 | 480 | 3 | 200 | 480 | 3 | 20 | 27 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 60 | 480 | -
|  | MC | ABB France | A26 | 5 | 28 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32-20 | 5 | 24 - 32 | 480 | 3
ABB3480A12.01 | A | FDS | ABB Oy | OS60J12 | 200 | 60 | 480 | 3 | 200 | 480 | 3 | 25 | 34 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 60 | 480 | -
|  | MC | ABB France | A30 | 5 | 34 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 480 | 3
ABB3480A12.02 | A | FDS | ABB Oy | OS60J12 | 200 | 60 | 480 | 3 | 200 | 480 | 3 | 25 | 34 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 60 | 480 | -
|  | MC | ABB France | A30 | 5 | 34 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 480 | 3
ABB3480A13.01 | A | FDS | ABB Oy | OS100J03 | 200 | 100 | 480 | 3 | 200 | 480 | 3 | 30 | 40 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 100 | 480 | -
|  | MC | ABB France | A40 | 5 | 42 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 18.0 - 42.0 | 480 | 3
ABB3480A13.02 | A | FDS | ABB Oy | OS100J03 | 200 | 100 | 480 | 3 | 200 | 480 | 3 | 30 | 40 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 100 | 480 | -
|  | MC | ABB France | A40 | 5 | 42 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 18.0 - 42.0 | 480 | 3
ABB3480A14.01 | A | FDS | ABB Oy | OS100J03 | 200 | 100 | 480 | 3 | 200 | 480 | 3 | 40 | 52 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 100 | 480 | -
|  | MC | ABB France | A50 | 5 | 54 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63 | 5 | 45 - 63 | 480 | 3
ABB3480A14.02 | A | FDS | ABB Oy | OS100J03 | 200 | 100 | 480 | 3 | 200 | 480 | 3 | 40 | 52 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 100 | 480 | -
|  | MC | ABB France | A50 | 5 | 54 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63-20 | 5 | 45 - 63 | 480 | 3
ABB3480A15.01 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 480 | 3 | 100 | 480 | 3 | 50 | 65 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 480 | -
|  | MC | ABB France | A63 | 10 | 65 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 480 | 3
ABB3480A15.02 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 480 | 3 | 100 | 480 | 3 | 50 | 65 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 480 | -
|  | MC | ABB France | A63 | 10 | 65 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 480 | 3
ABB3480A16.01 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 480 | 3 | 100 | 480 | 3 | 60 | 77 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 480 | -
|  | MC | ABB France | A75 | 10 | 80 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 18.0 - 80.0 | 480 | 3
ABB3480A16.02 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 480 | 3 | 100 | 480 | 3 | 60 | 77 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 480 | -
|  | MC | ABB France | A75 | 10 | 80 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 18.0 - 80.0 | 480 | 3
ABB3480A17.01 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 480 | 3 | 100 | 480 | 3 | 75 | 96 | 4800 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 480 | -
|  | MC | ABB AB, CEWE-Control | A110 | 10 | 110 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA110DU110 | 5 | 80 - 110 | 480 | 3
ABB3480A18.01 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 480 | 3 | 100 | 480 | 3 | 100 | 125 | 4800 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 480 | -
|  | MC | ABB AB, CEWE-Control | A145 | 10 | 130 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA200DU135 | 5 | 100 - 135 | 480 | 3
ABB3480A19.01 | A | FDS | ABB Oy | OS400JO3 | 200 | 400 | 480 | 3 | 200 | 480 | 3 | 125 | 156 | 4800 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 300 | 480 | -
|  | MC | ABB AB, CEWE-Control | A185 | 10 | 156 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA200DU175 | 5 | 130 - 175 | 480 | 3
ABB3480A20.01 | A | FDS | ABB Oy | OS400J03 | 200 | 400 | 480 | 3 | 200 | 480 | 3 | 150 | 180 | 9000 | 1, 6 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 350 | 480 | -
|  | MC | ABB AB, CEWE-Control | A210 | 18 | 192 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU235 | 5 | 165 - 235 | 480 | 3
ABB3480A21.01 | A | FDS | ABB Oy | OS400J03 | 200 | 400 | 480 | 3 | 200 | 480 | 3 | 200 | 240 | 9000 | 1, 6 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 400 | 480 | -
|  | MC | ABB AB, CEWE-Control | A260 | 18 | 248 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU310 | 5 | 220 - 310 | 480 | 3
ABB3480A22.01 | A | FDS | ABB Oy | OS600J03 | 200 | 600 | 480 | 3 | 200 | 480 | 3 | 250 | 302 | 9000 | 1, 6 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 600 | 480 | -
|  | MC | ABB AB, CEWE-Control | A300 | 18 | 302 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU310 | 5 | 220 - 310 | 480 | 3
Conditions of Acceptability:
|  | 1 | All of the specified individual components of the combination motor controller have been installed in an enclosure having
a specified internal volume in cubic inches. Additional testing of the combination motor controller is not required when
installed in an enclosure having the same or larger volume.
|  | 2 | When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from
the overcurrent protective devices and other components shall not be installed in this area.
|  | 3 | When specified, the overload relay heater table number shall be provided with the equipment.
|  | 4 | Unless otherwise specified, all connections between components are made with insulated wire having at least an ampacity of
100 percent of the rated motor current and connected to the terminals supplied with the individual components.
|  | 5 | The need for cautionary markings applicable to high fault short circuit current ratings, Type D a combination motor
controllers shall be considered in the end-product application.
|  | 6 | The TA450 overload relay requires the use of a mounting kit if mounted to the contactor. See the manufactures specifications.

## ABB-480V-Type C
Issued: 2006-11-07
Last Revised: 2009-09-22
ID Number | Combination Type | Component Type | Component Manufactuer | Component Catalog Desgination | Component Ratings |  |  |  | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in.) | Conditions of Acceptability | Combination UL File Reference
[5 empty] | kA | Max Amps | Volts | Poles
ABB3480C01.01 | C | CB | ABB Sace | S3L015TW | 65 | 15 | 480 | 3 | 35 | 480 | 3 | 0.5 | 1.1 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU1.4 | 5 | 1.0 - 1.4 | 480 | 3
ABB3480C01.02 | C | CB | ABB Sace | S3L015TW | 65 | 15 | 480 | 3 | 35 | 480 | 3 | 0.5 | 1.1 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU1.4-20 | 5 | 1.0 - 1.4 | 480 | 3
ABB3480C02.01 | C | CB | ABB Sace | T2S015TW | 35 | 15 | 480 | 3 | 35 | 480 | 3 | 0.5 | 1.1 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU1.4 | 5 | 1.0 - 1.4 | 480 | 3
ABB3480C02.02 | C | CB | ABB Sace | T2S015TW | 35 | 15 | 480 | 3 | 35 | 480 | 3 | 0.5 | 1.1 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU1.4-20 | 5 | 1.0 - 1.4 | 480 | 3
ABB3480C03.01 | C | CB | ABB Sace | S3L015TW | 65 | 15 | 480 | 3 | 35 | 480 | 3 | 0.75 | 1.6 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU1.8 | 5 | 1.3 - 1.8 | 480 | 3
ABB3480C03.02 | C | CB | ABB Sace | S3L015TW | 65 | 15 | 480 | 3 | 35 | 480 | 3 | 0.75 | 1.6 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU1.8-20 | 5 | 1.3 - 1.8 | 480 | 3
ABB3480C04.02 | C | CB | ABB Sace | T2S015TW | 35 | 15 | 480 | 3 | 35 | 480 | 3 | 0.75 | 1.6 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU1.8 | 5 | 1.3 - 1.8 | 480 | 3
ABB3480C04.02 | C | CB | ABB Sace | T2S015TW | 35 | 15 | 480 | 3 | 35 | 480 | 3 | 0.75 | 1.6 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU1.8-20 | 5 | 1.3 - 1.8 | 480 | 3
ABB3480C05.01 | C | CB | ABB Sace | S3L015TW | 65 | 15 | 480 | 3 | 35 | 480 | 3 | 1 | 2.1 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU2.4 | 5 | 1.7 - 2.4 | 480 | 3
ABB3480C05.02 | C | CB | ABB Sace | S3L015TW | 65 | 15 | 480 | 3 | 35 | 480 | 3 | 1 | 2.1 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU2.4-20 | 5 | 1.7 - 2.4 | 480 | 3
ABB3480C06.01 | C | CB | ABB Sace | T2S015TW | 35 | 15 | 480 | 3 | 35 | 480 | 3 | 1 | 2.1 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU2.4 | 5 | 1.7 - 2.4 | 480 | 3
ABB3480C06.02 | C | CB | ABB Sace | T2S015TW | 35 | 15 | 480 | 3 | 35 | 480 | 3 | 1 | 2.1 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU2.4-20 | 5 | 1.7 - 2.4 | 480 | 3
ABB3480C07.01 | C | CB | ABB Sace | S3L015TW | 65 | 15 | 480 | 3 | 35 | 480 | 3 | 1.5 | 3 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU4.0 | 5 | 2.8 - 4.0 | 480 | 3
ABB3480C07.02 | C | CB | ABB Sace | S3L015TW | 65 | 15 | 480 | 3 | 35 | 480 | 3 | 1.5 | 3 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU4.0-20 | 5 | 2.8 - 4.0 | 480 | 3
ABB3480C08.01 | C | CB | ABB Sace | T2S015TW | 35 | 15 | 480 | 3 | 35 | 480 | 3 | 1.5 | 3 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU4.0 | 5 | 2.8 - 4.0 | 480 | 3
ABB3480C08.02 | C | CB | ABB Sace | T2S015TW | 35 | 15 | 480 | 3 | 35 | 480 | 3 | 1.5 | 3 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU4.0-20 | 5 | 2.8 - 4.0 | 480 | 3
ABB3480C09.01 | C | CB | ABB Sace | S3L015TW | 65 | 15 | 480 | 3 | 35 | 480 | 3 | 2 | 3.4 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU4.0 | 5 | 2.8 - 4.0 | 480 | 3
ABB3480C09.02 | C | CB | ABB Sace | S3L015TW | 65 | 15 | 480 | 3 | 35 | 480 | 3 | 2 | 3.4 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU4.0-20 | 5 | 2.8 - 4.0 | 480 | 3
ABB3480C10.01 | C | CB | ABB Sace | T2S015TW | 35 | 15 | 480 | 3 | 35 | 480 | 3 | 2 | 3.4 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU4.0 | 5 | 2.8 - 4.0 | 480 | 3
ABB3480C10.02 | C | CB | ABB Sace | T2S015TW | 35 | 15 | 480 | 3 | 35 | 480 | 3 | 2 | 3.4 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU4.0-20 | 5 | 2.8 - 4.0 | 480 | 3
ABB3480C11.01 | C | CB | ABB Sace | S3L015TW | 65 | 15 | 480 | 3 | 35 | 480 | 3 | 3 | 4.8 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU6.5 | 5 | 4.5 - 6.5 | 480 | 3
ABB3480C11.02 | C | CB | ABB Sace | S3L015TW | 65 | 15 | 480 | 3 | 35 | 480 | 3 | 3 | 4.8 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU6.5-20 | 5 | 4.5 - 6.5 | 480 | 3
ABB3480C12.01 | C | CB | ABB Sace | T2S015TW | 35 | 15 | 480 | 3 | 35 | 480 | 3 | 3 | 4.8 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU6.5 | 5 | 4.5 - 6.5 | 480 | 3
ABB3480C12.02 | C | CB | ABB Sace | T2S015TW | 35 | 15 | 480 | 3 | 35 | 480 | 3 | 3 | 4.8 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU6.5-20 | 5 | 4.5 - 6.5 | 480 | 3
ABB3480C13.01 | C | CB | ABB Sace | S3L015TW | 65 | 15 | 480 | 3 | 35 | 480 | 3 | 5 | 7.6 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11 | 5 | 7.5 - 11 | 480 | 3
ABB3480C13.02 | C | CB | ABB Sace | S3L015TW | 65 | 15 | 480 | 3 | 35 | 480 | 3 | 5 | 7.6 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11-20 | 5 | 7.5 - 11 | 480 | 3
ABB3480C14.01 | C | CB | ABB Sace | T2S015TW | 35 | 15 | 480 | 3 | 35 | 480 | 3 | 5 | 7.6 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11 | 5 | 7.5 - 11 | 480 | 3
ABB3480C14.02 | C | CB | ABB Sace | T2S015TW | 35 | 15 | 480 | 3 | 35 | 480 | 3 | 5 | 7.6 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11-20 | 5 | 7.5 - 11 | 480 | 3
ABB3480C15.01 | C | CB | ABB Sace | S3L020TW | 65 | 20 | 480 | 3 | 35 | 480 | 3 | 7.5 | 11 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14 | 5 | 10 - 14.0 | 480 | 3
ABB3480C15.02 | C | CB | ABB Sace | S3L020TW | 65 | 20 | 480 | 3 | 35 | 480 | 3 | 7.5 | 11 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14-20 | 5 | 10 - 14.0 | 480 | 3
ABB3480C16.01 | C | CB | ABB Sace | T2S020TW | 35 | 20 | 480 | 3 | 35 | 480 | 3 | 7.5 | 11 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14 | 5 | 10 - 14.0 | 480 | 3
ABB3480C16.02 | C | CB | ABB Sace | T2S020TW | 35 | 20 | 480 | 3 | 35 | 480 | 3 | 7.5 | 11 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14-20 | 5 | 10 - 14.0 | 480 | 3
ABB3480C17.01 | C | CB | ABB Sace | S3L030TW | 65 | 30 | 480 | 3 | 35 | 480 | 3 | 10 | 14 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19 | 5 | 13 - 19 | 480 | 3
ABB3480C17.02 | C | CB | ABB Sace | S3L030TW | 65 | 30 | 480 | 3 | 35 | 480 | 3 | 10 | 14 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19-20 | 5 | 13 - 19 | 480 | 3
ABB3480C18.01 | C | CB | ABB Sace | T2S030TW | 35 | 20 | 480 | 3 | 35 | 480 | 3 | 10 | 14 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19 | 5 | 13 - 19 | 480 | 3
ABB3480C18.02 | C | CB | ABB Sace | T2S030TW | 35 | 20 | 480 | 3 | 35 | 480 | 3 | 10 | 14 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19-20 | 5 | 13 - 19 | 480 | 3
ABB3480C19.01 | C | CB | ABB Sace | S3L050TW | 85 | 50 | 480 | 3 | 35 | 480 | 3 | 15 | 21 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU25 | 5 | 18 - 25 | 480 | 3
ABB3480C19.02 | C | CB | ABB Sace | S3L050TW | 85 | 50 | 480 | 3 | 35 | 480 | 3 | 15 | 21 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU25-20 | 5 | 18 - 25 | 480 | 3
ABB3480C20.01 | C | CB | ABB Sace | T2S050TW | 35 | 40 | 480 | 3 | 35 | 480 | 3 | 15 | 21 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU25 | 5 | 18 - 25 | 480 | 3
ABB3480C20.02 | C | CB | ABB Sace | T2S050TW | 35 | 40 | 480 | 3 | 35 | 480 | 3 | 15 | 21 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU25-20 | 5 | 18 - 25 | 480 | 3
ABB3480C21.01 | C | CB | ABB Sace | S3L050TW | 85 | 50 | 480 | 3 | 35 | 480 | 3 | 20 | 27 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32 | 5 | 24 - 32 | 480 | 3
ABB3480C21.02 | C | CB | ABB Sace | S3L050TW | 85 | 50 | 480 | 3 | 35 | 480 | 3 | 20 | 27 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32-20 | 5 | 24 - 32 | 480 | 3
ABB3480C22.01 | C | CB | ABB Sace | T2S050TW | 35 | 40 | 480 | 3 | 35 | 480 | 3 | 20 | 27 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32 | 5 | 24 - 32 | 480 | 3
ABB3480C22.02 | C | CB | ABB Sace | T2S050TW | 35 | 40 | 480 | 3 | 35 | 480 | 3 | 20 | 27 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32-20 | 5 | 24 - 32 | 480 | 3
ABB3480C23.01 | C | CB | ABB Sace | S3L060TW | 85 | 60 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 480 | 3
ABB3480C23.02 | C | CB | ABB Sace | S3L060TW | 85 | 60 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 480 | 3
ABB3480C24.01 | C | CB | ABB Sace | TS3L060TW | 65 | 60 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 480 | 3
ABB3480C24.02 | C | CB | ABB Sace | TS3L060TW | 65 | 60 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 480 | 3
ABB3480C25.01 | C | CB | ABB Sace | S3L060TW | 85 | 60 | 480 | 3 | 65 | 480 | 3 | 30 | 40 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 480 | 3
ABB3480C25.02 | C | CB | ABB Sace | S3L060TW | 85 | 60 | 480 | 3 | 65 | 480 | 3 | 30 | 40 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 480 | 3
ABB3480C26.01 | C | CB | ABB Sace | TS3L060TW | 65 | 60 | 480 | 3 | 65 | 480 | 3 | 30 | 40 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 480 | 3
ABB3480C26.02 | C | CB | ABB Sace | TS3L060TW | 65 | 60 | 480 | 3 | 65 | 480 | 3 | 30 | 40 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 480 | 3
ABB3480C27.01 | C | CB | ABB Sace | S3L080TW | 85 | 80 | 480 | 3 | 85 | 480 | 3 | 40 | 52 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63 | 5 | 45 - 63 | 480 | 3
ABB3480C27.02 | C | CB | ABB Sace | S3L080TW | 85 | 80 | 480 | 3 | 85 | 480 | 3 | 40 | 52 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63-20 | 5 | 45 - 63 | 480 | 3
ABB3480C28.01 | C | CB | ABB Sace | TS3L080TW | 65 | 80 | 480 | 3 | 85 | 480 | 3 | 40 | 52 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 52 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63 | 5 | 45 - 63 | 480 | 3
ABB3480C28.02 | C | CB | ABB Sace | TS3L080TW | 65 | 80 | 480 | 3 | 85 | 480 | 3 | 40 | 52 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 52 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63-20 | 5 | 45 - 63 | 480 | 3
ABB3480C29.01 | C | CB | ABB Sace | S3L100TW | 85 | 100 | 480 | 3 | 85 | 480 | 3 | 50 | 65 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 480 | 3
ABB3480C29.02 | C | CB | ABB Sace | S3L100TW | 85 | 100 | 480 | 3 | 85 | 480 | 3 | 50 | 65 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 480 | 3
ABB3480C30.01 | C | CB | ABB Sace | TS3L100TW | 65 | 100 | 480 | 3 | 85 | 480 | 3 | 50 | 65 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 480 | 3
ABB3480C30.02 | C | CB | ABB Sace | TS3L100TW | 65 | 100 | 480 | 3 | 85 | 480 | 3 | 50 | 65 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 480 | 3
ABB3480C31.01 | C | CB | ABB Sace | S3L150TW | 85 | 150 | 480 | 3 | 85 | 480 | 3 | 60 | 77 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 480 | 3
ABB3480C31.02 | C | CB | ABB Sace | S3L150TW | 85 | 150 | 480 | 3 | 85 | 480 | 3 | 60 | 77 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 480 | 3
ABB3480C32.01 | C | CB | ABB Sace | T4L150TW | 100 | 150 | 480 | 3 | 85 | 480 | 3 | 60 | 77 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 480 | 3
ABB3480C32.02 | C | CB | ABB Sace | T4L150TW | 100 | 150 | 480 | 3 | 85 | 480 | 3 | 60 | 77 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 480 | 3
ABB3480C33.01 | C | CB | ABB Sace | S3L150TW | 85 | 150 | 480 | 3 | 85 | 480 | 3 | 75 | 96 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB AB,CEWE-Control | A110 | 10 | 110 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA110DU110 | 5 | 80 - 110 | 480 | 3
ABB3480C34.01 | C | CB | ABB Sace | T4L150TW | 100 | 150 | 480 | 3 | 85 | 480 | 3 | 75 | 96 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB AB,CEWE-Control | A110 | 10 | 110 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA110DU110 | 5 | 80 - 110 | 480 | 3
ABB3480C35.01 | C | CB | ABB Sace | S4N200TW | 25 | 200 | 480 | 3 | 65 | 480 | 3 | 100 | 124 | 4800 | 1 | E193298 V1 S1
|  | MC | ABB AB,CEWE-Control | A145 | 10 | 130 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA200DU135 | 5 | 100 - 135 | 480 | 3
ABB3480C36.01 | C | CB | ABB Sace | T4L200TW | 100 | 200 | 480 | 3 | 65 | 480 | 3 | 100 | 124 | 4800 | 1 | E193298 V1 S1
|  | MC | ABB AB,CEWE-Control | A145 | 10 | 130 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA200DU135 | 5 | 100 - 135 | 480 | 3
ABB3480C37.01 | C | CB | ABB Sace | S4N200TW | 25 | 200 | 480 | 3 | 85 | 480 | 3 | 125 | 156 | 4800 | 1 | E193298 V1 S1
|  | MC | ABB AB,CEWE-Control | A185 | 10 | 156 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA200DU175 | 5 | 130 - 175 | 480 | 3
ABB3480C38.01 | C | CB | ABB Sace | T4L200TW | 100 | 200 | 480 | 3 | 85 | 480 | 3 | 125 | 156 | 4800 | 1 | E193298 V1 S1
|  | MC | ABB AB,CEWE-Control | A185 | 10 | 156 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA20DU175 | 5 | 130 - 175 | 480 | 3
ABB3480C39.01 | C | CB | ABB Sace | S5N300TW | 35 | 300 | 480 | 3 | 85 | 480 | 3 | 150 | 180 | 9000 | 1, 6 | E193298 V1 S1
|  | MC | ABB AB,CEWE-Control | A210 | 18 | 192 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU235 | 5 | 165 - 235 | 480 | 3
ABB3480C40.01 | C | CB | ABB Sace | T4L250TW | 100 | 300 | 480 | 3 | 85 | 480 | 3 | 150 | 180 | 9000 | 1, 6 | E193298 V1 S1
|  | MC | ABB AB,CEWE-Control | A210 | 18 | 192 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU235 | 5 | 165 - 235 | 480 | 3
ABB3480C41.01 | C | CB | ABB Sace | S5N400TW | 35 | 400 | 480 | 3 | 85 | 480 | 3 | 200 | 240 | 9000 | 1, 6 | E193298 V1 S1
|  | MC | ABB AB,CEWE-Control | A260 | 18 | 248 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU310 | 5 | 220 - 310 | 480 | 3
ABB3480C42.01 | C | CB | ABB Sace | T5L400TW | 100 | 400 | 480 | 3 | 85 | 480 | 3 | 200 | 240 | 9000 | 1, 6 | E193298 V1 S1
|  | MC | ABB AB,CEWE-Control | A260 | 18 | 248 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU310 | 5 | 220 - 310 | 480 | 3
ABB3480C43.01 | C | CB | ABB Sace | S5N400TW | 35 | 400 | 480 | 3 | 85 | 480 | 3 | 250 | 302 | 9000 | 1, 6 | E193298 V1 S1
|  | MC | ABB AB,CEWE-Control | A300 | 18 | 302 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU310 | 5 | 220 - 310 | 480 | 3
ABB3480C44.01 | C | CB | ABB Sace | T5L400TW | 100 | 400 | 480 | 3 | 85 | 480 | 3 | 250 | 302 | 9000 | 1, 6 | E193298 V1 S1
|  | MC | ABB AB,CEWE-Control | A300 | 18 | 302 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU310 | 5 | 220 - 310 | 480 | 3
Conditions of Acceptability:
|  | 1 | All of the specified individual components of the combination motor controller have been installed in an enclosure having
a specified internal volume in cubic inches. Additional testing of the combination motor controller is not required when
installed in an enclosure having the same or larger volume.
|  | 2 | When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from
the overcurrent protective devices and other components shall not be installed in this area.
|  | 3 | When specified, the overload relay heater table number shall be provided with the equipment.
|  | 4 | Unless otherwise specified, all connections between components are made with insulated wire having at least an ampacity of
100 percent of the rated motor current and connected to the terminals supplied with the individual components.
|  | 5 | The need for cautionary markings applicable to high fault short circuit current ratings, Type D a combination motor
controllers shall be considered in the end-product application.
|  | 6 | The TA450 overload relay requires the use of a mounting kit if mounted to the contactor. See the manufactures specifications.

## ABB-480V-Type D
Issued: 2006-11-07
Last Revised: 2009-09-22
ID Number | Combination Type | Component Type | Component Manufactuer | Component Catalog Desgination | Component Ratings |  |  |  | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum ombination NEC FLC | Minimum Enclosure Volume (cu in.) | Conditions of Acceptability | Combination UL File Reference
[5 empty] | kA | Max Amps | Volts | Poles
ABB3480D01.01 | D | ICB | ABB Sace | S3L003MW | - | 3 | 480 | 3 | 35 | 480 | 3 | 0.5 | 1.1 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU1.4 | 5 | 1.0 - 1.4 | 480 | 3
ABB3480D01.02 | D | ICB | ABB Sace | S3L003MW | - | 3 | 480 | 3 | 35 | 480 | 3 | 0.5 | 1.1 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU1.4-20 | 5 | 1.0 - 1.4 | 480 | 3
ABB3480D02.01 | D | ICB | ABB Sace | TS3L003MW | - | 3 | 480 | 3 | 35 | 480 | 3 | 0.5 | 1.1 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU1.4 | 5 | 1.0 - 1.4 | 480 | 3
ABB3480D02.02 | D | ICB | ABB Sace | TS3L003MW | - | 3 | 480 | 3 | 35 | 480 | 3 | 0.5 | 1.1 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU1.4-20 | 5 | 1.0 - 1.4 | 480 | 3
ABB3480D03.01 | D | ICB | ABB Sace | S3L003MW | - | 3 | 480 | 3 | 35 | 480 | 3 | 0.75 | 1.6 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU1.8 | 5 | 1.3 - 1.8 | 480 | 3
ABB3480D03.02 | D | ICB | ABB Sace | S3L003MW | - | 3 | 480 | 3 | 35 | 480 | 3 | 0.75 | 1.6 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU1.8-20 | 5 | 1.3 - 1.8 | 480 | 3
ABB3480D04.01 | D | ICB | ABB Sace | TS3L003MW | - | 3 | 480 | 3 | 35 | 480 | 3 | 0.75 | 1.6 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU1.8 | 5 | 1.3 - 1.8 | 480 | 3
ABB3480D04.02 | D | ICB | ABB Sace | TS3L003MW | - | 3 | 480 | 3 | 35 | 480 | 3 | 0.75 | 1.6 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU1.8-20 | 5 | 1.3 - 1.8 | 480 | 3
ABB3480D05.01 | D | ICB | ABB Sace | S3L005MW | - | 5 | 480 | 3 | 35 | 480 | 3 | 1 | 2.1 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU2.4 | 5 | 1.7 - 2.4 | 480 | 3
ABB3480D05.02 | D | ICB | ABB Sace | S3L005MW | - | 5 | 480 | 3 | 35 | 480 | 3 | 1 | 2.1 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU2.4-20 | 5 | 1.7 - 2.4 | 480 | 3
ABB3480D06.01 | D | ICB | ABB Sace | TS3L005MW | - | 5 | 480 | 3 | 35 | 480 | 3 | 1 | 2.1 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU2.4 | 5 | 1.7 - 2.4 | 480 | 3
ABB3480D06.02 | D | ICB | ABB Sace | TS3L005MW | - | 5 | 480 | 3 | 35 | 480 | 3 | 1 | 2.1 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU2.4-20 | 5 | 1.7 - 2.4 | 480 | 3
ABB3480D07.01 | D | ICB | ABB Sace | S3L005MW | - | 5 | 480 | 3 | 35 | 480 | 3 | 1.5 | 3 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU4.0 | 5 | 2.8 - 4.0 | 480 | 3
ABB3480D07.02 | D | ICB | ABB Sace | S3L005MW | - | 5 | 480 | 3 | 35 | 480 | 3 | 1.5 | 3 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU4.0-20 | 5 | 2.8 - 4.0 | 480 | 3
ABB3480D08.01 | D | ICB | ABB Sace | TS3L005MW | - | 5 | 480 | 3 | 35 | 480 | 3 | 1.5 | 3 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU4.0 | 5 | 2.8 - 4.0 | 480 | 3
ABB3480D08.02 | D | ICB | ABB Sace | TS3L005MW | - | 5 | 480 | 3 | 35 | 480 | 3 | 1.5 | 3 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU4.0-20 | 5 | 2.8 - 4.0 | 480 | 3
ABB3480D09.01 | D | ICB | ABB Sace | S3L005MW | - | 5 | 480 | 3 | 35 | 480 | 3 | 2 | 3.4 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU4.0 | 5 | 2.8 - 4.0 | 480 | 3
ABB3480D09.02 | D | ICB | ABB Sace | S3L005MW | - | 5 | 480 | 3 | 35 | 480 | 3 | 2 | 3.4 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU4.0-20 | 5 | 2.8 - 4.0 | 480 | 3
ABB3480D10.01 | D | ICB | ABB Sace | TS3L005MW | - | 5 | 480 | 3 | 35 | 480 | 3 | 2 | 3.4 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU4.0 | 5 | 2.8 - 4.0 | 480 | 3
ABB3480D10.02 | D | ICB | ABB Sace | TS3L005MW | - | 5 | 480 | 3 | 35 | 480 | 3 | 2 | 3.4 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU4.0-20 | 5 | 2.8 - 4.0 | 480 | 3
ABB3480D11.01 | D | ICB | ABB Sace | S3L010MW | - | 10 | 480 | 3 | 35 | 480 | 3 | 3 | 4.8 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU6.5 | 5 | 4.5 - 6.5 | 480 | 3
ABB3480D11.02 | D | ICB | ABB Sace | S3L010MW | - | 10 | 480 | 3 | 35 | 480 | 3 | 3 | 4.8 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU6.5-20 | 5 | 4.5 - 6.5 | 480 | 3
ABB3480D12.01 | D | ICB | ABB Sace | TS3L010MW | - | 10 | 480 | 3 | 35 | 480 | 3 | 3 | 4.8 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU6.5 | 5 | 4.5 - 6.5 | 480 | 3
ABB3480D12.02 | D | ICB | ABB Sace | TS3L010MW | - | 10 | 480 | 3 | 35 | 480 | 3 | 3 | 4.8 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU6.5-20 | 5 | 4.5 - 6.5 | 480 | 3
ABB3480D13.01 | D | ICB | ABB Sace | S3L010MW | - | 10 | 480 | 3 | 35 | 480 | 3 | 5 | 7.6 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11 | 5 | 7.5 - 11 | 480 | 3
ABB3480D13.02 | D | ICB | ABB Sace | S3L010MW | - | 10 | 480 | 3 | 35 | 480 | 3 | 5 | 7.6 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11-20 | 5 | 7.5 - 11 | 480 | 3
ABB3480D14.01 | D | ICB | ABB Sace | TS3L010MW | - | 10 | 480 | 3 | 35 | 480 | 3 | 5 | 7.6 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11 | 5 | 7.5 - 11 | 480 | 3
ABB3480D14.02 | D | ICB | ABB Sace | TS3L010MW | - | 10 | 480 | 3 | 35 | 480 | 3 | 5 | 7.6 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11-20 | 5 | 7.5 - 11 | 480 | 3
ABB3480D15.01 | D | ICB | ABB Sace | S3L025MW | - | 25 | 480 | 3 | 35 | 480 | 3 | 7.5 | 11 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14 | 5 | 10 - 14.0 | 480 | 3
ABB3480D15.02 | D | ICB | ABB Sace | S3L025MW | - | 25 | 480 | 3 | 35 | 480 | 3 | 7.5 | 11 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14-20 | 5 | 10 - 14.0 | 480 | 3
ABB3480D16.01 | D | ICB | ABB Sace | TS3L025MW | - | 25 | 480 | 3 | 35 | 480 | 3 | 7.5 | 11 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14 | 5 | 10 - 14.0 | 480 | 3
ABB3480D16.02 | D | ICB | ABB Sace | TS3L025MW | - | 25 | 480 | 3 | 35 | 480 | 3 | 7.5 | 11 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14-20 | 5 | 10 - 14.0 | 480 | 3
ABB3480D17.01 | D | ICB | ABB Sace | S3L050MW | - | 50 | 480 | 3 | 35 | 480 | 3 | 10 | 14 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19 | 5 | 13 - 19 | 480 | 3
ABB3480D17.02 | D | ICB | ABB Sace | S3L050MW | - | 50 | 480 | 3 | 35 | 480 | 3 | 10 | 14 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19-20 | 5 | 13 - 19 | 480 | 3
ABB3480D18.01 | D | ICB | ABB Sace | T2S050MW | - | 50 | 480 | 3 | 35 | 480 | 3 | 10 | 14 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19 | 5 | 13 - 19 | 480 | 3
ABB3480D18.02 | D | ICB | ABB Sace | T2S050MW | - | 50 | 480 | 3 | 35 | 480 | 3 | 10 | 14 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19-20 | 5 | 13 - 19 | 480 | 3
ABB3480D19.01 | D | ICB | ABB Sace | S3L050MW | - | 50 | 480 | 3 | 35 | 480 | 3 | 15 | 21 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU25 | 5 | 18 - 25 | 480 | 3
ABB3480D19.02 | D | ICB | ABB Sace | S3L050MW | - | 50 | 480 | 3 | 35 | 480 | 3 | 15 | 21 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU25-20 | 5 | 18 - 25 | 480 | 3
ABB3480D20.01 | D | ICB | ABB Sace | T2S050MW | - | 50 | 480 | 3 | 35 | 480 | 3 | 15 | 21 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU25 | 5 | 18 - 25 | 480 | 3
ABB3480D20.02 | D | ICB | ABB Sace | T2S050MW | - | 50 | 480 | 3 | 35 | 480 | 3 | 15 | 21 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU25-20 | 5 | 18 - 25 | 480 | 3
ABB3480D21.01 | D | ICB | ABB Sace | S3L050MW | - | 50 | 480 | 3 | 35 | 480 | 3 | 20 | 27 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32 | 5 | 24 - 32 | 480 | 3
ABB3480D21.02 | D | ICB | ABB Sace | S3L050MW | - | 50 | 480 | 3 | 35 | 480 | 3 | 20 | 27 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32-20 | 5 | 24 - 32 | 480 | 3
ABB3480D22.01 | D | ICB | ABB Sace | T2S050MW | - | 50 | 480 | 3 | 35 | 480 | 3 | 20 | 27 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32 | 5 | 24 - 32 | 480 | 3
ABB3480D22.02 | D | ICB | ABB Sace | T2S050MW | - | 50 | 480 | 3 | 35 | 480 | 3 | 20 | 27 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32-20 | 5 | 24 - 32 | 480 | 3
ABB3480D23.01 | D | ICB | ABB Sace | S3L050MW | - | 50 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 480 | 3
ABB3480D23.02 | D | ICB | ABB Sace | S3L050MW | - | 50 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 480 | 3
ABB3480D24.01 | D | ICB | ABB Sace | TS3L050MW | - | 50 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 480 | 3
ABB3480D24.02 | D | ICB | ABB Sace | TS3L050MW | - | 50 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 480 | 3
ABB3480D25.01 | D | ICB | ABB Sace | S3L100MW | - | 100 | 480 | 3 | 65 | 480 | 3 | 30 | 40 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 480 | 3
ABB3480D25.02 | D | ICB | ABB Sace | S3L100MW | - | 100 | 480 | 3 | 65 | 480 | 3 | 30 | 40 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 480 | 3
ABB3480D26.01 | D | ICB | ABB Sace | TS3L100MW | - | 100 | 480 | 3 | 65 | 480 | 3 | 30 | 40 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 480 | 3
ABB3480D26.02 | D | ICB | ABB Sace | TS3L100MW | - | 100 | 480 | 3 | 65 | 480 | 3 | 30 | 40 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 480 | 3
ABB3480D27.01 | D | ICB | ABB Sace | S3L100MW | - | 100 | 480 | 3 | 85 | 480 | 3 | 40 | 52 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63 | 5 | 45 - 63 | 480 | 3
ABB3480D27.02 | D | ICB | ABB Sace | S3L100MW | - | 100 | 480 | 3 | 85 | 480 | 3 | 40 | 52 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63-20 | 5 | 45 - 63 | 480 | 3
ABB3480D28.01 | D | ICB | ABB Sace | TS3L100MW | - | 100 | 480 | 3 | 85 | 480 | 3 | 40 | 52 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63 | 5 | 45 - 63 | 480 | 3
ABB3480D28.02 | D | ICB | ABB Sace | TS3L100MW | - | 100 | 480 | 3 | 85 | 480 | 3 | 40 | 52 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63-20 | 5 | 45 - 63 | 480 | 3
ABB3480D28.01 | D | ICB | ABB Sace | S3L100MW | - | 100 | 480 | 3 | 85 | 480 | 3 | 50 | 65 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 480 | 3
ABB3480D28.02 | D | ICB | ABB Sace | S3L100MW | - | 100 | 480 | 3 | 85 | 480 | 3 | 50 | 65 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 480 | 3
ABB3480D29.01 | D | ICB | ABB Sace | T4L100MW | - | 100 | 480 | 3 | 85 | 480 | 3 | 50 | 65 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 480 | 3
ABB3480D29.02 | D | ICB | ABB Sace | T4L100MW | - | 100 | 480 | 3 | 85 | 480 | 3 | 50 | 65 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 480 | 3
ABB3480D30.01 | D | ICB | ABB Sace | S3L150MW | - | 150 | 480 | 3 | 85 | 480 | 3 | 60 | 77 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 480 | 3
ABB3480D30.02 | D | ICB | ABB Sace | S3L150MW | - | 150 | 480 | 3 | 85 | 480 | 3 | 60 | 77 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 480 | 3
ABB3480D31.01 | D | ICB | ABB Sace | T4L150MW | - | 150 | 480 | 3 | 85 | 480 | 3 | 60 | 77 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 480 | 3
ABB3480D31.02 | D | ICB | ABB Sace | T4L150MW | - | 150 | 480 | 3 | 85 | 480 | 3 | 60 | 77 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 480 | 3
ABB3480D32.01 | D | ICB | ABB Sace | S4L250MW | - | 250 | 480 | 3 | 85 | 480 | 3 | 75 | 96 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB AB,CEWE-Control | A110 | 10 | 110 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA110DU110 | 5 | 80 - 110 | 480 | 3
ABB3480D33.01 | D | ICB | ABB Sace | T4L250MW | - | 250 | 480 | 3 | 85 | 480 | 3 | 75 | 96 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB AB,CEWE-Control | A110 | 10 | 110 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA110DU110 | 5 | 80 - 110 | 480 | 3
ABB3480D34.01 | D | ICB | ABB Sace | S4N200MW | - | 200 | 480 | 3 | 65 | 480 | 3 | 100 | 124 | 4800 | 1,5 | E193298 V1 S1
|  | MC | ABB AB,CEWE-Control | A145 | 10 | 130 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA200DU135 | 5 | 100 - 135 | 480 | 3
ABB3480D35.01 | D | ICB | ABB Sace | T4L200MW | - | 200 | 480 | 3 | 65 | 480 | 3 | 100 | 124 | 4800 | 1,5 | E193298 V1 S1
|  | MC | ABB AB,CEWE-Control | A145 | 10 | 130 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA200DU135 | 5 | 100 - 135 | 480 | 3
ABB3480D36.01 | D | ICB | ABB Sace | S4N250MW | - | 250 | 480 | 3 | 85 | 480 | 3 | 125 | 156 | 4800 | 1,5 | E193298 V1 S1
|  | MC | ABB AB,CEWE-Control | A185 | 10 | 156 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA200DU175 | 5 | 130 - 175 | 480 | 3
ABB3480D37.01 | D | ICB | ABB Sace | T4L250MW | - | 250 | 480 | 3 | 85 | 480 | 3 | 125 | 156 | 4800 | 1,5 | E193298 V1 S1
|  | MC | ABB AB,CEWE-Control | A185 | 10 | 156 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA200DU175 | 5 | 130 - 175 | 480 | 3
ABB3480D38.01 | D | ICB | ABB Sace | S4N250MW | - | 250 | 480 | 3 | 85 | 480 | 3 | 150 | 180 | 9000 | 1, 5, 6 | E193298 V1 S1
|  | MC | ABB AB,CEWE-Control | A210 | 18 | 192 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU235 | 5 | 165 - 235 | 480 | 3
ABB3480D39.01 | D | ICB | ABB Sace | T4L250MW | - | 250 | 480 | 3 | 85 | 480 | 3 | 150 | 180 | 9000 | 1, 5, 6 | E193298 V1 S1
|  | MC | ABB AB,CEWE-Control | A210 | 18 | 192 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU235 | 5 | 165 - 235 | 480 | 3
ABB3480D40.01 | D | ICB | ABB Sace | S5N400MW | - | 400 | 480 | 3 | 85 | 480 | 3 | 200 | 240 | 9000 | 1, 5, 6 | E193298 V1 S1
|  | MC | ABB AB,CEWE-Control | A260 | 18 | 248 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU310 | 5 | 220 - 310 | 480 | 3
ABB3480D41.01 | D | ICB | ABB Sace | T5L400MW | - | 400 | 480 | 3 | 85 | 480 | 3 | 200 | 240 | 9000 | 1, 5, 6 | E193298 V1 S1
|  | MC | ABB AB,CEWE-Control | A260 | 18 | 248 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU310 | 5 | 220 - 310 | 480 | 3
ABB3480D42.01 | D | ICB | ABB Sace | S5N400MW | - | 400 | 480 | 3 | 85 | 480 | 3 | 250 | 302 | 9000 | 1, 5, 6 | E193298 V1 S1
|  | MC | ABB AB,CEWE-Control | A300 | 18 | 302 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU310 | 5 | 220 - 310 | 480 | 3
ABB3480D43.01 | D | ICB | ABB Sace | T5L400MW | - | 400 | 480 | 3 | 85 | 480 | 3 | 250 | 302 | 9000 | 1, 5, 6 | E193298 V1 S1
|  | MC | ABB AB,CEWE-Control | A300 | 18 | 302 | 480 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU310 | 5 | 220 - 310 | 480 | 3
Conditions of Acceptability:
|  | 1 | All of the specified individual components of the combination motor controller have been installed in an enclosure having | [11 empty] | Component manufactured by-
a specified internal volume in cubic inches. Additional testing of the combination motor controller is not required when
|  |  | installed in an enclosure having the same or larger volume. | [11 empty] | Contactor A9 - A75 ( ABB France )
Contactor A110 - A300 ( ABB CEWE Control AB )
|  | 2 | When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from | [11 empty] | Overload relay ( ABB Stotz- Kontakt )
|  |  | the overcurrent protective devices and other components shall not be installed in this area. | [11 empty] | Breaker ( ABB SACE )
|  | 3 | When specified, the overload relay heater table number shall be provided with the equipment.
|  | 4 | Unless otherwise specified, all connections between components are made with insulated wire having at least an ampacity of
100 percent of the rated motor current and connected to the terminals supplied with the individual components.
|  | 5 | The need for cautionary markings applicable to high fault short circuit current ratings, Type D a combination motor
controllers shall be considered in the end-product application.
|  | 6 | The TA450 overload relay requires the use of a mounting kit if mounted to the contactor. See the manufactures specifications.

## ABB - 240V - TYPE A
Issued: 2009-09-22
Last Revised: 2009-09-22
ID Number | Combination Type | Component Type | Component Manufactuer | Component Catalog Desgination | Component Ratings |  |  |  | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in.) | Conditions of Acceptability | Combination UL File Reference
[5 empty] | kA | Max Amps | Volts | Poles
ABB3240A01.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 240 | 3 | 200 | 240 | 3 | 0.5 | 2.2 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 6 | 240 | -
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU3.1 | 5 | 2.2 - 3.1 | 240 | 3
ABB3240A01.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 240 | 3 | 200 | 240 | 3 | 0.5 | 2.2 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 6 | 240 | -
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU3.1-20 | 5 | 2.2 - 3.1 | 240 | 3
ABB3240A02.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 240 | 3 | 200 | 240 | 3 | 0.75 | 3.2 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 10 | 240 | -
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU4.0 | 5 | 2.8 - 4.0 | 240 | 3
ABB3240A02.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 240 | 3 | 200 | 240 | 3 | 0.75 | 3.2 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 10 | 240 | -
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU4.0-20 | 5 | 2.8 - 4.0 | 240 | 3
ABB3240A03.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 240 | 3 | 200 | 240 | 3 | 1 | 4.2 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 15 | 240 | -
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU5.0 | 5 | 3.5 - 5.0 | 240 | 3
ABB3240A03.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 240 | 3 | 200 | 240 | 3 | 1 | 4.2 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 15 | 240 | -
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU5.0-20 | 5 | 3.5 - 5.0 | 240 | 3
ABB3240A04.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 240 | 3 | 200 | 240 | 3 | 1.5 | 6 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 20 | 240 | -
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU8.5 | 5 | 6.0 - 8.5 | 240 | 3
ABB3240A04.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 240 | 3 | 200 | 240 | 3 | 1.5 | 6 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 20 | 240 | -
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU8.5-20 | 5 | 6.0 - 8.5 | 240 | 3
ABB3240A05.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 240 | 3 | 200 | 240 | 3 | 2 | 6.8 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 25 | 240 | -
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU8.5 | 5 | 6.0 - 8.5 | 240 | 3
ABB3240A05.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 240 | 3 | 200 | 240 | 3 | 2 | 6.8 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 25 | 240 | -
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU8.5-20 | 5 | 6.0 - 8.5 | 240 | 3
ABB3240A06.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 240 | 3 | 200 | 240 | 3 | 3 | 9.6 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 240 | -
|  | MC | ABB France | A12 | 5 | 11 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU11 | 5 | 7.5 - 11 | 240 | 3
ABB3240A06.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 240 | 3 | 200 | 240 | 3 | 3 | 9.6 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 240 | -
|  | MC | ABB France | A12 | 5 | 11 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU11-20 | 5 | 7.5 - 11 | 240 | 3
ABB3240A07.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 240 | 3 | 200 | 240 | 3 | 5 | 15.2 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 240 | -
|  | MC | ABB France | A16 | 5 | 17 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU19 | 5 | 13 - 19 | 240 | 3
ABB3240A07.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 240 | 3 | 200 | 240 | 3 | 5 | 15.2 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 240 | -
|  | MC | ABB France | A16 | 5 | 17 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU19-20 | 5 | 13 - 19 | 240 | 3
ABB3240A08.01 | A | FDS | ABB Oy | OS60AJ12 | 200 | 60 | 240 | 3 | 200 | 240 | 3 | 7.5 | 22 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 60 | 240 | -
|  | MC | ABB France | A26 | 5 | 28 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU25 | 5 | 18 - 25 | 240 | 3
ABB3240A08.02 | A | FDS | ABB Oy | OS60AJ12 | 200 | 60 | 240 | 3 | 200 | 240 | 3 | 7.5 | 22 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 60 | 240 | -
|  | MC | ABB France | A26 | 5 | 28 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU25-20 | 5 | 18 - 25 | 240 | 3
ABB3240A09.01 | A | FDS | ABB Oy | OS60AJ12 | 200 | 60 | 240 | 3 | 200 | 240 | 3 | 10 | 28 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 60 | 240 | -
|  | MC | ABB France | A26 | 5 | 28 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU32 | 5 | 24 - 32 | 240 | 3
ABB3240A09.02 | A | FDS | ABB Oy | OS60AJ12 | 200 | 60 | 240 | 3 | 200 | 240 | 3 | 10 | 28 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 60 | 240 | -
|  | MC | ABB France | A26 | 5 | 28 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU32-20 | 5 | 24 -32 | 240 | 3
ABB3240A10.01 | A | FDS | ABB Oy | OS60AJ12 | 200 | 60 | 240 | 3 | 200 | 240 | 3 | 10 | 28 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 60 | 240 | -
|  | MC | ABB France | A30 | 5 | 34 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU32 | 5 | 24 - 32 | 240 | 3
ABB3240A10.02 | A | FDS | ABB Oy | OS60AJ12 | 200 | 60 | 240 | 3 | 200 | 240 | 3 | 10 | 28 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 60 | 240 | -
|  | MC | ABB France | A30 | 5 | 34 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU32-20 | 5 | 24 -32 | 240 | 3
ABB3240A11.01 | A | FDS | ABB Oy | OS100J03 | 200 | 100 | 240 | 3 | 200 | 240 | 3 | 15 | 42 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 100 | 240 | -
|  | MC | ABB France | A40 | 5 | 42 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA42DU42 | 5 | 29 - 42 | 240 | 3
ABB3240A11.02 | A | FDS | ABB Oy | OS100J03 | 200 | 100 | 240 | 3 | 200 | 240 | 3 | 15 | 42 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 100 | 240 | -
|  | MC | ABB France | A40 | 5 | 42 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA42DU42-20 | 5 | 29 - 42 | 240 | 3
ABB3240A12.01 | A | FDS | ABB Oy | OS100J03 | 200 | 100 | 240 | 3 | 100 | 240 | 3 | 20 | 54 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 100 | 240 | -
|  | MC | ABB France | A50 | 10 | 54 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA75DU63 | 5 | 45 - 63 | 240 | 3
ABB3240A12.02 | A | FDS | ABB Oy | OS100J03 | 200 | 100 | 240 | 3 | 100 | 240 | 3 | 20 | 54 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 100 | 240 | -
|  | MC | ABB France | A50 | 10 | 54 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA75DU63-20 | 5 | 45 - 63 | 240 | 3
ABB3240A13.01 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 240 | 3 | 100 | 240 | 3 | 25 | 68 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 240 | -
|  | MC | ABB France | A63 | 10 | 65 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA75DU80 | 5 | 60 - 80 | 240 | 3
ABB3240A13.02 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 240 | 3 | 100 | 240 | 3 | 25 | 68 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 240 | -
|  | MC | ABB France | A63 | 10 | 65 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA75DU80-20 | 5 | 60 - 80 | 240 | 3
ABB3240A14.01 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 240 | 3 | 100 | 240 | 3 | 30 | 80 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 240 | -
|  | MC | ABB France | A75 | 10 | 80 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA75DU80 | 5 | 60 - 80 | 240 | 3
ABB3240A14.02 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 240 | 3 | 100 | 240 | 3 | 30 | 80 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 240 | -
|  | MC | ABB France | A75 | 10 | 80 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA75DU80-20 | 5 | 60 - 80 | 240 | 3
ABB3240A15.01 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 240 | 3 | 100 | 240 | 3 | 40 | 104 | 4800 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 240 | -
|  | MC | ABB AB, CEWE-Control | A110 | 10 | 110 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA110DU110 | 5 | 80 - 110 | 240 | 3
ABB3240A16.01 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 240 | 3 | 100 | 240 | 3 | 50 | 130 | 4800 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 240 | -
|  | MC | ABB AB, CEWE-Control | A145 | 10 | 130 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA200DU135 | 5 | 100 - 135 | 240 | 3
ABB3240A17.01 | A | FDS | ABB Oy | OS400J03 | 200 | 400 | 240 | 3 | 200 | 240 | 3 | 60 | 154 | 4800 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 300 | 240 | -
|  | MC | ABB AB, CEWE-Control | A185 | 10 | 156 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA200DU175 | 5 | 130 - 175 | 240 | 3
ABB3240A18.01 | A | FDS | ABB Oy | OS400J03 | 200 | 400 | 240 | 3 | 200 | 240 | 3 | 75 | 192 | 9000 | 1,6 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 350 | 240 | -
|  | MC | ABB AB, CEWE-Control | A210 | 18 | 192 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA450DU235 | 5 | 165 - 235 | 240 | 3
ABB3240A19.01 | A | FDS | ABB Oy | OS400J03 | 200 | 400 | 240 | 3 | 200 | 240 | 3 | 100 | 248 | 9000 | 1,6 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 400 | 240 | -
|  | MC | ABB AB, CEWE-Control | A260 | 18 | 248 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA450DU310 | 5 | 220 - 310 | 240 | 3
ABB3240A20.01 | A | FDS | ABB Oy | OS600J03 | 200 | 600 | 240 | 3 | 200 | 240 | 3 | 100 | 248 | 9000 | 1,6 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 600 | 240 | -
|  | MC | ABB AB, CEWE-Control | A300 | 18 | 302 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA450DU310 | 5 | 220 - 310 | 240 | 3
Conditions of Acceptability:
|  | 1 | All of the specified individual components of the combination motor controller have been installed in an enclosure having
a specified internal volume in cubic inches. Additional testing of the combination motor controller is not required when
installed in an enclosure having the same or larger volume.
|  | 2 | When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from
the overcurrent protective devices and other components shall not be installed in this area.
|  | 3 | When specified, the overload relay heater table number shall be provided with the equipment.
|  | 4 | Unless otherwise specified, all connections between components are made with insulated wire having at least an ampacity of
100 percent of the rated motor current and connected to the terminals supplied with the individual components.
|  | 5 | The need for cautionary markings applicable to high fault short circuit current ratings, Type D a combination motor
controllers shall be considered in the end-product application.
|  | 6 | The TA450 overload relay requires the use of a mounting kit if mounted to the contactor. See the manufactures specifications.

## ABB - 240V -TYPE C
Issued: 2009-09-22
Last Revised: 2009-09-22
ID Number | Combination Type | Component Type | Component Manufactuer | Component Catalog Desgination | Component Ratings |  |  |  | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in.) | Conditions of Acceptability | Combination UL File Reference
[5 empty] | kA | Max Amps | Volts | Poles
ABB3240C01.01 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 240 | 3 | 35 | 240 | 3 | 0.5 | 2.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU3.1 | 5 | 2.2 - 3.1 | 240 | 3
ABB3240C01.02 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 240 | 3 | 35 | 240 | 3 | 0.5 | 2.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU3.1-20 | 5 | 2.2 - 3.1 | 240 | 3
ABB3240C02.01 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 240 | 3 | 35 | 240 | 3 | 0.5 | 2.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU3.1 | 5 | 2.2 - 3.1 | 240 | 3
ABB3240C02.02 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 240 | 3 | 35 | 240 | 3 | 0.5 | 2.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU3.1-20 | 5 | 2.2 - 3.1 | 240 | 3
ABB3240C03.01 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 240 | 3 | 35 | 240 | 3 | 0.75 | 3.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU4.0 | 5 | 2.8 - 4.0 | 240 | 3
ABB3240C03.02 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 240 | 3 | 35 | 240 | 3 | 0.75 | 3.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU4.0-20 | 5 | 2.8 - 4.0 | 240 | 3
ABB3240C04.01 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 240 | 3 | 35 | 240 | 3 | 0.75 | 3.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU4.0 | 5 | 2.8 - 4.0 | 240 | 3
ABB3240C04.02 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 240 | 3 | 35 | 240 | 3 | 0.75 | 3.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU4.0-20 | 5 | 2.8 - 4.0 | 240 | 3
ABB3240C05.01 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 240 | 3 | 35 | 240 | 3 | 1 | 4.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | -
|  | OLR | ABB Stotz-Kontakt | TA25DU5.0 | 5 | 3.5 - 5.0 | 240 | 3
ABB3240C05.02 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 240 | 3 | 35 | 240 | 3 | 1 | 4.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | -
|  | OLR | ABB Stotz-Kontakt | TA25DU5.0-20 | 5 | 3.5 - 5.0 | 240 | 3
ABB3240C06.01 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 240 | 3 | 35 | 240 | 3 | 1 | 4.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU5.0 | 5 | 3.5 - 5.0 | 240 | 3
ABB3240C06.02 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 240 | 3 | 35 | 240 | 3 | 1 | 4.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU5.0-20 | 5 | 3.5 - 5.0 | 240 | 3
ABB3240C07.01 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 240 | 3 | 35 | 240 | 3 | 1.5 | 6 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5 | 5 | 6.0 - 8.5 | 240 | 3
ABB3240C07.02 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 240 | 3 | 35 | 240 | 3 | 1.5 | 6 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5-20 | 5 | 6.0 - 8.5 | 240 | 3
ABB3240C08.01 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 240 | 3 | 35 | 240 | 3 | 1.5 | 6 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5 | 5 | 6.0 - 8.5 | 240 | 3
ABB3240C08.02 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 240 | 3 | 35 | 240 | 3 | 1.5 | 6 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5-20 | 5 | 6.0 - 8.5 | 240 | 3
ABB3240C09.01 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 240 | 3 | 35 | 240 | 3 | 2 | 6.8 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5 | 5 | 6.0 - 8.5 | 240 | 3
ABB3240C09.02 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 240 | 3 | 35 | 240 | 3 | 2 | 6.8 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5-20 | 5 | 6.0 - 8.5 | 240 | 3
ABB3240C10.01 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 240 | 3 | 35 | 240 | 3 | 2 | 6.8 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5 | 5 | 6.0 - 8.5 | 240 | 3
ABB3240C10.02 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 240 | 3 | 35 | 240 | 3 | 2 | 6.8 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5-20 | 5 | 6.0 - 8.5 | 240 | 3
ABB3240C11.01 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 240 | 3 | 35 | 240 | 3 | 3 | 9.6 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11 | 5 | 7.5 - 11 | 240 | 3
ABB3240C11.02 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 240 | 3 | 35 | 240 | 3 | 3 | 9.6 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11-20 | 5 | 7.5 - 11 | 240 | 3
ABB3240C12.01 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 240 | 3 | 35 | 240 | 3 | 3 | 9.6 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11 | 5 | 7.5 - 11 | 240 | 3
ABB3240C12.02 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 240 | 3 | 35 | 240 | 3 | 3 | 9.6 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11-20 | 5 | 7.5 - 11 | 240 | 3
ABB3240C13.01 | C | CB | ABB Sace | S3L025TW | 150 | 25 | 240 | 3 | 35 | 240 | 3 | 5 | 15.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19 | 5 | 13 - 19 | 240 | 3
ABB3240C13.02 | C | CB | ABB Sace | S3L025TW | 150 | 25 | 240 | 3 | 35 | 240 | 3 | 5 | 15.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19-20 | 5 | 13 - 19 | 240 | 3
ABB3240C14.01 | C | CB | ABB Sace | T2S025TW | 65 | 25 | 240 | 3 | 35 | 240 | 3 | 5 | 15.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19 | 5 | 13 - 19 | 240 | 3
ABB3240C14.02 | C | CB | ABB Sace | T2S025TW | 65 | 25 | 240 | 3 | 35 | 240 | 3 | 5 | 15.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19-20 | 5 | 13 - 19 | 240 | 3
ABB3240C15.01 | C | CB | ABB Sace | S3L040TW | 150 | 40 | 240 | 3 | 35 | 240 | 3 | 7.5 | 22 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU25 | 5 | 18 - 25 | 240 | 3
ABB3240C15.02 | C | CB | ABB Sace | S3L040TW | 150 | 40 | 240 | 3 | 35 | 240 | 3 | 7.5 | 22 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU25 | 5 | 18 - 25 | 240 | 3
ABB3240C16.01 | C | CB | ABB Sace | T2S040TW | 65 | 40 | 240 | 3 | 35 | 240 | 3 | 7.5 | 22 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU25 | 5 | 18 - 25 | 240 | 3
ABB3240C16.02 | C | CB | ABB Sace | T2S040TW | 65 | 40 | 240 | 3 | 35 | 240 | 3 | 7.5 | 22 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU25-20 | 5 | 18 - 25 | 240 | 3
ABB3240C17.01 | C | CB | ABB Sace | S3L050TW | 150 | 50 | 240 | 3 | 35 | 240 | 3 | 10 | 28 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32 | 5 | 24 - 32 | 240 | 3
ABB3240C17.02 | C | CB | ABB Sace | S3L050TW | 150 | 50 | 240 | 3 | 35 | 240 | 3 | 10 | 28 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32-20 | 5 | 24 - 32 | 240 | 3
ABB3240C18.01 | C | CB | ABB Sace | T2S050TW | 65 | 50 | 240 | 3 | 35 | 240 | 3 | 10 | 28 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32 | 5 | 24 - 32 | 240 | 3
ABB3240C18.02 | C | CB | ABB Sace | T2S050TW | 65 | 50 | 240 | 3 | 35 | 240 | 3 | 10 | 28 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32-20 | 5 | 24 - 32 | 240 | 3
ABB3240C19.01 | C | CB | ABB Sace | S3L040TW | 150 | 40 | 240 | 3 | 65 | 240 | 3 | 10 | 28 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU32 | 5 | 22 -32 | 240 | 3
ABB3240C19.02 | C | CB | ABB Sace | S3L040TW | 150 | 40 | 240 | 3 | 65 | 240 | 3 | 10 | 28 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU32-20 | 5 | 22 - 32 | 240 | 3
ABB3240C20.01 | C | CB | ABB Sace | T2S040TW | 65 | 40 | 240 | 3 | 65 | 240 | 3 | 10 | 28 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU32 | 5 | 22 - 32 | 240 | 3
ABB3240C20.02 | C | CB | ABB Sace | T2S040TW | 65 | 40 | 240 | 3 | 65 | 240 | 3 | 10 | 28 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU32-20 | 5 | 22 - 32 | 240 | 3
ABB3240C21.01 | C | CB | ABB Sace | S3L050TW | 150 | 50 | 240 | 3 | 65 | 240 | 3 | 10 | 28 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU32 | 5 | 22 - 32 | 240 | 3
ABB3240C21.02 | C | CB | ABB Sace | S3L050TW | 150 | 50 | 240 | 3 | 65 | 240 | 3 | 10 | 28 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU32-20 | 5 | 22 - 32 | 240 | 3
ABB3240C22.01 | C | CB | ABB Sace | T2S050TW | 65 | 50 | 240 | 3 | 65 | 240 | 3 | 10 | 28 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU32 | 5 | 22 - 32 | 240 | 3
ABB3240C22.02 | C | CB | ABB Sace | T2S050TW | 65 | 50 | 240 | 3 | 65 | 240 | 3 | 10 | 28 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU32-20 | 5 | 22 - 32 | 240 | 3
ABB3240C23.01 | C | CB | ABB Sace | S3L070TW | 150 | 70 | 240 | 3 | 65 | 240 | 3 | 15 | 42 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 240 | 3
ABB3240C23.02 | C | CB | ABB Sace | S3L070TW | 150 | 70 | 240 | 3 | 65 | 240 | 3 | 15 | 42 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 240 | 3
ABB3240C24.01 | C | CB | ABB Sace | T4H080TW | 150 | 80 | 240 | 3 | 65 | 240 | 3 | 15 | 42 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 240 | 3
ABB3240C24.02 | C | CB | ABB Sace | T4H080TW | 150 | 80 | 240 | 3 | 65 | 240 | 3 | 15 | 42 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 240 | 3
ABB3240C25.01 | C | CB | ABB Sace | TS3L080TW | 150 | 80 | 240 | 3 | 65 | 240 | 3 | 15 | 42 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 240 | 3
ABB3240C25.02 | C | CB | ABB Sace | TS3L080TW | 150 | 80 | 240 | 3 | 65 | 240 | 3 | 15 | 42 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 240 | 3
ABB3240C26.01 | C | CB | ABB Sace | S3L080TW | 150 | 80 | 240 | 3 | 85 | 240 | 3 | 20 | 54 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63 | 5 | 45 - 63 | 240 | 3
ABB3240C26.02 | C | CB | ABB Sace | S3L080TW | 150 | 80 | 240 | 3 | 85 | 240 | 3 | 20 | 54 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63-20 | 5 | 45 - 63 | 240 | 3
ABB3240C27.01 | C | CB | ABB Sace | T4L080TW | 200 | 100 | 240 | 3 | 85 | 240 | 3 | 20 | 54 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63 | 5 | 45 - 63 | 240 | 3
ABB3240C27.02 | C | CB | ABB Sace | T4L080TW | 200 | 100 | 240 | 3 | 85 | 240 | 3 | 20 | 54 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63-20 | 5 | 45 - 63 | 240 | 3
ABB3240C28.01 | C | CB | ABB Sace | TS3L080TW | 150 | 100 | 240 | 3 | 85 | 240 | 3 | 20 | 54 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63 | 5 | 45 - 63 | 240 | 3
ABB3240C28.02 | C | CB | ABB Sace | TS3L080TW | 150 | 100 | 240 | 3 | 85 | 240 | 3 | 20 | 54 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63-20 | 5 | 45 - 63 | 240 | 3
ABB3240C29.01 | C | CB | ABB Sace | S3L125TW | 150 | 125 | 240 | 3 | 85 | 240 | 3 | 25 | 68 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 240 | 3
ABB3240C29.02 | C | CB | ABB Sace | S3L125TW | 150 | 125 | 240 | 3 | 85 | 240 | 3 | 25 | 68 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 240 | 3
ABB3240C30.01 | C | CB | ABB Sace | T4L125TW | 200 | 125 | 240 | 3 | 85 | 240 | 3 | 25 | 68 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 240 | 3
ABB3240C30.02 | C | CB | ABB Sace | T4L125TW | 200 | 125 | 240 | 3 | 85 | 240 | 3 | 25 | 68 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 65 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 240 | 3
ABB3240C31.01 | C | CB | ABB Sace | S3L150TW | 150 | 150 | 240 | 3 | 85 | 240 | 3 | 30 | 80 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 240 | 3
ABB3240C31.02 | C | CB | ABB Sace | S3L150TW | 150 | 150 | 240 | 3 | 85 | 240 | 3 | 30 | 80 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 240 | 3
ABB3240C32.01 | C | CB | ABB Sace | T4L150TW | 200 | 150 | 240 | 3 | 85 | 240 | 3 | 30 | 80 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 240 | 3
ABB3240C32.02 | C | CB | ABB Sace | T4L150TW | 200 | 150 | 240 | 3 | 85 | 240 | 3 | 30 | 80 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 240 | 3
ABB3240C33.01 | C | CB | ABB Sace | S3L200TW | 150 | 200 | 240 | 3 | 85 | 240 | 3 | 40 | 104 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A110 | 10 | 110 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA110DU110 | 5 | 80 - 110 | 240 | 3
ABB3240C34.01 | C | CB | ABB Sace | T4L200TW | 200 | 200 | 240 | 3 | 85 | 240 | 3 | 40 | 104 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A110 | 10 | 110 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA110DU110 | 5 | 80 - 110 | 240 | 3
ABB3240C35.01 | C | CB | ABB Sace | S4N250TW | 65 | 250 | 240 | 3 | 65 | 240 | 3 | 50 | 130 | 4800 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A145 | 10 | 130 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA200DU150 | 5 | 110 - 150 | 240 | 3
ABB3240C36.01 | C | CB | ABB Sace | T4L200TW | 200 | 200 | 240 | 3 | 65 | 240 | 3 | 50 | 130 | 4800 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A145 | 10 | 130 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA200DU150 | 5 | 110 - 150 | 240 | 3
ABB3240C37.01 | C | CB | ABB Sace | S4N250TW | 65 | 250 | 240 | 3 | 85 | 240 | 3 | 60 | 154 | 4800 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A185 | 10 | 156 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA200DU175 | 5 | 130 - 175 | 240 | 3
ABB3240C38.01 | C | CB | ABB Sace | T4L250TW | 200 | 250 | 240 | 3 | 85 | 240 | 3 | 60 | 154 | 4800 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A185 | 10 | 156 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA200DU175 | 5 | 130 - 175 | 240 | 3
ABB3240C39.01 | C | CB | ABB Sace | S5N300TW | 65 | 300 | 240 | 3 | 85 | 240 | 3 | 75 | 192 | 9000 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A210 | 18 | 192 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU235 | 5 | 165 - 235 | 240 | 3
ABB3240C40.01 | C | CB | ABB Sace | T5L300TW | 200 | 300 | 240 | 3 | 85 | 240 | 3 | 75 | 192 | 9000 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A210 | 18 | 192 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU235 | 5 | 165 - 235 | 240 | 3
ABB3240C41.01 | C | CB | ABB Sace | S5N400TW | 65 | 400 | 240 | 3 | 85 | 240 | 3 | 100 | 248 | 9000 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A260 | 18 | 248 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU310 | 5 | 220 - 310 | 240 | 3
ABB3240C42.01 | C | CB | ABB Sace | T5L400TW | 200 | 400 | 240 | 3 | 85 | 240 | 3 | 100 | 248 | 9000 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A260 | 18 | 248 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU310 | 5 | 220 - 310 | 240 | 3
ABB3240C43.01 | C | CB | ABB Sace | S5N400TW | 65 | 400 | 240 | 3 | 85 | 240 | 3 | 100 | 248 | 9000 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A300 | 18 | 302 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU310 | 5 | 220 - 310 | 240 | 3
ABB3240C44.01 | C | CB | ABB Sace | T5L400TW | 200 | 400 | 240 | 3 | 85 | 240 | 3 | 100 | 248 | 9000 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A300 | 18 | 302 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU310 | 5 | 220 - 310 | 240 | 3
Conditions of Acceptability:
|  | 1 | All of the specified individual components of the combination motor controller have been installed in an enclosure having | [11 empty] | Component manufactured by-
a specified internal volume in cubic inches. Additional testing of the combination motor controller is not required when
|  |  | installed in an enclosure having the same or larger volume. | [11 empty] | Contactor A9 - A75 ( ABB France )
Contactor A110 - A300 ( ABB CEWE Control AB )
|  | 2 | When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from | [11 empty] | Overload relay ( ABB Stotz- Kontakt )
|  |  | the overcurrent protective devices and other components shall not be installed in this area. | [11 empty] | Breaker ( ABB SACE )
|  | 3 | When specified, the overload relay heater table number shall be provided with the equipment.
|  | 4 | Unless otherwise specified, all connections between components are made with insulated wire having at least an ampacity of
100 percent of the rated motor current and connected to the terminals supplied with the individual components.
|  | 5 | The need for cautionary markings applicable to high fault short circuit current ratings, Type D a combination motor
controllers shall be considered in the end-product application.
|  | 6 | The TA450 overload relay requires the use of a mounting kit if mounted to the contactor. See the manufactures specifications.

## ABB - 240V - TYPE D
Issued: 2009-09-22
Last Revised: 2009-09-22
ID Number | Combination Type | Component Type | Component Manufactuer | Component Catalog Desgination | Component Ratings |  |  |  | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in.) | Conditions of Acceptability | Combination UL File Reference
[5 empty] | kA | Max Amps | Volts | Poles
ABB3240D01.01 | D | ICB | ABB Sace | S3L005MW | - | 5 | 240 | 3 | 35 | 240 | 3 | 0.5 | 2.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU3.1 | 5 | 2.2 - 3.1 | 240 | 3
ABB3240D01.02 | D | ICB | ABB Sace | S3L005MW | - | 5 | 240 | 3 | 35 | 240 | 3 | 0.5 | 2.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU3.1-20 | 5 | 2.2 - 3.1 | 240 | 3
ABB3240D02.01 | D | ICB | ABB Sace | TS3L005MW | - | 5 | 240 | 3 | 35 | 240 | 3 | 0.5 | 2.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU3.1 | 5 | 2.2 - 3.1 | 240 | 3
ABB3240D02.02 | D | ICB | ABB Sace | TS3L005MW | - | 5 | 240 | 3 | 35 | 240 | 3 | 0.5 | 2.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU3.1-20 | 5 | 2.2 -3.1 | 240 | 3
ABB3240D03.01 | D | ICB | ABB Sace | S3L005MW | - | 5 | 240 | 3 | 35 | 240 | 3 | 0.75 | 3.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU4.0 | 5 | 2.8 - 4.0 | 240 | 3
ABB3240D03.02 | D | ICB | ABB Sace | S3L005MW | - | 5 | 240 | 3 | 35 | 240 | 3 | 0.75 | 3.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU4.0-20 | 5 | 2.8 - 4.0 | 240 | 3
ABB3240D04.01 | D | ICB | ABB Sace | TS3L005MW | - | 5 | 240 | 3 | 35 | 240 | 3 | 0.75 | 3.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU4.0 | 5 | 2.8 - 4.0 | 240 | 3
ABB3240D04.02 | D | ICB | ABB Sace | TS3L005MW | - | 5 | 240 | 3 | 35 | 240 | 3 | 0.75 | 3.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU4.0-20 | 5 | 2.8 - 4.0 | 240 | 3
ABB3240D05.01 | D | ICB | ABB Sace | S3L010MW | - | 10 | 240 | 3 | 35 | 240 | 3 | 1 | 4.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU5.0 | 5 | 3.5 - 5.0 | 240 | 3
ABB3240D05.02 | D | ICB | ABB Sace | S3L010MW | - | 10 | 240 | 3 | 35 | 240 | 3 | 1 | 4.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU5.0-20 | 5 | 3.5 - 5.0 | 240 | 3
ABB3240D06.01 | D | ICB | ABB Sace | TS3L010MW | - | 10 | 240 | 3 | 35 | 240 | 3 | 1 | 4.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU5.0 | 5 | 3.5 - 5.0 | 240 | 3
ABB3240D06.02 | D | ICB | ABB Sace | TS3L010MW | - | 10 | 240 | 3 | 35 | 240 | 3 | 1 | 4.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU5.0-20 | 5 | 3.5 - 5.0 | 240 | 3
ABB3240D07.01 | D | ICB | ABB Sace | S3L010MW | - | 10 | 240 | 3 | 35 | 240 | 3 | 1.5 | 6 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5 | 5 | 6.0 - 8.5 | 240 | 3
ABB3240D07.02 | D | ICB | ABB Sace | S3L010MW | - | 10 | 240 | 3 | 35 | 240 | 3 | 1.5 | 6 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5-20 | 5 | 6.0 - 8.5 | 240 | 3
ABB3240D08.01 | D | ICB | ABB Sace | TS3L010MW | - | 10 | 240 | 3 | 35 | 240 | 3 | 1.5 | 6 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5 | 5 | 6.0 - 8.5 | 240 | 3
ABB3240D08.02 | D | ICB | ABB Sace | TS3L010MW | - | 10 | 240 | 3 | 35 | 240 | 3 | 1.5 | 6 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5-20 | 5 | 6.0 - 8.5 | 240 | 3
ABB3240D09.01 | D | ICB | ABB Sace | S3L010MW | - | 10 | 240 | 3 | 35 | 240 | 3 | 2 | 6.8 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5 | 5 | 6.0 - 8.5 | 240 | 3
ABB3240D09.02 | D | ICB | ABB Sace | S3L010MW | - | 10 | 240 | 3 | 35 | 240 | 3 | 2 | 6.8 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5-20 | 5 | 6.0 - 8.5 | 240 | 3
ABB3240D10.01 | D | ICB | ABB Sace | TS3L010MW | - | 10 | 240 | 3 | 35 | 240 | 3 | 2 | 6.8 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5 | 5 | 6.0 - 8.5 | 240 | 3
ABB3240D10.02 | D | ICB | ABB Sace | TS3L010MW | - | 10 | 240 | 3 | 35 | 240 | 3 | 2 | 6.8 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5-20 | 5 | 6.0 - 8.5 | 240 | 3
ABB3240D11.01 | D | ICB | ABB Sace | S3L010MW | - | 10 | 240 | 3 | 35 | 240 | 3 | 3 | 9.6 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11 | 5 | 7.5 - 11 | 240 | 3
ABB3240D11.02 | D | ICB | ABB Sace | S3L010MW | - | 10 | 240 | 3 | 35 | 240 | 3 | 3 | 9.6 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11-20 | 5 | 7.5 - 11 | 240 | 3
ABB3240D12.01 | D | ICB | ABB Sace | TS3L025MW | - | 25 | 240 | 3 | 35 | 240 | 3 | 3 | 9.6 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11 | 5 | 7.5 - 11 | 240 | 3
ABB3240D12.02 | D | ICB | ABB Sace | TS3L025MW | - | 25 | 240 | 3 | 35 | 240 | 3 | 3 | 9.6 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11-20 | 5 | 7.5 - 11 | 240 | 3
ABB3240D13.01 | D | ICB | ABB Sace | S3L025MW | - | 25 | 240 | 3 | 35 | 240 | 3 | 5 | 15.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19 | 5 | 13 - 19 | 240 | 3
ABB3240D13.02 | D | ICB | ABB Sace | S3L025MW | - | 25 | 240 | 3 | 35 | 240 | 3 | 5 | 15.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19-20 | 5 | 13 - 19 | 240 | 3
ABB3240D14.01 | D | ICB | ABB Sace | T2S025MW | - | 25 | 240 | 3 | 35 | 240 | 3 | 5 | 15.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19 | 5 | 13 - 19 | 240 | 3
ABB3240D14.02 | D | ICB | ABB Sace | T2S025MW | - | 25 | 240 | 3 | 35 | 240 | 3 | 5 | 15.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19-20 | 5 | 13 - 19 | 240 | 3
ABB3240D15.01 | D | ICB | ABB Sace | S3L050MW | - | 50 | 240 | 3 | 35 | 240 | 3 | 7.5 | 22 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU25 | 5 | 18 - 25 | 240 | 3
ABB3240D15.02 | D | ICB | ABB Sace | S3L050MW | - | 50 | 240 | 3 | 35 | 240 | 3 | 7.5 | 22 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU25-20 | 5 | 18 - 25 | 240 | 3
ABB3240D16.01 | D | ICB | ABB Sace | T2S050MW | - | 50 | 240 | 3 | 35 | 240 | 3 | 7.5 | 22 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU25 | 5 | 18 - 25 | 240 | 3
ABB3240D16.02 | D | ICB | ABB Sace | T2S050MW | - | 50 | 240 | 3 | 35 | 240 | 3 | 7.5 | 22 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU25-20 | 5 | 18 - 25 | 240 | 3
ABB3240D17.01 | D | ICB | ABB Sace | S3L050MW | - | 50 | 240 | 3 | 35 | 240 | 3 | 10 | 28 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32 | 5 | 24 - 32 | 240 | 3
ABB3240D17.02 | D | ICB | ABB Sace | S3L050MW | - | 50 | 240 | 3 | 35 | 240 | 3 | 10 | 28 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32-20 | 5 | 24 - 32 | 240 | 3
ABB3240D18.01 | D | ICB | ABB Sace | T2S050MW | - | 50 | 240 | 3 | 35 | 240 | 3 | 10 | 28 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32 | 5 | 24 - 32 | 240 | 3
ABB3240D18.02 | D | ICB | ABB Sace | T2S050MW | - | 50 | 240 | 3 | 35 | 240 | 3 | 10 | 28 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32-20 | 5 | 24 - 32 | 240 | 3
ABB3240D19.01 | D | ICB | ABB Sace | S3L050MW | - | 50 | 240 | 3 | 65 | 240 | 3 | 10 | 28 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU32 | 5 | 22 - 32 | 240 | 3
ABB3240D19.02 | D | ICB | ABB Sace | S3L050MW | - | 50 | 240 | 3 | 65 | 240 | 3 | 10 | 28 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU32-20 | 5 | 22 - 32 | 240 | 3
ABB3240D20.01 | D | ICB | ABB Sace | T2S050MW | - | 50 | 240 | 3 | 65 | 240 | 3 | 10 | 28 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU32 | 5 | 22 - 32 | 240 | 3
ABB3240D20.02 | D | ICB | ABB Sace | T2S050MW | - | 50 | 240 | 3 | 65 | 240 | 3 | 10 | 28 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU32-20 | 5 | 22 - 32 | 240 | 3
ABB3240D21.01 | D | ICB | ABB Sace | S3L100MW | - | 100 | 240 | 3 | 65 | 240 | 3 | 15 | 42 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 240 | 3
ABB3240D21.02 | D | ICB | ABB Sace | S3L100MW | - | 100 | 240 | 3 | 65 | 240 | 3 | 15 | 42 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 240 | 3
ABB3240D22.01 | D | ICB | ABB Sace | T4H100MW | - | 100 | 240 | 3 | 65 | 240 | 3 | 15 | 42 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 240 | 3
ABB3240D22.02 | D | ICB | ABB Sace | T4H100MW | - | 100 | 240 | 3 | 65 | 240 | 3 | 15 | 42 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 240 | 3
ABB3240D23.01 | D | ICB | ABB Sace | TS3L100MW | - | 100 | 240 | 3 | 65 | 240 | 3 | 15 | 42 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 240 | 3
ABB3240D23.02 | D | ICB | ABB Sace | TS3L100MW | - | 100 | 240 | 3 | 65 | 240 | 3 | 15 | 42 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 240 | 3
ABB3240D24.01 | D | ICB | ABB Sace | S3L100MW | - | 100 | 240 | 3 | 85 | 240 | 3 | 20 | 54 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63 | 5 | 45 - 63 | 240 | 3
ABB3240D24.02 | D | ICB | ABB Sace | S3L100MW | - | 100 | 240 | 3 | 85 | 240 | 3 | 20 | 54 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63-20 | 5 | 45 - 63 | 240 | 3
ABB3240D25.01 | D | ICB | ABB Sace | T4L100MW | - | 100 | 240 | 3 | 85 | 240 | 3 | 20 | 54 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63 | 5 | 45 - 63 | 240 | 3
ABB3240D25.02 | D | ICB | ABB Sace | T4L100MW | - | 100 | 240 | 3 | 85 | 240 | 3 | 20 | 54 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63-20 | 5 | 45 - 63 | 240 | 3
ABB3240D26.01 | D | ICB | ABB Sace | TS3L100MW | - | 100 | 240 | 3 | 85 | 240 | 3 | 20 | 54 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63 | 5 | 45 - 63 | 240 | 3
ABB3240D26.02 | D | ICB | ABB Sace | TS3L100MW | - | 100 | 240 | 3 | 85 | 240 | 3 | 20 | 54 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63-20 | 5 | 45 - 63 | 240 | 3
ABB3240D27.01 | D | ICB | ABB Sace | S3L100MW | - | 100 | 240 | 3 | 85 | 240 | 3 | 25 | 68 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 240 | 3
ABB3240D27.02 | D | ICB | ABB Sace | S3L100MW | - | 100 | 240 | 3 | 85 | 240 | 3 | 25 | 68 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 240 | 3
ABB3240D28.01 | D | ICB | ABB Sace | T4L100MW | - | 100 | 240 | 3 | 85 | 240 | 3 | 25 | 68 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 240 | 3
ABB3240D28.02 | D | ICB | ABB Sace | T4L100MW | - | 100 | 240 | 3 | 85 | 240 | 3 | 25 | 68 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 240 | 3
ABB3240D29.01 | D | ICB | ABB Sace | S3L150MW | - | 150 | 240 | 3 | 85 | 240 | 3 | 30 | 80 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 240 | 3
ABB3240D29.02 | D | ICB | ABB Sace | S3L150MW | - | 150 | 240 | 3 | 85 | 240 | 3 | 30 | 80 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 240 | 3
ABB3240D30.01 | D | ICB | ABB Sace | T4L150MW | - | 150 | 240 | 3 | 85 | 240 | 3 | 30 | 80 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 240 | 3
ABB3240D30.02 | D | ICB | ABB Sace | T4L150MW | - | 150 | 240 | 3 | 85 | 240 | 3 | 30 | 80 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 240 | 3
ABB3240D31.01 | D | ICB | ABB Sace | S4L250MW | - | 250 | 240 | 3 | 85 | 240 | 3 | 40 | 104 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A110 | 10 | 110 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA110DU110 | 5 | 80 - 110 | 240 | 3
ABB3240D32.01 | D | ICB | ABB Sace | T4L150MW | - | 150 | 240 | 3 | 85 | 240 | 3 | 40 | 104 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A110 | 10 | 110 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA110DU110 | 5 | 80 - 110 | 240 | 3
ABB3240D33.01 | D | ICB | ABB Sace | S3L150MW | - | 150 | 240 | 3 | 65 | 240 | 3 | 50 | 130 | 4800 | 1,5 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A145 | 10 | 130 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA200DU150 | 5 | 110 - 150 | 240 | 3
ABB3240D34.01 | D | ICB | ABB Sace | T4L150MW | - | 150 | 240 | 3 | 65 | 240 | 3 | 50 | 130 | 4800 | 1,5 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A145 | 10 | 130 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA200DU150 | 5 | 110 - 150 | 240 | 3
ABB3240D35.01 | D | ICB | ABB Sace | S4L250MW | - | 250 | 240 | 3 | 85 | 240 | 3 | 60 | 154 | 4800 | 1,5 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A185 | 10 | 156 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA200DU175 | 5 | 130 - 175 | 240 | 3
ABB3240D36.01 | D | ICB | ABB Sace | T4L250MW | - | 250 | 240 | 3 | 85 | 240 | 3 | 60 | 154 | 4800 | 1,5 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A185 | 10 | 156 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA200DU175 | 5 | 130 - 175 | 240 | 3
ABB3240D37.01 | D | ICB | ABB Sace | S4L250MW | - | 250 | 240 | 3 | 85 | 240 | 3 | 75 | 192 | 9000 | 1,5,6 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A210 | 18 | 192 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA450DU235 | 5 | 165 - 235 | 240 | 3
ABB3240D38.01 | D | ICB | ABB Sace | T4L250MW | - | 250 | 240 | 3 | 85 | 240 | 3 | 75 | 192 | 9000 | 1,5,6 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A210 | 18 | 192 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU235 | 5 | 165 - 235 | 240 | 3
ABB3240D39.01 | D | ICB | ABB Sace | S5L400MW | - | 400 | 240 | 3 | 85 | 240 | 3 | 100 | 248 | 9000 | 1,5,6 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A260 | 18 | 248 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA450DU310 | 5 | 130 - 310 | 240 | 3
ABB3240D40.01 | D | ICB | ABB Sace | T5L400MW | - | 400 | 240 | 3 | 85 | 240 | 3 | 100 | 248 | 9000 | 1,5,6 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A260 | 18 | 248 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU310 | 5 | 130 - 310 | 240 | 3
ABB3240D41.01 | D | ICB | ABB Sace | S5L400MW | - | 400 | 240 | 3 | 85 | 240 | 3 | 100 | 248 | 9000 | 1,5,6 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A300 | 18 | 302 | 240 | 3
|  | OLR | ABB Stotz-kontakt | TA450DU310 | 5 | 130 - 310 | 240 | 3
ABB3240D42.01 | D | ICB | ABB Sace | T5L400MW | - | 400 | 240 | 3 | 85 | 240 | 3 | 100 | 248 | 9000 | 1,5,6 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A300 | 18 | 302 | 240 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU310 | 5 | 130 - 310 | 240 | 3
Conditions of Acceptability:
|  | 1 | All of the specified individual components of the combination motor controller have been installed in an enclosure having
a specified internal volume in cubic inches. Additional testing of the combination motor controller is not required when
installed in an enclosure having the same or larger volume.
|  | 2 | When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from
the overcurrent protective devices and other components shall not be installed in this area.
|  | 3 | When specified, the overload relay heater table number shall be provided with the equipment.
|  | 4 | Unless otherwise specified, all connections between components are made with insulated wire having at least an ampacity of
100 percent of the rated motor current and connected to the terminals supplied with the individual components.
|  | 5 | The need for cautionary markings applicable to high fault short circuit current ratings, Type D a combination motor
controllers shall be considered in the end-product application.
|  | 6 | The TA450 overload relay requires the use of a mounting kit if mounted to the contactor. See the manufactures specifications.

## ABB - 208V - TYPE A
Issued: 2009-09-22
Last Revised: 2009-09-22
ID Number | Combination Type | Component Type | Component Manufactuer | Component Catalog Desgination | Component Ratings |  |  |  | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in.) | Conditions of Acceptability | Combination UL File Reference
[5 empty] | kA | Max Amps | Volts | Poles
ABB3208A1.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 208 | 3 | 200 | 208 | 3 | 0.5 | 2.4 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 6 | 208 | -
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU3.1 | 5 | 2.2 - 3.1 | 208 | 3
ABB3208A1.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 208 | 3 | 200 | 208 | 3 | 0.5 | 2.4 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 6 | 208 | -
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU3.1-20 | 5 | 2.2 - 3.1 | 208 | 3
ABB3208A2.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 208 | 3 | 200 | 208 | 3 | 0.75 | 3.5 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 10 | 208 | -
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU5.0 | 5 | 3.5 - 5.0 | 208 | 3
ABB3208A2.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 208 | 3 | 200 | 208 | 3 | 0.75 | 3.5 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 10 | 208 | -
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU5.0-20 | 5 | 3.5 - 5.0 | 208 | 3
ABB3208A3.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 208 | 3 | 200 | 208 | 3 | 1 | 4.6 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 15 | 208 | -
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU6.5 | 5 | 4.5 - 6.5 | 208 | 3
ABB3208A3.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 208 | 3 | 200 | 208 | 3 | 1 | 4.6 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 15 | 208 | -
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU6.5-20 | 5 | 4.5 - 6.5 | 208 | 3
ABB3208A4.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 208 | 3 | 200 | 208 | 3 | 1.5 | 6.6 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 25 | 208 | -
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU8.5 | 5 | 6.0 - 8.5 | 208 | 3
ABB3208A4.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 208 | 3 | 200 | 208 | 3 | 1.5 | 6.6 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 25 | 208 | -
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU8.5-20 | 5 | 6.0 - 8.5 | 208 | 3
ABB3208A5.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 208 | 3 | 200 | 208 | 3 | 2 | 7.5 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 208 | -
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU11 | 5 | 7.5 - 11 | 208 | 3
ABB3208A5.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 208 | 3 | 200 | 208 | 3 | 2 | 7.5 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 208 | -
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU11-20 | 5 | 7.5 - 11 | 208 | 3
ABB3208A6.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 208 | 3 | 200 | 208 | 3 | 3 | 10.6 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 208 | -
|  | MC | ABB France | A12 | 5 | 11 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU14 | 5 | 10 - 14.0 | 208 | 3
ABB3208A6.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 208 | 3 | 200 | 208 | 3 | 3 | 10.6 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 208 | -
|  | MC | ABB France | A12 | 5 | 11 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU14-20 | 5 | 10 - 14.0 | 208 | 3
ABB3208A7.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 208 | 3 | 200 | 208 | 3 | 5 | 16.7 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 208 | -
|  | MC | ABB France | A16 | 5 | 17 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU19 | 5 | 13 - 19 | 208 | 3
ABB3208A7.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 208 | 3 | 200 | 208 | 3 | 5 | 16.7 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 208 | -
|  | MC | ABB France | A16 | 5 | 17 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU19-20 | 5 | 13 - 19 | 208 | 3
ABB3208A8.01 | A | FDS | ABB Oy | OS60AJ12 | 200 | 60 | 208 | 3 | 200 | 208 | 3 | 7.5 | 24.2 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 60 | 208 | -
|  | MC | ABB France | A26 | 5 | 28 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU32 | 5 | 24 - 32 | 208 | 3
ABB3208A8.02 | A | FDS | ABB Oy | OS60AJ12 | 200 | 60 | 208 | 3 | 200 | 208 | 3 | 7.5 | 24.2 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 60 | 208 | -
|  | MC | ABB France | A26 | 5 | 28 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU32-20 | 5 | 24 - 32 | 208 | 3
ABB3208A9.01 | A | FDS | ABB Oy | OS60AJ12 | 200 | 60 | 208 | 3 | 200 | 208 | 3 | 10 | 30.8 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 60 | 208 | -
|  | MC | ABB France | A30 | 5 | 34 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA42DU42 | 5 | 29 - 42 | 208 | 3
ABB3208A9.02 | A | FDS | ABB Oy | OS60AJ12 | 200 | 60 | 208 | 3 | 200 | 208 | 3 | 10 | 30.8 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 60 | 208 | -
|  | MC | ABB France | A30 | 5 | 34 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA42DU42-20 | 5 | 29 - 42 | 208 | 3
ABB3208A10.01 | A | FDS | ABB Oy | OS60AJ12 | 200 | 60 | 208 | 3 | 200 | 208 | 3 | 10 | 30.8 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 60 | 208 | -
|  | MC | ABB France | A40 | 5 | 42 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA42DU42 | 5 | 28 - 42 | 208 | 3
ABB3208A10.02 | A | FDS | ABB Oy | OS60AJ12 | 200 | 60 | 208 | 3 | 200 | 208 | 3 | 10 | 30.8 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 60 | 208 | -
|  | MC | ABB France | A40 | 5 | 42 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA42DU42-20 | 5 | 28 - 42 | 208 | 3
ABB3208A11.01 | A | FDS | ABB Oy | OS100J03 | 200 | 100 | 208 | 3 | 200 | 208 | 3 | 15 | 46.2 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 100 | 208 | -
|  | MC | ABB France | A50 | 5 | 54 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA75DU63 | 5 | 45 - 63 | 208 | 3
ABB3208A11.02 | A | FDS | ABB Oy | OS100J03 | 200 | 100 | 208 | 3 | 200 | 208 | 3 | 15 | 46.2 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 100 | 208 | -
|  | MC | ABB France | A50 | 5 | 54 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA75DU63-20 | 5 | 45 - 63 | 208 | 3
ABB3208A12.01 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 208 | 3 | 100 | 208 | 3 | 20 | 59.4 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 208 | -
|  | MC | ABB France | A63 | 10 | 65 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA75DU63 | 5 | 45 - 63 | 208 | 3
ABB3208A12.02 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 208 | 3 | 100 | 208 | 3 | 20 | 59.4 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 208 | -
|  | MC | ABB France | A63 | 10 | 65 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA75DU63-20 | 5 | 45 - 63 | 208 | 3
ABB3208A13.01 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 208 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 208 | -
|  | MC | ABB France | A75 | 10 | 80 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA75DU80 | 5 | 60 - 80 | 208 | 3
ABB3208A13.02 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 208 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 208 | -
|  | MC | ABB France | A75 | 10 | 80 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA75DU80-20 | 5 | 60 - 80 | 208 | 3
ABB3208A14.01 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 208 | 3 | 100 | 208 | 3 | 30 | 88 | 4800 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 208 | -
|  | MC | ABB AB, CEWE-Control | A110 | 10 | 110 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA110DU110 | 5 | 80 - 110 | 208 | 3
ABB3208A15.01 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 208 | 3 | 100 | 208 | 3 | 40 | 114 | 4800 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 208 | -
|  | MC | ABB AB, CEWE-Control | A145 | 10 | 130 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA200DU135 | 5 | 100 - 135 | 208 | 3
ABB3208A16.01 | A | FDS | ABB Oy | OS400J03 | 200 | 400 | 208 | 3 | 200 | 208 | 3 | 50 | 143 | 4800 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 300 | 208 | -
|  | MC | ABB AB, CEWE-Control | A185 | 10 | 156 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA200DU175 | 5 | 130 - 175 | 208 | 3
ABB3208A17.01 | A | FDS | ABB Oy | OS400J03 | 200 | 400 | 208 | 3 | 200 | 208 | 3 | 60 | 169 | 9000 | 1,6 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 350 | 208 | -
|  | MC | ABB AB, CEWE-Control | A210 | 10 | 192 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA450DU235 | 5 | 165 - 235 | 208 | 3
ABB3208A18.01 | A | FDS | ABB Oy | OS400J03 | 200 | 400 | 208 | 3 | 200 | 208 | 3 | 75 | 211 | 9000 | 1,6 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 400 | 208 | -
|  | MC | ABB AB, CEWE-Control | A260 | 18 | 248 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA450DU235 | 5 | 165 - 235 | 208 | 3
ABB3208A19.01 | A | FDS | ABB Oy | OS600J03 | 200 | 600 | 208 | 3 | 200 | 208 | 3 | 100 | 273 | 9000 | 1,6 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 600 | 208 | -
|  | MC | ABB AB, CEWE-Control | A300 | 18 | 302 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA450DU310 | 5 | 220 - 310 | 208 | 3
Conditions of Acceptability:
|  | 1 | All of the specified individual components of the combination motor controller have been installed in an enclosure having
a specified internal volume in cubic inches. Additional testing of the combination motor controller is not required when
installed in an enclosure having the same or larger volume.
|  | 2 | When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from
the overcurrent protective devices and other components shall not be installed in this area.
|  | 3 | When specified, the overload relay heater table number shall be provided with the equipment.
|  | 4 | Unless otherwise specified, all connections between components are made with insulated wire having at least an ampacity of
100 percent of the rated motor current and connected to the terminals supplied with the individual components.
|  | 5 | The need for cautionary markings applicable to high fault short circuit current ratings, Type D a combination motor
controllers shall be considered in the end-product application.
|  | 6 | The TA450 overload relay requires the use of a mounting kit if mounted to the contactor. See the manufactures specifications.

## ABB - 208V - TYPE C
Issued: 2009-09-22
Last Revised: 2009-09-22
ID Number | Combination Type | Component Type | Component Manufactuer | Component Catalog Desgination | Component Ratings |  |  |  | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in.) | Conditions of Acceptability | Combination UL File Reference
[5 empty] | kA | Max Amps | Volts | Poles
ABB3208C01.01 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 208 | 3 | 35 | 208 | 3 | 0.5 | 2.4 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU3.1 | 5 | 2.2 - 3.1 | 208 | 3
ABB3208C01.02 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 208 | 3 | 35 | 208 | 3 | 0.5 | 2.4 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU3.1-20 | 5 | 2.2 - 3.1 | 208 | 3
ABB3208C02.01 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 208 | 3 | 35 | 208 | 3 | 0.5 | 2.4 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU3.1 | 5 | 2.2 - 3.1 | 208
ABB3208C02.02 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 208 | 3 | 35 | 208 | 3 | 0.5 | 2.4 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU3.1-20 | 5 | 2.2 - 3.1 | 208
ABB3208C03.01 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 208 | 3 | 35 | 208 | 3 | 0.75 | 3.5 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU5.0 | 5 | 3.5 - 5.0 | 208 | 3
ABB3208C03.02 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 208 | 3 | 35 | 208 | 3 | 0.75 | 3.5 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU5.0-20 | 5 | 3.5 - 5.0 | 208 | 3
ABB3208C04.01 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 208 | 3 | 35 | 208 | 3 | 0.75 | 3.5 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU5.0 | 5 | 3.5 - 5.0 | 208 | 3
ABB3208C04.02 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 208 | 3 | 35 | 208 | 3 | 0.75 | 3.5 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU5.0-20 | 5 | 3.5 - 5.0 | 208 | 3
ABB3208C05.01 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 208 | 3 | 35 | 208 | 3 | 1 | 4.6 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU6.5 | 5 | 4.5 - 6.5 | 208 | 3
ABB3208C05.02 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 208 | 3 | 35 | 208 | 3 | 1 | 4.6 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU6.5-20 | 5 | 4.5 - 6.5 | 208 | 3
ABB3208C06.01 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 208 | 3 | 35 | 208 | 3 | 1 | 4.6 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU6.5 | 5 | 4.5 - 6.5 | 208 | 3
ABB3208C06.02 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 208 | 3 | 35 | 208 | 3 | 1 | 4.6 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU6.5-20 | 5 | 4.5 - 6.5 | 208 | 3
ABB3208C07.01 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 208 | 3 | 35 | 208 | 3 | 1.5 | 6.6 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5 | 5 | 6.0 - 8.5 | 208 | 3
ABB3208C07.02 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 208 | 3 | 35 | 208 | 3 | 1.5 | 6.6 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5-20 | 5 | 6.0 - 8.5 | 208 | 3
ABB3208C08.01 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 208 | 3 | 35 | 208 | 3 | 1.5 | 6.6 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5 | 5 | 6.0 - 8.5 | 208 | 3
ABB3208C08.02 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 208 | 3 | 35 | 208 | 3 | 1.5 | 6.6 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5-20 | 5 | 6.0 - 8.5 | 208 | 3
ABB3208C09.01 | C | CB | ABB Sace | S3L015TW | 150 | 10 | 208 | 3 | 35 | 208 | 3 | 2 | 7.5 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11 | 5 | 7.5 - 11 | 208 | 3
ABB3208C09.02 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 208 | 3 | 35 | 208 | 3 | 2 | 7.5 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11-20 | 5 | 7.5 - 11 | 208 | 3
ABB3208C10.01 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 208 | 3 | 35 | 208 | 3 | 2 | 7.5 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11 | 5 | 7.5 - 11 | 208 | 3
ABB3208C10.02 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 208 | 3 | 35 | 208 | 3 | 2 | 7.5 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11-20 | 5 | 7.5 - 11 | 208 | 3
ABB3208C11.01 | C | CB | ABB Sace | S3L020TW | 150 | 20 | 208 | 3 | 35 | 208 | 3 | 3 | 10.6 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14 | 5 | 10 - 14.0 | 208 | 3
ABB3208C11.02 | C | CB | ABB Sace | S3L020TW | 150 | 20 | 208 | 3 | 35 | 208 | 3 | 3 | 10.6 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14-20 | 5 | 10 - 14.0 | 208 | 3
ABB3208C12.01 | C | CB | ABB Sace | T2S020TW | 65 | 20 | 208 | 3 | 35 | 208 | 3 | 3 | 10.6 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14 | 5 | 10 - 14.0 | 208 | 3
ABB3208C12.02 | C | CB | ABB Sace | T2S020TW | 65 | 20 | 208 | 3 | 35 | 208 | 3 | 3 | 10.6 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14-20 | 5 | 10 - 14.0 | 208 | 3
ABB3208C13.01 | C | CB | ABB Sace | S3L030TW | 150 | 30 | 208 | 3 | 35 | 208 | 3 | 5 | 16.7 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19 | 5 | 13 - 19 | 208 | 3
ABB3208C13.02 | C | CB | ABB Sace | S3L030TW | 150 | 30 | 208 | 3 | 35 | 208 | 3 | 5 | 16.7 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19-20 | 5 | 13 - 19 | 208 | 3
ABB3208C14.01 | C | CB | ABB Sace | T2S030TW | 65 | 30 | 208 | 3 | 35 | 208 | 3 | 5 | 16.7 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19 | 5 | 13 - 19 | 208 | 3
ABB3208C14.02 | C | CB | ABB Sace | T2S030TW | 65 | 30 | 208 | 3 | 35 | 208 | 3 | 5 | 16.7 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19-20 | 5 | 13 - 19 | 208 | 3
ABB3208C15.01 | C | CB | ABB Sace | S3L040TW | 150 | 40 | 208 | 3 | 35 | 208 | 3 | 7.5 | 24.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32 | 5 | 24 - 32 | 208 | 3
ABB3208C15.02 | C | CB | ABB Sace | S3L040TW | 150 | 40 | 208 | 3 | 35 | 208 | 3 | 7.5 | 24.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32-20 | 5 | 24 - 32 | 208 | 3
ABB3208C16.01 | C | CB | ABB Sace | T2S030TW | 65 | 30 | 208 | 3 | 35 | 208 | 3 | 7.5 | 24.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32 | 5 | 24 - 32 | 208 | 3
ABB3208C16.02 | C | CB | ABB Sace | T2S030TW | 65 | 30 | 208 | 3 | 35 | 208 | 3 | 7.5 | 24.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32-20 | 5 | 24 - 32 | 208 | 3
ABB3208C17.01 | C | CB | ABB Sace | S3L050TW | 150 | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 208 | 3
ABB3208C17.02 | C | CB | ABB Sace | S3L050TW | 150 | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 208 | 3
ABB3208C18.01 | C | CB | ABB Sace | T4H050TW | 65 | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 208 | 3
ABB3208C18.02 | C | CB | ABB Sace | T4H050TW | 65 | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 208 | 3
ABB3208C19.01 | C | CB | ABB Sace | TS3L050TW | 65 | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 208 | 3
ABB3208C19.02 | C | CB | ABB Sace | TS3L050TW | 65 | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 208 | 3
ABB3208C20.01 | C | CB | ABB Sace | S3L050TW | 150 | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 208 | 3
ABB3208C20.02 | C | CB | ABB Sace | S3L050TW | 150 | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 208 | 3
ABB3208C21.01 | C | CB | ABB Sace | T2S050TW | 65 | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 208 | 3
ABB3208C21.02 | C | CB | ABB Sace | T2S050TW | 65 | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 208 | 3
ABB3208C22.01 | C | CB | ABB Sace | TS3L050TW | 150 | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 208 | 3
ABB3208C22.02 | C | CB | ABB Sace | TS3L050TW | 150 | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 208 | 3
ABB3208C23.01 | C | CB | ABB Sace | S3L070TW | 150 | 50 | 208 | 3 | 85 | 208 | 3 | 15 | 46.2 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 42 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63 | 5 | 45 - 63 | 208 | 3
ABB3208C23.02 | C | CB | ABB Sace | S3L070TW | 150 | 50 | 208 | 3 | 85 | 208 | 3 | 15 | 46.2 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 42 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63-20 | 5 | 45 - 63 | 208 | 3
ABB3208C24.01 | C | CB | ABB Sace | T4L080TW | 200 | 50 | 208 | 3 | 85 | 208 | 3 | 15 | 46.2 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 42 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63 | 5 | 45 - 63 | 208 | 3
ABB3208C24.02 | C | CB | ABB Sace | T4L080TW | 200 | 50 | 208 | 3 | 85 | 208 | 3 | 15 | 46.2 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 42 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63-20 | 5 | 45 -63 | 208 | 3
ABB3208C25.01 | C | CB | ABB Sace | TS3L080TW | 150 | 50 | 208 | 3 | 85 | 208 | 3 | 15 | 46.2 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 42 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63 | 5 | 45 - 63 | 208 | 3
ABB3208C25.02 | C | CB | ABB Sace | TS3L080TW | 150 | 50 | 208 | 3 | 85 | 208 | 3 | 15 | 46.2 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 42 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63-20 | 5 | 45 -63 | 208 | 3
ABB3208C26.01 | C | CB | ABB Sace | S3L100TW | 150 | 70 | 208 | 3 | 85 | 208 | 3 | 20 | 59.4 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A63 | 5 | 54 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63 | 5 | 45 - 63 | 208 | 3
ABB3208C26.02 | C | CB | ABB Sace | S3L100TW | 150 | 70 | 208 | 3 | 85 | 208 | 3 | 20 | 59.4 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A63 | 5 | 54 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63-20 | 5 | 45 - 63 | 208 | 3
ABB3208C27.01 | C | CB | ABB Sace | T4L100TW | 200 | 80 | 208 | 3 | 85 | 208 | 3 | 20 | 59.4 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A63 | 5 | 54 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63 | 5 | 45 -63 | 208 | 3
ABB3208C27.02 | C | CB | ABB Sace | T4L100TW | 200 | 80 | 208 | 3 | 85 | 208 | 3 | 20 | 59.4 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A63 | 5 | 54 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63-20 | 5 | 45 - 63 | 208 | 3
ABB3208C28.01 | C | CB | ABB Sace | TS3L100TW | 150 | 80 | 208 | 3 | 85 | 208 | 3 | 20 | 59.4 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A63 | 5 | 54 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63 | 5 | 45 - 63 | 208 | 3
ABB3208C28.02 | C | CB | ABB Sace | TS3L100TW | 150 | 80 | 208 | 3 | 85 | 208 | 3 | 20 | 59.4 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A63 | 5 | 54 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63-20 | 5 | 45 - 63 | 208 | 3
ABB3208C29.01 | C | CB | ABB Sace | S3L125TW | 150 | 100 | 208 | 3 | 85 | 208 | 3 | 25 | 74.8 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 65 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 208 | 3
ABB3208C29.02 | C | CB | ABB Sace | S3L125TW | 150 | 100 | 208 | 3 | 85 | 208 | 3 | 25 | 74.8 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 65 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 208 | 3
ABB3208C30.01 | C | CB | ABB Sace | T4L125TW | 200 | 100 | 208 | 3 | 85 | 208 | 3 | 25 | 74.8 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 65 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 208 | 3
ABB3208C30.02 | C | CB | ABB Sace | T4L125TW | 200 | 100 | 208 | 3 | 85 | 208 | 3 | 25 | 74.8 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 65 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 208 | 3
ABB3208C31.01 | C | CB | ABB Sace | TS3L125TW | 150 | 100 | 208 | 3 | 85 | 208 | 3 | 25 | 74.8 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 65 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 208 | 3
ABB3208C31.02 | C | CB | ABB Sace | TS3L150TW | 150 | 100 | 208 | 3 | 85 | 208 | 3 | 25 | 74.8 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 65 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 208 | 3
ABB3208C32.01 | C | CB | ABB Sace | S3L150TW | 150 | 125 | 208 | 3 | 85 | 208 | 3 | 30 | 88 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A110 | 10 | 110 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA110DU110 | 5 | 80 - 110 | 208 | 3
ABB3208C33.01 | C | CB | ABB Sace | T4L150TW | 200 | 125 | 208 | 3 | 85 | 208 | 3 | 30 | 88 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A110 | 10 | 110 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA110DU110 | 5 | 80 - 110 | 208 | 3
ABB3208C34.01 | C | CB | ABB Sace | S3L200TW | 150 | 125 | 208 | 3 | 65 | 208 | 3 | 40 | 114 | 4800 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A145 | 10 | 130 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA200DU135 | 5 | 100 - 135 | 208 | 3
ABB3208C35.01 | C | CB | ABB Sace | T4L200TW | 200 | 125 | 208 | 3 | 65 | 208 | 3 | 40 | 114 | 4800 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A145 | 10 | 130 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA200DU135 | 5 | 100 - 135 | 208 | 3
ABB3208C36.01 | C | CB | ABB Sace | S4N250TW | 65 | 125 | 208 | 3 | 85 | 208 | 3 | 50 | 143 | 4800 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A185 | 10 | 156 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA200DU175 | 5 | 130 - 175 | 208 | 3
ABB3208C37.01 | C | CB | ABB Sace | T4L250TW | 200 | 125 | 208 | 3 | 85 | 208 | 3 | 50 | 143 | 4800 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A185 | 10 | 156 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA200DU175 | 5 | 130 - 175 | 208 | 3
ABB3208C38.01 | C | CB | ABB Sace | S5N300TW | 200 | 150 | 208 | 3 | 85 | 208 | 3 | 60 | 169 | 9000 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A210 | 10 | 192 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU235 | 5 | 165 - 235 | 208 | 3
ABB3208C39.01 | C | CB | ABB Sace | T5L300TW | 200 | 150 | 208 | 3 | 85 | 208 | 3 | 60 | 169 | 9000 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A210 | 10 | 192 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU235 | 5 | 165 - 235 | 208 | 3
ABB3208C40.01 | C | CB | ABB Sace | S5N400TW | 100 | 200 | 208 | 3 | 85 | 208 | 3 | 75 | 211 | 9000 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A260 | 10 | 248 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU235 | 5 | 165 - 235 | 208 | 3
ABB3208C41.01 | C | CB | ABB Sace | T5L400TW | 200 | 200 | 208 | 3 | 85 | 208 | 3 | 75 | 211 | 9000 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A260 | 10 | 248 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU235 | 5 | 165 - 235 | 208 | 3
ABB3208C42.01 | C | CB | ABB Sace | S5N400TW | 100 | 250 | 208 | 3 | 85 | 208 | 3 | 100 | 273 | 9000 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A300 | 10 | 302 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU310 | 5 | 220 - 310 | 208 | 3
ABB3208C43.01 | C | CB | ABB Sace | T5L400TW | 200 | 250 | 208 | 3 | 85 | 208 | 3 | 100 | 273 | 9000 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A300 | 10 | 302 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU310 | 5 | 220 - 310 | 208 | 3
Conditions of Acceptability:
|  | 1 | All of the specified individual components of the combination motor controller have been installed in an enclosure having | [11 empty] | Component manufactured by-
a specified internal volume in cubic inches. Additional testing of the combination motor controller is not required when
|  |  | installed in an enclosure having the same or larger volume. | [11 empty] | Contactor A9 - A75 ( ABB France )
Contactor A110 - A300 ( ABB Automation technology AB )
|  | 2 | When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from | [11 empty] | Overload relay ( ABB Stotz- Kontakt )
|  |  | the overcurrent protective devices and other components shall not be installed in this area. | [11 empty] | Breaker ( ABB Sace )
|  | 3 | When specified, the overload relay heater table number shall be provided with the equipment.
|  | 4 | Unless otherwise specified, all connections between components are made with insulated wire having at least an ampacity of
100 percent of the rated motor current and connected to the terminals supplied with the individual components.
|  | 5 | The need for cautionary markings applicable to high fault short circuit current ratings, Type D a combination motor
controllers shall be considered in the end-product application.
|  | 6 | The TA450 overload relay requires the use of a mounting kit if mounted to the contactor. See the manufactures specifications.

## ABB - 208V - TYPE D
Issued: 2009-09-22
Last Revised: 2009-09-22
ID Number | Combination Type | Component Type | Component Manufactuer | Component Catalog Desgination | Component Ratings |  |  |  | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in.) | Conditions of Acceptability | Combination UL File Reference
[5 empty] | kA | Max Amps | Volts | Poles
ABB3208D01.01 | D | ICB | ABB Sace | S3L005MW | - | 5 | 208 | 3 | 35 | 208 | 3 | 0.5 | 2.4 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU3.1 | 5 | 2.2 - 3.1 | 208 | 3
ABB3208D01.02 | D | ICB | ABB Sace | S3L005MW | - | 5 | 208 | 3 | 35 | 208 | 3 | 0.5 | 2.4 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU3.1-20 | 5 | 2.2 - 3.1 | 208 | 3
ABB3208D02.01 | D | ICB | ABB Sace | TS3L005MW | - | 5 | 208 | 3 | 35 | 208 | 3 | 0.5 | 2.4 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU3.1 | 5 | 2.2 - 3.1 | 208
ABB3208D02.02 | D | ICB | ABB Sace | TS3L005MW | - | 5 | 208 | 3 | 35 | 208 | 3 | 0.5 | 2.4 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU3.1-20 | 5 | 2.2 - 3.1 | 208
ABB3208D03.01 | D | ICB | ABB Sace | S3L005MW | - | 5 | 208 | 3 | 35 | 208 | 3 | 0.75 | 3.5 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU5.0 | 5 | 3.5 - 5.0 | 208 | 3
ABB3208D03.02 | D | ICB | ABB Sace | S3L005MW | - | 5 | 208 | 3 | 35 | 208 | 3 | 0.75 | 3.5 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU5.0-20 | 5 | 3.5 - 5.0 | 208 | 3
ABB3208D04.01 | D | ICB | ABB Sace | TS3L005MW | - | 5 | 208 | 3 | 35 | 208 | 3 | 0.75 | 3.5 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU5.0 | 5 | 3.5 - 5.0 | 208 | 3
ABB3208D04.02 | D | ICB | ABB Sace | TS3L005MW | - | 5 | 208 | 3 | 35 | 208 | 3 | 0.75 | 3.5 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU5.0-20 | 5 | 3.5 - 5.0 | 208 | 3
ABB3208D05.01 | D | ICB | ABB Sace | S3L010MW | - | 10 | 208 | 3 | 35 | 208 | 3 | 1 | 4.6 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU6.5 | 5 | 4.5 - 6.5 | 208 | 3
ABB3208D05.02 | D | ICB | ABB Sace | S3L010MW | - | 10 | 208 | 3 | 35 | 208 | 3 | 1 | 4.6 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU6.5-20 | 5 | 4.5 - 6.5 | 208 | 3
ABB3208D06.01 | D | ICB | ABB Sace | TS3L010MW | - | 10 | 208 | 3 | 35 | 208 | 3 | 1 | 4.6 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU6.5 | 5 | 4.5 - 6.5 | 208 | 3
ABB3208D06.02 | D | ICB | ABB Sace | TS3L010MW | - | 10 | 208 | 3 | 35 | 208 | 3 | 1 | 4.6 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU6.5-20 | 5 | 4.5 - 6.5 | 208 | 3
ABB3208D07.01 | D | ICB | ABB Sace | S3L010MW | - | 10 | 208 | 3 | 35 | 208 | 3 | 1.5 | 6.6 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5 | 5 | 6.0 - 8.5 | 208 | 3
ABB3208D07.02 | D | ICB | ABB Sace | S3L010MW | - | 10 | 208 | 3 | 35 | 208 | 3 | 1.5 | 6.6 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5-20 | 5 | 6.0 - 8.5 | 208 | 3
ABB3208D08.01 | D | ICB | ABB Sace | TS3L010MW | - | 10 | 208 | 3 | 35 | 208 | 3 | 1.5 | 6.6 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5 | 5 | 6.0 - 8.5 | 208 | 3
ABB3208D08.02 | D | ICB | ABB Sace | TS3L010MW | - | 10 | 208 | 3 | 35 | 208 | 3 | 1.5 | 6.6 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5-20 | 5 | 6.0 - 8.5 | 208 | 3
ABB3208D09-01 | D | ICB | ABB Sace | S3L010MW | - | 10 | 208 | 3 | 35 | 208 | 3 | 2 | 7.5 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11 | 5 | 7.5 - 11 | 208 | 3
ABB3208D09-02 | D | ICB | ABB Sace | S3L010MW | - | 10 | 208 | 3 | 35 | 208 | 3 | 2 | 7.5 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11-20 | 5 | 7.5 - 11 | 208 | 3
ABB3208D10.01 | D | ICB | ABB Sace | TS3L010MW | - | 10 | 208 | 3 | 35 | 208 | 3 | 2 | 7.5 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11 | 5 | 7.5 - 11 | 208 | 3
ABB3208D10.02 | D | ICB | ABB Sace | TS3L010MW | - | 10 | 208 | 3 | 35 | 208 | 3 | 2 | 7.5 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11-20 | 5 | 7.5 - 11 | 208 | 3
ABB3208D11.01 | D | ICB | ABB Sace | S3L025MW | - | 25 | 208 | 3 | 35 | 208 | 3 | 3 | 10.6 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14 | 5 | 10 - 14.0 | 208 | 3
ABB3208D11.02 | D | ICB | ABB Sace | S3L025MW | - | 25 | 208 | 3 | 35 | 208 | 3 | 3 | 10.6 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14-20 | 5 | 10 - 14.0 | 208 | 3
ABB3208D12.01 | D | ICB | ABB Sace | TS3L025MW | - | 25 | 208 | 3 | 35 | 208 | 3 | 3 | 10.6 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14 | 5 | 10 - 14.0 | 208 | 3
ABB3208D12.02 | D | ICB | ABB Sace | TS3L025MW | - | 25 | 208 | 3 | 35 | 208 | 3 | 3 | 10.6 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14-20 | 5 | 10 - 14.0 | 208 | 3
ABB3208D13.01 | D | ICB | ABB Sace | S3L050MW | - | 50 | 208 | 3 | 35 | 208 | 3 | 5 | 16.7 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19 | 5 | 13 - 19 | 208 | 3
ABB3208D13.02 | D | ICB | ABB Sace | S3L050MW | - | 50 | 208 | 3 | 35 | 208 | 3 | 5 | 16.7 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19-20 | 5 | 13 - 19 | 208 | 3
ABB3208D14.01 | D | ICB | ABB Sace | T2S050MW | - | 50 | 208 | 3 | 35 | 208 | 3 | 5 | 16.7 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19 | 5 | 13 - 19 | 208 | 3
ABB3208D14.02 | D | ICB | ABB Sace | T2S050MW | - | 50 | 208 | 3 | 35 | 208 | 3 | 5 | 16.7 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19 | 5 | 13 - 19 | 208 | 3
ABB3208D15.01 | D | ICB | ABB Sace | S3L050MW | - | 50 | 208 | 3 | 35 | 208 | 3 | 7.5 | 24.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32 | 5 | 24 - 32 | 208 | 3
ABB3208D15.02 | D | ICB | ABB Sace | S3L050MW | - | 50 | 208 | 3 | 35 | 208 | 3 | 7.5 | 24.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32-20 | 5 | 24 - 32 | 208 | 3
ABB3208D16.01 | D | ICB | ABB Sace | T2S050MW | - | 50 | 208 | 3 | 35 | 208 | 3 | 7.5 | 24.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32 | 5 | 24 - 32 | 208 | 3
ABB3208D16.02 | D | ICB | ABB Sace | T2S050MW | - | 50 | 208 | 3 | 35 | 208 | 3 | 7.5 | 24.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32-20 | 5 | 24 - 32 | 208 | 3
ABB3208D17.01 | D | ICB | ABB Sace | S3L050MW | - | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 208 | 3
ABB3208D17.02 | D | ICB | ABB Sace | S3L050MW | - | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 208 | 3
ABB3208D18.01 | D | ICB | ABB Sace | T4H050MW | - | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 208 | 3
ABB3208D18.02 | D | ICB | ABB Sace | T4H050MW | - | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 208 | 3
ABB3208D19.01 | D | ICB | ABB Sace | TS3L050MW | - | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 208 | 3
ABB3208D19.02 | D | ICB | ABB Sace | TS3L050MW | - | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 208 | 3
ABB3208D20.01 | D | ICB | ABB Sace | S3L050MW | - | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 208 | 3
ABB3208D20.02 | D | ICB | ABB Sace | S3L050MW | - | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 208 | 3
ABB3208D21.01 | D | ICB | ABB Sace | T4H050MW | - | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 208 | 3
ABB3208D21.02 | D | ICB | ABB Sace | T4H050MW | - | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 208 | 3
ABB3208D22.01 | D | ICB | ABB Sace | TS3L050MW | - | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 208 | 3
ABB3208D22.02 | D | ICB | ABB Sace | TS3L050MW | - | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 208 | 3
ABB3208D23.01 | D | ICB | ABB Sace | S3L100MW | - | 100 | 208 | 3 | 85 | 208 | 3 | 15 | 46.2 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63 | 5 | 45 - 63 | 208 | 3
ABB3208D23.02 | D | ICB | ABB Sace | S3L100MW | - | 100 | 208 | 3 | 85 | 208 | 3 | 15 | 46.2 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63-20 | 5 | 45 - 63 | 208 | 3
ABB3208D24.01 | D | ICB | ABB Sace | T4H100MW | - | 100 | 208 | 3 | 85 | 208 | 3 | 15 | 46.2 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63 | 5 | 45 - 63 | 208 | 3
ABB3208D24.02 | D | ICB | ABB Sace | T4H100MW | - | 100 | 208 | 3 | 85 | 208 | 3 | 15 | 46.2 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63-20 | 5 | 45 - 63 | 208 | 3
ABB3208D25.01 | D | ICB | ABB Sace | TS3L100MW | - | 100 | 208 | 3 | 85 | 208 | 3 | 15 | 46.2 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63 | 5 | 45 - 63 | 208 | 3
ABB3208D25.02 | D | ICB | ABB Sace | TS3L100MW | - | 100 | 208 | 3 | 85 | 208 | 3 | 15 | 46.2 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63-20 | 5 | 45 - 63 | 208 | 3
ABB3208D26.01 | D | ICB | ABB Sace | S3L100MW | - | 100 | 208 | 3 | 85 | 208 | 3 | 20 | 59.4 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63 | 5 | 45 - 63 | 208 | 3
ABB3208D26.02 | D | ICB | ABB Sace | S3L100MW | - | 100 | 208 | 3 | 85 | 208 | 3 | 20 | 59.4 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63-20 | 5 | 45 - 63 | 208 | 3
ABB3208D27.01 | D | ICB | ABB Sace | T4L100MW | - | 100 | 208 | 3 | 85 | 208 | 3 | 20 | 59.4 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63 | 5 | 45 - 63 | 208 | 3
ABB3208D27.02 | D | ICB | ABB Sace | T4L100MW | - | 100 | 208 | 3 | 85 | 208 | 3 | 20 | 59.4 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63-20 | 5 | 45 - 63 | 208 | 3
ABB3208D28.01 | D | ICB | ABB Sace | S3L150MW | - | 150 | 208 | 3 | 85 | 208 | 3 | 25 | 74.8 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 208 | 3
ABB3208D28.02 | D | ICB | ABB Sace | S3L150MW | - | 150 | 208 | 3 | 85 | 208 | 3 | 25 | 74.8 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 208 | 3
ABB3208D29.01 | D | ICB | ABB Sace | T4L150MW | - | 150 | 208 | 3 | 85 | 208 | 3 | 25 | 74.8 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 208 | 3
ABB3208D29.02 | D | ICB | ABB Sace | T4L150MW | - | 150 | 208 | 3 | 85 | 208 | 3 | 25 | 74.8 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 208 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 208 | 3
ABB3208D30.01 | D | ICB | ABB Sace | S4L250MW | - | 250 | 208 | 3 | 85 | 208 | 3 | 30 | 88 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A110 | 10 | 110 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA110DU110 | 5 | 80 - 110 | 208 | 3
ABB3208D31.01 | D | ICB | ABB Sace | T4L150MW | - | 150 | 208 | 3 | 85 | 208 | 3 | 30 | 88 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A110 | 10 | 110 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA110DU110 | 5 | 80 - 110 | 208 | 3
ABB3208D32.01 | D | ICB | ABB Sace | S3L200MW | - | 200 | 208 | 3 | 65 | 208 | 3 | 40 | 114 | 4800 | 1,5 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A145 | 10 | 130 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA200DU135 | 5 | 100 - 135 | 208 | 3
ABB3208D33.01 | D | ICB | ABB Sace | T4L200MW | - | 200 | 208 | 3 | 65 | 208 | 3 | 40 | 114 | 4800 | 1,5 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A145 | 10 | 130 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA200DU135 | 5 | 100 - 135 | 208 | 3
ABB3208D34.01 | D | ICB | ABB Sace | S4N250MW | - | 250 | 208 | 3 | 85 | 208 | 3 | 50 | 143 | 4800 | 1,5 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A185 | 10 | 156 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA200DU175 | 5 | 130 - 175 | 208 | 3
ABB3208D35.01 | D | ICB | ABB Sace | T4L250MW | - | 250 | 208 | 3 | 85 | 208 | 3 | 50 | 143 | 4800 | 1,5 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A185 | 10 | 156 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA200DU175 | 5 | 130 - 175 | 208 | 3
ABB3208D36.01 | D | ICB | ABB Sace | S4N250MW | - | 300 | 208 | 3 | 85 | 208 | 3 | 60 | 169 | 9000 | 1,5,6 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A210 | 10 | 192 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA450DU235 | 5 | 165 - 235 | 208 | 3
ABB3208D37.01 | D | ICB | ABB Sace | T5L300MW | - | 300 | 208 | 3 | 85 | 208 | 3 | 60 | 169 | 9000 | 1,5,6 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A210 | 10 | 192 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA450DU235 | 5 | 165 - 235 | 208 | 3
ABB3208D38.01 | D | ICB | ABB Sace | S5N400MW | - | 400 | 208 | 3 | 85 | 208 | 3 | 75 | 211 | 9000 | 1,5,6 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A260 | 18 | 248 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA450DU235 | 5 | 165 - 235 | 208 | 3
ABB3208D39.01 | D | ICB | ABB Sace | T5L400MW | - | 400 | 208 | 3 | 85 | 208 | 3 | 75 | 211 | 9000 | 1,5,6 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A260 | 18 | 248 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA450DU235 | 5 | 165 - 235 | 208 | 3
ABB3208D40.01 | D | ICB | ABB Sace | S5N400MW | - | 400 | 208 | 3 | 85 | 208 | 3 | 100 | 273 | 9000 | 1,5,6 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A300 | 18 | 302 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA450DU310 | 5 | 220 - 310 | 208 | 3
ABB3208D41.01 | D | ICB | ABB Sace | T5L400MW | - | 400 | 208 | 3 | 85 | 208 | 3 | 100 | 273 | 9000 | 1,5,6 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A300 | 18 | 302 | 208 | 3
|  | OLR | ABB Stotz-kontakt | TA450DU310 | 5 | 220 - 310 | 208 | 3
Conditions of Acceptability:
|  | 1 | All of the specified individual components of the combination motor controller have been installed in an enclosure having
a specified internal volume in cubic inches. Additional testing of the combination motor controller is not required when
installed in an enclosure having the same or larger volume.
|  | 2 | When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from
the overcurrent protective devices and other components shall not be installed in this area.
|  | 3 | When specified, the overload relay heater table number shall be provided with the equipment.
|  | 4 | Unless otherwise specified, all connections between components are made with insulated wire having at least an ampacity of
100 percent of the rated motor current and connected to the terminals supplied with the individual components.
|  | 5 | The need for cautionary markings applicable to high fault short circuit current ratings, Type D a combination motor
controllers shall be considered in the end-product application.
|  | 6 | The TA450 overload relay requires the use of a mounting kit if mounted to the contactor. See the manufactures specifications.

## ABB - 200V - TYPE A
Issued: 2009-09-22
Last Revised: 2009-09-22
ID Number | Combination Type | Component Type | Component Manufactuer | Component Catalog Desgination | Component Ratings |  |  |  | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in.) | Conditions of Acceptability | Combination UL File Reference
[5 empty] | kA | Max Amps | Volts | Poles
ABB3200A01.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 200 | 3 | 200 | 200 | 3 | 0.5 | 2.5 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 6 | 200 | -
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU3.1 | 5 | 2.2 - 3.1 | 200 | 3
ABB3200A01.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 200 | 3 | 200 | 200 | 3 | 0.5 | 2.5 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 6 | 200 | -
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU3.1-20 | 5 | 2.2 - 3.1 | 200 | 3
ABB3200A02.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 200 | 3 | 200 | 200 | 3 | 0.75 | 3.7 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 10 | 200 | -
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU5.0 | 5 | 3.5 - 4.0 | 200 | 3
ABB3200A02.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 200 | 3 | 200 | 200 | 3 | 0.75 | 3.7 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 10 | 200 | -
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU5.0-20 | 5 | 3.5 - 4.0 | 200 | 3
ABB3200A03.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 200 | 3 | 200 | 200 | 3 | 1 | 4.8 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 15 | 200 | -
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU6.5 | 5 | 4.5 - 6.5 | 200 | 3
ABB3200A03.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 200 | 3 | 200 | 200 | 3 | 1 | 4.8 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 15 | 200 | -
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU6.5-20 | 5 | 4.5 - 6.5 | 200 | 3
ABB3200A04.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 200 | 3 | 200 | 200 | 3 | 1.5 | 6.9 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 25 | 200 | -
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU8.5 | 5 | 6.0 - 8.5 | 200 | 3
ABB3200A04.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 200 | 3 | 200 | 200 | 3 | 1.5 | 6.9 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 25 | 200 | -
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU8.5-20 | 5 | 6.0 - 8.5 | 200 | 3
ABB3200A05.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 200 | 3 | 200 | 200 | 3 | 2 | 7.8 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 200 | -
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU11 | 5 | 7.5 - 11 | 200 | 3
ABB3200A05.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 200 | 3 | 200 | 200 | 3 | 2 | 7.8 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 200 | -
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU11-20 | 5 | 7.5 - 11 | 200 | 3
ABB3200A06.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 200 | 3 | 200 | 200 | 3 | 3 | 11 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 200 | -
|  | MC | ABB France | A12 | 5 | 11 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU14 | 5 | 10 - 14.0 | 200 | 3
ABB3200A06.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 200 | 3 | 200 | 200 | 3 | 3 | 11 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 200 | -
|  | MC | ABB France | A12 | 5 | 11 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU14-20 | 5 | 10 - 14.0 | 200 | 3
ABB3200A07.01 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 200 | 3 | 200 | 200 | 3 | 5 | 17.5 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 200 | -
|  | MC | ABB France | A16 | 5 | 17 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU19 | 5 | 13 - 19 | 200 | 3
ABB3200A07.02 | A | FDS | ABB Oy | OS30AJ12 | 200 | 30 | 200 | 3 | 200 | 200 | 3 | 5 | 17.5 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 30 | 200 | -
|  | MC | ABB France | A16 | 5 | 17 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU19-20 | 5 | 13 - 19 | 200 | 3
ABB3200A08.01 | A | FDS | ABB Oy | OS60AJ12 | 200 | 60 | 200 | 3 | 200 | 200 | 3 | 7.5 | 25.3 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 60 | 200 | -
|  | MC | ABB France | A26 | 5 | 28 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU32 | 5 | 24 - 32 | 200 | 3
ABB3200A08.02 | A | FDS | ABB Oy | OS60AJ12 | 200 | 60 | 200 | 3 | 200 | 200 | 3 | 7.5 | 25.3 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 60 | 200 | -
|  | MC | ABB France | A26 | 5 | 28 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU32-20 | 5 | 24 - 32 | 200 | 3
ABB3200A09.01 | A | FDS | ABB Oy | OS60AJ12 | 200 | 60 | 200 | 3 | 200 | 200 | 3 | 10 | 32.2 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 60 | 200 | -
|  | MC | ABB France | A30 | 5 | 34 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA42DU42 | 5 | 28 - 42 | 200 | 3
ABB3200A09.02 | A | FDS | ABB Oy | OS60AJ12 | 200 | 60 | 200 | 3 | 200 | 200 | 3 | 10 | 32.2 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 60 | 200 | -
|  | MC | ABB France | A30 | 5 | 34 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA42DU42-20 | 5 | 28 - 42 | 200 | 3
ABB3200A10.01 | A | FDS | ABB Oy | OS60AJ12 | 200 | 60 | 200 | 3 | 200 | 200 | 3 | 10 | 32.2 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 60 | 200 | -
|  | MC | ABB France | A40 | 5 | 42 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA42DU42 | 5 | 28 - 42 | 200 | 3
ABB3200A10.02 | A | FDS | ABB Oy | OS60AJ12 | 200 | 60 | 200 | 3 | 200 | 200 | 3 | 10 | 32.2 | 1344 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 60 | 200 | -
|  | MC | ABB France | A40 | 5 | 42 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA42DU42-20 | 5 | 28 - 42 | 200 | 3
ABB3200A11.01 | A | FDS | ABB Oy | OS100J03 | 200 | 100 | 200 | 3 | 200 | 200 | 3 | 15 | 48.3 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 100 | 200 | -
|  | MC | ABB France | A50 | 5 | 54 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA75DU52 | 5 | 36 - 52 | 200 | 3
ABB3200A11.02 | A | FDS | ABB Oy | OS100J03 | 200 | 100 | 200 | 3 | 200 | 200 | 3 | 15 | 48.3 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 100 | 200 | -
|  | MC | ABB France | A50 | 5 | 54 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA75DU52-20 | 5 | 36 - 52 | 200 | 3
ABB3200A12.01 | A | FDS | ABB Oy | OS200J03 | 200 | 100 | 200 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 100 | 200 | -
|  | MC | ABB France | A63 | 10 | 65 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA75DU80 | 5 | 60 - 80 | 200 | 3
ABB3200A12.02 | A | FDS | ABB Oy | OS200J03 | 200 | 100 | 200 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 100 | 200 | -
|  | MC | ABB France | A63 | 10 | 65 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA75DU80-20 | 5 | 60 - 80 | 200 | 3
ABB3200A13.01 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 200 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 200 | -
|  | MC | ABB France | A75 | 10 | 80 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA75DU80 | 5 | 60 - 80 | 200 | 3
ABB3200A13.02 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 200 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2560 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 200 | -
|  | MC | ABB France | A75 | 10 | 80 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA75DU80-20 | 5 | 60 - 80 | 200 | 3
ABB3200A14.01 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 200 | 3 | 100 | 200 | 3 | 30 | 92 | 4800 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 200 | -
|  | MC | ABB AB, CEWE-Control | A110 | 10 | 110 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA110DU110 | 5 | 80 - 110 | 200 | 3
ABB3200A15.01 | A | FDS | ABB Oy | OS200J03 | 200 | 200 | 200 | 3 | 100 | 200 | 3 | 40 | 120 | 4800 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 200 | 200 | -
|  | MC | ABB AB, CEWE-Control | A145 | 10 | 130 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA200DU135 | 5 | 100 - 135 | 200 | 3
ABB3200A16.01 | A | FDS | ABB Oy | OS400J03 | 200 | 400 | 200 | 3 | 200 | 200 | 3 | 50 | 150 | 4800 | 1 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 300 | 200 | -
|  | MC | ABB AB, CEWE-Control | A185 | 10 | 156 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA200DU175 | 5 | 130 - 175 | 200 | 3
ABB3200A17.01 | A | FDS | ABB Oy | OS400J03 | 200 | 400 | 200 | 3 | 200 | 200 | 3 | 60 | 177 | 9000 | 1,6 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 350 | 200 | -
|  | MC | ABB AB, CEWE-Control | A210 | 10 | 192 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA450DU235 | 5 | 165 - 235 | 200 | 3
ABB3200A18.01 | A | FDS | ABB Oy | OS400J03 | 200 | 400 | 200 | 3 | 200 | 200 | 3 | 75 | 221 | 9000 | 1,6 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 400 | 200 | -
|  | MC | ABB AB, CEWE-Control | A260 | 18 | 248 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA450DU310 | 5 | 220 - 310 | 200 | 3
ABB3200A19.01 | A | FDS | ABB Oy | OS600J03 | 200 | 600 | 200 | 3 | 200 | 200 | 3 | 100 | 285 | 9000 | 1,6 | E193298 V1 S1
|  | F | Bussmann | Class J | 200 | 600 | 200 | -
|  | MC | ABB AB, CEWE-Control | A300 | 18 | 302 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA450DU310 | 5 | 220 - 310 | 200 | 3
Conditions of Acceptability:
|  | 1 | All of the specified individual components of the combination motor controller have been installed in an enclosure having
a specified internal volume in cubic inches. Additional testing of the combination motor controller is not required when
installed in an enclosure having the same or larger volume.
|  | 2 | When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from
the overcurrent protective devices and other components shall not be installed in this area.
|  | 3 | When specified, the overload relay heater table number shall be provided with the equipment.
|  | 4 | Unless otherwise specified, all connections between components are made with insulated wire having at least an ampacity of
100 percent of the rated motor current and connected to the terminals supplied with the individual components.
|  | 5 | The need for cautionary markings applicable to high fault short circuit current ratings, Type D a combination motor
controllers shall be considered in the end-product application.
|  | 6 | The TA450 overload relay requires the use of a mounting kit if mounted to the contactor. See the manufactures specifications.

## ABB - 200V - TYPE C
Issued: 2009-09-22
Last Revised: 2009-09-22
ID Number | Combination Type | Component Type | Component Manufactuer | Component Catalog Desgination | Component Ratings |  |  |  | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in.) | Conditions of Acceptability | Combination UL File Reference
[5 empty] | kA | Max Amps | Volts | Poles
ABB3200C01.01 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 200 | 3 | 35 | 200 | 3 | 0.5 | 2.5 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU3.1 | 5 | 2.2 - 3.1 | 200 | 3
ABB3200C01.02 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 200 | 3 | 35 | 200 | 3 | 0.5 | 2.5 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-kontakt | TA25DU3.1-20 | 5 | 2.2 - 3.1 | 200 | 3
ABB3200C02.01 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 200 | 3 | 35 | 200 | 3 | 0.5 | 2.5 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU3.1 | 5 | 2.2 - 3.1 | 200
ABB3200C02.02 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 200 | 3 | 35 | 200 | 3 | 0.5 | 2.5 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU3.1-20 | 5 | 2.2 - 3.1 | 200 | 3
ABB3200C03.01 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 200 | 3 | 35 | 200 | 3 | 0.75 | 3.7 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU5.0 | 5 | 3.5 - 5.0 | 200 | 3
ABB3200C03.02 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 200 | 3 | 35 | 200 | 3 | 0.75 | 3.7 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU5.0-20 | 5 | 3.5 - 5.0 | 200 | 3
ABB3200C04.01 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 200 | 3 | 35 | 200 | 3 | 0.75 | 3.7 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU5.0 | 5 | 3.5 - 5.0 | 200 | 3
ABB3200C04.02 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 200 | 3 | 35 | 200 | 3 | 0.75 | 3.7 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU5.0-20 | 5 | 3.5 - 5.0 | 200 | 3
ABB3200C05.01 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 200 | 3 | 35 | 200 | 3 | 1 | 4.8 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU6.5 | 5 | 4.5 - 6.5 | 200 | 3
ABB3200C05.02 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 200 | 3 | 35 | 200 | 3 | 1 | 4.8 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU6.5-20 | 5 | 4.5 - 6.5 | 200 | 3
ABB3200C06.01 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 200 | 3 | 35 | 200 | 3 | 1 | 4.8 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU6.5 | 5 | 4.5 - 6.5 | 200 | 3
ABB3200C06.02 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 200 | 3 | 35 | 200 | 3 | 1 | 4.8 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU6.5-20 | 5 | 4.5 - 6.5 | 200 | 3
ABB3200C07.01 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 200 | 3 | 35 | 200 | 3 | 1.5 | 6.9 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5 | 5 | 6.0 - 8.5 | 200 | 3
ABB3200C07.02 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 200 | 3 | 35 | 200 | 3 | 1.5 | 6.9 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5-20 | 5 | 6.0 - 8.5 | 200 | 3
ABB3200C08.01 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 200 | 3 | 35 | 200 | 3 | 1.5 | 6.9 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5 | 5 | 6.0 - 8.5 | 200 | 3
ABB3200C08.02 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 200 | 3 | 35 | 200 | 3 | 1.5 | 6.9 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5-20 | 5 | 6.0 - 8.5 | 200 | 3
ABB3200C09.01 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 200 | 3 | 35 | 200 | 3 | 2 | 7.8 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11 | 5 | 7.5 - 11 | 200 | 3
ABB3200C09.02 | C | CB | ABB Sace | S3L015TW | 150 | 15 | 200 | 3 | 35 | 200 | 3 | 2 | 7.8 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11-20 | 5 | 7.5 - 11 | 200 | 3
ABB3200C10.01 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 200 | 3 | 35 | 200 | 3 | 2 | 7.8 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11 | 5 | 7.5 - 11 | 200 | 3
ABB3200C10.02 | C | CB | ABB Sace | T2S015TW | 65 | 15 | 200 | 3 | 35 | 200 | 3 | 2 | 7.8 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11-20 | 5 | 7.5 - 11 | 200 | 3
ABB3200C11.01 | C | CB | ABB Sace | S3L020TW | 150 | 20 | 200 | 3 | 35 | 200 | 3 | 3 | 11 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14 | 5 | 10 - 14.0 | 200 | 3
ABB3200C11.02 | C | CB | ABB Sace | S3L020TW | 150 | 20 | 200 | 3 | 35 | 200 | 3 | 3 | 11 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14-20 | 5 | 10 - 14.0 | 200 | 3
ABB3200C12.01 | C | CB | ABB Sace | T2S020TW | 65 | 20 | 200 | 3 | 35 | 200 | 3 | 3 | 11 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14 | 5 | 10 - 14.0 | 200 | 3
ABB3200C12.02 | C | CB | ABB Sace | T2S020TW | 65 | 20 | 200 | 3 | 35 | 200 | 3 | 3 | 11 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14-20 | 5 | 10 - 14.0 | 200 | 3
ABB3200C13.01 | C | CB | ABB Sace | S3L030TW | 150 | 30 | 200 | 3 | 35 | 200 | 3 | 3 | 11 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14 | 5 | 10 - 14.0 | 200 | 3
ABB3200C13.02 | C | CB | ABB Sace | S3L030TW | 150 | 30 | 200 | 3 | 35 | 200 | 3 | 3 | 11 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14-20 | 5 | 10 - 14.0 | 200 | 3
ABB3200C14.01 | C | CB | ABB Sace | T2S030TW | 65 | 30 | 200 | 3 | 35 | 200 | 3 | 3 | 11 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14 | 5 | 10 - 14.0 | 200 | 3
ABB3200C14.02 | C | CB | ABB Sace | T2S030TW | 65 | 30 | 200 | 3 | 35 | 200 | 3 | 3 | 11 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14-20 | 5 | 10 - 14.0 | 200 | 3
ABB3200C15.01 | C | CB | ABB Sace | S3L040TW | 150 | 40 | 200 | 3 | 35 | 200 | 3 | 5 | 17.5 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19 | 5 | 13 - 19 | 200 | 3
ABB3200C15.02 | C | CB | ABB Sace | S3L040TW | 150 | 40 | 200 | 3 | 35 | 200 | 3 | 5 | 17.5 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19-20 | 5 | 13 - 19 | 200 | 3
ABB3200C16.01 | C | CB | ABB Sace | T2S030TW | 65 | 30 | 200 | 3 | 35 | 200 | 3 | 5 | 17.5 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19 | 5 | 13 - 19 | 200 | 3
ABB3200C16.02 | C | CB | ABB Sace | T2S030TW | 65 | 30 | 200 | 3 | 35 | 200 | 3 | 5 | 17.5 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19-20 | 5 | 13 - 19 | 200 | 3
ABB3200C17.01 | C | CB | ABB Sace | S3L040TW | 150 | 40 | 200 | 3 | 35 | 200 | 3 | 7.5 | 25.3 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32 | 5 | 24 - 32 | 200 | 3
ABB3200C17.02 | C | CB | ABB Sace | S3L040TW | 150 | 40 | 200 | 3 | 35 | 200 | 3 | 7.5 | 25.3 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32-20 | 5 | 24 - 32 | 200 | 3
ABB3200C18.01 | C | CB | ABB Sace | T2S030TW | 65 | 30 | 200 | 3 | 35 | 200 | 3 | 7.5 | 25.3 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32 | 5 | 24 - 32 | 200 | 3
ABB3200C18.02 | C | CB | ABB Sace | T2S030TW | 65 | 30 | 200 | 3 | 35 | 200 | 3 | 7.5 | 25.3 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32-20 | 5 | 24 - 32 | 200 | 3
ABB3200C19.01 | C | CB | ABB Sace | S3L050TW | 150 | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 200 | 3
ABB3200C19.02 | C | CB | ABB Sace | S3L050TW | 150 | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 200 | 3
ABB3200C20.01 | C | CB | ABB Sace | T2S050TW | 65 | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 200 | 3
ABB3200C20.02 | C | CB | ABB Sace | T2S050TW | 65 | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 200 | 3
ABB3200C21.01 | C | CB | ABB Sace | TS3L050TW | 65 | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 200 | 3
ABB3200C21.02 | C | CB | ABB Sace | TS3L050TW | 65 | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 200 | 3
ABB3200C22.01 | C | CB | ABB Sace | S3L050TW | 150 | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 200 | 3
ABB3200C22.02 | C | CB | ABB Sace | S3L050TW | 150 | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 200 | 3
ABB3200C23.01 | C | CB | ABB Sace | T2S050TW | 65 | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 200 | 3
ABB3200C23.02 | C | CB | ABB Sace | T2S050TW | 65 | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 200 | 3
ABB3200C24.01 | C | CB | ABB Sace | TS3L050TW | 65 | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 200 | 3
ABB3200C24.02 | C | CB | ABB Sace | TS3L050TW | 65 | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1344 | 1 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 200 | 3
ABB3200C25.01 | C | CB | ABB Sace | S3L070TW | 150 | 70 | 200 | 3 | 85 | 200 | 3 | 15 | 48.3 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU52 | 5 | 36 - 52 | 200 | 3
ABB3200C25.02 | C | CB | ABB Sace | S3L070TW | 150 | 70 | 200 | 3 | 85 | 200 | 3 | 15 | 48.3 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU52-20 | 5 | 36 - 52 | 200 | 3
ABB3200C26.01 | C | CB | ABB Sace | T4H080TW | 65 | 80 | 200 | 3 | 85 | 200 | 3 | 15 | 48.3 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU52 | 5 | 36 - 52 | 200 | 3
ABB3200C26.02 | C | CB | ABB Sace | T4H080TW | 65 | 80 | 200 | 3 | 85 | 200 | 3 | 15 | 48.3 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU52-20 | 5 | 36 - 52 | 200 | 3
ABB3200C27.01 | C | CB | ABB Sace | TS3L080TW | 150 | 80 | 200 | 3 | 85 | 200 | 3 | 15 | 48.3 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU52 | 5 | 36 - 52 | 200 | 3
ABB3200C27.02 | C | CB | ABB Sace | TS3L080TW | 150 | 80 | 200 | 3 | 85 | 200 | 3 | 15 | 48.3 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU52-20 | 5 | 36 - 52 | 200 | 3
ABB3200C28.01 | C | CB | ABB Sace | S3L100TW | 150 | 100 | 200 | 3 | 85 | 200 | 3 | 20 | 62.1 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 200 | 3
ABB3200C28.02 | C | CB | ABB Sace | S3L100TW | 150 | 100 | 200 | 3 | 85 | 200 | 3 | 20 | 62.1 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 200 | 3
ABB3200C29.01 | C | CB | ABB Sace | T4H100TW | 150 | 100 | 200 | 3 | 85 | 200 | 3 | 20 | 62.1 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 200 | 3
ABB3200C29.02 | C | CB | ABB Sace | T4H100TW | 150 | 100 | 200 | 3 | 85 | 200 | 3 | 20 | 62.1 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 200 | 3
ABB3200C30.01 | C | CB | ABB Sace | TS3L100TW | 150 | 100 | 200 | 3 | 85 | 200 | 3 | 20 | 62.1 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 200 | 3
ABB3200C30.02 | C | CB | ABB Sace | TS3L100TW | 150 | 100 | 200 | 3 | 85 | 200 | 3 | 20 | 62.1 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 200 | 3
ABB3200C31.01 | C | CB | ABB Sace | S3L125TW | 150 | 125 | 200 | 3 | 85 | 200 | 3 | 25 | 78.2 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 200 | 3
ABB3200C31.02 | C | CB | ABB Sace | S3L125TW | 150 | 125 | 200 | 3 | 85 | 200 | 3 | 25 | 78.2 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 200 | 3
ABB3200C32.01 | C | CB | ABB Sace | T4H125TW | 150 | 125 | 200 | 3 | 85 | 200 | 3 | 25 | 78.2 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 200 | 3
ABB3200C32.02 | C | CB | ABB Sace | T4H125TW | 150 | 125 | 200 | 3 | 85 | 200 | 3 | 25 | 78.2 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 200 | 3
ABB3200C33.01 | C | CB | ABB Sace | TS3L125TW | 150 | 125 | 200 | 3 | 85 | 200 | 3 | 25 | 78.2 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 200 | 3
ABB3200C33.02 | C | CB | ABB Sace | TS3L125TW | 150 | 125 | 200 | 3 | 85 | 200 | 3 | 25 | 78.2 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 200 | 3
ABB3200C34.01 | C | CB | ABB Sace | S3L150TW | 150 | 150 | 200 | 3 | 85 | 200 | 3 | 30 | 92 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A110 | 10 | 110 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA110DU110 | 5 | 80 - 110 | 200 | 3
ABB3200C35.01 | C | CB | ABB Sace | T4L150TW | 200 | 150 | 200 | 3 | 85 | 200 | 3 | 30 | 92 | 2560 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A110 | 10 | 110 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA110DU110 | 5 | 80 - 110 | 200 | 3
ABB3200C36.01 | C | CB | ABB Sace | S3L200TW | 150 | 200 | 200 | 3 | 65 | 200 | 3 | 40 | 120 | 4800 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A145 | 10 | 130 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA200DU135 | 5 | 100 - 135 | 200 | 3
ABB3200C37.01 | C | CB | ABB Sace | T4L200TW | 200 | 200 | 200 | 3 | 65 | 200 | 3 | 40 | 120 | 4800 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A145 | 10 | 130 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA200DU135 | 5 | 100 - 135 | 200 | 3
ABB3200C38.01 | C | CB | ABB Sace | S4N250TW | 200 | 250 | 200 | 3 | 85 | 200 | 3 | 50 | 150 | 4800 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A185 | 10 | 156 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA200DU175 | 5 | 130 - 175 | 200 | 3
ABB3200C39.01 | C | CB | ABB Sace | T4L250TW | 200 | 250 | 200 | 3 | 85 | 200 | 3 | 50 | 150 | 4800 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A185 | 10 | 156 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA200DU175 | 5 | 130 - 175 | 200 | 3
ABB3200C40.01 | C | CB | ABB Sace | S5N300TW | 200 | 300 | 200 | 3 | 85 | 200 | 3 | 60 | 177 | 9000 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A210 | 10 | 192 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU310 | 5 | 220 - 310 | 200 | 3
ABB3200C41.01 | C | CB | ABB Sace | T5L300TW | 200 | 300 | 200 | 3 | 85 | 200 | 3 | 60 | 177 | 9000 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A210 | 10 | 192 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU310 | 5 | 220 - 310 | 200 | 3
ABB3200C42.01 | C | CB | ABB Sace | S5N400TW | 200 | 400 | 200 | 3 | 85 | 200 | 3 | 75 | 221 | 9000 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A260 | 18 | 248 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU310 | 5 | 220 - 310 | 200 | 3
ABB3200C43.01 | C | CB | ABB Sace | T5L400TW | 200 | 400 | 200 | 3 | 85 | 200 | 3 | 75 | 221 | 9000 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A260 | 18 | 248 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU310 | 5 | 220 - 310 | 200 | 3
ABB3200C44.01 | C | CB | ABB Sace | S5N400TW | 200 | 400 | 200 | 3 | 85 | 200 | 3 | 100 | 285 | 9000 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A300 | 18 | 302 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU310 | 5 | 220 - 310 | 200 | 3
ABB3200C45.01 | C | CB | ABB Sace | T5L400TW | 200 | 400 | 200 | 3 | 85 | 200 | 3 | 100 | 285 | 9000 | 1 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A300 | 18 | 302 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU310 | 5 | 220 - 310 | 200 | 3
Conditions of Acceptability:
|  | 1 | All of the specified individual components of the combination motor controller have been installed in an enclosure having
a specified internal volume in cubic inches. Additional testing of the combination motor controller is not required when
installed in an enclosure having the same or larger volume.
|  | 2 | When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from
the overcurrent protective devices and other components shall not be installed in this area.
|  | 3 | When specified, the overload relay heater table number shall be provided with the equipment.
|  | 4 | Unless otherwise specified, all connections between components are made with insulated wire having at least an ampacity of
100 percent of the rated motor current and connected to the terminals supplied with the individual components.
|  | 5 | The need for cautionary markings applicable to high fault short circuit current ratings, Type D a combination motor
controllers shall be considered in the end-product application.
|  | 6 | The TA450 overload relay requires the use of a mounting kit if mounted to the contactor. See the manufactures specifications.

## ABB - 200V - TYPE D
Issued: 2009-09-22
Last Revised: 2009-09-22
ID Number | Combination Type | Component Type | Component Manufactuer | Component Catalog Desgination | Component Ratings |  |  |  | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in.) | Conditions of Acceptability | Combination UL File Reference
[5 empty] | kA | Max Amps | Volts | Poles
ABB3200D01.01 | D | ICB | ABB Sace | S3L005MW | - | 5 | 200 | 3 | 35 | 200 | 3 | 0.5 | 2.5 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU3.1 | 5 | 2.2 - 3.1 | 200 | 3
ABB3200D01.02 | D | ICB | ABB Sace | S3L005MW | - | 5 | 200 | 3 | 35 | 200 | 3 | 0.5 | 2.5 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU3.1-20 | 5 | 2.2 - 3.1 | 200 | 3
ABB3200D02.01 | D | ICB | ABB Sace | TS3L005MW | - | 5 | 200 | 3 | 35 | 200 | 3 | 0.5 | 2.5 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU3.1 | 5 | 2.2 - 3.1 | 200 | 3
ABB3200D02.02 | D | ICB | ABB Sace | TS3L005MW | - | 5 | 200 | 3 | 35 | 200 | 3 | 0.5 | 2.5 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU3.1-20 | 5 | 2.2 - 3.1 | 200 | 3
ABB3200D03.01 | D | ICB | ABB Sace | S3L005MW | - | 5 | 200 | 3 | 35 | 200 | 3 | 0.75 | 3.7 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU5.0 | 5 | 3.5 - 5.0 | 200 | 3
ABB3200D03.02 | D | ICB | ABB Sace | S3L005MW | - | 5 | 200 | 3 | 35 | 200 | 3 | 0.75 | 3.7 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU5.0-20 | 5 | 3.5 - 5.0 | 200 | 3
ABB3200D04.01 | D | ICB | ABB Sace | TS3L005MW | - | 5 | 200 | 3 | 35 | 200 | 3 | 0.75 | 3.7 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU5.0 | 5 | 3.5 - 5.0 | 200 | 3
ABB3200D04.02 | D | ICB | ABB Sace | TS3L005MW | - | 5 | 200 | 3 | 35 | 200 | 3 | 0.75 | 3.7 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU5.0-20 | 5 | 3.5 - 5.0 | 200 | 3
ABB3200D05.01 | D | ICB | ABB Sace | S3L010MW | - | 10 | 200 | 3 | 35 | 200 | 3 | 1 | 4.8 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU6.5 | 5 | 4.5 - 6.5 | 200 | 3
ABB3200D05.02 | D | ICB | ABB Sace | S3L010MW | - | 10 | 200 | 3 | 35 | 200 | 3 | 1 | 4.8 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU6.5-20 | 5 | 4.5- 6.5 | 200 | 3
ABB3200D06.01 | D | ICB | ABB Sace | TS3L010MW | - | 10 | 200 | 3 | 35 | 200 | 3 | 1 | 4.8 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU6.5 | 5 | 4.5 - 6.5 | 200 | 3
ABB3200D06.02 | D | ICB | ABB Sace | TS3L010MW | - | 10 | 200 | 3 | 35 | 200 | 3 | 1 | 4.8 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU6.5-20 | 5 | 4.5- 6.5 | 200 | 3
ABB3200D07.01 | D | ICB | ABB Sace | S3L010MW | - | 10 | 200 | 3 | 35 | 200 | 3 | 1.5 | 6.9 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5 | 5 | 6.0 - 8.5 | 200 | 3
ABB3200D07.02 | D | ICB | ABB Sace | S3L010MW | - | 10 | 200 | 3 | 35 | 200 | 3 | 1.5 | 6.9 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5-20 | 5 | 6.0 - 8.5 | 200 | 3
ABB3200D08.01 | D | ICB | ABB Sace | TS3L010MW | - | 10 | 200 | 3 | 35 | 200 | 3 | 1.5 | 6.9 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5 | 5 | 6.0 - 8.5 | 200 | 3
ABB3200D08.02 | D | ICB | ABB Sace | TS3L010MW | - | 10 | 200 | 3 | 35 | 200 | 3 | 1.5 | 6.9 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU8.5-20 | 5 | 6.0 - 8.5 | 200 | 3
ABB3200D09.01 | D | ICB | ABB Sace | S3L010MW | - | 10 | 200 | 3 | 35 | 200 | 3 | 2 | 7.8 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11 | 5 | 7.5 - 11 | 200 | 3
ABB3200D09.02 | D | ICB | ABB Sace | S3L010MW | - | 10 | 200 | 3 | 35 | 200 | 3 | 2 | 7.8 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11-20 | 5 | 7.5 - 11 | 200 | 3
ABB3200D10.01 | D | ICB | ABB Sace | TS3L010MW | - | 10 | 200 | 3 | 35 | 200 | 3 | 2 | 7.8 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11 | 5 | 7.5 - 11 | 200 | 3
ABB3200D10.02 | D | ICB | ABB Sace | TS3L010MW | - | 10 | 200 | 3 | 35 | 200 | 3 | 2 | 7.8 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A9 | 5 | 9 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU11-20 | 5 | 7.5 - 11 | 200 | 3
ABB3200D11.01 | D | ICB | ABB Sace | S3L025MW | - | 25 | 200 | 3 | 35 | 200 | 3 | 3 | 11 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14 | 5 | 10 - 14.0 | 200 | 3
ABB3200D11.02 | D | ICB | ABB Sace | S3L025MW | - | 25 | 200 | 3 | 35 | 200 | 3 | 3 | 11 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14-20 | 5 | 10 - 14.0 | 200 | 3
ABB3200D12.01 | D | ICB | ABB Sace | TS3L025MW | - | 25 | 200 | 3 | 35 | 200 | 3 | 3 | 11 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14 | 5 | 10 - 14.0 | 200 | 3
ABB3200D12.02 | D | ICB | ABB Sace | TS3L025MW | - | 25 | 200 | 3 | 35 | 200 | 3 | 3 | 11 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A12 | 5 | 11 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14-20 | 5 | 10 - 14.0 | 200 | 3
ABB3200D13.01 | D | ICB | ABB Sace | S3L025MW | - | 25 | 200 | 3 | 35 | 200 | 3 | 3 | 11 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14 | 5 | 10 - 14.0 | 200 | 3
ABB3200D13.02 | D | ICB | ABB Sace | S3L025MW | - | 25 | 200 | 3 | 35 | 200 | 3 | 3 | 11 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14-20 | 5 | 10 - 14.0 | 200 | 3
ABB3200D14.01 | D | ICB | ABB Sace | TS3L025MW | - | 25 | 200 | 3 | 35 | 200 | 3 | 3 | 11 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14 | 5 | 10 - 14.0 | 200 | 3
ABB3200D14.02 | D | ICB | ABB Sace | TS3L025MW | - | 25 | 200 | 3 | 35 | 200 | 3 | 3 | 11 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A16 | 5 | 17 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU14-20 | 5 | 10 - 14.0 | 200 | 3
ABB3200D15.01 | D | ICB | ABB Sace | S3L050MW | - | 50 | 200 | 3 | 35 | 200 | 3 | 5 | 17.5 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19 | 5 | 13 - 19 | 200 | 3
ABB3200D15.02 | D | ICB | ABB Sace | S3L050MW | - | 50 | 200 | 3 | 35 | 200 | 3 | 5 | 17.5 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19-20 | 5 | 13 - 19 | 200 | 3
ABB3200D16.01 | D | ICB | ABB Sace | T2S050MW | - | 50 | 200 | 3 | 35 | 200 | 3 | 5 | 17.5 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19 | 5 | 13 - 19 | 200 | 3
ABB3200D16.02 | D | ICB | ABB Sace | T2S050MW | - | 50 | 200 | 3 | 35 | 200 | 3 | 5 | 17.5 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU19-20 | 5 | 13 - 19 | 200 | 3
ABB3200D17.01 | D | ICB | ABB Sace | S3L050MW | - | 50 | 200 | 3 | 35 | 200 | 3 | 7.5 | 25.3 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32 | 5 | 24 - 32 | 200 | 3
ABB3200D17.02 | D | ICB | ABB Sace | S3L050MW | - | 50 | 200 | 3 | 35 | 200 | 3 | 7.5 | 25.3 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32-20 | 5 | 24 - 32 | 200 | 3
ABB3200D18.01 | D | ICB | ABB Sace | T2S050MW | - | 50 | 200 | 3 | 35 | 200 | 3 | 7.5 | 25.3 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32 | 5 | 24 - 32 | 200 | 3
ABB3200D18.02 | D | ICB | ABB Sace | T2S050MW | - | 50 | 200 | 3 | 35 | 200 | 3 | 7.5 | 25.3 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A26 | 5 | 28 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA25DU32-20 | 5 | 24 - 32 | 200 | 3
ABB3200D19.01 | D | ICB | ABB Sace | S3L050MW | - | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 200 | 3
ABB3200D19.02 | D | ICB | ABB Sace | S3L050MW | - | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 200 | 3
ABB3200D20.01 | D | ICB | ABB Sace | T4H050MW | - | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 200 | 3
ABB3200D20.02 | D | ICB | ABB Sace | T4H050MW | - | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 200 | 3
ABB3200D21.01 | D | ICB | ABB Sace | TS3L050MW | - | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 200 | 3
ABB3200D21.02 | D | ICB | ABB Sace | TS3L050MW | - | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A30 | 5 | 34 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 200 | 3
ABB3200D22.01 | D | ICB | ABB Sace | S3L050MW | - | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 200 | 3
ABB3200D22.02 | D | ICB | ABB Sace | S3L050MW | - | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 200 | 3
ABB3200D23.01 | D | ICB | ABB Sace | T4H050MW | - | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 200 | 3
ABB3200D23.02 | D | ICB | ABB Sace | T4H050MW | - | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 200 | 3
ABB3200D24.01 | D | ICB | ABB Sace | TS3L050MW | - | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42 | 5 | 29 - 42 | 200 | 3
ABB3200D24.02 | D | ICB | ABB Sace | TS3L050MW | - | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1344 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A40 | 5 | 42 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA42DU42-20 | 5 | 29 - 42 | 200 | 3
ABB3200D25.01 | D | ICB | ABB Sace | S3L100MW | - | 100 | 200 | 3 | 85 | 200 | 3 | 15 | 48.3 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63 | 5 | 45 - 63 | 200 | 3
ABB3200D25.02 | D | ICB | ABB Sace | S3L100MW | - | 100 | 200 | 3 | 85 | 200 | 3 | 15 | 48.3 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63-20 | 5 | 45 - 63 | 200 | 3
ABB3200D26.01 | D | ICB | ABB Sace | T4H100MW | - | 100 | 200 | 3 | 85 | 200 | 3 | 15 | 48.3 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63 | 5 | 45 - 63 | 200 | 3
ABB3200D26.02 | D | ICB | ABB Sace | T4H100MW | - | 100 | 200 | 3 | 85 | 200 | 3 | 15 | 48.3 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63-20 | 5 | 45 - 63 | 200 | 3
ABB3200D27.01 | D | ICB | ABB Sace | TS3L100MW | - | 100 | 200 | 3 | 85 | 200 | 3 | 15 | 48.3 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63 | 5 | 45 - 63 | 200 | 3
ABB3200D27.02 | D | ICB | ABB Sace | TS3L100MW | - | 100 | 200 | 3 | 85 | 200 | 3 | 15 | 48.3 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A50 | 5 | 54 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU63-20 | 5 | 45 - 63 | 200 | 3
ABB3200D28.01 | D | ICB | ABB Sace | S3L100MW | - | 100 | 200 | 3 | 85 | 200 | 3 | 20 | 62.1 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 200 | 3
ABB3200D28.02 | D | ICB | ABB Sace | S3L100MW | - | 100 | 200 | 3 | 85 | 200 | 3 | 20 | 62.1 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 200 | 3
ABB3200D29.01 | D | ICB | ABB Sace | T4L100MW | - | 100 | 200 | 3 | 85 | 200 | 3 | 20 | 62.1 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 200 | 3
ABB3200D29.02 | D | ICB | ABB Sace | T4L100MW | - | 100 | 200 | 3 | 85 | 200 | 3 | 20 | 62.1 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A63 | 10 | 65 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 200 | 3
ABB3200D30.01 | D | ICB | ABB Sace | S3L150MW | - | 150 | 200 | 3 | 85 | 200 | 3 | 25 | 78.2 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 200 | 3
ABB3200D30.02 | D | ICB | ABB Sace | S3L150MW | - | 150 | 200 | 3 | 85 | 200 | 3 | 25 | 78.2 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 200 | 3
ABB3200D31.01 | D | ICB | ABB Sace | T4L150MW | - | 150 | 200 | 3 | 85 | 200 | 3 | 25 | 78.2 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80 | 5 | 60 - 80 | 200 | 3
ABB3200D31.02 | D | ICB | ABB Sace | T4L150MW | - | 150 | 200 | 3 | 85 | 200 | 3 | 25 | 78.2 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB France | A75 | 10 | 80 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA75DU80-20 | 5 | 60 - 80 | 200 | 3
ABB3200D32.01 | D | ICB | ABB Sace | S4L250MW | - | 250 | 200 | 3 | 85 | 200 | 3 | 30 | 92 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A110 | 10 | 110 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA110DU110 | 5 | 80 - 110 | 200 | 3
ABB3200D33.01 | D | ICB | ABB Sace | T4L150MW | - | 150 | 200 | 3 | 85 | 200 | 3 | 30 | 92 | 2560 | 1,5 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A110 | 10 | 110 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA110DU110 | 5 | 80 - 110 | 200 | 3
ABB3200D34.01 | D | ICB | ABB Sace | S4N250MW | - | 250 | 200 | 3 | 65 | 200 | 3 | 40 | 120 | 4800 | 1,5 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A145 | 10 | 130 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA200DU135 | 5 | 100 - 135 | 200 | 3
ABB3200D35.01 | D | ICB | ABB Sace | T4L200MW | - | 200 | 200 | 3 | 65 | 200 | 3 | 40 | 120 | 4800 | 1,5 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A145 | 10 | 130 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA200DU135 | 5 | 100 - 135 | 200 | 3
ABB3200D36.01 | D | ICB | ABB Sace | S4N250MW | - | 250 | 200 | 3 | 85 | 200 | 3 | 50 | 150 | 4800 | 1,5 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A185 | 10 | 156 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA200DU175 | 5 | 130 - 175 | 200 | 3
ABB3200D37.01 | D | ICB | ABB Sace | T4L250MW | - | 250 | 200 | 3 | 85 | 200 | 3 | 50 | 150 | 4800 | 1,5 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A185 | 10 | 156 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA200DU175 | 5 | 130 - 175 | 200 | 3
ABB3200D38.01 | D | ICB | ABB Sace | S4N250MW | - | 250 | 200 | 3 | 85 | 200 | 3 | 60 | 177 | 9000 | 1,5,6 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A210 | 10 | 192 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU235 | 5 | 165 - 235 | 200 | 3
ABB3200D39.01 | D | ICB | ABB Sace | T5L300MW | - | 300 | 200 | 3 | 85 | 200 | 3 | 60 | 177 | 9000 | 1,5,6 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A210 | 10 | 192 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU235 | 5 | 165 - 235 | 200 | 3
ABB3200D40.01 | D | ICB | ABB Sace | S5N400MW | - | 400 | 200 | 3 | 85 | 200 | 3 | 75 | 221 | 9000 | 1,5,6 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A260 | 18 | 248 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU310 | 5 | 220 - 310 | 200 | 3
ABB3200D41.01 | D | ICB | ABB Sace | T5L400MW | - | 400 | 200 | 3 | 85 | 200 | 3 | 75 | 221 | 9000 | 1,5,6 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A260 | 18 | 248 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU310 | 5 | 220 - 310 | 200 | 3
ABB3200D42.01 | D | ICB | ABB Sace | S5N400TW | - | 400 | 200 | 3 | 85 | 200 | 3 | 100 | 285 | 9000 | 1,5,6 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A300 | 18 | 302 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU310 | 5 | 220 - 310 | 200 | 3
ABB3200D43.01 | D | ICB | ABB Sace | T5L400MW | - | 400 | 200 | 3 | 85 | 200 | 3 | 100 | 285 | 9000 | 1,5,6 | E193298 V1 S1
|  | MC | ABB AB, CEWE-Control | A300 | 18 | 302 | 200 | 3
|  | OLR | ABB Stotz-Kontakt | TA450DU310 | 5 | 220 - 310 | 200 | 3
Conditions of Acceptability:
|  | 1 | All of the specified individual components of the combination motor controller have been installed in an enclosure having
a specified internal volume in cubic inches. Additional testing of the combination motor controller is not required when
installed in an enclosure having the same or larger volume.
|  | 2 | When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from
the overcurrent protective devices and other components shall not be installed in this area.
|  | 3 | When specified, the overload relay heater table number shall be provided with the equipment.
|  | 4 | Unless otherwise specified, all connections between components are made with insulated wire having at least an ampacity of
100 percent of the rated motor current and connected to the terminals supplied with the individual components.
|  | 5 | The need for cautionary markings applicable to high fault short circuit current ratings, Type D a combination motor
controllers shall be considered in the end-product application.
|  | 6 | The TA450 overload relay requires the use of a mounting kit if mounted to the contactor. See the manufactures specifications.