## Advantage Type C
Issued: 2006-05-18
Last Revised: 2006-05-18
Combination Motor Controllers for use in Industrial Control Panels
ID Number | Combination Type | Individual Component | [6 empty] | Combination SCCR | [5 empty] | Conditions of Acceptability | Combination Starter UL File | Motor Control Center UL File
|  | Component Type | Manufacturer | Patial Catalog Nos. | Ratings |  |  |  | SCCR kA | Volts | Phase | Hp | NEC FLC | Min. Enclosure Volume (cu. ft.)
[5 empty] | SCCR kA | Max. Amps | Volts | No. Poles
ADC0001 | C | CB | Eaton | HFD3015L | 65 | 15 | 200 | 3 | 65 | 200 | 3 | 1 | 4.8 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200MLCFC | 5 | 27
ADC0002 |  | CB | Eaton | HFD3015L | 65 | 15 | 230 |  |  | 230 |  | 1 | 4.2
|  | STR |  | W200MLCFC | 5 | 27
ADC0003 | C | CB | Eaton | HFD3015L | 65 | 15 | 460 | 3 | 65 | 460 | 3 | 3 | 4.8 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200MLCFC | 5 | 27
ADC0004 |  | CB | Eaton | HFD3015L | 25 | 15 | 575 |  | 25 | 575 |  | 3 | 3.9 |  | (1) (5) (6a) (7a)
|  | STR |  | W200MLCFC | 5 | 27
ADC0005 | C | CB | Eaton | FDC3015L | 100 | 15 | 200 | 3 | 100 | 200 | 3 | 1 | 4.8 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200MLCFC | 5 | 27
ADC0006 |  | CB | Eaton | FDC3015L | 100 | 15 | 230 |  |  | 230 |  | 1 | 4.2
|  | STR |  | W200MLCFC | 5 | 27
ADC0007 | C | CB | Eaton | FDC3015L | 100 | 15 | 460 | 3 | 100 | 469 | 3 | 3 | 4.8 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200MLCFC | 5 | 27
ADC0008 |  | CB | Eaton | FDC3015L | 35 | 15 | 575 |  | 35 | 575 |  | 3 | 3.9 |  | (1) (5) (6a) (7a)
|  | STR |  | W200MLCFC | 5 | 27
ADC0009 | C | CB | Eaton | EGH3015FFG | 65 | 15 | 200 | 3 | 65 | 200 | 3 | 1 | 4.8 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200MLCFC | 5 | 27
ADC0010 |  | CB | Eaton | EGH3015FFG | 65 | 15 | 230 |  |  | 230 |  | 1 | 4.2
|  | STR |  | W200MLCFC | 5 | 27
ADC0011 |  | CB | Eaton | EGH3015FFG | 65 | 15 | 460 |  |  | 460 |  | 3 | 4.8
|  | STR |  | W200MLCFC | 5 | 27
ADC0012 | C | CB | Eaton | HFD3015L | 65 | 15 | 200 | 3 | 100 | 200 | 3 | 1 | 4.8 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200kA | 70
|  | STR |  | W200MLCFC | 5 | 27
ADC0013 | C | CB | Eaton | HFD3015L | 65 | 15 | 230 |  |  | 230 |  | 1 | 4.2
|  | C. Limiter |  | LFD3070R | 200kA | 70
|  | STR |  | W200MLCFC | 5 | 27
ADC0014 | C | CB | Eaton | HFD3015L | 65 | 15 | 460 | 3 | 100 | 460 | 3 | 3 | 4.8 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200kA | 70
|  | STR |  | W200MLCFC | 5 | 27
ADC0015 | C | CB | Eaton | HFD3015L | 65 | 15 | 575 |  |  | 575 |  | 3 | 3.9 |  | (1) (5) (6a) (7a)
|  | C. Limiter |  | LFD3070R | 200kA | 70
|  | STR |  | W200MLCFC | 5 | 27
ADC0016 | C | CB | Eaton | HFD3015L | 65 | 15 | 200 | 3 | 65 | 200 | 3 | 1 | 4.8 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M1CFC | 5 | 27
ADC0017 |  | CB | Eaton | HFD3015L | 65 | 15 | [5 empty] | 3 | 11
|  | STR |  | W200M1CFC | 5 | 27
ADC0018 |  | CB | Eaton | HFD3030L | 65 | 30 | [5 empty] | 5 | 17.5
|  | STR |  | W200M1CFC | 5 | 27
ADC0019 |  | CB | Eaton | HFD3050L | 65 | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | W200M1CFC | 5 | 27
ADC0020 | C | CB | Eaton | HFD3015L | 65 | 15 | 230 | 3 | 65 | 230 | 3 | 1 | 4.2 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M1CFC | 5 | 27
ADC0021 |  | CB | Eaton | HFD3015L | 65 | 15 | [5 empty] | 3 | 9.6
|  | STR |  | W200M1CFC | 5 | 27
ADC0022 |  | CB | Eaton | HFD3030L | 65 | 30 | [5 empty] | 5 | 15.2
|  | STR |  | W200M1CFC | 5 | 27
ADC0023 |  | CB | Eaton | HFD3050L | 65 | 50 | [5 empty] | 7.5 | 22
|  | STR |  | W200M1CFC | 5 | 27
ADC0024 | C | CB | Eaton | HFD3015L | 65 | 15 | 460 | 3 | 65 | 460 | 3 | 3 | 4.8 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M1CFC | 5 | 27
ADC0025 |  | CB | Eaton | HFD3015L | 65 | 15 | [5 empty] | 5 | 7.6
|  | STR |  | W200M1CFC | 5 | 27
ADC0026 |  | CB | Eaton | HFD3030L | 65 | 30 | [5 empty] | 10 | 14
|  | STR |  | W200M1CFC | 5 | 27
ADC0027 | C | CB | Eaton | HFD3015L | 25 | 15 | 575 | 3 | 25 | 575 | 3 | 3 | 3.9 | 0.695 | (1) (5) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M1CFC | 5 | 27
ADC0028 |  | CB | Eaton | HFD3015L | 25 | 15 | [5 empty] | 5 | 6.1
|  | STR |  | W200M1CFC | 5 | 27
ADC0029 |  | CB | Eaton | HFD3015L | 25 | 15 | [5 empty] | 10 | 11
|  | STR |  | W200M1CFC | 5 | 27
ADC0030 | C | CB | Eaton | FDC3015L | 100 | 15 | 200 | 3 | 100 | 200 | 3 | 1 | 4.8 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M1CFC | 5 | 27
ADC0031 |  | CB | Eaton | FDC3015L | 100 | 15 | [5 empty] | 3 | 11
|  | STR |  | W200M1CFC | 5 | 27
ADC0032 |  | CB | Eaton | FDC3030L | 100 | 30 | [5 empty] | 5 | 17.5
|  | STR |  | W200M1CFC | 5 | 27
ADC0033 |  | CB | Eaton | FDC3050L | 100 | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | W200M1CFC | 5 | 27
ADC0034 | C | CB | Eaton | FDC3015L | 65 | 15 | 230 | 3 | 100 | 230 | 3 | 1 | 4.2 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M1CFC | 5 | 27
ADC0035 |  | CB | Eaton | FDC3015L | 100 | 15 | [5 empty] | 3 | 9.6
|  | STR |  | W200M1CFC | 5 | 27
ADC0036 |  | CB | Eaton | FDC3030L | 100 | 30 | [5 empty] | 5 | 15.2
|  | STR |  | W200M1CFC | 5 | 27
ADC0037 |  | CB | Eaton | FDC3050L | 100 | 50 | [5 empty] | 7.5 | 22
|  | STR |  | W200M1CFC | 5 | 27
ADC0038 | C | CB | Eaton | FDC3015L | 100 | 15 | 460 | 3 | 100 | 460 | 3 | 3 | 4.8 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M1CFC | 5 | 27
ADC0039 |  | CB | Eaton | FDC3015L | 100 | 15 | [5 empty] | 5 | 7.6
|  | STR |  | W200M1CFC | 5 | 27
ADC0040 |  | CB | Eaton | FDC3030L | 100 | 30 | [5 empty] | 10 | 14
|  | STR |  | W200M1CFC | 5 | 27
ADC0041 | C | CB | Eaton | FDC3015L | 35 | 15 | 575 | 3 | 35 | 575 | 3 | 3 | 3.9 | 0.695 | (1) (5) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M1CFC | 5 | 27
ADC0042 |  | CB | Eaton | FDC3015L | 35 | 15 | [5 empty] | 5 | 6.1
|  | STR |  | W200M1CFC | 5 | 27
ADC0043 |  | CB | Eaton | FDC3015L | 35 | 15 | [5 empty] | 10 | 11
|  | STR |  | W200M1CFC | 5 | 27
ADC0044 | C | CB | Eaton | EGH3015FFG | 65 | 15 | 200 | 3 | 65 | 200 | 3 | 1 | 4.8 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M1CFC | 5 | 27
ADC0045 |  | CB | Eaton | EGH3015FFG | 65 | 15 | [5 empty] | 3 | 11
|  | STR |  | W200M1CFC | 5 | 27
ADC0046 |  | CB | Eaton | EGH3030FFG | 65 | 30 | [5 empty] | 5 | 17.5
|  | STR |  | W200M1CFC | 5 | 27
ADC0047 |  | CB | Eaton | EGH3050FFG | 65 | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | W200M1CFC | 5 | 27
ADC0048 | C | CB | Eaton | EGH3015FFG | 65 | 15 | 230 | 3 | 65 | 230 | 3 | 1 | 4.2 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M1CFC | 5 | 27
ADC0049 |  | CB | Eaton | EGH3015FFG | 65 | 15 | [5 empty] | 3 | 9.6
|  | STR |  | W200M1CFC | 5 | 27
ADC0050 |  | CB | Eaton | EGH3030FFG | 65 | 30 | [5 empty] | 5 | 15.2
|  | STR |  | W200M1CFC | 5 | 27
ADC0051 |  | CB | Eaton | EGH3050FFG | 65 | 50 | [5 empty] | 7.5 | 22
|  | STR |  | W200M1CFC | 5 | 27
ADC0052 | C | CB | Eaton | EGH3015FFG | 65 | 15 | 460 | 3 | 65 | 460 | 3 | 3 | 4.8 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M1CFC | 5 | 27
ADC0053 |  | CB | Eaton | EGH3015FFG | 65 | 15 | [5 empty] | 5 | 7.6
|  | STR |  | W200M1CFC | 5 | 27
ADC0054 |  | CB | Eaton | EGH3030FFG | 65 | 30 | [5 empty] | 10 | 14
|  | STR |  | W200M1CFC | 5 | 27
ADC0055 | C | CB | Eaton | HFD3015L | 65 | 15 | 200 | 3 | 100 | 200 | 3 | 1 | 4.8 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200kA | 70
|  | STR |  | W200M1CFC | 5 | 27
ADC0056 |  | CB | Eaton | HFD3015L | 65 | 15 | [5 empty] | 3 | 11
|  | C. Limiter |  | LFD3070R | 200kA | 70
|  | STR |  | W200M1CFC | 5 | 27
ADC0057 |  | CB | Eaton | HFD3030L | 65 | 30 | [5 empty] | 5 | 17.5
|  | C. Limiter |  | LFD3070R | 200kA | 70
|  | STR |  | W200M1CFC | 5 | 27
ADC0058 |  | CB | Eaton | HFD3050L | 65 | 50 | [5 empty] | 7.5 | 25.3
|  | C. Limiter |  | LFD3070R | 200kA | 70
|  | STR |  | W200M1CFC | 5 | 27
ADC0059 | C | CB | Eaton | HFD3015L | 65 | 15 | 230 | 3 | 100 | 230 | 3 | 1 | 4.2 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200kA | 70
|  | STR |  | W200M1CFC | 5 | 27
ADC0060 |  | CB | Eaton | HFD3015L | 65 | 15 | [5 empty] | 3 | 9.6
|  | C. Limiter |  | LFD3070R | 200kA | 70
|  | STR |  | W200M1CFC | 5 | 27
ADC0061 |  | CB | Eaton | HFD3030L | 65 | 30 | [5 empty] | 5 | 15.2
|  | C. Limiter |  | LFD3070R | 200kA | 70
|  | STR |  | W200M1CFC | 5 | 27
ADC0062 |  | CB | Eaton | HFD3050L | 65 | 50 | [5 empty] | 7.5 | 22
|  | C. Limiter |  | LFD3070R | 200kA | 70
|  | STR |  | W200M1CFC | 5 | 27
ADC0063 | C | CB | Eaton | HFD3015L | 65 | 15 | 460 | 3 | 100 | 460 | 3 | 3 | 4.7 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1
|  | C. Limiter |  | LFD3070R | 200kA | 70
|  | STR |  | W200M1CFC | 5 | 27
ADC0064 |  | CB | Eaton | HFD3015L | 65 | 15 | [5 empty] | 5 | 7.6
|  | C. Limiter |  | LFD3070R | 200kA | 70
|  | STR |  | W200M1CFC | 5 | 27
ADC0065 |  | CB | Eaton | HFD3030L | 65 | 30 | [5 empty] | 10 | 14
|  | C. Limiter |  | LFD3070R | 200kA | 70
|  | STR |  | W200M1CFC | 5 | 27
ADC0066 | C | CB | Eaton | HFD3015L | 25 | 15 | 575 | 3 | 100 | 575 | 3 | 3 | 3.9 | 0.695 | (1) (5) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1
|  | C. Limiter |  | LFD3070R | 200kA | 70
|  | STR |  | W200M1CFC | 5 | 27
ADC0067 |  | CB | Eaton | HFD3015L | 25 | 15 | [5 empty] | 5 | 6.1
|  | C. Limiter |  | LFD3070R | 200kA | 70
|  | STR |  | W200M1CFC | 5 | 27
ADC0068 |  | CB | Eaton | HFD3015L | 25 | 15 | [5 empty] | 10 | 11
|  | C. Limiter |  | LFD3070R | 200kA | 70
|  | STR |  | W200M1CFC | 5 | 27
ADC0060 | C | CB | Eaton | HFD3050L | 65 | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 0.695 | (1) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M2CFC | 5 | 45
ADC0070 |  | CB | Eaton | HFD3050L | 65 | 50 | 230 |  |  | 230 |  | 10 | 28
|  | STR |  | W200M2CFC | 5 | 45
ADC0071 |  | CB | Eaton | HFD3070L | 65 | 70 | [5 empty] | 15 | 42
|  | STR |  | W200M2CFC | 5 | 45
ADC0072 | C | CB | Eaton | HFD3050L | 65 | 50 | 460 | 3 | 65 | 460 | 3 | 25 | 34 | 0.695 | (1) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M2CFC | 5 | 45
ADC0073 |  | CB | Eaton | HFD3030L | 25 | 30 | 575 |  | 25 | 575 |  | 15 | 17 |  | (1) (5) (6a) (7a)
|  | STR |  | W200M2CFC | 5 | 45
ADC0074 |  | CB | Eaton | HFD3050L | 25 | 50 | [5 empty] | 25 | 27
|  | STR |  | W200M2CFC | 5 | 45
ADC0075 | C | CB | Eaton | FDC3050L | 100 | 50 | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 0.695 | (1) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M2CFC | 5 | 45
ADC0076 |  | CB | Eaton | FDC3050L | 100 | 50 | 230 |  |  | 230 |  | 10 | 28
|  | STR |  | W200M2CFC | 5 | 45
ADC0077 |  | CB | Eaton | FDC3070L | 100 | 70 | [5 empty] | 15 | 42
|  | STR |  | W200M2CFC | 5 | 45
ADC0078 | C | CB | Eaton | FDC3050L | 100 | 50 | 460 | 3 | 100 | 460 | 3 | 25 | 34 | 0.695 | (1) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M2CFC | 5 | 45
ADC0079 |  | CB | Eaton | FDC3030L | 35 | 30 | 575 |  | 35 | 575 |  | 15 | 17 |  | (1) (5) (6a) (7a)
|  | STR |  | W200M2CFC | 5 | 45
ADC0080 |  | CB | Eaton | FDC3050L | 35 | 50 | [5 empty] | 25 | 27
|  | STR |  | W200M2CFC | 5 | 45
ADC0081 | C | CB | Eaton | EGH3050FFG | 65 | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 0.695 | (1) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M2CFC | 5 | 45
ADC0082 |  | CB | Eaton | EGH3050FFG | 65 | 50 | 230 |  |  | 230 |  | 10 | 28
|  | STR |  | W200M2CFC | 5 | 45
ADC0083 |  | CB | Eaton | EGH3070FFG | 65 | 70 | [5 empty] | 15 | 42
|  | STR |  | W200M2CFC | 5 | 45
ADC0084 |  | CB | Eaton | EGH3050FFG | 65 | 50 | 460 |  |  | 460 |  | 25 | 34
|  | STR |  | W200M2CFC | 5 | 45
ADC0085 | C | CB | Eaton | HFD3050L | 65 | 50 | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 0.695 | (1) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200kA | 70
|  | STR |  | W200M2CFC | 5 | 45
ADC0086 | C | CB | Eaton | HFD3050L | 65 | 50 | 230 | 3 | 100 | 230 | 3 | 10 | 28 | 0.695 | (1) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200kA | 70
|  | STR |  | W200M2CFC | 5 | 45
ADC0087 |  | CB |  | HDF3070L | 65 | 70 | [5 empty] | 15 | 42
|  | C. Limiter |  | LFD3070R | 200kA | 70
|  | STR |  | W200M2CFC | 5 | 45
ADC0088 | C | CB | Eaton | HFD3050L | 65 | 50 | 460 | 3 | 100 | 460 | 3 | 25 | 34 | 0.695 | (1) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200kA | 70
|  | STR |  | W200M2CFC | 5 | 45
ADC0089 | C | CB | Eaton | HFD3030L | 25 | 30 | 575 | 3 | 100 | 575 | 3 | 15 | 17 | 0.695 | (1) (5) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200kA | 70
|  | STR |  | W200M2CFC | 5 | 45
ADC0090 |  | CB |  | HFD3050L | 25 | 50 | [5 empty] | 25 | 27
|  | C. Limiter |  | LFD3070R | 200kA | 70
|  | STR |  | W200M2CFC | 5 | 45
ADC0091 | C | CB | Eaton | HFD3100L | 65 | 100 | 200 | 3 | 65 | 200 | 3 | 20 | 62.1 | 1.06 | (1) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M3CFC | 5 | 90
ADC0092 |  | CB | Eaton | HFD3100L | 65 | 100 | [5 empty] | 25 | 78.2
|  | STR |  | W200M3CFC | 5 | 90
ADC0093 | C | CB | Eaton | HFD3100L | 65 | 100 | 230 | 3 | 65 | 230 | 3 | 25 | 68
|  | STR |  | W200M3CFC | 5 | 90
ADC0094 |  | CB | Eaton | HFD3100L | 65 | 100 | [5 empty] | 30 | 80
|  | STR |  | W200M3CFC | 5 | 90
ADC0095 | C | CB | Eaton | HFD3100L | 65 | 100 | 460 | 3 | 65 | 460 | 3 | 50 | 65 | 1.06 | (1) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M3CFC | 5 | 90
ADC0096 | C | CB | Eaton | HFD3050L | 25 | 50 | 575 | 3 | 25 | 575 | 3 | 30 | 32 |  | (1) (5) (6b) (7c)
|  | STR |  | W200M3CFC | 5 | 90
ADC0097 |  | CB | Eaton | HFD3100L | 25 | 100 | [5 empty] | 50 | 52 |  | (1) (5) (6b) (7e)
|  | STR |  | W200M3CFC | 5 | 90
ADC0098 | C | CB | Eaton | FDC3100L | 100 | 100 | 200 | 3 | 100 | 200 | 3 | 20 | 62.1 | 1.06 | (1) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M3CFC | 5 | 90
ADC0099 |  | CB | Eaton | FDC3100L | 100 | 100 | [5 empty] | 25 | 78.2
|  | STR |  | W200M3CFC | 5 | 90
ADC0100 | C | CB | Eaton | FDC3100L | 100 | 100 | 230 | 3 | 100 | 230 | 3 | 25 | 68
|  | STR |  | W200M3CFC | 5 | 90
ADC0101 |  | CB | Eaton | FDC3100L | 100 | 100 | [5 empty] | 30 | 80
|  | STR |  | W200M3CFC | 5 | 90
ADC0102 | C | CB | Eaton | FDC3100L | 100 | 100 | 460 | 3 | 100 | 460 | 3 | 50 | 65 | 1.06 | (1) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M3CFC | 5 | 90
ADC0103 | C | CB | Eaton | FDC3050L | 35 | 50 | 575 | 3 | 35 | 575 | 3 | 30 | 32 |  | (1) (5) (6b) (7c)
|  | STR |  | W200M3CFC | 5 | 90
ADC0104 |  | CB | Eaton | FDC3100L | 35 | 100 | [5 empty] | 50 | 52 |  | (1) (5) (6b) (7e)
|  | STR |  | W200M3CFC | 5 | 90
ADC0105 | C | CB | Eaton | EGH3100FFG | 65 | 100 | 200 | 3 | 65 | 200 | 3 | 20 | 62.1 | 1.06 | (1) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M3CFC | 5 | 90
ADC0106 |  | CB | Eaton | EGH3100FFG | 65 | 100 | [5 empty] | 25 | 78.2
|  | STR |  | W200M3CFC | 5 | 90
ADC0107 | C | CB | Eaton | EGH3100FFG | 65 | 100 | 230 | 3 | 65 | 230 | 3 | 25 | 68
|  | STR |  | W200M3CFC | 5 | 90
ADC0108 |  | CB | Eaton | EGH3100FFG | 65 | 100 | [5 empty] | 30 | 80
|  | STR |  | W200M3CFC | 5 | 90
ADC0109 | C | CB | Eaton | EGH3100FFG | 65 | 100 | 460 | 3 | 65 | 460 | 3 | 50 | 65
|  | STR |  | W200M3CFC | 5 | 90
ADC0110 | C | CB | Eaton | HFD3100L | 65 | 100 | 200 | 3 | 100 | 200 | 3 | 20 | 62.1 | 1.78 | (1) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3150R | 200kA | 150
|  | STR |  | W200M3CFC | 5 | 90
ADC0111 |  | CB | Eaton | HFD3100L | 65 | 100 | [5 empty] | 25 | 78.2
|  | C. Limiter |  | LFD3150R | 200kA | 150
|  | STR |  | W200M3CFC | 5 | 90
ADC0112 | C | CB | Eaton | HFD3100L | 65 | 100 | 230 | 3 | 100 | 230 | 3 | 25 | 68 | 1.78 | (1) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3150R | 200kA | 150
|  | STR |  | W200M3CFC | 5 | 90
ADC0113 |  | CB | Eaton | HFD3100L | 65 | 100 | [5 empty] | 30 | 80
|  | C. Limiter |  | LFD3150R | 200kA | 150
|  | STR |  | W200M3CFC | 5 | 90
ADC0114 | C | CB | Eaton | HFD3100L | 65 | 100 | 460 | 3 | 100 | 460 | 3 | 50 | 65 | 1.78 | (1) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3150R | 200kA | 150
|  | STR |  | W200M3CFC | 5 | 90
ADC0115 | C | CB | Eaton | HFD3050L | 65kA | 50 | 575 | 3 | 100 | 575 | 3 | 30 | 32 | 1.78 | (1) (5) (6b) (7C) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3150R | 200kA | 150
|  | STR |  | W200M3CFC | 5 | 90
ADC0116 |  | CB | Eaton | HFD3100L | 65 | 100 | [5 empty] | 50 | 52 |  | (1) (5) (6b) (7e)
|  | C. Limiter |  | LFD3150R | 200kA | 150
|  | STR |  | W200M3CFC | 5 | 90
ADC0117 | C | CB | Eaton | HJD3150 | 65 | 150 | 200 | 3 | 65 | 200 | 3 | 40 | 120 | 1.42 | (1) (5) (7f) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M4CFC | 10 | 135
ADC0118 |  | CB | Eaton | HJD3200 | 65 | 200 | 230 |  |  | 230 |  | 50 | 130
|  | STR |  | W200M4CFC | 10 | 135
ADC0119 | C | CB | Eaton | HJD3200 | 65 | 200 | 460 | 3 | 65 | 460 | 3 | 100 | 124 | 1.42 | (1) (5) (7f) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M4CFC | 10 | 135
ADC0120 |  | CB | Eaton | HJD3150 | 25 | 200 | 575 |  | 25 | 575 |  | 100 | 99 |  | (1) (5) (7f)
|  | STR |  | W200M4CFC | 10 | 135
ADC0121 | C | CB | Eaton | JDC3150 | 100 | 150 | 200 | 3 | 100 | 200 | 3 | 40 | 120 | 1.42 | (1) (5) (7f) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M4CFC | 10 | 135
ADC0122 |  | CB | Eaton | JDC3200 | 65 | 200 | 230 |  |  | 230 |  | 50 | 130
|  | STR |  | W200M4CFC | 10 | 135
ADC0123 | C | CB | Eaton | JDC3200 | 65 | 200 | 460 | 3 | 100 | 460 | 3 | 100 | 124 | 1.42 | (1) (5) (7f) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M4CFC | 10 | 135
ADC0124 |  | CB | Eaton | JDC3150 | 35 | 150 | 575 |  | 35 | 575 |  | 100 | 99
|  | STR |  | W200M4CFC | 10 | 135
ADC0125 | C | CB | Eaton | HJD3250 | 65 | 250 | 200 | 3 | 65 | 200 | 3 | 50 | 150 | 2.15 | (1) (5) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M5CFC | 10 | 270
ADC0126 |  | CB |  | HKD3400 | 65 | 400 | [5 empty] | 75 | 221
|  | STR |  | W200M5CFC | 10 | 270
ADC0127 | C | CB | Eaton | HJD3250 | 65 | 250 | 230 |  | 65 | 230 |  | 60 | 154
|  | STR |  | W200M5CFC | 10 | 270
ADC0128 |  | CB |  | HKD3400 | 65 | 400 | [5 empty] | 100 | 248
|  | STR |  | W200M5CFC | 10 | 270
ADC0129 | C | CB | Eaton | HJD3250 | 65 | 250 | 460 | 3 | 65 | 460 | 3 | 125 | 156 | 2.15 | (1) (5) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M5CFC | 10 | 270
ADC0130 |  | CB |  | HKD3400 | 65 | 400 | [5 empty] | 200 | 240
|  | STR |  | W200M5CFC | 10 | 270
ADC0131 | C | CB | Eaton | HJD3250 | 65 | 250 | 575 | 3 | 25 | 575 | 3 | 150 | 144 | 2.15 | (1) (5) (7j)
|  | STR |  | W200M5CFC | 10 | 270
ADC0132 |  | CB |  | HKD3400 | 35 | 400 |  |  | 25 |  |  | 200 | 192
|  | STR |  | W200M5CFC | 10 | 270
ADC0133 | C | CB | Eaton | JDC3250 | 100 | 250 | 200 | 3 | 100 | 200 | 3 | 50 | 150 | 2.15 | (1) (5) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M5CFC | 10 | 270
ADC0134 |  | CB |  | KDC3400 | 100 | 400 | [5 empty] | 75 | 221
|  | STR |  | W200M5CFC | 10 | 270
ADC0135 | C | CB | Eaton | JDC3250 | 100 | 250 | 230 |  | 100 | 230 |  | 60 | 154
|  | STR |  | W200M5CFC | 10 | 270
ADC0136 |  | CB |  | KDC3400 | 100 | 400 | [5 empty] | 100 | 248
|  | STR |  | W200M5CFC | 10 | 270
ADC0137 | C | CB | Eaton | JDC3250 | 100 | 250 | 460 | 3 | 100 | 460 | 3 | 125 | 156 | 2.15 | (1) (5) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M5CFC | 10 | 270
ADC0138 |  | CB |  | KDC3400 | 100 | 400 | [5 empty] | 200 | 240
|  | STR |  | W200M5CFC | 10 | 270
ADC0139 | C | CB | Eaton | JDC3250 | 35 | 250 | 575 |  | 50 | 575 |  | 150 | 144
|  | STR |  | W200M5CFC | 10 | 270
ADC0140 |  | CB |  | KDC3400 | 50 | 400 |  |  | 100 |  |  | 200 | 192
|  | STR |  | W200M5CFC | 10 | 270
ADC0141 | C | CB | Eaton | HLD3600 | 65 | 600 | 200 | 3 | 65 | 200 | 3 | 150 | 414 | 2.15 | (1) (5) (7s) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M6CFC | 18 | 540
ADC0142 | C | CB | Eaton | HMDL3800 | 65 | 800 | 230 |  |  | 230 |  | 200 | 552
|  | STR |  | W200M6CFC | 18 | 540
ADC0143 | C | CB | Eaton | HLD3600 | 65 | 600 | 460 |  | 65 | 460 |  | 350 | 414
|  | STR |  | W200M6CFC | 18 | 540
ADC0144 |  | CB |  | HMDL3800 | 65 | 800 | [5 empty] | 400 | 477
|  | STR |  | W200M6CFC | 18 | 540
ADC0145 | C | CB | Eaton | HLD3600 | 35 | 600 | 575 |  | 35 | 575 |  | 400 | 382
|  | STR |  | W200M6CFC | 18 | 540
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment. See Table 3
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6a) = Install Terminal End Cover TEC1 (6085C42H01) to line side of circuit breaker.
(6b) = Install Terminal end Cover TEC2 (6085C42H02) to line side of circuit breaker.
(7) See Table 7 for internal wiring between load side of short circuit protective device & line side of starter.
Table 7 - Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
| Wire Code | Wire Size | Wire Code | Wire Size
| 7a | 12 awg. | 7j | 4/0 awg.
| 7b | 10 awg. | 7k | 250kcml
| 7c | 8 awg. | 7l | 350kcml
| 7d | 6 awg. | 7m | 4/0 awg. (3)
| 7e | 4 awg. | 7n | 4/0 awg. (4)
| 7f | 2 awg. | 7p | 250kcml (2)
| 7g | 1/0 awg. | 7r | 350kcml (3)
| 7h | 2/0 awg. | 7s | 4/0 awg. (2)

## Advantage Type D
Issued: 2006-05-18
Last Revised: 2006-05-18
Combination Motor Controllers for use in Industrial Control Panels
ID Number | Combination Type | Individual Component | [6 empty] | Combination SCCR | [5 empty] | Conditions of Acceptability | Combination Starter UL File | Motor Control Center UL File
|  | Component Type | Manufacturer | Patial Catalog Nos. | Ratings |  |  |  | SCCR kA | Volts | Phase | Hp | NEC FLC | Min. Enclosure Volume (cu. ft.)
[5 empty] | SCCR kA | Max. Amps | Volts | No. Poles
ADD0001 | D | ICB | Eaton | HMCPS007*** | - | 7 | 200 | 3 | 100kA | 200 | 3 | 1 | 4.8 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200MLCFC | 5 | 27
ADD0002 |  | ICB | Eaton | HMCPS007*** | - | 7 | 230 |  |  | 230 |  | 1 | 4.2
|  | STR |  | W200MLCFC | 5 | 27
ADD0003 | D | ICB | Eaton | HMCP003*** | - | 3 | 460 | 3 | 100kA | 460 | 3 | 1 | 2.1
|  | STR |  | W200MLCFC | 5 | 27
ADD0004 |  | ICB | Eaton | HMCPS007*** | - | 7 | [5 empty] | 3 | 4.8
|  | STR |  | W200MLCFC | 5 | 27
ADD0005 | D | ICB | Eaton | HMCP003*** | - | 3 | 575 | 3 | 25kA | 575 | 3 | 1 | 1.7 | 0.695 | (1) (5) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200MLCFC | 5 | 27
ADD0006 |  | ICB | Eaton | HMCPS007*** | - | 7 | [5 empty] | 3 | 3.9
|  | STR |  | W200MLCFC | 5 | 27
ADD0007 | D | ICB | Eaton | HMCPE007*** | - | 7 | 200 | 3 | 100kA | 200 | 3 | 1 | 4.8 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200MLCFC | 5 | 27
ADD0008 |  | ICB | Eaton | HMCPE007*** | - | 7 | 230 |  |  | 230 |  | 1 | 4.2
|  | STR |  | W200MLCFC | 5 | 27
ADD0009 | D | ICB | Eaton | HMCPE003*** | - | 3 | 460 | 3 | 100kA | 460 | 3 | 1 | 2.1
|  | STR |  | W200MLCFC | 5 | 27
ADD0010 |  | ICB | Eaton | HMCPE007*** | - | 7 | [5 empty] | 3 | 4.8
|  | STR |  | W200MLCFC | 5 | 27
ADD0011 | D | ICB | Eaton | HMCPS007*** | - | 7 | 200 | 3 | 100kA | 200 | 3 | 1 | 4.8 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3007R | - | 7
|  | STR |  | W200MLCFC | 5 | 27
ADD0012 | D | ICB | Eaton | HMCPS007*** | - | 7 | 230 | 3 | 100kA | 230 | 3 | 1 | 4.2
|  | C. Limiter |  | ELC3007R | - | 7
|  | STR |  | W200MLCFC | 5 | 27
ADD0013 | D | ICB | Eaton | HMCP003*** | - | 3 | 460 | 3 | 100kA | 460 | 3 | 1 | 2.1 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3003R | - | 3
|  | STR |  | W200MLCFC | 5 | 27
ADD0014 | D | ICB | Eaton | HMCPS007*** | - | 7 | [5 empty] | 3 | 4.8
|  | C. Limiter |  | ELC3007R | - | 7
|  | STR |  | W200MLCFC | 5 | 27
ADD0015 | D | ICB | Eaton | HMCP003*** | - | 3 | 575 | 3 | 100kA | 575 | 3 | 1 | 1.7 | 0.695 | (1) (5) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3003R | - | 3
|  | STR |  | W200MLCFC | 5 | 27
ADD0016 | D | ICB | Eaton | HMCPS007*** | - | 7 | 200 | 3 | 100kA | 200 | 3 | 1 | 4.8 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M1CFC | 5 | 27
ADD0017 |  | ICB | Eaton | HMCP015*** | - | 15 | [5 empty] | 3 | 11
|  | STR |  | W200M1CFC | 5 | 27
ADD0018 |  | ICB | Eaton | HMCP030*** | - | 30 | [5 empty] | 5 | 17.5
|  | STR |  | W200M1CFC | 5 | 27
ADD0019 |  | ICB | Eaton | HMCP050*** | - | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | W200M1CFC | 5 | 27
ADD0020 | D | ICB | Eaton | HMCPS007*** | - | 7 | 230 | 3 | 100kA | 230 | 3 | 1 | 4.2 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M1CFC | 5 | 27
ADD0021 |  | ICB | Eaton | HMCP015*** | - | 15 | [5 empty] | 3 | 9.6
|  | STR |  | W200M1CFC | 5 | 27
ADD0022 |  | ICB | Eaton | HMCP030*** | - | 30 | [5 empty] | 5 | 15.2
|  | STR |  | W200M1CFC | 5 | 27
ADD0023 |  | ICB | Eaton | HMCP050*** | - | 50 | [5 empty] | 7.5 | 22
|  | STR |  | W200M1CFC | 5 | 27
ADD0024 | D | ICB | Eaton | HMCP003*** | - | 3 | 460 | 3 | 100kA | 460 | 3 | 1 | 2.1 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M1CFC | 5 | 27
ADD0025 |  | ICB | Eaton | HMCPS007*** | - | 7 | [5 empty] | 3 | 4.8
|  | STR |  | W200M1CFC | 5 | 27
ADD0026 |  | ICB | Eaton | HMCP015*** | - | 15 | [5 empty] | 5 | 7.6
|  | STR |  | W200M1CFC | 5 | 27
ADD0027 |  | ICB | Eaton | HMCP030*** | - | 30 | [5 empty] | 10 | 14
|  | STR |  | W200M1CFC | 5 | 27
ADD0028 | D | ICB | Eaton | HMCPS003*** | - | 3 | 575 | 3 | 25kA | 575 | 3 | 1 | 1.7 | 0.695 | (1) (5) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M1CFC | 5 | 27
ADD0029 |  | ICB | Eaton | HMCPS007*** | - | 7 | [5 empty] | 3 | 3.9
|  | STR |  | W200M1CFC | 5 | 27
ADD0030 |  | ICB | Eaton | HMCP015*** | - | 15 | [5 empty] | 5 | 6.1
|  | STR |  | W200M1CFC | 5 | 27
ADD0031 |  | ICB | Eaton | HMCP030*** | - | 30 | [5 empty] | 10 | 11
|  | STR |  | W200M1CFC | 5 | 27
ADD0032 | D | ICB | Eaton | HMCPE007*** | - | 7 | 200 | 3 | 100kA | 200 | 3 | 1 | 4.8 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M1CFC | 5 | 27
ADD0033 |  | ICB | Eaton | HMCPE015*** | - | 15 | [5 empty] | 3 | 11
|  | STR |  | W200M1CFC | 5 | 27
ADD0034 |  | ICB | Eaton | HMCPE030*** | - | 30 | [5 empty] | 5 | 17.5
|  | STR |  | W200M1CFC | 5 | 27
ADD0035 |  | ICB | Eaton | HMCPE050*** | - | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | W200M1CFC | 5 | 27
ADD0036 | D | ICB | Eaton | HMCPE007*** | - | 7 | 230 | 3 | 100kA | 230 | 3 | 1 | 4.2 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M1CFC | 5 | 27
ADD0037 |  | ICB | Eaton | HMCPE015*** | - | 15 | [5 empty] | 3 | 9.6
|  | STR |  | W200M1CFC | 5 | 27
ADD0038 |  | ICB | Eaton | HMCPE030*** | - | 30 | [5 empty] | 5 | 15.2
|  | STR |  | W200M1CFC | 5 | 27
ADD0039 |  | ICB | Eaton | HMCPE050*** | - | 50 | [5 empty] | 7.5 | 22
|  | STR |  | W200M1CFC | 5 | 27
ADD0040 | D | ICB | Eaton | HMCPE003*** | - | 3 | 460 | 3 | 100kA | 460 | 3 | 1 | 2.1 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M1CFC | 5 | 27
ADD0041 |  | ICB | Eaton | HMCPE007*** | - | 7 | [5 empty] | 3 | 4.8
|  | STR |  | W200M1CFC | 5 | 27
ADD0042 |  | ICB | Eaton | HMCPE015*** | - | 15 | [5 empty] | 5 | 7.6
|  | STR |  | W200M1CFC | 5 | 27
ADD0043 |  | ICB | Eaton | HMCPE030*** | - | 30 | [5 empty] | 10 | 14
|  | STR |  | W200M1CFC | 5 | 27
ADD0044 | D | ICB | Eaton | HMCPS007*** | - | 7 | 200 | 3 | 100kA | 200 | 3 | 1 | 4.8 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3007R | - | 7
|  | STR |  | W200M1CFC | 5 | 27
ADD0045 | D | ICB | Eaton | HMCP015*** | - | 15 | [5 empty] | 3 | 11
|  | C. Limiter |  | ELC3015R | - | 15
|  | STR |  | W200M1CFC | 5 | 27
ADD0046 | D | ICB | Eaton | HMCP030*** | - | 30 | 200 | 3 | 100kA | 200 | 3 | 5 | 17.5 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3030R | - | 30
|  | STR |  | W200M1CFC | 5 | 27
ADD0047 | D | ICB | Eaton | HMCP050*** | - | 50 | [5 empty] | 7.5 | 25.3
|  | C. Limiter |  | ELC3050R | - | 50
|  | STR |  | W200M1CFC | 5 | 27
ADD0048 | D | ICB | Eaton | HMCPS007*** | - | 7 | 230 | 3 | 100kA | 230 | 3 | 1 | 4.2 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3007R | - | 7
|  | STR |  | W200M1CFC | 5 | 27
ADD0049 | D | ICB | Eaton | HMCP015*** | - | 15 | [5 empty] | 3 | 9.6
|  | C. Limiter |  | ELC3015R | - | 15
|  | STR |  | W200M1CFC | 5 | 27
ADD0050 | D | ICB | Eaton | HMCP030*** | - | 30 | 230 | 3 | 100kA | 230 | 3 | 5 | 15.2 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3030R | - | 30
|  | STR |  | W200M1CFC | 5 | 27
ADD0051 | D | ICB | Eaton | HMCP050*** | - | 50 | [5 empty] | 7.5 | 22
|  | C. Limiter |  | ELC3050R | - | 50
|  | STR |  | W200M1CFC | 5 | 27
ADD0052 | D | ICB | Eaton | HMCP003*** | - | 3 | 460 | 3 | 100kA | 460 | 3 | 1 | 2.1 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3003R | - | 3
|  | STR |  | W200M1CFC | 5 | 27
ADD0053 | D | ICB | Eaton | HMCPS007*** | - | 7 | [5 empty] | 3 | 4.8
|  | C. Limiter |  | ELC3007R | - | 7
|  | STR |  | W200M1CFC | 5 | 27
ADD0054 | D | ICB | Eaton | HMCP015*** | - | 15 | 460 | 3 | 100kA | 460 | 3 | 5 | 7.6 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3015R | - | 15
|  | STR |  | W200M1CFC | 5 | 27
ADD0055 | D | ICB | Eaton | HMCP030*** | - | 30 | [5 empty] | 10 | 14
|  | C. Limiter |  | ELC3030R | - | 30
|  | STR |  | W200M1CFC | 5 | 27
ADD0056 | D | ICB | Eaton | HMCP003*** | - | 3 | 575 | 3 | 100kA | 575 | 3 | 1 | 1.7 | 0.695 | (1) (5) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3003R | - | 3
|  | STR |  | W200M1CFC | 5 | 27
ADD0057 | D | ICB | Eaton | HMCPS007*** | - | 7 | [5 empty] | 3 | 3.9
|  | C. Limiter |  | ELC3007R | - | 7
|  | STR |  | W200M1CFC | 5 | 27
ADD0058 | D | ICB | Eaton | HMCP015*** | - | 15 | 575 | 3 | 100kA | 575 | 3 | 5 | 6.1 | 0.695 | (1) (5) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3015R | - | 15
|  | STR |  | W200M1CFC | 5 | 27
ADD0059 | D | ICB | Eaton | HMCP030*** | - | 30 | [5 empty] | 10 | 11
|  | C. Limiter |  | ELC3030R | - | 30
|  | STR |  | W200M1CFC | 5 | 27
ADD0060 | D | ICB | Eaton | HMCP050*** | - | 50 | 200 | 3 | 100kA | 200 | 3 | 10 | 32.2 | 0.695 | (1) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M2CFC | 5 | 45
ADD0061 |  | ICB | Eaton | HMCP050*** | - | 50 | 230 |  |  | 230 |  | 10 | 28
|  | STR |  | W200M2CFC | 5 | 45
ADD0062 |  | ICB | Eaton | HMCP070*** | - | 70 | [5 empty] | 15 | 42
|  | STR |  | W200M2CFC | 5 | 45
ADD0063 | D | ICB | Eaton | HMCP050*** | - | 50 | 460 | 3 | 100kA | 460 | 3 | 25 | 34 | 0.695 | (1) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M2CFC | 5 | 45
ADD0064 |  | ICB | Eaton | HMCP030*** | - | 30 | 575 |  |  | 575 |  | 15 | 17 |  | (1) (5) (6a) (7a)
|  | STR |  | W200M2CFC | 5 | 45
ADD0065 |  | ICB | Eaton | HMCP050*** | - | 50 | [5 empty] | 25 | 27
|  | STR |  | W200M2CFC | 5 | 45
ADD0066 | D | ICB | Eaton | HMCPE050*** | - | 50 | 200 | 3 | 100kA | 200 | 3 | 10 | 32.2 | 0.695 | (1) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M2CFC | 5 | 45
ADD0067 |  | ICB | Eaton | HMCPE050*** | - | 50 | 230 |  |  | 230 |  | 10 | 28
|  | STR |  | W200M2CFC | 5 | 45
ADD0068 |  | ICB | Eaton | HMCPE070*** | - | 70 | [5 empty] | 15 | 42
|  | STR |  | W200M2CFC | 5 | 45
ADD0069 | D | ICB | Eaton | HMCPE050*** | - | 50 | 460 | 3 | 100kA | 460 | 3 | 25 | 34
|  | STR |  | W200M2CFC | 5 | 45
ADD0070 | D | ICB | Eaton | HMCP050*** | - | 50 | 200 | 3 | 100kA | 200 | 3 | 10 | 32.2 | 0.695 | (1) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3050R | - | 50
|  | STR |  | W200M2CFC | 5 | 45
ADD0071 | D | ICB | Eaton | HMCP050*** | - | 50 | 230 |  | 100kA | 230 | 3 | 10 | 28
|  | C. Limiter |  | ELC3050R | - | 50
|  | STR |  | W200M2CFC | 5 | 45
ADD0072 | D | ICB | Eaton | HMCP070*** | - | 70 | [5 empty] | 15 | 42
|  | C. Limiter |  | ELC3070R | - | 70
|  | STR |  | W200M2CFC | 5 | 45
ADD0073 | D | ICB | Eaton | HMCP050*** | - | 50 | 460 | 3 | 100kA | 460 | 3 | 25 | 34 | 0.695 | (1) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3050R | - | 50
|  | STR |  | W200M2CFC | 5 | 45
ADD0074 | D | ICB | Eaton | HMCP030*** | - | 30 | 575 | 3 | 100kA | 575 | 3 | 15 | 17 |  | (1) (5) (6a) (7a)
|  | C. Limiter |  | ELC3030R | - | 30
|  | STR |  | W200M2CFC | 5 | 45
ADD0075 | D | ICB | Eaton | HMCP050*** | - | 50 | [5 empty] | 25 | 27
|  | C. Limiter |  | ELC3050R | - | 50
|  | STR |  | W200M2CFC | 5 | 45
ADD0076 | D | ICB | Eaton | HMCP100*** | - | 100 | 200 | 3 | 100kA | 200 | 3 | 20 | 62.1 | 1.06 | (1) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M3CFC | 5 | 90
ADD0077 |  | ICB | Eaton | HMCP100*** | - | 100 | [5 empty] | 25 | 78.2
|  | STR |  | W200M3CFC | 5 | 90
ADD0078 | D | ICB | Eaton | HMCP100*** | - | 100 | 230 | 3 | 100kA | 230 | 3 | 25 | 68
|  | STR |  | W200M3CFC | 5 | 90
ADD0079 |  | ICB | Eaton | HMCP100*** | - | 100 | [5 empty] | 30 | 80
|  | STR |  | W200M3CFC | 5 | 90
ADD0080 | D | ICB | Eaton | HMCP100*** | - | 100 | 460 | 3 | 100kA | 460 | 3 | 50 | 65 | 1.06 | (1) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M3CFC | 5 | 90
ADD0081 | D | ICB | Eaton | HMCP050*** | - | 50 | 575 | 3 | 25kA | 575 | 3 | 30 | 32 |  | (1) (5) (6b) (7e)
|  | STR |  | W200M3CFC | 5 | 90
ADD0082 |  | ICB | Eaton | HMCP100*** | - | 100 | [5 empty] | 50 | 52
|  | STR |  | W200M3CFC | 5 | 90
ADD0083 | D | ICB | Eaton | HMCPE100*** | - | 100 | 200 | 3 | 100kA | 200 | 3 | 20 | 62.1 | 1.06 | (1) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M3CFC | 5 | 90
ADDD0084 |  | ICB | Eaton | HMCPE100*** | - | 100 | [5 empty] | 25 | 78.2
|  | STR |  | W200M3CFC | 5 | 90
ADD0085 | D | ICB | Eaton | HMCPE100*** | - | 100 | 230 | 3 | 100kA | 230 | 3 | 25 | 68
|  | STR |  | W200M3CFC | 5 | 90
ADD0086 |  | ICB | Eaton | HMCPE100*** | - | 100 | [5 empty] | 30 | 80
|  | STR |  | W200M3CFC | 5 | 90
ADD0087 | D | ICB | Eaton | HMCPE100*** | - | 100 | 460 | 3 | 100kA | 460 | 3 | 50 | 65
|  | STR |  | W200M3CFC | 5 | 90
ADD0088 | D | ICB | Eaton | HMCP100*** | - | 100 | 200 | 3 | 100kA | 200 | 3 | 20 | 62.1 | 1.42 | (1) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3100R | - | 100
|  | STR |  | W200M3CFC | 5 | 90
ADD0089 | D | ICB | Eaton | HMCP100*** | - | 100 | [5 empty] | 25 | 78.2
|  | C. Limiter |  | ELC3100R | - | 100
|  | STR |  | W200M3CFC | 5 | 90
ADD0090 | D | ICB | Eaton | HMCP100*** | - | 100 | 230 | 3 | 100kA | 230 | 3 | 25 | 68 | 1.42 | (1) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3100R | - | 100
|  | STR |  | W200M3CFC | 5 | 90
ADD0091 | D | ICB | Eaton | HMCP100*** | - | 100 | [5 empty] | 30 | 80
|  | C. Limiter |  | ELC3100R | - | 100
|  | STR |  | W200M3CFC | 5 | 90
ADD0092 | D | ICB | Eaton | HMCP100*** | - | 100 | 460 | 3 | 100kA | 460 | 3 | 50 | 65 | 1.42 | (1) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3100R | - | 100
|  | STR |  | W200M3CFC | 5 | 90
ADD0093 | D | ICB | Eaton | HMCP050*** | - | 50 | 575 | 3 | 100kA | 575 | 3 | 30 | 32 | 1.42 | (1) (5) (6b) (7c)
|  | C. Limiter |  | ELC3050R | - | 50
|  | STR |  | W200M3CFC | 5 | 90
ADD0094 | D | ICB | Eaton | HMCP100*** | - | 100 | [5 empty] | 50 | 52 |  | (1) (5) (6b) (7e)
|  | C. Limiter |  | ELC3100R | - | 100
|  | STR |  | W200M3CFC | 5 | 90
ADD0095 | D | ICB | Eaton | HMCP150*** | - | 150 | 200 | 3 | 65kA | 200 | 3 | 40 | 120 | 1.06 | (1) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1
|  | STR |  | W200M4CFC | 10 | 135
ADD0096 |  | ICB | Eaton | HMCP150*** | - | 150 | 230 |  | 65kA | 230 |  | 40 | 120
|  | STR |  | W200M4CFC | 10 | 135
ADD0097 | D | ICB | Eaton | HMCP150*** | - | 150 | 460 | 3 | 65kA | 460 | 3 | 75 | 96 | 1.06 | (1) (5) (7e)
|  | STR |  | W200M4CFC | 10 | 135
ADD0098 |  | ICB | Eaton | HMCP150*** | - | 150 | 575 |  | 25kA | 575 |  | 100 | 99 |  | (1) (5) (6b (7e)
|  | STR |  | W200M4CFC | 10 | 135
ADD0099 | D | ICB | Eaton | HMCP150*** | - | 150 | 200 | 3 | 100kA | 200 | 3 | 40 | 120 | 1.42 | (1) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1
|  | C. Limiter |  | EL3150R | - | 150
|  | STR |  | W200M4CFC | 10 | 135
ADD0100 | D | ICB | Eaton | HMCP150*** | - | 150 | 230 |  | 100kA | 230 |  | 40 | 120
|  | C. Limiter |  | EL3150R | - | 150
|  | STR |  | W200M4CFC | 10 | 135
ADD0101 | D | ICB | Eaton | HMCP150*** | - | 150 | 460 | 3 | 100kA | 460 | 3 | 75 | 96 | 1.42 | (1) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1
|  | C. Limiter |  | EL3150R | - | 150
|  | STR |  | W200M4CFC | 10 | 135
ADD0102 | D | ICB | Eaton | HMCP150*** | - | 150 | 575 |  | 100kA | 575 |  | 100 | 99 |  | (1) (5) (6b) (7e)
|  | C. Limiter |  | EL3150R | - | 150
|  | STR |  | W200M4CFC | 10 | 135
ADD0103 | D | ICB | Eaton | HMCP250*** | - | 250 | 200 | 3 | 100kA | 200 | 3 | 50 | 150 | 2.15 | (1) (5) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M5CFC | 10 | 270
ADD0104 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 75 | 221
|  | STR |  | W200M5CFC | 10 | 270
ADD0105 | D | ICB | Eaton | HMCP250*** | - | 250 | 230 |  | 100kA | 230 |  | 60 | 154
|  | STR |  | W200M5CFC | 10 | 270
ADD0106 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 100 | 248
|  | STR |  | W200M5CFC | 10 | 270
ADD0107 | D | ICB | Eaton | HMCP250*** | - | 250 | 460 | 3 | 100kA | 460 | 3 | 125 | 156 | 2.15 | (1) (5) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M5CFC | 10 | 270
ADD0108 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 200 | 240
|  | STR |  | W200M5CFC | 10 | 270
ADD0109 | D | ICB | Eaton | HMCP250*** | - | 250 | 575 |  | 25kA | 575 |  | 150 | 144
|  | STR |  | W200M5CFC | 10 | 270
ADD0110 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 200 | 192
|  | STR |  | W200M5CFC | 10 | 270
ADD0111 | D | ICB | Eaton | HMCP600*** | - | 600 | 200 | 3 | 100kA | 200 | 3 | 150 | 414 | 2.15 | (1) (5) (7s) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | W200M6CFC | 18 | 540
ADD0112 | D | ICB | Eaton | HMCP12Y8W | - | 1200 | 230 |  |  | 230 |  | 200 | 552
|  | STR |  | W200M6CFC | 18 | 540
ADD0113 | D | ICB | Eaton | HMCP600*** | - | 600 | 460 | 3 | 100kA | 460 | 3 | 350 | 414
|  | STR |  | W200M6CFC | 18 | 540
ADD0114 |  | ICB |  | HMCP1200*** | - | 1200 | [5 empty] | 400 | 477
|  | STR |  | W200M6CFC | 18 | 540
ADD0115 | D | ICB | Eaton | HMCP600*** | - | 600 | 575 | 3 | 25Ka | 575 | 3 | 400 | 382
|  | STR |  | W200M6CFC | 18 | 540
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment. See Table 3
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6a) = Install Terminal End Cover TEC1 (6085C42H01) to line side of circuit breaker.
(6b) = Install Terminal end Cover TEC2 (6085C42H02) to line side of circuit breaker.
(7) See Table 7 for internal wiring between load side of short circuit protective device & line side of starter.
Table 7 - Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
| Wire Code | Wire Size | Wire Code | Wire Size
| 7a | 12 awg. | 7j | 4/0 awg.
| 7b | 10 awg. | 7k | 250kcml
| 7c | 8 awg. | 7l | 350kcml
| 7d | 6 awg. | 7m | 4/0 awg. (3)
| 7e | 4 awg. | 7n | 4/0 awg. (4)
| 7f | 2 awg. | 7p | 250kcml (2)
| 7g | 1/0 awg. | 7r | 350kcml (3)
| 7h | 2/0 awg. | 7s | 4/0 awg. (2)

## A200 Type C
Issued: 2006-05-18
Last Revised: 2006-05-18
Combination Motor Controllers for use in Industrial Control Panels
ID Number | Combination Type | Individual Component | [6 empty] | Combination SCCR | [5 empty] | Conditions of Acceptability | Combination Starter UL File | Motor Control Center UL File
|  | Component Type | Manufacturer | Partial Catalog No. | Ratings |  |  |  | SCCR kA | Volts | Phase | Hp | NEC FLC | Min. Enclosure Volume (cu. ft.)
[5 empty] | SCCR kA | Max. Amps | Volts | No. Poles
A200C001 | C | CB | Eaton | EGH3025FFG | 100 | 25 | 208 | 3 | 65 | 208 | 3 | 3 | 10.6 | 0.695 | (1) (3) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M1C*** | 5 | 27
A200C002 |  | CB |  | EGH3035FFG | 100 | 35 | [5 empty] | 5 | 16.7
|  | STR |  | A200M1C*** | 5 | 27
A200C003 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | A200M1C*** | 5 | 27
A200C004 | C | CB | Eaton | EGH3025FFG | 100 | 25 | 240 | 3 | 65 | 230 | 3 | 3 | 9.6 | 0.695 | (1) (3) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M1C*** | 5 | 27
A200C005 |  | CB |  | EGH3035FFG | 100 | 35 | [5 empty] | 5 | 15.2
|  | STR |  | A200M1C*** | 5 | 27
A200C006 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 7.5 | 22
|  | STR |  | A200M1C*** | 5 | 27
A200C007 | C | CB | Eaton | EGH3020FFG | 65 | 20 | 480 | 3 | 65 | 460 | 3 | 5 | 7.6 | 0.695 | (1) (3) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M1C*** | 5 | 27
A200C008 |  | CB |  | EGH3030FFG | 65 | 30 | [5 empty] | 7.5 | 11
|  | STR |  | A200M1C*** | 5 | 27
A200C009 |  | CB |  | EGH3035FFG | 65 | 35 | [5 empty] | 10 | 14
|  | STR |  | A200M1C*** | 5 | 27
A200C010 | C | CB | Eaton | HFD3025L | 100 | 25 | 208 | 3 | 65 | 208 | 3 | 3 | 10.6 | 0.695 | (1) (3) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M1C*** | 5 | 27
A200C011 |  | CB |  | HFD3035L | 100 | 35 | [5 empty] | 5 | 16.7
|  | STR |  | A200M1C*** | 5 | 27
A200C012 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | A200M1C*** | 5 | 27
A200C013 | C | CB | Eaton | HFD3025L | 100 | 25 | 240 | 3 | 65 | 230 | 3 | 3 | 9.6 | 0.695 | (1) (3) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M1C*** | 5 | 27
A200C014 |  | CB |  | HFD3035L | 100 | 35 | [5 empty] | 5 | 15.2
|  | STR |  | A200M1C*** | 5 | 27
A200C015 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 22
|  | STR |  | A200M1C*** | 5 | 27
A200C016 | C | CB | Eaton | HFD3020L | 65 | 20 | 480 | 3 | 65 | 460 | 3 | 5 | 7.6 | 0.695 | (1) (3) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M1C*** | 5 | 27
A200C017 |  | CB |  | HFD3030L | 65 | 30 | [5 empty] | 7.5 | 11
|  | STR |  | A200M1C*** | 5 | 27
A200C018 |  | CB |  | HFD3035L | 65 | 35 | [5 empty] | 10 | 14
|  | STR |  | A200M1C*** | 5 | 27
A200C019 | C | CB | Eaton | HFD3015L | 25 | 15 | 600 | 3 | 25 | 575 | 3 | 5 | 6.1 | 0.695 | (1) (3) (6a) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M1C*** | 5 | 27
A200C020 |  | CB |  | HFD3015L | 25 | 15 | [5 empty] | 7.5 | 9
|  | STR |  | A200M1C*** | 5 | 27
A200C021 |  | CB |  | HFD3025L | 25 | 25 | [5 empty] | 10 | 11
|  | STR |  | A200M1C*** | 5 | 27
A200C022 | C | CB | Eaton | FDC3025L | 200 | 25 | 208 | 3 | 100 | 208 | 3 | 3 | 10.6 | 0.695 | (1) (3) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M1C*** | 5 | 27
A200C023 |  | CB |  | FDC3035L | 200 | 35 | [5 empty] | 5 | 16.7
|  | STR |  | A200M1C*** | 5 | 27
A200C024 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | A200M1C*** | 5 | 27
A200C025 | C | CB | Eaton | FDC3025L | 200 | 25 | 240 | 3 | 100 | 230 | 3 | 3 | 9.6 | 0.695 | (1) (3) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M1C*** | 5 | 27
A200C026 |  | CB |  | FDC3035L | 200 | 35 | [5 empty] | 5 | 15.2
|  | STR |  | A200M1C*** | 5 | 27
A200C027 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 22
|  | STR |  | A200M1C*** | 5 | 27
A200C028 | C | CB | Eaton | FDC3020L | 100 | 20 | 480 | 3 | 100 | 460 | 3 | 5 | 7.6 | 0.695 | (1) (3) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M1C*** | 5 | 27
A200C029 |  | CB |  | FDC3030L | 100 | 30 | [5 empty] | 7.5 | 11
|  | STR |  | A200M1C*** | 5 | 27
A200C030 |  | CB |  | FDC3035L | 100 | 35 | [5 empty] | 10 | 14
|  | STR |  | A200M1C*** | 5 | 27
A200C031 | C | CB | Eaton | FDC3015L | 35 | 15 | 600 | 3 | 35 | 575 | 3 | 5 | 6.1 | 0.695 | (1) (3) (6a) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M1C*** | 5 | 27
A200C032 |  | CB |  | FDC3015L | 35 | 15 | [5 empty] | 7.5 | 9
|  | STR |  | A200M1C*** | 5 | 27
A200C033 |  | CB |  | FDC3025L | 35 | 25 | [5 empty] | 10 | 11
|  | STR |  | A200M1C*** | 5 | 27
A200C034 | C | CB | Eaton | FB3015PL | 200 | 15 | 600 | 3 | 100 | 575 | 3 | 5 | 6.1 | 0.695 | (1) (3) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M1C*** | 5 | 27
A200C035 |  | CB |  | FB3015PL | 200 | 15 | [5 empty] | 7.5 | 9
|  | STR |  | A200M1C*** | 5 | 27
A200C036 |  | CB |  | FB3025PL | 200 | 25 | [5 empty] | 10 | 11
|  | STR |  | A200M1C*** | 5 | 27
A200C037 | C | CB | Eaton | HFD3015L | 25 | 15 | 600 | 3 | 100 | 575 | 3 | 5 | 6.1 | 0.695 | (1) (3) (7a) | - | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | A200M1C*** | 5 | 27
A200C038 | C | CB | Eaton | HFD3015L | 25 | 15 | 600 | 3 | 100 | 575 | 3 | 7.5 | 9
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | A200M1C*** | 5 | 27
A200C039 | C | CB | Eaton | HFD3025L | 25 | 25 | 600 | 3 | 100 | 575 | 3 | 10 | 11
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | A200M1C*** | 5 | 27
A200C040 | C | CB | Eaton | EGH3035FFG | 100 | 35 | 208 | 3 | 65 | 208 | 3 | 5 | 16.7 | 0.695 | (1) (3) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M2C*** | 5 | 45
A200C041 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | A200M2C*** | 5 | 45
A200C042 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 10 | 30.8
|  | STR |  | A200M2C*** | 5 | 45
A200C043 | C | CB | Eaton | EGH3050FFG | 100 | 50 | 240 | 3 | 65 | 230 | 3 | 7.5 | 22 | 0.695 | (1) (3) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M2C*** | 5 | 45
A200C044 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 10 | 28
|  | STR |  | A200M2C*** | 5 | 45
A200C045 |  | CB |  | EH3070FFG | 100 | 70 | [5 empty] | 15 | 42
|  | STR |  | A200M2C*** | 5 | 45
A200C046 | C | CB | Eaton | EGH3050FFG | 65 | 50 | 480 | 3 | 65 | 460 | 3 | 15 | 21 | 0.695 | (1) (3) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M2C*** | 5 | 45
A200C047 |  | CB |  | EGH3050FFG | 65 | 50 | [5 empty] | 20 | 27
|  | STR |  | A200M2C*** | 5 | 45
A200C048 |  | CB |  | EGH3050FFG | 65 | 50 | [5 empty] | 25 | 34
|  | STR |  | A200M2C*** | 5 | 45
A200C049 | C | CB | Eaton | HFD3035L | 100 | 35 | 208 | 3 | 65 | 208 | 3 | 5 | 16.7 | 0.695 | (1) (3) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M2C*** | 5 | 45
A200C050 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | A200M2C*** | 5 | 45
A200C051 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 10 | 30.8
|  | STR |  | A200M2C*** | 5 | 45
A200C052 | C | CB | Eaton | HFD3050L | 100 | 50 | 240 | 3 | 65 | 230 | 3 | 7.5 | 22 | 0.695 | (1) (3) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M2C*** | 5 | 45
A200C053 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 10 | 28
|  | STR |  | A200M2C*** | 5 | 45
A200C054 |  | CB |  | HFD3070L | 100 | 70 | [5 empty] | 15 | 42
|  | STR |  | A200M2C*** | 5 | 45
A200C055 | C | CB | Eaton | HFD3050L | 65 | 50 | 480 | 3 | 65 | 460 | 3 | 15 | 21 | 0.695 | (1) (3) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M2C*** | 5 | 45
A200C056 |  | CB |  | HFD3050L | 65 | 50 | [5 empty] | 20 | 27
|  | STR |  | A200M2C*** | 5 | 45
A200C057 |  | CB |  | HFD3050L | 65 | 50 | [5 empty] | 25 | 34
|  | STR |  | A200M2C*** | 5 | 45
A200C058 | C | CB | Eaton | HFD3035L | 25 | 35 | 600 | 3 | 25 | 575 | 3 | 15 | 17 | 0.695 | (1) (3) (6a) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M2C*** | 5 | 45
A200C059 |  | CB |  | HFD3050L | 25 | 50 | [5 empty] | 20 | 22
|  | STR |  | A200M2C*** | 5 | 45
A200C060 |  | CB |  | HFD3050L | 25 | 50 | [5 empty] | 25 | 27
|  | STR |  | A200M2C*** | 5 | 45
A200C061 | C | CB | Eaton | FDC3035L | 200 | 35 | 208 | 3 | 100 | 208 | 3 | 5 | 16.7 | 0.695 | (1) (3) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M2C*** | 5 | 45
A200C062 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | A200M2C*** | 5 | 45
A200C063 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 10 | 30.8
|  | STR |  | A200M2C*** | 5 | 45
A200C064 | C | CB | Eaton | FDC3050L | 200 | 50 | 240 | 3 | 100 | 230 | 3 | 7.5 | 22 | 0.695 | (1) (3) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M2C*** | 5 | 45
A200C065 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 10 | 28
|  | STR |  | A200M2C*** | 5 | 45
A200C066 |  | CB |  | FDC3070L | 200 | 70 | [5 empty] | 15 | 42
|  | STR |  | A200M2C*** | 5 | 45
A200C067 | C | CB | Eaton | FDC3050L | 100 | 50 | 480 | 3 | 100 | 460 | 3 | 15 | 21 | 0.695 | (1) (3) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M2C*** | 5 | 45
A200C068 |  | CB |  | FDC3050L | 100 | 50 | [5 empty] | 20 | 27
|  | STR |  | A200M2C*** | 5 | 45
A200C069 |  | CB |  | FDC3050L | 100 | 50 | [5 empty] | 25 | 34
|  | STR |  | A200M2C*** | 5 | 45
A200C070 | C | CB | Eaton | FDC3035L | 35 | 35 | 600 | 3 | 35 | 575 | 3 | 15 | 17 | 0.695 | (1) (3) (6a) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M2C*** | 5 | 45
A200C071 |  | CB |  | FDC3050L | 35 | 50 | [5 empty] | 20 | 22
|  | STR |  | A200M2C*** | 5 | 45
A200C072 |  | CB |  | FDC3050L | 35 | 50 | [5 empty] | 25 | 27
|  | STR |  | A200M2C*** | 5 | 45
A200C073 | C | CB | Eaton | FB3035PL | 200 | 35 | 600 | 3 | 100 | 575 | 3 | 15 | 17 | 0.695 | (1) (3) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M2C*** | 5 | 45
A200C074 |  | CB |  | FB3050PL | 200 | 50 | [5 empty] | 20 | 22
|  | STR |  | A200M2C*** | 5 | 45
A200C075 |  | CB |  | FB3050PL | 200 | 50 | [5 empty] | 25 | 27
|  | STR |  | A200M2C*** | 5 | 45
A200C076 | C | CB | Eaton | HFD3035L | 25 | 35 | 600 | 3 | 100 | 575 | 3 | 15 | 17 | 0.695 | (1) (3) (7c) | - | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | A200M2C*** | 5 | 45
A200C077 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 20 | 22
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | A200M2C*** | 5 | 45
A200C078 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 25 | 27
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | A200M2C*** | 5 | 45
A200C079 | C | CB | Eaton | EGH3070FFG | 100 | 70 | 208 | 3 | 65 | 208 | 3 | 15 | 46.2 | 1.06 | (1) (3) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M3C*** | 5 | 90
A200C080 |  | CB |  | EGH3090FFG | 100 | 90 | [5 empty] | 20 | 59.4
|  | STR |  | A200M3C*** | 5 | 90
A200C081 |  | CB |  | EGH3125FFG | 100 | 125 | [5 empty] | 25 | 74.8
|  | STR |  | A200M3C*** | 5 | 90
A200C082 | C | CB | Eaton | EGH3090FFG | 100 | 90 | 240 | 3 | 65 | 230 | 3 | 20 | 54 | 1.06 | (1) (3) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M3C*** | 5 | 90
A200C083 |  | CB |  | EGH3125FFG | 100 | 125 | [5 empty] | 25 | 68
|  | STR |  | A200M3C*** | 5 | 90
A200C084 |  | CB |  | EGH3125FFG | 100 | 125 | [5 empty] | 30 | 80
|  | STR |  | A200M3C*** | 5 | 90
A200C085 | C | CB | Eaton | EGH3060FFG | 65 | 60 | 480 | 3 | 65 | 460 | 3 | 30 | 40 | 1.06 | (1) (3) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M3C*** | 5 | 90
A200C086 |  | CB |  | EGH3090FFG | 65 | 90 | [5 empty] | 40 | 52
|  | STR |  | A200M3C*** | 5 | 90
A200C087 |  | CB |  | EGH3100FFG | 65 | 100 | [5 empty] | 50 | 65
|  | STR |  | A200M3C*** | 5 | 90
A200C088 | C | CB | Eaton | HFD3070L | 100 | 70 | 208 | 3 | 65 | 208 | 3 | 15 | 46.2 | 1.06 | (1) (3) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M3C*** | 5 | 90
A200C089 |  | CB |  | HFD3090L | 100 | 90 | [5 empty] | 20 | 59.4
|  | STR |  | A200M3C*** | 5 | 90
A200C090 |  | CB |  | HFD3125L | 100 | 125 | [5 empty] | 25 | 74.8
|  | STR |  | A200M3C*** | 5 | 90
A200C091 | C | CB | Eaton | HFD3090L | 100 | 90 | 240 | 3 | 65 | 230 | 3 | 20 | 54 | 1.06 | (1) (3) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M3C*** | 5 | 90
A200C092 |  | CB |  | HFD3125L | 100 | 125 | [5 empty] | 25 | 68
|  | STR |  | A200M3C*** | 5 | 90
A200C093 |  | CB |  | HFD3125L | 100 | 125 | [5 empty] | 30 | 80
|  | STR |  | A200M3C*** | 5 | 90
A200C094 | C | CB | Eaton | HFD3060L | 65 | 60 | 480 | 3 | 65 | 460 | 3 | 30 | 40 | 1.06 | (1) (3) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M3C*** | 5 | 90
A200C095 |  | CB |  | HFD3090L | 65 | 90 | [5 empty] | 40 | 52
|  | STR |  | A200M3C*** | 5 | 90
A200C096 |  | CB |  | HFD3100L | 65 | 100 | [5 empty] | 50 | 65
|  | STR |  | A200M3C*** | 5 | 90
A200C097 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 25 | 575 | 3 | 30 | 32 | 1.06 | (1) (3) (6b) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M3C*** | 5 | 90
A200C098 |  | CB |  | HFD3060L | 25 | 60 | [5 empty] | 40 | 41
|  | STR |  | A200M3C*** | 5 | 90
A200C099 |  | CB |  | HFD3090L | 25 | 90 | [5 empty] | 50 | 52
|  | STR |  | A200M3C*** | 5 | 90
A200C100 | C | CB | Eaton | FDC3070L | 200 | 70 | 208 | 3 | 100 | 208 | 3 | 15 | 46.2 | 1.06 | (1) (3) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M3C*** | 5 | 90
A200C101 |  | CB |  | FDC3090L | 200 | 90 | [5 empty] | 20 | 59.4
|  | STR |  | A200M3C*** | 5 | 90
A200C102 |  | CB |  | FDC3125L | 200 | 125 | [5 empty] | 25 | 74.8
|  | STR |  | A200M3C*** | 5 | 90
A200C103 | C | CB | Eaton | FDC3090L | 200 | 90 | 240 | 3 | 100 | 230 | 3 | 20 | 54 | 1.06 | (1) (3) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M3C*** | 5 | 90
A200C104 |  | CB |  | FDC3125L | 200 | 125 | [5 empty] | 25 | 68
|  | STR |  | A200M3C*** | 5 | 90
A200C105 |  | CB |  | FDC3125L | 200 | 125 | [5 empty] | 30 | 80
|  | STR |  | A200M3C*** | 5 | 90
A200C106 | C | CB | Eaton | FDC3060L | 100 | 60 | 480 | 3 | 100 | 460 | 3 | 30 | 40 | 1.06 | (1) (3) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M3C*** | 5 | 90
A200C107 |  | CB |  | FDC3090L | 100 | 90 | [5 empty] | 40 | 52
|  | STR |  | A200M3C*** | 5 | 90
A200C108 |  | CB |  | FDC3100L | 100 | 100 | [5 empty] | 50 | 65
|  | STR |  | A200M3C*** | 5 | 90
A200C109 | C | CB | Eaton | FDC3050L | 35 | 50 | 600 | 3 | 35 | 575 | 3 | 30 | 32 | 1.06 | (1) (3) (6b) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M3C*** | 5 | 90
A200C110 |  | CB |  | FDC3060L | 35 | 60 | [5 empty] | 40 | 41
|  | STR |  | A200M3C*** | 5 | 90
A200C111 |  | CB |  | FDC3090L | 35 | 90 | [5 empty] | 50 | 52
|  | STR |  | A200M3C*** | 5 | 90
A200C112 | C | CB | Eaton | FB3050PL | 200 | 50 | 600 | 3 | 100 | 575 | 3 | 30 | 32 | 1.42 | (1) (3) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M3C*** | 5 | 90
A200C113 |  | CB |  | FB3060PL | 200 | 60 | [5 empty] | 40 | 41
|  | STR |  | A200M3C*** | 5 | 90
A200C114 |  | CB |  | FB3090PL | 200 | 90 | [5 empty] | 50 | 52
|  | STR |  | A200M3C*** | 5 | 90
A200C115 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 30 | 32 | 1.42 | (1) (3) (7e) | - | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | A200M3C*** | 5 | 90
A200C116 | C | CB | Eaton | HFD3060L | 25 | 60 | 600 | 3 | 100 | 575 | 3 | 40 | 41
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | A200M3C*** | 5 | 90
A200C117 | C | CB | Eaton | HFD3090L | 25 | 90 | 600 | 3 | 100 | 575 | 3 | 50 | 52
|  | C. Limiter |  | LFD3150R | 200 | 150
|  | STR |  | A200M3C*** | 5 | 90
A200C118 | C | CB | Eaton | JGH3125FAG | 100 | 125 | 208 | 3 | 65 | 208 | 3 | 25 | 74.8 | 1.42 | (1) (3) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M4C*** | 10 | 135
A200C119 |  | CB |  | JGH3150FAG | 100 | 150 | [5 empty] | 30 | 88
|  | STR |  | A200M4C*** | 10 | 135
A200C120 |  | CB |  | JGH3175FAG | 100 | 175 | [5 empty] | 40 | 114
|  | STR |  | A200M4C*** | 10 | 135
A200C121 | C | CB | Eaton | JGH3125FAG | 100 | 125 | 240 | 3 | 65 | 230 | 3 | 30 | 80 | 1.42 | (1) (3) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M4C*** | 10 | 135
A200C122 |  | CB |  | JGH3150FAG | 100 | 150 | [5 empty] | 40 | 104
|  | STR |  | A200M4C*** | 10 | 135
A200C123 |  | CB |  | JGH3200FAG | 100 | 200 | [5 empty] | 50 | 130
|  | STR |  | A200M4C*** | 10 | 135
A200C124 | C | CB | Eaton | JGH3125FAG | 65 | 125 | 480 | 3 | 65 | 460 | 3 | 60 | 77 | 1.42 | (1) (3) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M4C*** | 10 | 135
A200C125 |  | CB |  | JGH3150FAG | 65 | 150 | [5 empty] | 75 | 96
|  | STR |  | A200M4C*** | 10 | 135
A200C126 |  | CB |  | JGH3175FAG | 65 | 175 | [5 empty] | 100 | 124
|  | STR |  | A200M4C*** | 10 | 135
A200C127 | C | CB | Eaton | JGH3100FAG | 25 | 100 | 600 | 3 | 25 | 575 | 3 | 60 | 62 | 1.42 | (1) (3) (6b) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M4C*** | 10 | 135
A200C128 |  | CB |  | JGH3125FAG | 25 | 125 | [5 empty] | 75 | 77
|  | STR |  | A200M4C*** | 10 | 135
A200C129 |  | CB |  | JGH3150FAG | 25 | 150 | [5 empty] | 100 | 99
|  | STR |  | A200M4C*** | 10 | 135
A200C130 | C | CB | Eaton | HJD3125 | 100 | 125 | 208 | 3 | 65 | 208 | 3 | 25 | 74.8 | 1.42 | (1) (3) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M4C*** | 10 | 135
A200C131 |  | CB |  | HJD3150 | 100 | 150 | [5 empty] | 30 | 88
|  | STR |  | A200M4C*** | 10 | 135
A200C132 |  | CB |  | HJD3175 | 100 | 175 | [5 empty] | 40 | 114
|  | STR |  | A200M4C*** | 10 | 135
A200C133 | C | CB | Eaton | HJD3175 | 100 | 125 | 240 | 3 | 65 | 230 | 3 | 30 | 80 | 1.42 | (1) (3) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M4C*** | 10 | 135
A200C134 |  | CB |  | HJD3150 | 100 | 150 | [5 empty] | 40 | 104
|  | STR |  | A200M4C*** | 10 | 135
A200C135 |  | CB |  | HJD3200 | 100 | 200 | [5 empty] | 50 | 130
|  | STR |  | A200M4C*** | 10 | 135
A200C136 | C | CB | Eaton | HJD3125 | 65 | 125 | 480 | 3 | 65 | 460 | 3 | 60 | 77 | 1.42 | (1) (3) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M4C*** | 10 | 135
A200C137 |  | CB |  | HJD3150 | 65 | 150 | [5 empty] | 75 | 96
|  | STR |  | A200M4C*** | 10 | 135
A200C138 |  | CB |  | HJD3175 | 65 | 175 | [5 empty] | 100 | 124
|  | STR |  | A200M4C*** | 10 | 135
A200C139 | C | CB | Eaton | HJD3100 | 25 | 100 | 600 | 3 | 25 | 575 | 3 | 60 | 62 | 1.42 | (1) (3) (6b) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M4C*** | 10 | 135
A200C140 |  | CB |  | HJD3125 | 25 | 125 | [5 empty] | 75 | 77
|  | STR |  | A200M4C*** | 10 | 135
A200C141 |  | CB |  | HJD3150 | 25 | 150 | [5 empty] | 100 | 99
|  | STR |  | A200M4C*** | 10 | 135
A200C142 | C | CB | Eaton | JDC3125 | 200 | 125 | 208 | 3 | 100 | 208 | 3 | 25 | 74.8 | 1.42 | (1) (3) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M4C*** | 10 | 135
A200C143 |  | CB |  | JDC3150 | 200 | 150 | [5 empty] | 30 | 88
|  | STR |  | A200M4C*** | 10 | 135
A200C144 |  | CB |  | JDC3175 | 200 | 175 | [5 empty] | 40 | 114
|  | STR |  | A200M4C*** | 10 | 135
A200C145 | C | CB | Eaton | JDC3125 | 200 | 125 | 240 | 3 | 100 | 230 | 3 | 30 | 80 | 1.42 | (1) (3) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M4C*** | 10 | 135
A200C146 |  | CB |  | JDC3150 | 200 | 150 | [5 empty] | 40 | 104
|  | STR |  | A200M4C*** | 10 | 135
A200C147 |  | CB |  | JDC3200 | 200 | 200 | [5 empty] | 50 | 130
|  | STR |  | A200M4C*** | 10 | 135
A200C148 | C | CB | Eaton | JDC3125 | 100 | 125 | 480 | 3 | 100 | 460 | 3 | 60 | 77 | 1.42 | (1) (3) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M4C*** | 10 | 135
A200C149 |  | CB |  | JDC3150 | 100 | 150 | [5 empty] | 75 | 96
|  | STR |  | A200M4C*** | 10 | 135
A200C150 |  | CB |  | JDC3175 | 100 | 175 | [5 empty] | 100 | 124
|  | STR |  | A200M4C*** | 10 | 135
A200C151 | C | CB | Eaton | JDC3100 | 35 | 100 | 600 | 3 | 35 | 575 | 3 | 60 | 62 | 1.42 | (1) (3) (6b) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M4C*** | 10 | 135
A200C152 |  | CB |  | JDC3125 | 35 | 125 | [5 empty] | 75 | 77
|  | STR |  | A200M4C*** | 10 | 135
A200C153 |  | CB |  | JDC3150 | 35 | 150 | [5 empty] | 100 | 99
|  | STR |  | A200M4C*** | 10 | 135
A200C154 | C | CB | Eaton | LA3100PR | 200 | 100 | 600 | 3 | 100 | 575 | 3 | 60 | 62 | 2.5 | (1) (3) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M4C*** | 10 | 135
A200C155 |  | CB |  | LA3125PR | 200 | 125 | [5 empty] | 75 | 77
|  | STR |  | A200M4C*** | 10 | 135
A200C156 |  | CB |  | LA3150PR | 200 | 150 | [5 empty] | 100 | 99
|  | STR |  | A200M4C*** | 10 | 135
A200C157 | C | CB | Eaton | HKD3200 | 100 | 200 | 208 | 3 | 65 | 208 | 3 | 50 | 143 | 2.15 | (1) (3) (7j) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M5C*** | 10 | 270
A200C158 |  | CB |  | HKD3250 | 100 | 250 | [5 empty] | 60 | 169
|  | STR |  | A200M5C*** | 10 | 270
A200C159 |  | CB |  | HKD3350 | 100 | 350 | [5 empty] | 75 | 211
|  | STR |  | A200M5C*** | 10 | 270
A200C160 | C | CB | Eaton | HKD3250 | 100 | 250 | 240 | 3 | 65 | 230 | 3 | 60 | 154 | 2.15 | (1) (3) (7j) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M5C*** | 10 | 270
A200C161 |  | CB |  | HKD3300 | 100 | 300 | [5 empty] | 75 | 192
|  | STR |  | A200M5C*** | 10 | 270
A200C162 |  | CB |  | HKD3400 | 100 | 400 | [5 empty] | 100 | 248
|  | STR |  | A200M5C*** | 10 | 270
A200C163 | C | CB | Eaton | HKD3250 | 65 | 250 | 480 | 3 | 65 | 460 | 3 | 125 | 156 | 2.15 | (1) (3) (7j) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M5C*** | 10 | 270
A200C164 |  | CB |  | HKD3250 | 65 | 250 | [5 empty] | 150 | 180
|  | STR |  | A200M5C*** | 10 | 270
A200C165 |  | CB |  | HKD3350 | 65 | 350 | [5 empty] | 200 | 240
|  | STR |  | A200M5C*** | 10 | 270
A200C166 | C | CB | Eaton | HKD3175 | 25 | 175 | 600 | 3 | 25 | 575 | 3 | 125 | 125 | 2.15 | (1) (3) (7j) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M5C*** | 10 | 270
A200C167 |  | CB |  | HKD3200 | 25 | 200 | [5 empty] | 150 | 144
|  | STR |  | A200M5C*** | 10 | 270
A200C168 |  | CB |  | HKD3300 | 25 | 300 | [5 empty] | 200 | 192
|  | STR |  | A200M5C*** | 10 | 270
A200C169 | C | CB | Eaton | KDC3200 | 200 | 200 | 208 | 3 | 100 | 208 | 3 | 50 | 143 | 2.15 | (1) (3) (7j) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M5C*** | 10 | 270
A200C170 |  | CB |  | KDC3250 | 200 | 250 | [5 empty] | 60 | 169
|  | STR |  | A200M5C*** | 10 | 270
A200C171 |  | CB |  | KDC3350 | 200 | 350 | [5 empty] | 75 | 211
|  | STR |  | A200M5C*** | 10 | 270
A200C172 | C | CB | Eaton | KDC3250 | 200 | 250 | 240 | 3 | 100 | 230 | 3 | 60 | 154 | 2.15 | (1) (3) (7j) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M5C*** | 10 | 270
A200C173 |  | CB |  | KDC3300 | 200 | 300 | [5 empty] | 75 | 192
|  | STR |  | A200M5C*** | 10 | 270
A200C174 |  | CB |  | KDC3400 | 200 | 400 | [5 empty] | 100 | 248
|  | STR |  | A200M5C*** | 10 | 270
A200C175 | C | CB | Eaton | KDC3250 | 100 | 250 | 480 | 3 | 100 | 460 | 3 | 125 | 156 | 2.15 | (1) (3) (7j) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M5C*** | 10 | 270
A200C176 |  | CB |  | KDC3250 | 100 | 250 | [5 empty] | 150 | 180
|  | STR |  | A200M5C*** | 10 | 270
A200C177 |  | CB |  | KDC3350 | 100 | 350 | [5 empty] | 200 | 240
|  | STR |  | A200M5C*** | 10 | 270
A200C178 | C | CB | Eaton | KDC3175 | 50 | 175 | 600 | 3 | 50 | 575 | 3 | 125 | 125 | 2.15 | (1) (3) (7j) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M5C*** | 10 | 270
A200C179 |  | CB |  | KDC3200 | 50 | 200 | [5 empty] | 150 | 144
|  | STR |  | A200M5C*** | 10 | 270
A200C180 |  | CB |  | KDC3300 | 50 | 300 | [5 empty] | 200 | 192
|  | STR |  | A200M5C*** | 10 | 270
A200C181 | C | CB | Eaton | LA3175PR | 200 | 175 | 600 | 3 | 100 | 575 | 3 | 125 | 125 | 2.5 | (1) (3) (7j) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M5C*** | 10 | 270
A200C182 |  | CB |  | LA3200PR | 200 | 200 | [5 empty] | 150 | 144
|  | STR |  | A200M5C*** | 10 | 270
A200C183 |  | CB |  | LA3300PR | 200 | 300 | [5 empty] | 200 | 192
|  | STR |  | A200M5C*** | 10 | 270
A200C184 | C | CB | Eaton | HLD3400 | 100 | 400 | 208 | 3 | 65 | 208 | 3 | 100 | 273 | 2.15 | (1) (3) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M6C*** | 18 | 540
A200C185 |  | CB |  | HLD3600 | 100 | 600 | [5 empty] | 125 | 343
|  | STR |  | A200M6C*** | 18 | 540
A200C186 |  | CB |  | HLD3600 | 100 | 600 | [5 empty] | 150 | 396
|  | STR |  | A200M6C*** | 18 | 540
A200C187 | C | CB | Eaton | HLD3500 | 100 | 500 | 240 | 3 | 65 | 230 | 3 | 125 | 312 | 2.15 | (1) (3) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M6C*** | 18 | 540
A200C188 |  | CB |  | HLD3600 | 100 | 600 | [5 empty] | 150 | 360
|  | STR |  | A200M6C*** | 18 | 540
A200C189 |  | CB |  | HLD3600 | 100 | 600 | [5 empty] | 200 | 480
|  | STR |  | A200M6C*** | 18 | 540
A200C190 | C | CB | Eaton | HLD3600 | 65 | 600 | 480 | 3 | 65 | 460 | 3 | 300 | 361 | 2.15 | (1) (3) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M6C*** | 18 | 540
A200C191 |  | CB |  | HLD3600 | 65 | 600 | [5 empty] | 350 | 414
|  | STR |  | A200M6C*** | 18 | 540
A200C192 |  | CB |  | HLD3600 | 65 | 600 | [5 empty] | 400 | 477
|  | STR |  | A200M6C*** | 18 | 540
A200C193 | C | CB | Eaton | HLD3500 | 35 | 500 | 600 | 3 | 35 | 575 | 3 | 300 | 289 | 2.15 | (1) (3) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M6C*** | 18 | 540
A200C194 |  | CB |  | HLD3600 | 35 | 600 | [5 empty] | 350 | 336
|  | STR |  | A200M6C*** | 18 | 540
A200C195 |  | CB |  | HLD3600 | 35 | 600 | [5 empty] | 400 | 382
|  | STR |  | A200M6C*** | 18 | 540
A200C196 | C | CB | Eaton | HND3800T33W + 8NES400T | 100 | 400 | 208 | 3 | 65 | 208 | 3 | 100 | 273 | 3.23 | (1) (3) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M6C*** | 18 | 540
A200C197 |  | CB |  | HND3800T33W + 8NES600T | 100 | 600 | [5 empty] | 125 | 343
|  | STR |  | A200M6C*** | 18 | 540
A200C198 |  | CB |  | HND3800T33W + 8NES600T | 100 | 600 | [5 empty] | 150 | 396
|  | STR |  | A200M6C*** | 18 | 540
A200C199 | C | CB | Eaton | HND3800T33W + 8NES500T | 100 | 500 | 240 | 3 | 65 | 230 | 3 | 125 | 312 | 3.23 | (1) (3) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M6C*** | 18 | 540
A200C200 |  | CB |  | HND3800T33W + 8NES600T | 100 | 600 | [5 empty] | 150 | 360
|  | STR |  | A200M6C*** | 18 | 540
A200C201 |  | CB |  | HND3800T33W + 8NES600T | 100 | 600 | [5 empty] | 200 | 480
|  | STR |  | A200M6C*** | 18 | 540
A200C202 | C | CB | Eaton | HND3800T33W + 8NES600T | 65 | 600 | 480 | 3 | 65 | 460 | 3 | 300 | 361 | 3.23 | (1) (3) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M6C*** | 18 | 540
A200C203 |  | CB |  | HND3800T33W + 8NES600T | 65 | 600 | [5 empty] | 350 | 414
|  | STR |  | A200M6C*** | 18 | 540
A200C204 |  | CB |  | HND3800T33W + 8NES600T | 65 | 600 | [5 empty] | 400 | 477
|  | STR |  | A200M6C*** | 18 | 540
A200C205 | C | CB | Eaton | HND3800T33W + 8NES500T | 35 | 500 | 600 | 3 | 35 | 575 | 3 | 300 | 289 | 3.23 | (1) (3) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M6C*** | 18 | 540
A200C206 |  | CB |  | HND3800T33W + 8NES600T | 35 | 600 | [5 empty] | 350 | 336
|  | STR |  | A200M6C*** | 18 | 540
A200C207 |  | CB |  | HND3800T33W + 8NES600T | 35 | 600 | [5 empty] | 400 | 382
|  | STR |  | A200M6C*** | 18 | 540
A200C208 | C | CB | Eaton | NB3400P | 200 | 400 | 208 | 3 | 100 | 208 | 3 | 100 | 273 | 3.6 | (1) (3) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M6C*** | 18 | 540
A200C209 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 125 | 343
|  | STR |  | A200M6C*** | 18 | 540
A200C210 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 150 | 396
|  | STR |  | A200M6C*** | 18 | 540
A200C211 | C | CB | Eaton | NB3500P | 200 | 500 | 240 | 3 | 100 | 230 | 3 | 125 | 312 | 3.6 | (1) (3) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M6C*** | 18 | 540
A200C212 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 150 | 360
|  | STR |  | A200M6C*** | 18 | 540
A200C213 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 200 | 480
|  | STR |  | A200M6C*** | 18 | 540
A200C214 | C | CB | Eaton | NB3600P | 200 | 600 | 480 | 3 | 100 | 460 | 3 | 300 | 361 | 3.6 | (1) (3) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M6C*** | 18 | 540
A200C215 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 350 | 414
|  | STR |  | A200M6C*** | 18 | 540
A200C216 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 400 | 477
|  | STR |  | A200M6C*** | 18 | 540
A200C217 | C | CB | Eaton | NB3500P | 200 | 500 | 600 | 3 | 100 | 575 | 3 | 300 | 289 | 3.6 | (1) (3) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M6C*** | 18 | 540
A200C218 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 350 | 336
|  | STR |  | A200M6C*** | 18 | 540
A200C219 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 400 | 382
|  | STR |  | A200M6C*** | 18 | 540
A200C220 | C | CB | Eaton | HND321T33W + 12NES1200T | 100 | 1200 | 240 | 3 | 65 | 230 | 3 | 200 | 480 | 11.67 | (1) (3) (7m) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M7C*** | 30 | 810
A200C221 |  | CB |  | HND321T33W + 12NES1200T | 100 | 1200 | [5 empty] | 250 | 604
|  | STR |  | A200M7C*** | 30 | 810
A200C222 |  | CB |  | HND321T33W + 12NES1200T | 100 | 1200 | [5 empty] | 300 | 722
|  | STR |  | A200M7C*** | 30 | 810
A200C223 | C | CB | Eaton | HND321T33W + 12NES1200T | 65 | 1200 | 480 | 3 | 65 | 460 | 3 | 400 | 477 | 11.67 | (1) (3) (7m) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M7C*** | 30 | 810
A200C224 |  | CB |  | HND321T33W + 12NES1200T | 65 | 1200 | [5 empty] | 500 | 590
|  | STR |  | A200M7C*** | 30 | 810
A200C225 |  | CB |  | HND321T33W + 12NES1200T | 65 | 1200 | [5 empty] | 600 | 714
|  | STR |  | A200M7C*** | 30 | 810
A200C226 | C | CB | Eaton | NDC312T33W + 12NES1200T | 200 | 1200 | 240 | 3 | 65 | 230 | 3 | 200 | 480 | 11.67 | (1) (3) (7m) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M7C*** | 30 | 810
A200C227 |  | CB |  | NDC312T33W + 12NES1200T | 200 | 1200 | [5 empty] | 250 | 604
|  | STR |  | A200M7C*** | 30 | 810
A200C228 |  | CB |  | NDC312T33W + 12NES1200T | 200 | 1200 | [5 empty] | 300 | 722
|  | STR |  | A200M7C*** | 30 | 810
A200C229 | C | CB | Eaton | NDC312T33W + 12NES1200T | 100 | 1200 | 480 | 3 | 65 | 460 | 3 | 400 | 477 | 11.67 | (1) (3) (7m) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M7C*** | 30 | 810
A200C230 |  | CB |  | NDC312T33W + 12NES1200T | 100 | 1200 | [5 empty] | 500 | 590
|  | STR |  | A200M7C*** | 30 | 810
A200C231 |  | CB |  | NDC312T33W + 12NES1200T | 100 | 1200 | [5 empty] | 600 | 714
|  | STR |  | A200M7C*** | 30 | 810
A200C232 | C | CB | Eaton | EGH3025FFG | 100 | 25 | 208 | 3 | 65 | 208 | 3 | 3 | 10.6 | 0.695 | (1) (3) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M1C*** | 5 | 27
A200C233 |  | CB |  | EGH3035FFG | 100 | 35 | [5 empty] | 5 | 16.7
|  | STR |  | A210M1C*** | 5 | 27
A200C234 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | A210M1C*** | 5 | 27
A200C235 | C | CB | Eaton | EGH3025FFG | 100 | 25 | 240 | 3 | 65 | 230 | 3 | 3 | 9.6 | 0.695 | (1) (3) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M1C*** | 5 | 27
A200C236 |  | CB |  | EGH3035FFG | 100 | 35 | [5 empty] | 5 | 15.2
|  | STR |  | A210M1C*** | 5 | 27
A200C237 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 7.5 | 22
|  | STR |  | A210M1C*** | 5 | 27
A200C238 | C | CB | Eaton | EGH3020FFG | 65 | 20 | 480 | 3 | 65 | 460 | 3 | 5 | 7.6 | 0.695 | (1) (3) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M1C*** | 5 | 27
A200C239 |  | CB |  | EGH3030FFG | 65 | 30 | [5 empty] | 7.5 | 11
|  | STR |  | A210M1C*** | 5 | 27
A200C240 |  | CB |  | EGH3035FFG | 65 | 35 | [5 empty] | 10 | 14
|  | STR |  | A210M1C*** | 5 | 27
A200C241 | C | CB | Eaton | HFD3025L | 100 | 25 | 208 | 3 | 65 | 208 | 3 | 3 | 10.6 | 0.695 | (1) (3) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M1C*** | 5 | 27
A200C242 |  | CB |  | HFD3035L | 100 | 35 | [5 empty] | 5 | 16.7
|  | STR |  | A210M1C*** | 5 | 27
A200C243 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | A210M1C*** | 5 | 27
A200C244 | C | CB | Eaton | HFD3025L | 100 | 25 | 240 | 3 | 65 | 230 | 3 | 3 | 9.6 | 0.695 | (1) (3) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M1C*** | 5 | 27
A200C245 |  | CB |  | HFD3035L | 100 | 35 | [5 empty] | 5 | 15.2
|  | STR |  | A210M1C*** | 5 | 27
A200C246 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 22
|  | STR |  | A210M1C*** | 5 | 27
A200C247 | C | CB | Eaton | HFD3020L | 65 | 20 | 480 | 3 | 65 | 460 | 3 | 5 | 7.6 | 0.695 | (1) (3) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M1C*** | 5 | 27
A200C248 |  | CB |  | HFD3030L | 65 | 30 | [5 empty] | 7.5 | 11
|  | STR |  | A210M1C*** | 5 | 27
A200C249 |  | CB |  | HFD3035L | 65 | 35 | [5 empty] | 10 | 14
|  | STR |  | A210M1C*** | 5 | 27
A200C250 | C | CB | Eaton | HFD3015L | 25 | 15 | 600 | 3 | 25 | 575 | 3 | 5 | 6.1 | 0.695 | (1) (3) (6a) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M1C*** | 5 | 27
A200C251 |  | CB |  | HFD3015L | 25 | 15 | [5 empty] | 7.5 | 9
|  | STR |  | A210M1C*** | 5 | 27
A200C252 |  | CB |  | HFD3025L | 25 | 25 | [5 empty] | 10 | 11
|  | STR |  | A210M1C*** | 5 | 27
A200C253 | C | CB | Eaton | FDC3025L | 200 | 25 | 208 | 3 | 100 | 208 | 3 | 3 | 10.6 | 0.695 | (1) (3) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M1C*** | 5 | 27
A200C254 |  | CB |  | FDC3035L | 200 | 35 | [5 empty] | 5 | 16.7
|  | STR |  | A210M1C*** | 5 | 27
A200C255 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | A210M1C*** | 5 | 27
A200C256 | C | CB | Eaton | FDC3025L | 200 | 25 | 240 | 3 | 100 | 230 | 3 | 3 | 9.6 | 0.695 | (1) (3) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M1C*** | 5 | 27
A200C257 |  | CB |  | FDC3035L | 200 | 35 | [5 empty] | 5 | 15.2
|  | STR |  | A210M1C*** | 5 | 27
A200C258 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 22
|  | STR |  | A210M1C*** | 5 | 27
A200C259 | C | CB | Eaton | FDC3020L | 100 | 20 | 480 | 3 | 100 | 460 | 3 | 5 | 7.6 | 0.695 | (1) (3) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M1C*** | 5 | 27
A200C260 |  | CB |  | FDC3030L | 100 | 30 | [5 empty] | 7.5 | 11
|  | STR |  | A210M1C*** | 5 | 27
A200C261 |  | CB |  | FDC3035L | 100 | 35 | [5 empty] | 10 | 14
|  | STR |  | A210M1C*** | 5 | 27
A200C262 | C | CB | Eaton | FDC3015L | 35 | 15 | 600 | 3 | 35 | 575 | 3 | 5 | 6.1 | 0.695 | (1) (3) (6a) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M1C*** | 5 | 27
A200C263 |  | CB |  | FDC3015L | 35 | 15 | [5 empty] | 7.5 | 9
|  | STR |  | A210M1C*** | 5 | 27
A200C264 |  | CB |  | FDC3025L | 35 | 25 | [5 empty] | 10 | 11
|  | STR |  | A210M1C*** | 5 | 27
A200C265 | C | CB | Eaton | FB3015PL | 200 | 15 | 600 | 3 | 100 | 575 | 3 | 5 | 6.1 | 0.695 | (1) (3) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M1C*** | 5 | 27
A200C266 |  | CB |  | FB3015PL | 200 | 15 | [5 empty] | 7.5 | 9
|  | STR |  | A210M1C*** | 5 | 27
A200C267 |  | CB |  | FB3025PL | 200 | 25 | [5 empty] | 10 | 11
|  | STR |  | A210M1C*** | 5 | 27
A200C268 | C | CB | Eaton | HFD3015L | 25 | 15 | 600 | 3 | 100 | 575 | 3 | 5 | 6.1 | 0.695 | (1) (3) (7a) | - | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | A210M1C*** | 5 | 27
A200C269 | C | CB | Eaton | HFD3015L | 25 | 15 | 600 | 3 | 100 | 575 | 3 | 7.5 | 9
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | A210M1C*** | 5 | 27
A200C270 | C | CB | Eaton | HFD3025L | 25 | 25 | 600 | 3 | 100 | 575 | 3 | 10 | 11
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | A210M1C*** | 5 | 27
A200C271 | C | CB | Eaton | EGH3035FFG | 100 | 35 | 208 | 3 | 65 | 208 | 3 | 5 | 16.7 | 0.695 | (1) (3) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M2C*** | 5 | 45
A200C272 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | A210M2C*** | 5 | 45
A200C273 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 10 | 30.8
|  | STR |  | A210M2C*** | 5 | 45
A200C274 | C | CB | Eaton | EGH3050FFG | 100 | 50 | 240 | 3 | 65 | 230 | 3 | 7.5 | 22 | 0.695 | (1) (3) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M2C*** | 5 | 45
A200C275 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 10 | 28
|  | STR |  | A210M2C*** | 5 | 45
A200C276 |  | CB |  | EH3070FFG | 100 | 70 | [5 empty] | 15 | 42
|  | STR |  | A210M2C*** | 5 | 45
A200C277 | C | CB | Eaton | EGH3050FFG | 65 | 50 | 480 | 3 | 65 | 460 | 3 | 15 | 21 | 0.695 | (1) (3) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M2C*** | 5 | 45
A200C278 |  | CB |  | EGH3050FFG | 65 | 50 | [5 empty] | 20 | 27
|  | STR |  | A210M2C*** | 5 | 45
A200C279 |  | CB |  | EGH3050FFG | 65 | 50 | [5 empty] | 25 | 34
|  | STR |  | A210M2C*** | 5 | 45
A200C280 | C | CB | Eaton | HFD3035L | 100 | 35 | 208 | 3 | 65 | 208 | 3 | 5 | 16.7 | 0.695 | (1) (3) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M2C*** | 5 | 45
A200C281 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | A210M2C*** | 5 | 45
A200C282 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 10 | 30.8
|  | STR |  | A210M2C*** | 5 | 45
A200C283 | C | CB | Eaton | HFD3050L | 100 | 50 | 240 | 3 | 65 | 230 | 3 | 7.5 | 22 | 0.695 | (1) (3) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M2C*** | 5 | 45
A200C284 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 10 | 28
|  | STR |  | A210M2C*** | 5 | 45
A200C285 |  | CB |  | HFD3070L | 100 | 70 | [5 empty] | 15 | 42
|  | STR |  | A210M2C*** | 5 | 45
A200C286 | C | CB | Eaton | HFD3050L | 65 | 50 | 480 | 3 | 65 | 460 | 3 | 15 | 21 | 0.695 | (1) (3) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M2C*** | 5 | 45
A200C287 |  | CB |  | HFD3050L | 65 | 50 | [5 empty] | 20 | 27
|  | STR |  | A210M2C*** | 5 | 45
A200C288 |  | CB |  | HFD3050L | 65 | 50 | [5 empty] | 25 | 34
|  | STR |  | A210M2C*** | 5 | 45
A200C289 | C | CB | Eaton | HFD3035L | 25 | 35 | 600 | 3 | 25 | 575 | 3 | 15 | 17 | 0.695 | (1) (3) (6a) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M2C*** | 5 | 45
A200C290 |  | CB |  | HFD3050L | 25 | 50 | [5 empty] | 20 | 22
|  | STR |  | A210M2C*** | 5 | 45
A200C291 |  | CB |  | HFD3050L | 25 | 50 | [5 empty] | 25 | 27
|  | STR |  | A210M2C*** | 5 | 45
A200C292 | C | CB | Eaton | FDC3035L | 200 | 35 | 208 | 3 | 100 | 208 | 3 | 5 | 16.7 | 0.695 | (1) (3) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M2C*** | 5 | 45
A200C293 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | A210M2C*** | 5 | 45
A200C294 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 10 | 30.8
|  | STR |  | A210M2C*** | 5 | 45
A200C295 | C | CB | Eaton | FDC3050L | 200 | 50 | 240 | 3 | 100 | 230 | 3 | 7.5 | 22 | 0.695 | (1) (3) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M2C*** | 5 | 45
A200C296 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 10 | 28
|  | STR |  | A210M2C*** | 5 | 45
A200C297 |  | CB |  | FDC3070L | 200 | 70 | [5 empty] | 15 | 42
|  | STR |  | A210M2C*** | 5 | 45
A200C298 | C | CB | Eaton | FDC3050L | 100 | 50 | 480 | 3 | 100 | 460 | 3 | 15 | 21 | 0.695 | (1) (3) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M2C*** | 5 | 45
A200C299 |  | CB |  | FDC3050L | 100 | 50 | [5 empty] | 20 | 27
|  | STR |  | A210M2C*** | 5 | 45
A200C300 |  | CB |  | FDC3050L | 100 | 50 | [5 empty] | 25 | 34
|  | STR |  | A210M2C*** | 5 | 45
A200C301 | C | CB | Eaton | FDC3035L | 35 | 35 | 600 | 3 | 35 | 575 | 3 | 15 | 17 | 0.695 | (1) (3) (6a) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M2C*** | 5 | 45
A200C302 |  | CB |  | FDC3050L | 35 | 50 | [5 empty] | 20 | 22
|  | STR |  | A210M2C*** | 5 | 45
A200C303 |  | CB |  | FDC3050L | 35 | 50 | [5 empty] | 25 | 27
|  | STR |  | A210M2C*** | 5 | 45
A200C304 | C | CB | Eaton | FB3035PL | 200 | 35 | 600 | 3 | 100 | 575 | 3 | 15 | 17 | 0.695 | (1) (3) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M2C*** | 5 | 45
A200C305 |  | CB |  | FB3050PL | 200 | 50 | [5 empty] | 20 | 22
|  | STR |  | A210M2C*** | 5 | 45
A200C306 |  | CB |  | FB3050PL | 200 | 50 | [5 empty] | 25 | 27
|  | STR |  | A210M2C*** | 5 | 45
A200C307 | C | CB | Eaton | HFD3035L | 25 | 35 | 600 | 3 | 100 | 575 | 3 | 15 | 17 | 0.695 | (1) (3) (7c) | - | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | A210M2C*** | 5 | 45
A200C308 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 20 | 22
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | A210M2C*** | 5 | 45
A200C309 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 25 | 27
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | A210M2C*** | 5 | 45
A200C310 | C | CB | Eaton | EGH3070FFG | 100 | 70 | 208 | 3 | 65 | 208 | 3 | 15 | 46.2 | 1.06 | (1) (3) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M3C*** | 5 | 90
A200C311 |  | CB |  | EGH3090FFG | 100 | 90 | [5 empty] | 20 | 59.4
|  | STR |  | A210M3C*** | 5 | 90
A200C312 |  | CB |  | EGH3125FFG | 100 | 125 | [5 empty] | 25 | 74.8
|  | STR |  | A210M3C*** | 5 | 90
A200C313 | C | CB | Eaton | EGH3090FFG | 100 | 90 | 240 | 3 | 65 | 230 | 3 | 20 | 54 | 1.06 | (1) (3) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M3C*** | 5 | 90
A200C314 |  | CB |  | EGH3125FFG | 100 | 125 | [5 empty] | 25 | 68
|  | STR |  | A210M3C*** | 5 | 90
A200C315 |  | CB |  | EGH3125FFG | 100 | 125 | [5 empty] | 30 | 80
|  | STR |  | A210M3C*** | 5 | 90
A200C316 | C | CB | Eaton | EGH3060FFG | 65 | 60 | 480 | 3 | 65 | 460 | 3 | 30 | 40 | 1.06 | (1) (3) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M3C*** | 5 | 90
A200C317 |  | CB |  | EGH3090FFG | 65 | 90 | [5 empty] | 40 | 52
|  | STR |  | A210M3C*** | 5 | 90
A200C318 |  | CB |  | EGH3100FFG | 65 | 100 | [5 empty] | 50 | 65
|  | STR |  | A210M3C*** | 5 | 90
A200C319 | C | CB | Eaton | HFD3070L | 100 | 70 | 208 | 3 | 65 | 208 | 3 | 15 | 46.2 | 1.06 | (1) (3) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M3C*** | 5 | 90
A200C320 |  | CB |  | HFD3090L | 100 | 90 | [5 empty] | 20 | 59.4
|  | STR |  | A210M3C*** | 5 | 90
A200C321 |  | CB |  | HFD3125L | 100 | 125 | [5 empty] | 25 | 74.8
|  | STR |  | A210M3C*** | 5 | 90
A200C322 | C | CB | Eaton | HFD3090L | 100 | 90 | 240 | 3 | 65 | 230 | 3 | 20 | 54 | 1.06 | (1) (3) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M3C*** | 5 | 90
A200C323 |  | CB |  | HFD3125L | 100 | 125 | [5 empty] | 25 | 68
|  | STR |  | A210M3C*** | 5 | 90
A200C324 |  | CB |  | HFD3125L | 100 | 125 | [5 empty] | 30 | 80
|  | STR |  | A210M3C*** | 5 | 90
A200C325 | C | CB | Eaton | HFD3060L | 65 | 60 | 480 | 3 | 65 | 460 | 3 | 30 | 40 | 1.06 | (1) (3) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M3C*** | 5 | 90
A200C326 |  | CB |  | HFD3090L | 65 | 90 | [5 empty] | 40 | 52
|  | STR |  | A210M3C*** | 5 | 90
A200C327 |  | CB |  | HFD3100L | 65 | 100 | [5 empty] | 50 | 65
|  | STR |  | A210M3C*** | 5 | 90
A200C328 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 25 | 575 | 3 | 30 | 32 | 1.06 | (1) (3) (6b) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M3C*** | 5 | 90
A200C329 |  | CB |  | HFD3060L | 25 | 60 | [5 empty] | 40 | 41
|  | STR |  | A210M3C*** | 5 | 90
A200C330 |  | CB |  | HFD3090L | 25 | 90 | [5 empty] | 50 | 52
|  | STR |  | A210M3C*** | 5 | 90
A200C331 | C | CB | Eaton | FDC3070L | 200 | 70 | 208 | 3 | 100 | 208 | 3 | 15 | 46.2 | 1.06 | (1) (3) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M3C*** | 5 | 90
A200C332 |  | CB |  | FDC3090L | 200 | 90 | [5 empty] | 20 | 59.4
|  | STR |  | A210M3C*** | 5 | 90
A200C333 |  | CB |  | FDC3125L | 200 | 125 | [5 empty] | 25 | 74.8
|  | STR |  | A210M3C*** | 5 | 90
A200C334 | C | CB | Eaton | FDC3090L | 200 | 90 | 240 | 3 | 100 | 230 | 3 | 20 | 54 | 1.06 | (1) (3) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M3C*** | 5 | 90
A200C335 |  | CB |  | FDC3125L | 200 | 125 | [5 empty] | 25 | 68
|  | STR |  | A210M3C*** | 5 | 90
A200C336 |  | CB |  | FDC3125L | 200 | 125 | [5 empty] | 30 | 80
|  | STR |  | A210M3C*** | 5 | 90
A200C337 | C | CB | Eaton | FDC3060L | 100 | 60 | 480 | 3 | 100 | 460 | 3 | 30 | 40 | 1.06 | (1) (3) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M3C*** | 5 | 90
A200C338 |  | CB |  | FDC3090L | 100 | 90 | [5 empty] | 40 | 52
|  | STR |  | A210M3C*** | 5 | 90
A200C339 |  | CB |  | FDC3100L | 100 | 100 | [5 empty] | 50 | 65
|  | STR |  | A210M3C*** | 5 | 90
A200C340 | C | CB | Eaton | FDC3050L | 35 | 50 | 600 | 3 | 35 | 575 | 3 | 30 | 32 | 1.06 | (1) (3) (6b) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M3C*** | 5 | 90
A200C341 |  | CB |  | FDC3060L | 35 | 60 | [5 empty] | 40 | 41
|  | STR |  | A210M3C*** | 5 | 90
A200C342 |  | CB |  | FDC3090L | 35 | 90 | [5 empty] | 50 | 52
|  | STR |  | A210M3C*** | 5 | 90
A200C343 | C | CB | Eaton | FB3050PL | 200 | 50 | 600 | 3 | 100 | 575 | 3 | 30 | 32 | 1.42 | (1) (3) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M3C*** | 5 | 90
A200C344 |  | CB |  | FB3060PL | 200 | 60 | [5 empty] | 40 | 41
|  | STR |  | A210M3C*** | 5 | 90
A200C345 |  | CB |  | FB3090PL | 200 | 90 | [5 empty] | 50 | 52
|  | STR |  | A210M3C*** | 5 | 90
A200C346 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 30 | 32 | 1.42 | (1) (3) (7e) | - | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | A210M3C*** | 5 | 90
A200C347 | C | CB | Eaton | HFD3060L | 25 | 60 | 600 | 3 | 100 | 575 | 3 | 40 | 41
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | A210M3C*** | 5 | 90
A200C348 | C | CB | Eaton | HFD3090L | 25 | 90 | 600 | 3 | 100 | 575 | 3 | 50 | 52
|  | C. Limiter |  | LFD3150R | 200 | 150
|  | STR |  | A210M3C*** | 5 | 90
A200C349 | C | CB | Eaton | JGH3125FAG | 100 | 125 | 208 | 3 | 65 | 208 | 3 | 25 | 74.8 | 1.42 | (1) (3) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M4C*** | 10 | 135
A200C350 |  | CB |  | JGH3150FAG | 100 | 150 | [5 empty] | 30 | 88
|  | STR |  | A210M4C*** | 10 | 135
A200C351 |  | CB |  | JGH3175FAG | 100 | 175 | [5 empty] | 40 | 114
|  | STR |  | A210M4C*** | 10 | 135
A200C352 | C | CB | Eaton | JGH3125FAG | 100 | 125 | 240 | 3 | 65 | 230 | 3 | 30 | 80 | 1.42 | (1) (3) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M4C*** | 10 | 135
A200C353 |  | CB |  | JGH3150FAG | 100 | 150 | [5 empty] | 40 | 104
|  | STR |  | A210M4C*** | 10 | 135
A200C354 |  | CB |  | JGH3200FAG | 100 | 200 | [5 empty] | 50 | 130
|  | STR |  | A210M4C*** | 10 | 135
A200C355 | C | CB | Eaton | JGH3125FAG | 65 | 125 | 480 | 3 | 65 | 460 | 3 | 60 | 77 | 1.42 | (1) (3) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M4C*** | 10 | 135
A200C356 |  | CB |  | JGH3150FAG | 65 | 150 | [5 empty] | 75 | 96
|  | STR |  | A210M4C*** | 10 | 135
A200C357 |  | CB |  | JGH3175FAG | 65 | 175 | [5 empty] | 100 | 124
|  | STR |  | A210M4C*** | 10 | 135
A200C358 | C | CB | Eaton | JGH3100FAG | 35 | 100 | 600 | 3 | 25 | 575 | 3 | 60 | 62 | 1.42 | (1) (3) (6b) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M4C*** | 10 | 135
A200C359 |  | CB |  | JGH3125FAG | 35 | 125 | [5 empty] | 75 | 77
|  | STR |  | A210M4C*** | 10 | 135
A200C360 |  | CB |  | JGH3150FAG | 35 | 150 | [5 empty] | 100 | 99
|  | STR |  | A210M4C*** | 10 | 135
A200C361 | C | CB | Eaton | HJD3125 | 100 | 125 | 208 | 3 | 65 | 208 | 3 | 25 | 74.8 | 1.42 | (1) (3) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M4C*** | 10 | 135
A200C362 |  | CB |  | HJD3150 | 100 | 150 | [5 empty] | 30 | 88
|  | STR |  | A210M4C*** | 10 | 135
A200C363 |  | CB |  | HJD3175 | 100 | 175 | [5 empty] | 40 | 114
|  | STR |  | A210M4C*** | 10 | 135
A200C364 | C | CB | Eaton | HJD3125 | 100 | 125 | 240 | 3 | 65 | 230 | 3 | 30 | 80 | 1.42 | (1) (3) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M4C*** | 10 | 135
A200C365 |  | CB |  | HJD3150 | 100 | 150 | [5 empty] | 40 | 104
|  | STR |  | A210M4C*** | 10 | 135
A200C366 |  | CB |  | HJD3200 | 100 | 200 | [5 empty] | 50 | 130
|  | STR |  | A210M4C*** | 10 | 135
A200C367 | C | CB | Eaton | HJD3125 | 65 | 125 | 480 | 3 | 65 | 460 | 3 | 60 | 77 | 1.42 | (1) (3) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M4C*** | 10 | 135
A200C368 |  | CB |  | HJD3150 | 65 | 150 | [5 empty] | 75 | 96
|  | STR |  | A210M4C*** | 10 | 135
A200C369 |  | CB |  | HJD3175 | 65 | 175 | [5 empty] | 100 | 124
|  | STR |  | A210M4C*** | 10 | 135
A200C370 | C | CB | Eaton | HJD3100 | 25 | 100 | 600 | 3 | 25 | 575 | 3 | 60 | 62 | 1.42 | (1) (3) (6b) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M4C*** | 10 | 135
A200C371 |  | CB |  | HJD3125 | 25 | 125 | [5 empty] | 75 | 77
|  | STR |  | A210M4C*** | 10 | 135
A200C372 |  | CB |  | HJD3150 | 25 | 150 | [5 empty] | 100 | 99
|  | STR |  | A210M4C*** | 10 | 135
A200C373 | C | CB | Eaton | JDC3125 | 200 | 125 | 208 | 3 | 100 | 208 | 3 | 25 | 74.8 | 1.42 | (1) (3) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M4C*** | 10 | 135
A200C374 |  | CB |  | JDC3150 | 200 | 150 | [5 empty] | 30 | 88
|  | STR |  | A210M4C*** | 10 | 135
A200C375 |  | CB |  | JDC3175 | 200 | 175 | [5 empty] | 40 | 114
|  | STR |  | A210M4C*** | 10 | 135
A200C376 | C | CB | Eaton | JDC3125 | 200 | 125 | 240 | 3 | 100 | 230 | 3 | 30 | 80 | 1.42 | (1) (3) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M4C*** | 10 | 135
A200C377 |  | CB |  | JDC3150 | 200 | 150 | [5 empty] | 40 | 104
|  | STR |  | A210M4C*** | 10 | 135
A200C378 |  | CB |  | JDC3200 | 200 | 200 | [5 empty] | 50 | 130
|  | STR |  | A210M4C*** | 10 | 135
A200C379 | C | CB | Eaton | JDC3125 | 100 | 125 | 480 | 3 | 100 | 460 | 3 | 60 | 77 | 1.42 | (1) (3) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M4C*** | 10 | 135
A200C380 |  | CB |  | JDC3150 | 100 | 150 | [5 empty] | 75 | 96
|  | STR |  | A210M4C*** | 10 | 135
A200C381 |  | CB |  | JDC3175 | 100 | 175 | [5 empty] | 100 | 124
|  | STR |  | A210M4C*** | 10 | 135
A200C382 | C | CB | Eaton | JDC3100 | 35 | 100 | 600 | 3 | 35 | 575 | 3 | 60 | 62 | 1.42 | (1) (3) (6b) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M4C*** | 10 | 135
A200C383 |  | CB |  | JDC3125 | 35 | 125 | [5 empty] | 75 | 77
|  | STR |  | A210M4C*** | 10 | 135
A200C384 |  | CB |  | JDC3150 | 35 | 150 | [5 empty] | 100 | 99
|  | STR |  | A210M4C*** | 10 | 135
A200C385 | C | CB | Eaton | LA3100PR | 200 | 100 | 600 | 3 | 100 | 575 | 3 | 60 | 62 | 2.5 | (1) (3) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M4C*** | 10 | 135
A200C386 |  | CB |  | LA3125PR | 200 | 125 | [5 empty] | 75 | 77
|  | STR |  | A210M4C*** | 10 | 135
A200C387 |  | CB |  | LA3150PR | 200 | 150 | [5 empty] | 100 | 99
|  | STR |  | A210M4C*** | 10 | 135
A200C388 | C | CB | Eaton | HKD3200 | 100 | 200 | 208 | 3 | 65 | 208 | 3 | 50 | 143 | 2.15 | (1) (3) (7j) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M5C*** | 10 | 270
A200C389 |  | CB |  | HKD3250 | 100 | 250 | [5 empty] | 60 | 169
|  | STR |  | A210M5C*** | 10 | 270
A200C390 |  | CB |  | HKD3350 | 100 | 350 | [5 empty] | 75 | 211
|  | STR |  | A210M5C*** | 10 | 270
A200C391 | C | CB | Eaton | HKD3250 | 100 | 250 | 240 | 3 | 65 | 230 | 3 | 60 | 154 | 2.15 | (1) (3) (7j) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M5C*** | 10 | 270
A200C392 |  | CB |  | HKD3300 | 100 | 300 | [5 empty] | 75 | 192
|  | STR |  | A210M5C*** | 10 | 270
A200C393 |  | CB |  | HKD3400 | 100 | 400 | [5 empty] | 100 | 248
|  | STR |  | A210M5C*** | 10 | 270
A200C394 | C | CB | Eaton | HKD3250 | 65 | 250 | 480 | 3 | 65 | 460 | 3 | 125 | 156 | 2.15 | (1) (3) (7j) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M5C*** | 10 | 270
A200C395 |  | CB |  | HKD3250 | 65 | 250 | [5 empty] | 150 | 180
|  | STR |  | A210M5C*** | 10 | 270
A200C396 |  | CB |  | HKD3350 | 65 | 350 | [5 empty] | 200 | 240
|  | STR |  | A210M5C*** | 10 | 270
A200C397 | C | CB | Eaton | HKD3175 | 35 | 175 | 600 | 3 | 25 | 575 | 3 | 125 | 125 | 2.15 | (1) (3) (7j) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M5C*** | 10 | 270
A200C398 |  | CB |  | HKD3200 | 35 | 200 | [5 empty] | 150 | 144
|  | STR |  | A210M5C*** | 10 | 270
A200C399 |  | CB |  | HKD3300 | 35 | 300 | [5 empty] | 200 | 192
|  | STR |  | A210M5C*** | 10 | 270
A200C400 | C | CB | Eaton | KDC3200 | 200 | 200 | 208 | 3 | 100 | 208 | 3 | 50 | 143 | 2.15 | (1) (3) (7j) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M5C*** | 10 | 270
A200C401 |  | CB |  | KDC3250 | 200 | 250 | [5 empty] | 60 | 169
|  | STR |  | A210M5C*** | 10 | 270
A200C402 |  | CB |  | KDC3350 | 200 | 350 | [5 empty] | 75 | 211
|  | STR |  | A210M5C*** | 10 | 270
A200C403 | C | CB | Eaton | KDC3250 | 200 | 250 | 240 | 3 | 100 | 230 | 3 | 60 | 154 | 2.15 | (1) (3) (7j) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M5C*** | 10 | 270
A200C404 |  | CB |  | KDC3300 | 200 | 300 | [5 empty] | 75 | 192
|  | STR |  | A210M5C*** | 10 | 270
A200C405 |  | CB |  | KDC3400 | 200 | 400 | [5 empty] | 100 | 248
|  | STR |  | A210M5C*** | 10 | 270
A200C406 | C | CB | Eaton | KDC3250 | 100 | 250 | 480 | 3 | 100 | 460 | 3 | 125 | 156 | 2.15 | (1) (3) (7j) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M5C*** | 10 | 270
A200C407 |  | CB |  | KDC3250 | 100 | 250 | [5 empty] | 150 | 180
|  | STR |  | A210M5C*** | 10 | 270
A200C408 |  | CB |  | KDC3350 | 100 | 350 | [5 empty] | 200 | 240
|  | STR |  | A210M5C*** | 10 | 270
A200C409 | C | CB | Eaton | KDC3175 | 50 | 175 | 600 | 3 | 50 | 575 | 3 | 125 | 125 | 2.15 | (1) (3) (7j) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M5C*** | 10 | 270
A200C410 |  | CB |  | KDC3200 | 50 | 200 | [5 empty] | 150 | 144
|  | STR |  | A210M5C*** | 10 | 270
A200C411 |  | CB |  | KDC3300 | 50 | 300 | [5 empty] | 200 | 192
|  | STR |  | A210M5C*** | 10 | 270
A200C412 | C | CB | Eaton | LA3175PR | 200 | 175 | 600 | 3 | 50 | 575 | 3 | 125 | 125 | 2.5 | (1) (3) (7j) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M5C*** | 10 | 270
A200C413 |  | CB |  | LA3200PR | 200 | 200 | [5 empty] | 150 | 144
|  | STR |  | A210M5C*** | 10 | 270
A200C414 |  | CB |  | LA3300PR | 200 | 300 | [5 empty] | 200 | 192
|  | STR |  | A210M5C*** | 10 | 270
A200C415 | C | CB | Eaton | HLD3400 | 100 | 400 | 208 | 3 | 65 | 208 | 3 | 100 | 273 | 2.87 | (1) (3) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M6C*** | 18 | 540
A200C416 |  | CB |  | HLD3600 | 100 | 600 | [5 empty] | 125 | 343
|  | STR |  | A210M6C*** | 18 | 540
A200C417 |  | CB |  | HLD3600 | 100 | 600 | [5 empty] | 150 | 396
|  | STR |  | A210M6C*** | 18 | 540
A200C418 | C | CB | Eaton | HLD3500 | 100 | 500 | 240 | 3 | 65 | 230 | 3 | 125 | 312 | 2.87 | (1) (3) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M6C*** | 18 | 540
A200C419 |  | CB |  | HLD3600 | 100 | 600 | [5 empty] | 150 | 360
|  | STR |  | A210M6C*** | 18 | 540
A200C420 |  | CB |  | HLD3600 | 100 | 600 | [5 empty] | 200 | 480
|  | STR |  | A210M6C*** | 18 | 540
A200C421 | C | CB | Eaton | HLD3600 | 65 | 600 | 480 | 3 | 65 | 460 | 3 | 300 | 361 | 2.87 | (1) (3) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M6C*** | 18 | 540
A200C422 |  | CB |  | HLD3600 | 65 | 600 | [5 empty] | 350 | 414
|  | STR |  | A210M6C*** | 18 | 540
A200C423 |  | CB |  | HLD3600 | 65 | 600 | [5 empty] | 400 | 477
|  | STR |  | A210M6C*** | 18 | 540
A200C424 | C | CB | Eaton | HLD3500 | 35 | 500 | 600 | 3 | 35 | 575 | 3 | 300 | 289 | 2.87 | (1) (3) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M6C*** | 18 | 540
A200C425 |  | CB |  | HLD3600 | 35 | 600 | [5 empty] | 350 | 336
|  | STR |  | A210M6C*** | 18 | 540
A200C426 |  | CB |  | HLD3600 | 35 | 600 | [5 empty] | 400 | 382
|  | STR |  | A210M6C*** | 18 | 540
A200C427 | C | CB | Eaton | HND3800T33W + 8NES400T | 100 | 400 | 208 | 3 | 65 | 208 | 3 | 100 | 273 | 3.23 | (1) (3) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M6C*** | 18 | 540
A200C428 |  | CB |  | HND3800T33W + 8NES600T | 100 | 600 | [5 empty] | 125 | 343
|  | STR |  | A210M6C*** | 18 | 540
A200C429 |  | CB |  | HND3800T33W + 8NES600T | 100 | 600 | [5 empty] | 150 | 396
|  | STR |  | A210M6C*** | 18 | 540
A200C430 | C | CB | Eaton | HND3800T33W + 8NES500T | 100 | 500 | 240 | 3 | 65 | 230 | 3 | 125 | 312 | 3.23 | (1) (3) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M6C*** | 18 | 540
A200C431 |  | CB |  | HND3800T33W + 8NES600T | 100 | 600 | [5 empty] | 150 | 360
|  | STR |  | A210M6C*** | 18 | 540
A200C432 |  | CB |  | HND3800T33W + 8NES600T | 100 | 600 | [5 empty] | 200 | 480
|  | STR |  | A210M6C*** | 18 | 540
A200C433 | C | CB | Eaton | HND3800T33W + 8NES600T | 65 | 600 | 480 | 3 | 65 | 460 | 3 | 300 | 361 | 3.23 | (1) (3) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M6C*** | 18 | 540
A200C434 |  | CB |  | HND3800T33W + 8NES600T | 65 | 600 | [5 empty] | 350 | 414
|  | STR |  | A210M6C*** | 18 | 540
A200C435 |  | CB |  | HND3800T33W + 8NES600T | 65 | 600 | [5 empty] | 400 | 477
|  | STR |  | A210M6C*** | 18 | 540
A200C436 | C | CB | Eaton | HND3800T33W + 8NES500T | 35 | 500 | 600 | 3 | 35 | 575 | 3 | 300 | 289 | 3.23 | (1) (3) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M6C*** | 18 | 540
A200C437 |  | CB |  | HND3800T33W + 8NES600T | 35 | 600 | [5 empty] | 350 | 336
|  | STR |  | A210M6C*** | 18 | 540
A200C438 |  | CB |  | HND3800T33W + 8NES600T | 35 | 600 | [5 empty] | 400 | 382
|  | STR |  | A210M6C*** | 18 | 540
A200C439 | C | CB | Eaton | NB3400P | 200 | 400 | 208 | 3 | 100 | 208 | 3 | 100 | 273 | 3.6 | (1) (3) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M6C*** | 18 | 540
A200C440 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 125 | 343
|  | STR |  | A210M6C*** | 18 | 540
A200C441 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 150 | 396
|  | STR |  | A210M6C*** | 18 | 540
A200C442 | C | CB | Eaton | NB3500P | 200 | 500 | 240 | 3 | 100 | 230 | 3 | 125 | 312 | 3.6 | (1) (3) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M6C*** | 18 | 540
A200C443 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 150 | 360
|  | STR |  | A210M6C*** | 18 | 540
A200C444 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 200 | 480
|  | STR |  | A210M6C*** | 18 | 540
A200C445 | C | CB | Eaton | NB3600P | 200 | 600 | 480 | 3 | 100 | 460 | 3 | 300 | 361 | 3.6 | (1) (3) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M6C*** | 18 | 540
A200C446 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 350 | 414
|  | STR |  | A210M6C*** | 18 | 540
A200C447 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 400 | 477
|  | STR |  | A210M6C*** | 18 | 540
A200C448 | C | CB | Eaton | NB3500P | 200 | 500 | 600 | 3 | 100 | 575 | 3 | 300 | 289 | 3.6 | (1) (3) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M6C*** | 18 | 540
A200C449 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 350 | 336
|  | STR |  | A210M6C*** | 18 | 540
A200C450 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 400 | 382
|  | STR |  | A210M6C*** | 18 | 540
A200C451 | C | CB | Eaton | HND321T33W + 12NES1200T | 100 | 1200 | 240 | 3 | 65 | 230 | 3 | 200 | 480 | 11.67 | (1) (3) (7m) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M7C*** | 30 | 810
A200C452 |  | CB |  | HND321T33W + 12NES1200T | 100 | 1200 | [5 empty] | 250 | 604
|  | STR |  | A210M7C*** | 30 | 810
A200C453 |  | CB |  | HND321T33W + 12NES1200T | 100 | 1200 | [5 empty] | 300 | 722
|  | STR |  | A210M7C*** | 30 | 810
A200C454 | C | CB | Eaton | HND321T33W + 12NES1200T | 65 | 1200 | 480 | 3 | 65 | 460 | 3 | 400 | 477 | 11.67 | (1) (3) (7m) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M7C*** | 30 | 810
A200C455 |  | CB |  | HND321T33W + 12NES1200T | 65 | 1200 | [5 empty] | 500 | 590
|  | STR |  | A210M7C*** | 30 | 810
A200C456 |  | CB |  | HND321T33W + 12NES1200T | 65 | 1200 | [5 empty] | 600 | 714
|  | STR |  | A210M7C*** | 30 | 810
A200C457 | C | CB | Eaton | NDC312T33W + 12NES1200T | 200 | 1200 | 240 | 3 | 65 | 230 | 3 | 200 | 480 | 11.67 | (1) (3) (7m) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M7C*** | 30 | 810
A200C458 |  | CB |  | NDC312T33W + 12NES1200T | 200 | 1200 | [5 empty] | 250 | 604
|  | STR |  | A210M7C*** | 30 | 810
A200C459 |  | CB |  | NDC312T33W + 12NES1200T | 200 | 1200 | [5 empty] | 300 | 722
|  | STR |  | A210M7C*** | 30 | 810
A200C460 | C | CB | Eaton | NDC312T33W + 12NES1200T | 100 | 1200 | 480 | 3 | 65 | 460 | 3 | 400 | 477 | 11.67 | (1) (3) (7m) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M7C*** | 30 | 810
A200C461 |  | CB |  | NDC312T33W + 12NES1200T | 100 | 1200 | [5 empty] | 500 | 590
|  | STR |  | A210M7C*** | 30 | 810
A200C462 |  | CB |  | NDC312T33W + 12NES1200T | 100 | 1200 | [5 empty] | 600 | 714
|  | STR |  | A210M7C*** | 30 | 810
A200C463 | C | CB | Eaton | EGH3025FFG | 100 | 25 | 208 | 3 | 65 | 208 | 3 | 3 | 10.6 | 0.695 | (1) (7a) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K1C* | 5 | 27
A200C464 |  | CB |  | EGH3035FFG | 100 | 35 | [5 empty] | 5 | 16.7
|  | MC |  | A201K1C* | 5 | 27
A200C465 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 7.5 | 24.2
|  | MC |  | A201K1C* | 5 | 27
A200C466 | C | CB | Eaton | EGH3025FFG | 100 | 25 | 240 | 3 | 65 | 230 | 3 | 3 | 9.6 | 0.695 | (1) (7a) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K1C* | 5 | 27
A200C467 |  | CB |  | EGH3035FFG | 100 | 35 | [5 empty] | 5 | 15.2
|  | MC |  | A201K1C* | 5 | 27
A200C468 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 7.5 | 22
|  | MC |  | A201K1C* | 5 | 27
A200C469 | C | CB | Eaton | EGH3020FFG | 65 | 20 | 480 | 3 | 65 | 460 | 3 | 5 | 7.6 | 0.695 | (1) (7a) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K1C* | 5 | 27
A200C470 |  | CB |  | EGH3030FFG | 65 | 30 | [5 empty] | 7.5 | 11
|  | MC |  | A201K1C* | 5 | 27
A200C471 |  | CB |  | EGH3035FFG | 65 | 35 | [5 empty] | 10 | 14
|  | MC |  | A201K1C* | 5 | 27
A200C472 | C | CB | Eaton | HFD3025L | 100 | 25 | 208 | 3 | 65 | 208 | 3 | 3 | 10.6 | 0.695 | (1) (7a) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K1C* | 5 | 27
A200C473 |  | CB |  | HFD3035L | 100 | 35 | [5 empty] | 5 | 16.7
|  | MC |  | A201K1C* | 5 | 27
A200C474 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 24.2
|  | MC |  | A201K1C* | 5 | 27
A200C475 | C | CB | Eaton | HFD3025L | 100 | 25 | 240 | 3 | 65 | 230 | 3 | 3 | 9.6 | 0.695 | (1) (7a) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K1C* | 5 | 27
A200C476 |  | CB |  | HFD3035L | 100 | 35 | [5 empty] | 5 | 15.2
|  | MC |  | A201K1C* | 5 | 27
A200C477 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 22
|  | MC |  | A201K1C* | 5 | 27
A200C478 | C | CB | Eaton | HFD3020L | 65 | 20 | 480 | 3 | 65 | 460 | 3 | 5 | 7.6 | 0.695 | (1) (7a) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K1C* | 5 | 27
A200C479 |  | CB |  | HFD3030L | 65 | 30 | [5 empty] | 7.5 | 11
|  | MC |  | A201K1C* | 5 | 27
A200C480 |  | CB |  | HFD3035L | 65 | 35 | [5 empty] | 10 | 14
|  | MC |  | A201K1C* | 5 | 27
A200C481 | C | CB | Eaton | HFD3015L | 25 | 15 | 600 | 3 | 25 | 575 | 3 | 5 | 6.1 | 0.695 | (1) (6a) (7a) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K1C* | 5 | 27
A200C482 |  | CB |  | HFD3025L | 25 | 25 | [5 empty] | 7.5 | 9
|  | MC |  | A201K1C* | 5 | 27
A200C483 |  | CB |  | HFD3030L | 25 | 30 | [5 empty] | 10 | 11
|  | MC |  | A201K1C* | 5 | 27
A200C484 | C | CB | Eaton | FDC3025L | 200 | 25 | 208 | 3 | 100 | 208 | 3 | 3 | 10.6 | 0.695 | (1) (7a) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K1C* | 5 | 27
A200C485 |  | CB |  | FDC3050L | 200 | 35 | [5 empty] | 5 | 16.7
|  | MC |  | A201K1C* | 5 | 27
A200C486 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 24.2
|  | MC |  | A201K1C* | 5 | 27
A200C487 | C | CB | Eaton | FDC3025L | 200 | 25 | 240 | 3 | 100 | 230 | 3 | 3 | 9.6 | 0.695 | (1) (7a) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K1C* | 5 | 27
A200C488 |  | CB |  | FDC3035L | 200 | 35 | [5 empty] | 5 | 15.2
|  | MC |  | A201K1C* | 5 | 27
A200C489 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 22
|  | MC |  | A201K1C* | 5 | 27
A200C490 | C | CB | Eaton | FDC3020L | 100 | 20 | 480 | 3 | 100 | 460 | 3 | 5 | 7.6 | 0.695 | (1) (7a) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K1C* | 5 | 27
A200C491 |  | CB |  | FDC3030L | 100 | 30 | [5 empty] | 7.5 | 11
|  | MC |  | A201K1C* | 5 | 27
A200C492 |  | CB |  | FDC3035L | 100 | 35 | [5 empty] | 10 | 14
|  | MC |  | A201K1C* | 5 | 27
A200C493 | C | CB | Eaton | FDC3015L | 35 | 15 | 600 | 3 | 35 | 575 | 3 | 5 | 6.1 | 0.695 | (1) (6a) (7a) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K1C* | 5 | 27
A200C494 |  | CB |  | FDC3025L | 35 | 25 | [5 empty] | 7.5 | 9
|  | MC |  | A201K1C* | 5 | 27
A200C495 |  | CB |  | FDC3030L | 35 | 30 | [5 empty] | 10 | 11
|  | MC |  | A201K1C* | 5 | 27
A200C496 | C | CB | Eaton | HFD3015L | 25 | 15 | 600 | 3 | 100 | 575 | 3 | 5 | 6.1 | 0.695 | (1) (7a) | - | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | MC |  | A201K1C* | 5 | 27
A200C497 | C | CB | Eaton | HFD3025L | 25 | 25 | 600 | 3 | 100 | 575 | 3 | 7.5 | 9
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | MC |  | A201K1C* | 5 | 27
A200C498 | C | CB | Eaton | HFD3030L | 25 | 30 | 600 | 3 | 100 | 575 | 3 | 10 | 11
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | MC |  | A201K1C* | 5 | 27
A200C499 | C | CB | Eaton | EGH3035FFG | 100 | 35 | 208 | 3 | 65 | 208 | 3 | 5 | 16.7 | 0.695 | (1) (7c) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K2C* | 5 | 45
A200C500 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 7.5 | 24.2
|  | MC |  | A201K2C* | 5 | 45
A200C501 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 10 | 30.8
|  | MC |  | A201K2C* | 5 | 45
A200C502 | C | CB | Eaton | EGH3050FFG | 100 | 50 | 240 | 3 | 65 | 230 | 3 | 7.5 | 22 | 0.695 | (1) (7c) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K2C* | 5 | 45
A200C503 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 10 | 28
|  | MC |  | A201K2C* | 5 | 45
A200C504 |  | CB |  | EGH3070FFG | 100 | 70 | [5 empty] | 15 | 42
|  | MC |  | A201K2C* | 5 | 45
A200C505 | C | CB | Eaton | EGH3050FFG | 65 | 50 | 480 | 3 | 65 | 460 | 3 | 15 | 21 | 0.695 | (1) (7c) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K2C* | 5 | 45
A200C506 |  | CB |  | EGH3050FFG | 65 | 50 | [5 empty] | 20 | 27
|  | MC |  | A201K2C* | 5 | 45
A200C507 |  | CB |  | EGH3050FFG | 65 | 50 | [5 empty] | 25 | 34
|  | MC |  | A201K2C* | 5 | 45
A200C508 | C | CB | Eaton | HFD3035L | 100 | 35 | 208 | 3 | 65 | 208 | 3 | 5 | 16.7 | 0.695 | (1) (7c) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K2C* | 5 | 45
A200C509 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 24.2
|  | MC |  | A201K2C* | 5 | 45
A200C510 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 10 | 30.8
|  | MC |  | A201K2C* | 5 | 45
A200C511 | C | CB | Eaton | HFD3050L | 100 | 50 | 240 | 3 | 65 | 230 | 3 | 7.5 | 22 | 0.695 | (1) (7c) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K2C* | 5 | 45
A200C512 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 10 | 28
|  | MC |  | A201K2C* | 5 | 45
A200C513 |  | CB |  | HFD3070L | 100 | 70 | [5 empty] | 15 | 42
|  | MC |  | A201K2C* | 5 | 45
A200C514 | C | CB | Eaton | HFD3050L | 65 | 50 | 480 | 3 | 65 | 460 | 3 | 15 | 21 | 0.695 | (1) (7c) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K2C* | 5 | 45
A200C515 |  | CB |  | HFD3050L | 65 | 50 | [5 empty] | 20 | 27
|  | MC |  | A201K2C* | 5 | 45
A200C516 |  | CB |  | HFD3050L | 65 | 50 | [5 empty] | 25 | 34
|  | MC |  | A201K2C* | 5 | 45
A200C517 | C | CB | Eaton | HFD3035L | 25 | 35 | 600 | 3 | 25 | 575 | 3 | 15 | 17 | 0.695 | (1) (6a) (7c) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K2C* | 5 | 45
A200C518 |  | CB |  | HFD3050L | 25 | 50 | [5 empty] | 20 | 22
|  | MC |  | A201K2C* | 5 | 45
A200C519 |  | CB |  | HFD3050L | 25 | 50 | [5 empty] | 25 | 27
|  | MC |  | A201K2C* | 5 | 45
A200C520 | C | CB | Eaton | FDC3035L | 200 | 35 | 208 | 3 | 100 | 208 | 3 | 5 | 16.7 | 0.695 | (1) (7c) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K2C* | 5 | 45
A200C521 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 24.2
|  | MC |  | A201K2C* | 5 | 45
A200C522 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 10 | 30.8
|  | MC |  | A201K2C* | 5 | 45
A200C523 | C | CB | Eaton | FDC3050L | 200 | 50 | 240 | 3 | 100 | 230 | 3 | 7.5 | 22 | 0.695 | (1) (7c) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K2C* | 5 | 45
A200C524 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 10 | 28
|  | MC |  | A201K2C* | 5 | 45
A200C525 |  | CB |  | FDC3070L | 200 | 70 | [5 empty] | 15 | 42
|  | MC |  | A201K2C* | 5 | 45
A200C526 | C | CB | Eaton | FDC3050L | 100 | 50 | 480 | 3 | 100 | 460 | 3 | 15 | 21 | 0.695 | (1) (7c) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K2C* | 5 | 45
A200C527 |  | CB |  | FDC3050L | 100 | 50 | [5 empty] | 20 | 27
|  | MC |  | A201K2C* | 5 | 45
A200C528 |  | CB |  | FDC3050L | 100 | 50 | [5 empty] | 25 | 34
|  | MC |  | A201K2C* | 5 | 45
A200C529 | C | CB | Eaton | FDC3035L | 35 | 35 | 600 | 3 | 35 | 575 | 3 | 15 | 17 | 0.695 | (1) (6a) (7c) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K2C* | 5 | 45
A200C530 |  | CB |  | FDC3050L | 35 | 50 | [5 empty] | 20 | 22
|  | MC |  | A201K2C* | 5 | 45
A200C531 |  | CB |  | FDC3050L | 35 | 50 | [5 empty] | 25 | 27
|  | MC |  | A201K2C* | 5 | 45
A200C532 | C | CB | Eaton | HFD3035L | 25 | 35 | 600 | 3 | 100 | 575 | 3 | 15 | 17 | 0.695 | (1) (7c) | - | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | MC |  | A201K2C* | 5 | 45
A200C533 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 20 | 22
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | MC |  | A201K2C* | 5 | 45
A200C534 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 25 | 27
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | MC |  | A201K2C* | 5 | 45
A200C535 | C | CB | Eaton | EGH3070FFG | 100 | 70 | 208 | 3 | 65 | 208 | 3 | 15 | 46.2 | 1.06 | (1) (7e) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K3C* | 5 | 90
A200C536 |  | CB |  | EGH3090FFG | 100 | 90 | [5 empty] | 20 | 59.4
|  | MC |  | A201K3C* | 5 | 90
A200C537 |  | CB |  | EGH3125FFG | 100 | 125 | [5 empty] | 25 | 74.8
|  | MC |  | A201K3C* | 5 | 90
A200C538 | C | CB | Eaton | EGH3090FFG | 100 | 90 | 240 | 3 | 65 | 230 | 3 | 20 | 54 | 1.06 | (1) (7e) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K3C* | 5 | 90
A200C539 |  | CB |  | EGH3125FFG | 100 | 125 | [5 empty] | 25 | 68
|  | MC |  | A201K3C* | 5 | 90
A200C540 |  | CB |  | EGH3125FFG | 100 | 125 | [5 empty] | 30 | 80
|  | MC |  | A201K3C* | 5 | 90
A200C541 | C | CB | Eaton | EGH3060FFG | 65 | 60 | 480 | 3 | 65 | 460 | 3 | 30 | 40 | 1.06 | (1) (7e) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K3C* | 5 | 90
A200C542 |  | CB |  | EGH3090FFG | 65 | 90 | [5 empty] | 40 | 52
|  | MC |  | A201K3C* | 5 | 90
A200C543 |  | CB |  | EGH3100FFG | 65 | 100 | [5 empty] | 50 | 65
|  | MC |  | A201K3C* | 5 | 90
A200C544 | C | CB | Eaton | HFD3070L | 100 | 70 | 208 | 3 | 65 | 208 | 3 | 15 | 46.2 | 1.06 | (1) (7e) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K3C* | 5 | 90
A200C545 |  | CB |  | HFD3090L | 100 | 90 | [5 empty] | 20 | 59.4
|  | MC |  | A201K3C* | 5 | 90
A200C546 |  | CB |  | HFD3125L | 100 | 125 | [5 empty] | 25 | 74.8
|  | MC |  | A201K3C* | 5 | 90
A200C547 | C | CB | Eaton | HFD3090L | 100 | 90 | 240 | 3 | 65 | 230 | 3 | 20 | 54 | 1.06 | (1) (7e) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K3C* | 5 | 90
A200C548 |  | CB |  | HFD3125L | 100 | 125 | [5 empty] | 25 | 68
|  | MC |  | A201K3C* | 5 | 90
A200C549 |  | CB |  | HFD3125L | 100 | 125 | [5 empty] | 30 | 80
|  | MC |  | A201K3C* | 5 | 90
A200C550 | C | CB | Eaton | HFD3060L | 65 | 60 | 480 | 3 | 65 | 460 | 3 | 30 | 40 | 1.06 | (1) (7e) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K3C* | 5 | 90
A200C551 |  | CB |  | HFD3090L | 65 | 90 | [5 empty] | 40 | 52
|  | MC |  | A201K3C* | 5 | 90
A200C552 |  | CB |  | HFD3100L | 65 | 100 | [5 empty] | 50 | 65
|  | MC |  | A201K3C* | 5 | 90
A200C553 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 25 | 575 | 3 | 30 | 32 | 1.06 | (1) (6b) (7e) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K3C* | 5 | 90
A200C554 |  | CB |  | HFD3060L | 25 | 60 | [5 empty] | 40 | 41
|  | MC |  | A201K3C* | 5 | 90
A200C555 |  | CB |  | HFD3090L | 25 | 90 | [5 empty] | 50 | 52
|  | MC |  | A201K3C* | 5 | 90
A200C556 | C | CB | Eaton | FDC3070L | 200 | 70 | 208 | 3 | 100 | 208 | 3 | 15 | 46.2 | 1.06 | (1) (7e) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K3C* | 5 | 90
A200C557 |  | CB |  | FDC3090L | 200 | 90 | [5 empty] | 20 | 59.4
|  | MC |  | A201K3C* | 5 | 90
A200C558 |  | CB |  | FDC3125L | 200 | 125 | [5 empty] | 25 | 74.8
|  | MC |  | A201K3C* | 5 | 90
A200C559 | C | CB | Eaton | FDC3090L | 200 | 90 | 240 | 3 | 100 | 230 | 3 | 20 | 54 | 1.06 | (1) (7e) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K3C* | 5 | 90
A200C560 |  | CB |  | FDC3125L | 200 | 125 | [5 empty] | 25 | 68
|  | MC |  | A201K3C* | 5 | 90
A200C561 |  | CB |  | FDC3125L | 200 | 125 | [5 empty] | 30 | 80
|  | MC |  | A201K3C* | 5 | 90
A200C562 | C | CB | Eaton | FDC3060L | 100 | 60 | 480 | 3 | 100 | 460 | 3 | 30 | 40 | 1.06 | (1) (7e) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K3C* | 5 | 90
A200C563 |  | CB |  | FDC3090L | 100 | 90 | [5 empty] | 40 | 52
|  | MC |  | A201K3C* | 5 | 90
A200C564 |  | CB |  | FDC3100L | 100 | 100 | [5 empty] | 50 | 65
|  | MC |  | A201K3C* | 5 | 90
A200C565 | C | CB | Eaton | FDC3050L | 35 | 50 | 600 | 3 | 35 | 575 | 3 | 30 | 32 | 1.06 | (1) (6b) (7e) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K3C* | 5 | 90
A200C566 |  | CB |  | FDC3060L | 35 | 60 | [5 empty] | 40 | 41
|  | MC |  | A201K3C* | 5 | 90
A200C567 |  | CB |  | FDC3090L | 35 | 90 | [5 empty] | 50 | 52
|  | MC |  | A201K3C* | 5 | 90
A200C568 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 30 | 32 | 1.42 | (1) (7e) | - | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | MC |  | A201K3C* | 5 | 90
A200C569 | C | CB | Eaton | HFD3060L | 25 | 60 | 600 | 3 | 100 | 575 | 3 | 40 | 41
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | MC |  | A201K3C* | 5 | 90
A200C570 | C | CB | Eaton | HFD3090L | 25 | 90 | 600 | 3 | 100 | 575 | 3 | 50 | 52
|  | C. Limiter |  | LFD3150R | 200 | 150
|  | MC |  | A201K3C* | 5 | 90
A200C571 | C | CB | Eaton | HJD3125 | 100 | 125 | 208 | 3 | 65 | 208 | 3 | 25 | 74.8 | 1.42 | (1) (7f) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K4C* | 10 | 135
A200C572 |  | CB |  | HJD3150 | 100 | 150 | [5 empty] | 30 | 88
|  | MC |  | A201K4C* | 10 | 135
A200C573 |  | CB |  | HJD3175 | 100 | 175 | [5 empty] | 40 | 114
|  | MC |  | A201K4C* | 10 | 135
A200C574 | C | CB | Eaton | HJD3125 | 100 | 125 | 240 | 3 | 65 | 230 | 3 | 30 | 80 | 1.42 | (1) (7f) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K4C* | 10 | 135
A200C575 |  | CB |  | HJD3150 | 100 | 150 | [5 empty] | 40 | 104
|  | MC |  | A201K4C* | 10 | 135
A200C576 |  | CB |  | HJD3200 | 100 | 200 | [5 empty] | 50 | 130
|  | MC |  | A201K4C* | 10 | 135
A200C577 | C | CB | Eaton | HJD3125 | 65 | 125 | 480 | 3 | 65 | 460 | 3 | 60 | 77 | 1.42 | (1) (7f) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K4C* | 10 | 135
A200C578 |  | CB |  | HJD3150 | 65 | 150 | [5 empty] | 75 | 96
|  | MC |  | A201K4C* | 10 | 135
A200C579 |  | CB |  | HJD3175 | 65 | 175 | [5 empty] | 100 | 124
|  | MC |  | A201K4C* | 10 | 135
A200C580 | C | CB | Eaton | HJD3100 | 25 | 100 | 600 | 3 | 25 | 575 | 3 | 60 | 62 | 1.42 | (1) (6b) (7f) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K4C* | 10 | 135
A200C581 |  | CB |  | HJD3125 | 25 | 125 | [5 empty] | 75 | 77
|  | MC |  | A201K4C* | 10 | 135
A200C582 |  | CB |  | HJD3150 | 25 | 150 | [5 empty] | 100 | 99
|  | MC |  | A201K4C* | 10 | 135
A200C583 | C | CB | Eaton | EGH3025FFG | 100 | 25 | 208 | 3 | 65 | 208 | 3 | 3 | 10.6 | 0.695 | (1) (7a) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K1C* | 5 | 27
A200C584 |  | CB |  | EGH3035FFG | 100 | 35 | [5 empty] | 5 | 16.7
|  | MC |  | A251K1C* | 5 | 27
A200C585 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 7.5 | 24.2
|  | MC |  | A251K1C* | 5 | 27
A200C586 | C | CB | Eaton | EGH3025FFG | 100 | 25 | 240 | 3 | 65 | 230 | 3 | 3 | 9.6 | 0.695 | (1) (7a) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K1C* | 5 | 27
A200C587 |  | CB |  | EGH3035FFG | 100 | 35 | [5 empty] | 5 | 15.2
|  | MC |  | A251K1C* | 5 | 27
A200C588 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 7.5 | 22
|  | MC |  | A251K1C* | 5 | 27
A200C589 | C | CB | Eaton | EGH3020FFG | 65 | 20 | 480 | 3 | 65 | 460 | 3 | 5 | 7.6 | 0.695 | (1) (7a) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K1C* | 5 | 27
A200C590 |  | CB |  | EGH3030FFG | 65 | 30 | [5 empty] | 7.5 | 11
|  | MC |  | A251K1C* | 5 | 27
A200C591 |  | CB |  | EGH3035FFG | 65 | 35 | [5 empty] | 10 | 14
|  | MC |  | A251K1C* | 5 | 27
A200C592 | C | CB | Eaton | HFD3025L | 100 | 25 | 208 | 3 | 65 | 208 | 3 | 3 | 10.6 | 0.695 | (1) (7a) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K1C* | 5 | 27
A200C593 |  | CB |  | HFD3035L | 100 | 35 | [5 empty] | 5 | 16.7
|  | MC |  | A251K1C* | 5 | 27
A200C594 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 24.2
|  | MC |  | A251K1C* | 5 | 27
A200C595 | C | CB | Eaton | HFD3025L | 100 | 25 | 240 | 3 | 65 | 230 | 3 | 3 | 9.6 | 0.695 | (1) (7a) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K1C* | 5 | 27
A200C596 |  | CB |  | HFD3035L | 100 | 35 | [5 empty] | 5 | 15.2
|  | MC |  | A251K1C* | 5 | 27
A200C597 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 22
|  | MC |  | A251K1C* | 5 | 27
A200C598 | C | CB | Eaton | HFD3020L | 65 | 20 | 480 | 3 | 65 | 460 | 3 | 5 | 7.6 | 0.695 | (1) (7a) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K1C* | 5 | 27
A200C599 |  | CB |  | HFD3030L | 65 | 30 | [5 empty] | 7.5 | 11
|  | MC |  | A251K1C* | 5 | 27
A200C600 |  | CB |  | HFD3035L | 65 | 35 | [5 empty] | 10 | 14
|  | MC |  | A251K1C* | 5 | 27
A200C601 | C | CB | Eaton | HFD3015L | 25 | 15 | 600 | 3 | 25 | 575 | 3 | 5 | 6.1 | 0.695 | (1) (6a) (7a) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K1C* | 5 | 27
A200C602 |  | CB |  | HFD3025L | 25 | 25 | [5 empty] | 7.5 | 9
|  | MC |  | A251K1C* | 5 | 27
A200C603 |  | CB |  | HFD3030L | 25 | 30 | [5 empty] | 10 | 11
|  | MC |  | A251K1C* | 5 | 27
A200C604 | C | CB | Eaton | FDC3025L | 200 | 25 | 208 | 3 | 100 | 208 | 3 | 3 | 10.6 | 0.695 | (1) (7a) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K1C* | 5 | 27
A200C605 |  | CB |  | FDC3050L | 200 | 35 | [5 empty] | 5 | 16.7
|  | MC |  | A251K1C* | 5 | 27
A200C606 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 24.2
|  | MC |  | A251K1C* | 5 | 27
A200C607 | C | CB | Eaton | FDC3025L | 200 | 25 | 240 | 3 | 100 | 230 | 3 | 3 | 9.6 | 0.695 | (1) (7a) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K1C* | 5 | 27
A200C608 |  | CB |  | FDC3035L | 200 | 35 | [5 empty] | 5 | 15.2
|  | MC |  | A251K1C* | 5 | 27
A200C609 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 22
|  | MC |  | A251K1C* | 5 | 27
A200C610 | C | CB | Eaton | FDC3020L | 100 | 20 | 480 | 3 | 100 | 460 | 3 | 5 | 7.6 | 0.695 | (1) (7a) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K1C* | 5 | 27
A200C611 |  | CB |  | FDC3030L | 100 | 30 | [5 empty] | 7.5 | 11
|  | MC |  | A251K1C* | 5 | 27
A200C612 |  | CB |  | FDC3035L | 100 | 35 | [5 empty] | 10 | 14
|  | MC |  | A251K1C* | 5 | 27
A200C613 | C | CB | Eaton | FDC3015L | 35 | 15 | 600 | 3 | 35 | 575 | 3 | 5 | 6.1 | 0.695 | (1) (6a) (7a) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K1C* | 5 | 27
A200C614 |  | CB |  | FDC3025L | 35 | 25 | [5 empty] | 7.5 | 9
|  | MC |  | A251K1C* | 5 | 27
A200C615 |  | CB |  | FDC3030L | 35 | 30 | [5 empty] | 10 | 11
|  | MC |  | A251K1C* | 5 | 27
A200C616 | C | CB | Eaton | HFD3015L | 25 | 15 | 600 | 3 | 100 | 575 | 3 | 5 | 6.1 | 0.695 | (1) (7a) | - | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | MC |  | A251K1C* | 5 | 27
A200C617 | C | CB | Eaton | HFD3025L | 25 | 25 | 600 | 3 | 100 | 575 | 3 | 7.5 | 9
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | MC |  | A251K1C* | 5 | 27
A200C618 | C | CB | Eaton | HFD3030L | 25 | 30 | 600 | 3 | 100 | 575 | 3 | 10 | 11
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | MC |  | A251K1C* | 5 | 27
A200C619 | C | CB | Eaton | EGH3035FFG | 100 | 35 | 208 | 3 | 65 | 208 | 3 | 5 | 16.7 | 0.695 | (1) (7c) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K2C* | 5 | 45
A200C620 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 7.5 | 24.2
|  | MC |  | A251K2C* | 5 | 45
A200C621 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 10 | 30.8
|  | MC |  | A251K2C* | 5 | 45
A200C622 | C | CB | Eaton | EGH3050FFG | 100 | 50 | 240 | 3 | 65 | 230 | 3 | 7.5 | 22 | 0.695 | (1) (7c) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K2C* | 5 | 45
A200C623 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 10 | 28
|  | MC |  | A251K2C* | 5 | 45
A200C624 |  | CB |  | EGH3070FFG | 100 | 70 | [5 empty] | 15 | 42
|  | MC |  | A251K2C* | 5 | 45
A200C625 | C | CB | Eaton | EGH3050FFG | 65 | 50 | 480 | 3 | 65 | 460 | 3 | 15 | 21 | 0.695 | (1) (7c) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K2C* | 5 | 45
A200C626 |  | CB |  | EGH3050FFG | 65 | 50 | [5 empty] | 20 | 27
|  | MC |  | A251K2C* | 5 | 45
A200C627 |  | CB |  | EGH3050FFG | 65 | 50 | [5 empty] | 25 | 34
|  | MC |  | A251K2C* | 5 | 45
A200C628 | C | CB | Eaton | HFD3035L | 100 | 35 | 208 | 3 | 65 | 208 | 3 | 5 | 16.7 | 0.695 | (1) (7c) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K2C* | 5 | 45
A200C629 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 24.2
|  | MC |  | A251K2C* | 5 | 45
A200C630 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 10 | 30.8
|  | MC |  | A251K2C* | 5 | 45
A200C631 | C | CB | Eaton | HFD3050L | 100 | 50 | 240 | 3 | 65 | 230 | 3 | 7.5 | 22 | 0.695 | (1) (7c) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K2C* | 5 | 45
A200C632 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 10 | 28
|  | MC |  | A251K2C* | 5 | 45
A200C633 |  | CB |  | HFD3070L | 100 | 70 | [5 empty] | 15 | 42
|  | MC |  | A251K2C* | 5 | 45
A200C634 | C | CB | Eaton | HFD3050L | 65 | 50 | 480 | 3 | 65 | 460 | 3 | 15 | 21 | 0.695 | (1) (7c) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K2C* | 5 | 45
A200C635 |  | CB |  | HFD3050L | 65 | 50 | [5 empty] | 20 | 27
|  | MC |  | A201K2C* | 5 | 45
A200C636 |  | CB |  | HFD3050L | 65 | 50 | [5 empty] | 25 | 34
|  | MC |  | A251K2C* | 5 | 45
A200C637 | C | CB | Eaton | HFD3035L | 25 | 35 | 600 | 3 | 25 | 575 | 3 | 15 | 17 | 0.695 | (1) (6a) (7c) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K2C* | 5 | 45
A200C638 |  | CB |  | HFD3050L | 25 | 50 | [5 empty] | 20 | 22
|  | MC |  | A251K2C* | 5 | 45
A200C639 |  | CB |  | HFD3050L | 25 | 50 | [5 empty] | 25 | 27
|  | MC |  | A251K2C* | 5 | 45
A200C640 | C | CB | Eaton | FDC3035L | 200 | 35 | 208 | 3 | 100 | 208 | 3 | 5 | 16.7 | 0.695 | (1) (7c) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K2C* | 5 | 45
A200C641 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 24.2
|  | MC |  | A251K2C* | 5 | 45
A200C642 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 10 | 30.8
|  | MC |  | A251K2C* | 5 | 45
A200C643 | C | CB | Eaton | FDC3050L | 200 | 50 | 240 | 3 | 100 | 230 | 3 | 7.5 | 22 | 0.695 | (1) (7c) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K2C* | 5 | 45
A200C644 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 10 | 28
|  | MC |  | A251K2C* | 5 | 45
A200C645 |  | CB |  | FDC3070L | 200 | 70 | [5 empty] | 15 | 42
|  | MC |  | A251K2C* | 5 | 45
A200C646 | C | CB | Eaton | FDC3050L | 100 | 50 | 480 | 3 | 100 | 460 | 3 | 15 | 21 | 0.695 | (1) (7c) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K2C* | 5 | 45
A200C647 |  | CB |  | FDC3050L | 100 | 50 | [5 empty] | 20 | 27
|  | MC |  | A201K2C* | 5 | 45
A200C648 |  | CB |  | FDC3050L | 100 | 50 | [5 empty] | 25 | 34
|  | MC |  | A251K2C* | 5 | 45
A200C649 | C | CB | Eaton | FDC3035L | 35 | 35 | 600 | 3 | 35 | 575 | 3 | 15 | 17 | 0.695 | (1) (6a) (7c) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K2C* | 5 | 45
A200C650 |  | CB |  | FDC3050L | 35 | 50 | [5 empty] | 20 | 22
|  | MC |  | A251K2C* | 5 | 45
A200C651 |  | CB |  | FDC3050L | 35 | 50 | [5 empty] | 25 | 27
|  | MC |  | A251K2C* | 5 | 45
A200C652 | C | CB | Eaton | HFD3035L | 25 | 35 | 600 | 3 | 100 | 575 | 3 | 15 | 17 | 0.695 | (1) (7c) | - | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | MC |  | A251K2C* | 5 | 45
A200C653 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 20 | 22
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | MC |  | A251K2C* | 5 | 45
A200C654 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 25 | 27
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | MC |  | A251K2C* | 5 | 45
A200C655 | C | CB | Eaton | EGH3070FFG | 100 | 70 | 208 | 3 | 65 | 208 | 3 | 15 | 46.2 | 1.06 | (1) (7e) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K3C* | 5 | 90
A200C656 |  | CB |  | EGH3090FFG | 100 | 90 | [5 empty] | 20 | 59.4
|  | MC |  | A251K3C* | 5 | 90
A200C657 |  | CB |  | EGH3125FFG | 100 | 125 | [5 empty] | 25 | 74.8
|  | MC |  | A251K3C* | 5 | 90
A200C658 | C | CB | Eaton | EGH3090FFG | 100 | 90 | 240 | 3 | 65 | 230 | 3 | 20 | 54 | 1.06 | (1) (7e) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K3C* | 5 | 90
A200C659 |  | CB |  | EGH3125FFG | 100 | 125 | [5 empty] | 25 | 68
|  | MC |  | A251K3C* | 5 | 90
A200C660 |  | CB |  | EGH3125FFG | 100 | 125 | [5 empty] | 30 | 80
|  | MC |  | A251K3C* | 5 | 90
A200C661 | C | CB | Eaton | EGH3060FFG | 65 | 60 | 480 | 3 | 65 | 460 | 3 | 30 | 40 | 1.06 | (1) (7e) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K3C* | 5 | 90
A200C662 |  | CB |  | EGH3090FFG | 65 | 90 | [5 empty] | 40 | 52
|  | MC |  | A251K3C* | 5 | 90
A200C663 |  | CB |  | EGH3100FFG | 65 | 100 | [5 empty] | 50 | 65
|  | MC |  | A251K3C* | 5 | 90
A200C664 | C | CB | Eaton | HFD3070L | 100 | 70 | 208 | 3 | 65 | 208 | 3 | 15 | 46.2 | 1.06 | (1) (7e) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K3C* | 5 | 90
A200C665 |  | CB |  | HFD3090L | 100 | 90 | [5 empty] | 20 | 59.4
|  | MC |  | A251K3C* | 5 | 90
A200C666 |  | CB |  | HFD3125L | 100 | 125 | [5 empty] | 25 | 74.8
|  | MC |  | A251K3C* | 5 | 90
A200C667 | C | CB | Eaton | HFD3090L | 100 | 90 | 240 | 3 | 65 | 230 | 3 | 20 | 54 | 1.06 | (1) (7e) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K3C* | 5 | 90
A200C668 |  | CB |  | HFD3125L | 100 | 125 | [5 empty] | 25 | 68
|  | MC |  | A251K3C* | 5 | 90
A200C669 |  | CB |  | HFD3125L | 100 | 125 | [5 empty] | 30 | 80
|  | MC |  | A251K3C* | 5 | 90
A200C670 | C | CB | Eaton | HFD3060L | 65 | 60 | 480 | 3 | 65 | 460 | 3 | 30 | 40 | 1.06 | (1) (7e) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K3C* | 5 | 90
A200C671 |  | CB |  | HFD3090L | 65 | 90 | [5 empty] | 40 | 52
|  | MC |  | A251K3C* | 5 | 90
A200C672 |  | CB |  | HFD3100L | 65 | 100 | [5 empty] | 50 | 65
|  | MC |  | A251K3C* | 5 | 90
A200C673 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 25 | 575 | 3 | 30 | 32 | 1.06 | (1) (6b) (7e) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K3C* | 5 | 90
A200C674 |  | CB |  | HFD3060L | 25 | 60 | [5 empty] | 40 | 41
|  | MC |  | A251K3C* | 5 | 90
A200C675 |  | CB |  | HFD3090L | 25 | 90 | [5 empty] | 50 | 52
|  | MC |  | A251K3C* | 5 | 90
A200C676 | C | CB | Eaton | FDC3070L | 200 | 70 | 208 | 3 | 100 | 208 | 3 | 15 | 46.2 | 1.06 | (1) (7e) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A201K3C* | 5 | 90
A200C677 |  | CB |  | FDC3090L | 200 | 90 | [5 empty] | 20 | 59.4
|  | MC |  | A251K3C* | 5 | 90
A200C678 |  | CB |  | FDC3125L | 200 | 125 | [5 empty] | 25 | 74.8
|  | MC |  | A251K3C* | 5 | 90
A200C679 | C | CB | Eaton | FDC3090L | 200 | 90 | 240 | 3 | 100 | 230 | 3 | 20 | 54 | 1.06 | (1) (7e) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K3C* | 5 | 90
A200C680 |  | CB |  | FDC3125L | 200 | 125 | [5 empty] | 25 | 68
|  | MC |  | A251K3C* | 5 | 90
A200C681 |  | CB |  | FDC3125L | 200 | 125 | [5 empty] | 30 | 80
|  | MC |  | A251K3C* | 5 | 90
A200C682 | C | CB | Eaton | FDC3060L | 100 | 60 | 480 | 3 | 100 | 460 | 3 | 30 | 40 | 1.06 | (1) (7e) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K3C* | 5 | 90
A200C683 |  | CB |  | FDC3090L | 100 | 90 | [5 empty] | 40 | 52
|  | MC |  | A251K3C* | 5 | 90
A200C684 |  | CB |  | FDC3100L | 100 | 100 | [5 empty] | 50 | 65
|  | MC |  | A251K3C* | 5 | 90
A200C685 | C | CB | Eaton | FDC3050L | 35 | 50 | 600 | 3 | 35 | 575 | 3 | 30 | 32 | 1.06 | (1) (6b) (7e) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K3C* | 5 | 90
A200C686 |  | CB |  | FDC3060L | 35 | 60 | [5 empty] | 40 | 41
|  | MC |  | A251K3C* | 5 | 90
A200C687 |  | CB |  | FDC3090L | 35 | 90 | [5 empty] | 50 | 52
|  | MC |  | A251K3C* | 5 | 90
A200C688 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 30 | 32 | 1.42 | (1) (7e) | - | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | MC |  | A251K3C* | 5 | 90
A200C689 | C | CB | Eaton | HFD3060L | 25 | 60 | 600 | 3 | 100 | 575 | 3 | 40 | 41
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | MC |  | A251K3C* | 5 | 90
A200C690 | C | CB | Eaton | HFD3090L | 25 | 90 | 600 | 3 | 100 | 575 | 3 | 50 | 52
|  | C. Limiter |  | LFD3150R | 200 | 150
|  | MC |  | A251K3C* | 5 | 90
A200C691 | C | CB | Eaton | HJD3125 | 100 | 125 | 208 | 3 | 65 | 208 | 3 | 25 | 74.8 | 1.42 | (1) (7f) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K4C* | 10 | 135
A200C692 |  | CB |  | HJD3150 | 100 | 150 | [5 empty] | 30 | 88
|  | MC |  | A251K4C* | 10 | 135
A200C693 |  | CB |  | HJD3175 | 100 | 175 | [5 empty] | 40 | 114
|  | MC |  | A251K4C* | 10 | 135
A200C694 | C | CB | Eaton | HJD3125 | 100 | 125 | 240 | 3 | 65 | 230 | 3 | 30 | 80 | 1.42 | (1) (7f) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K4C* | 10 | 135
A200C695 |  | CB |  | HJD3150 | 100 | 150 | [5 empty] | 40 | 104
|  | MC |  | A251K4C* | 10 | 135
A200C696 |  | CB |  | HJD3200 | 100 | 200 | [5 empty] | 50 | 130
|  | MC |  | A251K4C* | 10 | 135
A200C697 | C | CB | Eaton | HJD3125 | 65 | 125 | 480 | 3 | 65 | 460 | 3 | 60 | 77 | 1.42 | (1) (7f) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K4C* | 10 | 135
A200C698 |  | CB |  | HJD3150 | 65 | 150 | [5 empty] | 75 | 96
|  | MC |  | A251K4C* | 10 | 135
A200C699 |  | CB |  | HJD3175 | 65 | 175 | [5 empty] | 100 | 124
|  | MC |  | A251K4C* | 10 | 135
A200C700 | C | CB | Eaton | HJD3100 | 25 | 100 | 600 | 3 | 25 | 575 | 3 | 60 | 62 | 1.42 | (1) (6b) (7f) | - | E47048 Vol. 2 Sec. 2
|  | MC |  | A251K4C* | 10 | 135
A200C701 |  | CB |  | HJD3125 | 25 | 125 | [5 empty] | 75 | 77
|  | MC |  | A251K4C* | 10 | 135
A200C702 |  | CB |  | HJD3150 | 25 | 150 | [5 empty] | 100 | 99
|  | MC |  | A251K4C* | 10 | 135
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = See Table 3 for maximum Heater sizes.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6a) = Install Terminal End Cover TEC1 (6085C42H01) to line side of circuit breaker.
(6b) = Install Terminal end Cover TEC2 (6085C42H02) to line side of circuit breaker.
(7) See table (7) for internal wiring between load side of short circuit protective device & line side of starter.
| Table 7 - Internal Power Wiring | [5 empty] | Table 3 - Maximum Heater Size
| Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation). | [5 empty] | Starter Cat. No. | Nema Size | Maximum Heater
| Wire Code | Wire Size | Wire Code | Wire Size
| 7a | 12 awg. | 7j | 4/0 awg. |  |  | A200M1C*** | 1 | FH51
| 7b | 10 awg. | 7k | 250kcml |  |  | A200M2C*** | 2 | FH57
| 7c | 8 awg. | 7l | 350kcml |  |  | A200M3C*** | 3 | FH88
| 7d | 6 awg. | 7m | 4/0 awg. (3) |  |  | A200M4C*** | 4 | FH93
| 7e | 4 awg. | 7n | 4/0 awg. (4) |  |  | A200M5C*** | 5 | FH32
| 7f | 2 awg. | 7p | 250kcml (2) |  |  | A200M6C*** | 6 | FH33
| 7g | 1/0 awg. | 7r | 350kcml (3) |  |  | A210M1C*** | 1 | FH51
| 7h | 2/0 awg. | 7s | 4/0 awg. (2) |  |  | A210M2C*** | 2 | FH57
[7 empty] | A210M3C*** | 3 | FH88
[7 empty] | A210M4C*** | 4 | FH93
[7 empty] | A210M5C*** | 5 | FH32
[7 empty] | A210M6C*** | 6 | FH33

## A200 Type D
Issued: 2006-05-18
Last Revised: 2006-05-18
Combination Motor Controllers for use in Industrial Control Panels
ID Number | Combination Type | Individual Component | [6 empty] | Combination SCCR | [5 empty] | Conditions of Acceptability | Combination Starter UL File | Motor Control Center UL File
|  | Component Type | Manufacturer | Partial Catalog No. | Ratings |  |  |  | SCCR kA | Volts | Phase | Hp | NEC FLC | Min. Enclosure Volume (cu. ft.)
[5 empty] | SCCR kA | Max. Amps | Volts | No. Poles
A200D001 | D | ICB | Eaton | HMCP030*** | - | 30 | 208 | 3 | 100 | 208 | 3 | 3 | 10.6 | 0.695 | (1) (3) (5) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M1C*** | 5 | 27
A200D002 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 5 | 16.7
|  | STR |  | A200M1C*** | 5 | 27
A200D003 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 7.5 | 24.2
|  | STR |  | A200M1C*** | 5 | 27
A200D004 | D | ICB | Eaton | HMCP030*** | - | 30 | 240 | 3 | 100 | 230 | 3 | 3 | 9.6 | 0.695 | (1) (3) (5) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M1C*** | 5 | 27
A200D005 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 5 | 15.2
|  | STR |  | A200M1C*** | 5 | 27
A200D006 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 7.5 | 22
|  | STR |  | A200M1C*** | 5 | 27
A200D007 | D | ICB | Eaton | HMCP015*** | - | 15 | 480 | 3 | 100 | 460 | 3 | 5 | 7.6 | 0.695 | (1) (3) (5) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M1C*** | 5 | 27
A200D008 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 7.5 | 11
|  | STR |  | A200M1C*** | 5 | 27
A200D009 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 10 | 14
|  | STR |  | A200M1C*** | 5 | 27
A200D010 | D | ICB | Eaton | HMCP015*** | - | 15 | 600 | 3 | 50 | 575 | 3 | 5 | 6.1 | 0.695 | (1) 3) (5) (6a) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M1C*** | 5 | 27
A200D011 |  | ICB |  | HMCP015*** | - | 15 | [5 empty] | 7.5 | 9
|  | STR |  | A200M1C*** | 5 | 27
A200D012 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 10 | 11
|  | STR |  | A200M1C*** | 5 | 27
A200D013 | D | ICB | Eaton | HMCP030*** | - | 30 | 208 | 3 | 100 | 208 | 3 | 3 | 10.6 | 0.695 | (1) (3) (5) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M1C*** | 5 | 27
A200D014 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 5 | 16.7
|  | STR |  | A200M1C*** | 5 | 27
A200D015 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 7.5 | 24.2
|  | STR |  | A200M1C*** | 5 | 27
A200D016 | D | ICB | Eaton | HMCP030*** | - | 30 | 240 | 3 | 100 | 230 | 3 | 3 | 9.6 | 0.695 | (1) (3) (5) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M1C*** | 5 | 27
A200D017 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 5 | 15.2
|  | STR |  | A200M1C*** | 5 | 27
A200D018 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 7.5 | 22
|  | STR |  | A200M1C*** | 5 | 27
A200D019 | D | ICB | Eaton | HMCP015*** | - | 15 | 480 | 3 | 100 | 460 | 3 | 5 | 7.6 | 0.695 | (1) (3) (5) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M1C*** | 5 | 27
A200D020 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 7.5 | 11
|  | STR |  | A200M1C*** | 5 | 27
A200D021 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 10 | 14
|  | STR |  | A200M1C*** | 5 | 27
A200D022 | D | ICB | Eaton | HMCP015*** | - | 15 | 600 | 3 | 100 | 575 | 3 | 5 | 6.1 | 0.695 | (1) (3) (5) (7a) | - | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3015R | - | 15
|  | STR. |  | A200M1C*** | 5 | 27
A200D023 | D | ICB | Eaton | HMCP015*** | - | 15 | 600 | 3 | 100 | 575 | 3 | 7.5 | 9
|  | C. Limiter |  | ELC3015R | - | 15
|  | STR. |  | A200M1C*** | 5 | 27
A200D024 | D | ICB | Eaton | HMCP030*** | - | 30 | 600 | 3 | 100 | 575 | 3 | 10 | 11
|  | C. Limiter |  | ELC3030R | - | 30
|  | STR. |  | A200M1C*** | 5 | 27
A200D025 | D | ICB | Eaton | HMCP030*** | - | 30 | 208 | 3 | 100 | 208 | 3 | 5 | 16.7 | 0.695 | (1) (3) (5) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M2C*** | 5 | 45
A200D026 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | A200M2C*** | 5 | 45
A200D027 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 10 | 30.8
|  | STR |  | A200M2C*** | 5 | 45
A200D028 | D | ICB | Eaton | HMCP030*** | - | 30 | 240 | 3 | 100 | 230 | 3 | 5 | 15.2 | 0.695 | (1) (3) (5) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M2C*** | 5 | 45
A200D029 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 7.5 | 22
|  | STR |  | A200M2C*** | 5 | 45
A200D030 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 10 | 28
|  | STR |  | A200M2C*** | 5 | 45
A200D031 | D | ICB | Eaton | HMCP050*** | - | 50 | 480 | 3 | 100 | 460 | 3 | 15 | 21 | 0.695 | (1) (3) (5) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M2C*** | 5 | 45
A200D032 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 20 | 27
|  | STR |  | A200M2C*** | 5 | 45
A200D033 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 25 | 34
|  | STR |  | A200M2C*** | 5 | 45
A200D034 | D | ICB | Eaton | HMCP030*** | - | 30 | 600 | 3 | 50 | 575 | 3 | 15 | 17 | 0.695 | (1) (3) (5) (6a) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M2C*** | 5 | 45
A200D035 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 20 | 22
|  | STR |  | A200M2C*** | 5 | 45
A200D036 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 25 | 27
|  | STR |  | A200M2C*** | 5 | 45
A200D037 | D | ICB | Eaton | HMCP030*** | - | 30 | 208 | 3 | 100 | 208 | 3 | 5 | 16.7 | 0.695 | (1) (3) (5) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M2C*** | 5 | 45
A200D038 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | A200M2C*** | 5 | 45
A200D039 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 10 | 30.8
|  | STR |  | A200M2C*** | 5 | 45
A200D040 | D | ICB | Eaton | HMCP030*** | - | 30 | 240 | 3 | 100 | 230 | 3 | 5 | 15.2 | 0.695 | (1) (3) (5) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M2C*** | 5 | 45
A200D041 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 7.5 | 22
|  | STR |  | A200M2C*** | 5 | 45
A200D042 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 10 | 28
|  | STR |  | A200M2C*** | 5 | 45
A200D043 | D | ICB | Eaton | HMCP050*** | - | 50 | 480 | 3 | 100 | 460 | 3 | 15 | 21 | 0.695 | (1) (3) (5) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M2C*** | 5 | 45
A200D044 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 20 | 27
|  | STR |  | A200M2C*** | 5 | 45
A200D045 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 25 | 34
|  | STR |  | A200M2C*** | 5 | 45
A200D046 | D | ICB | Eaton | HMCP030*** | - | 30 | 600 | 3 | 100 | 575 | 3 | 15 | 17 | 0.695 | (1) (3) (5) (7c) | - | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3030R | - | 30
|  | STR. |  | A200M2C*** | 5 | 45
A200D047 | D | ICB | Eaton | HMCPE050*** | - | 50 | 600 | 3 | 100 | 575 | 3 | 20 | 22
|  | C. Limiter |  | ELC3050R | - | 50
|  | STR. |  | A200M2C*** | 5 | 45
A200D048 | D | ICB | Eaton | HMCPE050*** | - | 50 | 600 | 3 | 100 | 575 | 3 | 25 | 27
|  | C. Limiter |  | ELC3050R | - | 50
|  | STR. |  | A200M2C*** | 5 | 45
A200D049 | D | ICB | Eaton | HMCP100*** | - | 100 | 208 | 3 | 100 | 208 | 3 | 15 | 46.2 | 1.06 | (1) (3) (5) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M3C*** | 5 | 90
A200D050 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 20 | 59.4
|  | STR |  | A200M3C*** | 5 | 90
A200D051 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 25 | 74.8
|  | STR |  | A200M3C*** | 5 | 90
A200D052 | D | ICB | Eaton | HMCP100*** | - | 100 | 240 | 3 | 100 | 230 | 3 | 20 | 54 | 1.06 | (1) (3) (5) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M3C*** | 5 | 90
A200D053 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 25 | 68
|  | STR |  | A200M3C*** | 5 | 90
A200D054 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 30 | 80
|  | STR |  | A200M3C*** | 5 | 90
A200D055 | D | ICB | Eaton | HMCP100*** | - | 100 | 480 | 3 | 100 | 460 | 3 | 30 | 40 | 1.06 | (1) (3) (5) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M3C*** | 5 | 90
A200D056 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 40 | 52
|  | STR |  | A200M3C*** | 5 | 90
A200D057 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 50 | 65
|  | STR |  | A200M3C*** | 5 | 90
A200D058 | D | ICB | Eaton | HMCP050*** | - | 50 | 600 | 3 | 50 | 575 | 3 | 30 | 32 | 1.06 | (1) (3) (5) (6b) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M3C*** | 5 | 90
A200D059 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 40 | 41
|  | STR |  | A200M3C*** | 5 | 90
A200D060 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 50 | 52
|  | STR |  | A200M3C*** | 5 | 90
A200D061 | D | ICB | Eaton | HMCPE100*** | - | 100 | 208 | 3 | 100 | 208 | 3 | 15 | 46.2 | 1.06 | (1) (3) (5) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M3C*** | 5 | 90
A200D062 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 20 | 59.4
|  | STR |  | A200M3C*** | 5 | 90
A200D063 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 25 | 74.8
|  | STR |  | A200M3C*** | 5 | 90
A200D064 | D | ICB | Eaton | HMCPE100*** | - | 100 | 240 | 3 | 100 | 230 | 3 | 20 | 54 | 1.06 | (1) (3) (5) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M3C*** | 5 | 90
A200D065 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 25 | 68
|  | STR |  | A200M3C*** | 5 | 90
A200D066 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 30 | 80
|  | STR |  | A200M3C*** | 5 | 90
A200D067 | D | ICB | Eaton | HMCPE100*** | - | 100 | 480 | 3 | 100 | 460 | 3 | 30 | 40 | 1.06 | (1) (3) (5) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M3C*** | 5 | 90
A200D068 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 40 | 52
|  | STR |  | A200M3C*** | 5 | 90
A200D069 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 50 | 65
|  | STR |  | A200M3C*** | 5 | 90
A200D070 | D | ICB | Eaton | HMCP050*** | - | 50 | 600 | 3 | 100 | 575 | 3 | 30 | 32 | 1.42 | (1) (3) (5) (7e) | - | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3050R | - | 50
|  | STR. |  | A200M3C*** | 5 | 90
A200D071 | D | ICB | Eaton | HMCP100*** | - | 100 | 600 | 3 | 100 | 575 | 3 | 40 | 41
|  | C. Limiter |  | ELC3100R | - | 100
|  | STR. |  | A200M3C*** | 5 | 90
A200D072 | D | ICB | Eaton | HMCP100*** | - | 100 | 600 | 3 | 100 | 575 | 3 | 50 | 52
|  | C. Limiter |  | ELC3100R | - | 100
|  | STR. |  | A200M3C*** | 5 | 90
A200D073 | D | ICB | Eaton | HMCP150*** | - | 150 | 208 | 3 | 100 | 208 | 3 | 25 | 74.8 | 1.42 | (1) (3) (5) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M4C*** | 10 | 135
A200D074 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 30 | 88
|  | STR |  | A200M4C*** | 10 | 135
A200D075 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 40 | 114
|  | STR |  | A200M4C*** | 10 | 135
A200D076 | D | ICB | Eaton | HMCP150*** | - | 150 | 240 | 3 | 100 | 230 | 3 | 25 | 68 | 1.42 | (1) (3) (5) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M4C*** | 10 | 135
A200D077 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 30 | 80
|  | STR |  | A200M4C*** | 10 | 135
A200D078 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 40 | 104
|  | STR |  | A200M4C*** | 10 | 135
A200D079 | D | ICB | Eaton | HMCP150*** | - | 150 | 480 | 3 | 100 | 460 | 3 | 60 | 77 | 1.42 | (1) (3) (5) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M4C*** | 10 | 135
A200D080 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 75 | 96
|  | STR |  | A200M4C*** | 10 | 135
A200D081 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 100 | 124
|  | STR |  | A200M4C*** | 10 | 135
A200D082 | D | ICB | Eaton | HMCP150*** | - | 150 | 600 | 3 | 50 | 575 | 3 | 60 | 62 | 1.42 | (1) (3) (5) 6b) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M4C*** | 10 | 135
A200D083 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 75 | 77
|  | STR |  | A200M4C*** | 10 | 135
A200D084 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 100 | 99
|  | STR |  | A200M4C*** | 10 | 135
A200D085 | D | ICB | Eaton | HMCP150*** | - | 150 | 600 | 3 | 100 | 575 | 3 | 60 | 62 | 1.42 | (1) (3) (5) (7f) | - | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR. |  | A200M4C*** | 10 | 135
A200D086 | D | ICB | Eaton | HMCP150*** | - | 150 | 600 | 3 | 100 | 575 | 3 | 75 | 77
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR. |  | A200M4C*** | 10 | 135
A200D087 | D | ICB | Eaton | HMCP150*** | - | 150 | 600 | 3 | 100 | 575 | 3 | 100 | 99
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR. |  | A200M4C*** | 10 | 135
A200D088 | D | ICB | Eaton | HMCP250*** | - | 250 | 208 | 3 | 100 | 208 | 3 | 50 | 143 | 2.15 | (1) (3) (5) (7j) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M5C*** | 10 | 270
A200D089 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 60 | 169
|  | STR |  | A200M5C*** | 10 | 270
A200D090 |  | ICB |  | A200M5C*** | - | 400 | [5 empty] | 75 | 211
|  | STR |  | A200M5C*** | 10 | 270
A200D091 | D | ICB | Eaton | HMCP250*** | - | 250 | 240 | 3 | 100 | 230 | 3 | 60 | 154 | 2.15 | (1) (3) (5) (7j) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M5C*** | 10 | 270
A200D092 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 75 | 192
|  | STR |  | A200M5C*** | 10 | 270
A200D093 |  | ICB |  | A200M5C*** | - | 400 | [5 empty] | 100 | 248
|  | STR |  | A200M5C*** | 10 | 270
A200D094 | D | ICB | Eaton | HMCP250*** | - | 250 | 480 | 3 | 100 | 460 | 3 | 125 | 156 | 2.15 | (1) (3) (5) (7j) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M5C*** | 10 | 270
A200D095 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 150 | 180
|  | STR |  | A200M5C*** | 10 | 270
A200D096 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 200 | 240
|  | STR |  | A200M5C*** | 10 | 270
A200D097 | D | ICB | Eaton | HMCP250*** | - | 250 | 600 | 3 | 50 | 575 | 3 | 125 | 125 | 2.15 | (1) (3) (5) (7j) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M5C*** | 10 | 270
A200D098 |  | ICB |  | HMCP250*** | - | 250 | [5 empty] | 150 | 144
|  | STR |  | A200M5C*** | 10 | 270
A200D099 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 200 | 192
|  | STR |  | A200M5C*** | 10 | 270
A200D100 | D | ICB | Eaton | HMCP600*** | - | 600 | 208 | 3 | 100 | 208 | 3 | 100 | 273 | 2.87 | (1) (3) (5) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M6C*** | 18 | 540
A200D101 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 125 | 343
|  | STR |  | A200M6C*** | 18 | 540
A200D102 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 150 | 396
|  | STR |  | A200M6C*** | 18 | 540
A200D103 | D | ICB | Eaton | HMCP600*** | - | 600 | 240 | 3 | 100 | 230 | 3 | 125 | 312 | 2.87 | (1) (3) (5) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M6C*** | 18 | 540
A200D104 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 150 | 360
|  | STR |  | A200M6C*** | 18 | 540
A200D105 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 200 | 480
|  | STR |  | A200M6C*** | 18 | 540
A200D106 | D | ICB | Eaton | HMCP600*** | - | 600 | 480 | 3 | 100 | 460 | 3 | 300 | 361 | 2.87 | (1) (3) (5) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M6C*** | 18 | 540
A200D107 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 350 | 414
|  | STR |  | A200M6C*** | 18 | 540
A200D108 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 400 | 477
|  | STR |  | A200M6C*** | 18 | 540
A200D109 | D | ICB | Eaton | HMCP030*** | - | 30 | 208 | 3 | 100 | 208 | 3 | 3 | 10.6 | 0.695 | (1) (3) (5) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M1C*** | 5 | 27
A200D110 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 5 | 16.7
|  | STR |  | A210M1C*** | 5 | 27
A200D111 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 7.5 | 24.2
|  | STR |  | A210M1C*** | 5 | 27
A200D112 | D | ICB | Eaton | HMCP030*** | - | 30 | 240 | 3 | 100 | 230 | 3 | 3 | 9.6 | 0.695 | (1) (3) (5) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M1C*** | 5 | 27
A200D113 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 5 | 15.2
|  | STR |  | A210M1C*** | 5 | 27
A200D114 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 7.5 | 22
|  | STR |  | A210M1C*** | 5 | 27
A200D115 | D | ICB | Eaton | HMCP015*** | - | 15 | 480 | 3 | 100 | 460 | 3 | 5 | 7.6 | 0.695 | (1) (3) (5) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M1C*** | 5 | 27
A200D116 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 7.5 | 11
|  | STR |  | A210M1C*** | 5 | 27
A200D117 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 10 | 14
|  | STR |  | A210M1C*** | 5 | 27
A200D118 | D | ICB | Eaton | HMCP015*** | - | 15 | 600 | 3 | 50 | 575 | 3 | 5 | 6.1 | 0.695 | (1) (3) (5) (6a) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M1C*** | 5 | 27
A200D119 |  | ICB |  | HMCP015*** | - | 15 | [5 empty] | 7.5 | 9
|  | STR |  | A210M1C*** | 5 | 27
A200D120 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 10 | 11
|  | STR |  | A210M1C*** | 5 | 27
A200D121 | D | ICB | Eaton | HMCPE030*** | - | 30 | 208 | 3 | 100 | 208 | 3 | 3 | 10.6 | 0.695 | (1) (3) (5) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M1C*** | 5 | 27
A200D122 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 5 | 16.7
|  | STR |  | A210M1C*** | 5 | 27
A200D123 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 7.5 | 24.2
|  | STR |  | A210M1C*** | 5 | 27
A200D124 | D | ICB | Eaton | HMCPE030*** | - | 30 | 240 | 3 | 100 | 230 | 3 | 3 | 9.6 | 0.695 | (1) (3) (5) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M1C*** | 5 | 27
A200D125 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 5 | 15.2
|  | STR |  | A210M1C*** | 5 | 27
A200D126 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 7.5 | 22
|  | STR |  | A210M1C*** | 5 | 27
A200D127 | D | ICB | Eaton | HMCPE015*** | - | 15 | 480 | 3 | 100 | 460 | 3 | 5 | 7.6 | 0.695 | (1) (3) (5) (7a) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M1C*** | 5 | 27
A200D128 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 7.5 | 11
|  | STR |  | A210M1C*** | 5 | 27
A200D129 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 10 | 14
|  | STR |  | A210M1C*** | 5 | 27
A200D130 | D | ICB | Eaton | HMCP015*** | - | 15 | 600 | 3 | 100 | 575 | 3 | 5 | 6.1 | 0.695 | (1) (3) (5) (7a) | - | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3015R | - | 15
|  | STR. |  | A210M1C*** | 5 | 27
A200D131 | D | ICB | Eaton | HMCP015*** | - | 15 | 600 | 3 | 100 | 575 | 3 | 7.5 | 9
|  | C. Limiter |  | ELC3015R | - | 15
|  | STR. |  | A210M1C*** | 5 | 27
A200D132 | D | ICB | Eaton | HMCP030*** | - | 30 | 600 | 3 | 100 | 575 | 3 | 10 | 11
|  | C. Limiter |  | ELC3030R | - | 30
|  | STR. |  | A210M1C*** | 5 | 27
A200D133 | D | ICB | Eaton | HMCP030*** | - | 30 | 208 | 3 | 100 | 208 | 3 | 5 | 16.7 | 0.695 | (1) (3) (5) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M2C*** | 5 | 45
A200D134 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | A210M2C*** | 5 | 45
A200D135 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 10 | 30.8
|  | STR |  | A210M2C*** | 5 | 45
A200D136 | D | ICB | Eaton | HMCP030*** | - | 30 | 240 | 3 | 100 | 230 | 3 | 5 | 15.2 | 0.695 | (1) (3) (5) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M2C*** | 5 | 45
A200D137 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 7.5 | 22
|  | STR |  | A210M2C*** | 5 | 45
A200D138 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 10 | 28
|  | STR |  | A210M2C*** | 5 | 45
A200D139 | D | ICB | Eaton | HMCP050*** | - | 50 | 480 | 3 | 100 | 460 | 3 | 15 | 21 | 0.695 | (1) (3) (5) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M2C*** | 5 | 45
A200D140 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 20 | 27
|  | STR |  | A210M2C*** | 5 | 45
A200D141 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 25 | 34
|  | STR |  | A210M2C*** | 5 | 45
A200D142 | D | ICB | Eaton | HMCP030*** | - | 30 | 600 | 3 | 50 | 575 | 3 | 15 | 17 | 0.695 | (1) (3) (5) (6a) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M2C*** | 5 | 45
A200D143 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 20 | 22
|  | STR |  | A210M2C*** | 5 | 45
A200D144 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 25 | 27
|  | STR |  | A210M2C*** | 5 | 45
A200D145 | D | ICB | Eaton | HMCPE030*** | - | 30 | 208 | 3 | 100 | 208 | 3 | 5 | 16.7 | 0.695 | (1) (3) (5) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M2C*** | 5 | 45
A200D146 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | A210M2C*** | 5 | 45
A200D147 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 10 | 30.8
|  | STR |  | A210M2C*** | 5 | 45
A200D148 | D | ICB | Eaton | HMCPE030*** | - | 30 | 240 | 3 | 100 | 230 | 3 | 5 | 15.2 | 0.695 | (1) (3) (5) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A200M2C*** | 5 | 45
A200D149 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 7.5 | 22
|  | STR |  | A200M2C*** | 5 | 45
A200D150 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 10 | 28
|  | STR |  | A200M2C*** | 5 | 45
A200D151 | D | ICB | Eaton | HMCPE050*** | - | 50 | 480 | 3 | 100 | 460 | 3 | 15 | 21 | 0.695 | (1) (3) (5) (7c) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M2C*** | 5 | 45
A200D152 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 20 | 27
|  | STR |  | A210M2C*** | 5 | 45
A200D153 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 25 | 34
|  | STR |  | A210M2C*** | 5 | 45
A200D154 | D | ICB | Eaton | HMCP030*** | - | 30 | 600 | 3 | 100 | 575 | 3 | 15 | 17 | 0.695 | (1) (3) (5) (7c) | - | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3030R | - | 30
|  | STR. |  | A210M2C*** | 5 | 45
A200D155 | D | ICB | Eaton | HMCPE050*** | - | 50 | 600 | 3 | 100 | 575 | 3 | 20 | 22
|  | C. Limiter |  | ELC3050R | - | 50
|  | STR. |  | A210M2C*** | 5 | 45
A200D156 | D | ICB | Eaton | HMCPE050*** | - | 50 | 600 | 3 | 100 | 575 | 3 | 25 | 27
|  | C. Limiter |  | ELC3050R | - | 50
|  | STR. |  | A210M2C*** | 5 | 45
A200D157 | D | ICB | Eaton | HMCP100*** | - | 100 | 208 | 3 | 100 | 208 | 3 | 15 | 46.2 | 1.06 | (1) (3) (5) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M3C*** | 5 | 90
A200D158 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 20 | 59.4
|  | STR |  | A210M3C*** | 5 | 90
A200D159 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 25 | 74.8
|  | STR |  | A210M3C*** | 5 | 90
A200D160 | D | ICB | Eaton | HMCP100*** | - | 100 | 240 | 3 | 100 | 230 | 3 | 20 | 54 | 1.06 | (1) (3) (5) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M3C*** | 5 | 90
A200D161 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 25 | 68
|  | STR |  | A210M3C*** | 5 | 90
A200D162 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 30 | 80
|  | STR |  | A210M3C*** | 5 | 90
A200D163 | D | ICB | Eaton | HMCP100*** | - | 100 | 480 | 3 | 100 | 460 | 3 | 30 | 40 | 1.06 | (1) (3) (5) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M3C*** | 5 | 90
A200D164 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 40 | 52
|  | STR |  | A210M3C*** | 5 | 90
A200D165 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 50 | 65
|  | STR |  | A210M3C*** | 5 | 90
A200D166 | D | ICB | Eaton | HMCP050*** | - | 50 | 600 | 3 | 50 | 575 | 3 | 30 | 32 | 1.06 | (1) (3) (5) (6b) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M3C*** | 5 | 90
A200D167 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 40 | 41
|  | STR |  | A210M3C*** | 5 | 90
A200D168 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 50 | 52
|  | STR |  | A210M3C*** | 5 | 90
A200D169 | D | ICB | Eaton | HMCPE100*** | - | 100 | 208 | 3 | 100 | 208 | 3 | 15 | 46.2 | 1.06 | (1) (3) (5) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M3C*** | 5 | 90
A200D170 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 20 | 59.4
|  | STR |  | A210M3C*** | 5 | 90
A200D171 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 25 | 74.8
|  | STR |  | A210M3C*** | 5 | 90
A200D172 | D | ICB | Eaton | HMCPE100*** | - | 100 | 240 | 3 | 100 | 230 | 3 | 20 | 54 | 1.06 | (1) (3) (5) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M3C*** | 5 | 90
A200D173 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 25 | 68
|  | STR |  | A210M3C*** | 5 | 90
A200D174 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 30 | 80
|  | STR |  | A210M3C*** | 5 | 90
A200D175 | D | ICB | Eaton | HMCPE100*** | - | 100 | 480 | 3 | 100 | 460 | 3 | 30 | 40 | 1.06 | (1) (3) (5) (7e) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M3C*** | 5 | 90
A200D176 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 40 | 52
|  | STR |  | A210M3C*** | 5 | 90
A200D177 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 50 | 65
|  | STR |  | A210M3C*** | 5 | 90
A200D178 | D | ICB | Eaton | HMCP050*** | - | 50 | 600 | 3 | 100 | 575 | 3 | 30 | 32 | 1.42 | (1) (3) (5) (7e) | - | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3050R | - | 50
|  | STR. |  | A210M3C*** | 5 | 90
A200D179 | D | ICB | Eaton | HMCP100*** | - | 100 | 600 | 3 | 100 | 575 | 3 | 40 | 41
|  | C. Limiter |  | ELC3100R | - | 100
|  | STR. |  | A210M3C*** | 5 | 90
A200D180 | D | ICB | Eaton | HMCP100*** | - | 100 | 600 | 3 | 100 | 575 | 3 | 50 | 52
|  | C. Limiter |  | ELC3100R | - | 100
|  | STR. |  | A210M3C*** | 5 | 90
A200D181 | D | ICB | Eaton | HMCP150*** | - | 150 | 208 | 3 | 100 | 208 | 3 | 25 | 74.8 | 1.06 | (1) (3) (5) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M4C*** | 10 | 135
A200D182 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 30 | 88
|  | STR |  | A210M4C*** | 10 | 135
A200D183 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 40 | 114
|  | STR |  | A210M4C*** | 10 | 135
A200D184 | D | ICB | Eaton | HMCP150*** | - | 150 | 240 | 3 | 100 | 230 | 3 | 25 | 68 | 1.06 | (1) (3) (5) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M4C*** | 10 | 135
A200D185 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 30 | 80
|  | STR |  | A210M4C*** | 10 | 135
A200D186 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 40 | 104
|  | STR |  | A210M4C*** | 10 | 135
A200D187 | D | ICB | Eaton | HMCP150*** | - | 150 | 480 | 3 | 100 | 460 | 3 | 60 | 77 | 1.06 | (1) (3) (5) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M4C*** | 10 | 135
A200D188 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 75 | 96
|  | STR |  | A210M4C*** | 10 | 135
A200D189 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 100 | 124
|  | STR |  | A210M4C*** | 10 | 135
A200D190 | D | ICB | Eaton | HMCP150*** | - | 150 | 600 | 3 | 50 | 575 | 3 | 60 | 62 | 1.06 | (1) (3) (5) (6b) (7f) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M4C*** | 10 | 135
A200D191 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 75 | 77
|  | STR |  | A210M4C*** | 10 | 135
A200D192 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 100 | 99
|  | STR |  | A210M4C*** | 10 | 135
A200D193 | D | ICB | Eaton | HMCP150*** | - | 150 | 600 | 3 | 100 | 575 | 3 | 60 | 62 | 1.42 | (1) (3) (5) (7f) | - | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR. |  | A210M4C*** | 10 | 135
A200D194 | D | ICB | Eaton | HMCP150*** | - | 150 | 600 | 3 | 100 | 575 | 3 | 75 | 77
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR. |  | A210M4C*** | 10 | 135
A200D195 | D | ICB | Eaton | HMCP150*** | - | 150 | 600 | 3 | 100 | 575 | 3 | 100 | 99
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR. |  | A210M4C*** | 10 | 135
A200D196 | D | ICB | Eaton | HMCP250*** | - | 250 | 208 | 3 | 100 | 208 | 3 | 50 | 143 | 2.15 | (1) (3) (5) (7j) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M5C*** | 10 | 270
A200D197 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 60 | 169
|  | STR |  | A210M5C*** | 10 | 270
A200D198 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 75 | 211
|  | STR |  | A210M5C*** | 10 | 270
A200D199 | D | ICB | Eaton | HMCP250*** | - | 250 | 240 | 3 | 100 | 230 | 3 | 60 | 154 | 2.15 | (1) (3) (5) (7j) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M5C*** | 10 | 270
A200D200 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 75 | 192
|  | STR |  | A210M5C*** | 10 | 270
A200D201 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 100 | 248
|  | STR |  | A210M5C*** | 10 | 270
A200D202 | D | ICB | Eaton | HMCP250*** | - | 250 | 480 | 3 | 100 | 460 | 3 | 125 | 156 | 2.15 | (1) (3) (5) (7j) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M5C*** | 10 | 270
A200D203 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 150 | 180
|  | STR |  | A210M5C*** | 10 | 270
A200D204 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 200 | 240
|  | STR |  | A210M5C*** | 10 | 270
A200D205 | D | ICB | Eaton | HMCP250*** | - | 250 | 600 | 3 | 50 | 575 | 3 | 125 | 125 | 2.15 | (1) (3) (5) (7j) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M5C*** | 10 | 270
A200D206 |  | ICB |  | HMCP250*** | - | 250 | [5 empty] | 150 | 144
|  | STR |  | A210M5C*** | 10 | 270
A200D207 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 200 | 192
|  | STR |  | A210M5C*** | 10 | 270
A200D208 | D | ICB | Eaton | HMCP600*** | - | 600 | 208 | 3 | 100 | 208 | 3 | 100 | 273 | 2.87 | (1) (3) (5) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M6C*** | 18 | 540
A200D209 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 125 | 343
|  | STR |  | A210M6C*** | 18 | 540
A200D210 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 150 | 396
|  | STR |  | A210M6C*** | 18 | 540
A200D211 | D | ICB | Eaton | HMCP600*** | - | 600 | 240 | 3 | 100 | 230 | 3 | 125 | 312 | 2.87 | (1) (3) (5) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M6C*** | 18 | 540
A200D212 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 150 | 360
|  | STR |  | A210M6C*** | 18 | 540
A200D213 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 200 | 480
|  | STR |  | A210M6C*** | 18 | 540
A200D214 | D | ICB | Eaton | HMCP600*** | - | 600 | 480 | 3 | 100 | 460 | 3 | 300 | 361 | 2.87 | (1) (3) (5) (7s) | - | E47048 Vol. 2 Sec. 2
|  | STR |  | A210M6C*** | 18 | 540
A200D215 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 350 | 414
|  | STR |  | A210M6C*** | 18 | 540
A200D216 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 400 | 477
|  | STR |  | A210M6C*** | 18 | 540
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = See Table 3 for maximum Heater sizes.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6a) = Install Terminal End Cover TEC1 (6085C42H01) to line side of circuit breaker.
(6b) = Install Terminal end Cover TEC2 (6085C42H02) to line side of circuit breaker.
(7) See table (7) for internal wiring between load side of short circuit protective device & line side of starter.
| Table 7 - Internal Power Wiring | [5 empty] | Table 3 - Maximum Heater Size
| Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation). | [5 empty] | Starter Cat. No. | Nema Size | Maximum Heater
| Wire Code | Wire Size | Wire Code | Wire Size
| 7a | 12 awg. | 7j | 4/0 awg. |  |  | A200M1C*** | 1 | FH51
| 7b | 10 awg. | 7k | 250kcml |  |  | A200M2C*** | 2 | FH57
| 7c | 8 awg. | 7l | 350kcml |  |  | A200M3C*** | 3 | FH88
| 7d | 6 awg. | 7m | 4/0 awg. (3) |  |  | A200M4C*** | 4 | FH93
| 7e | 4 awg. | 7n | 4/0 awg. (4) |  |  | A200M5C*** | 5 | FH32
| 7f | 2 awg. | 7p | 250kcml (2) |  |  | A200M6C*** | 6 | FH33
| 7g | 1/0 awg. | 7r | 350kcml (3) |  |  | A210M1C*** | 1 | FH51
| 7h | 2/0 awg. | 7s | 4/0 awg. (2) |  |  | A210M2C*** | 2 | FH57
[7 empty] | A210M3C*** | 3 | FH88
[7 empty] | A210M4C*** | 4 | FH93
[7 empty] | A210M5C*** | 5 | FH32
[7 empty] | A210M6C*** | 6 | FH33

## IT-EM Type C
Issued: 2006-05-18
Last Revised: 2006-05-18
Combination Motor Controllers for use in Industrial Control Panels
ID Number | Combination Type | Individual Component | [6 empty] | Combination SCCR | [5 empty] | Conditions of Acceptability | Combination Starter UL File | Motor Control Center UL File
|  | Component Type | Manufacturer | Catalog No. | Ratings |  |  |  | SCCR kA | Volts | Phase | Hp | NEC FLC | Min. Enclosure Volume (cu. ft.)
[5 empty] | SCCR kA | Max. Amps | Volts | No. Poles
ITC0001 | C | CB | Eaton | EGH3015FFG | 65 | 15 | 200 | 3 | 65kA | 200 | 3 | 1 | 4.8 | 0.33 | (1) (7a) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITC0002 |  | CB |  | EGH3015FFG | 65 | 15 | [5 empty] | 1.5 | 6.9
|  | STR |  | N101CS1*3A | 5 | 27
TIC0004 | C | CB | Eaton | EGH3015FFG | 65 | 15 | 208 | 3 | 65kA | 208 | 3 | 1 | 4.6 | 0.33 | (1) (7a) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITC0005 |  | CB |  | EGH3015FFG | 65 | 15 | [5 empty] | 1.5 | 6.6
|  | STR |  | N101CS1*3A | 5 | 27
ITC0006 | C | CB | Eaton | EGH3015FFG | 65 | 15 | 240 | 3 | 65kA | 230 | 3 | 1 | 4.2 | 0.33 | (1) (7a) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITC0007 |  | CB |  | EGH3015FFG | 65 | 15 | [5 empty] | 1.5 | 6
|  | STR |  | N101CS1*3A | 5 | 27
ITC0008 | C | CB | Eaton | EGH3015FFG | 65 | 15 | 380 | 3 | 65kA | 380 | 3 | 2 | 4.3 | 0.33 | (1) (7a) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITC0009 |  | CB |  | EGH3015FFG | 65 | 15 | 480 | 3 | 65kA | 460 | 3 | 3 | 4.8
|  | STR |  | N101CS1*3A | 5 | 27
ITC0010 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
ITC0011 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITC0012 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITC0013 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITC0014 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITC0015 | C | CB | Eaton | EGH3015FFG | 65 | 15 | 200 | 3 | 65kA | 200 | 3 | 2 | 7.8 | 0.33 | (1) (7a) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITC0016 |  | CB |  | EGH3015FFG | 65 | 15 | [5 empty] | 3 | 11
|  | STR |  | N101CS1*3A | 5 | 27
ITC0017 | C | CB | Eaton | EGH3015FFG | 65 | 15 | 208 | 3 | 65kA | 208 | 3 | 2 | 7.5 | 0.33 | (1) (7a) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITC0018 |  | CB |  | EGH3015FFG | 65 | 15 | [5 empty] | 3 | 10.6
|  | STR |  | N101CS1*3A | 5 | 27
ITC0019 | C | CB | Eaton | EGH3015FFG | 65 | 15 | 240 | 3 | 65kA | 240 | 3 | 2 | 6.8 | 0.33 | (1) (7a) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITC0020 |  | CB |  | EGH3015FFG | 65 | 15 | [5 empty] | 3 | 9.6
|  | STR |  | N101CS1*3A | 5 | 27
ITC0021 | C | CB | Eaton | EGH3015FFG | 65 | 15 | 380 | 3 | 65kA | 380 | 3 | 2 | 4.3 | 0.33 | (1) (7a) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITC0022 |  | CB |  | EGH3015FFG | 65 | 15 | [5 empty] | 3 | 6.1
|  | STR |  | N101CS1*3A | 5 | 27
ITC0023 |  | CB |  | EGH3015FFG | 65 | 15 | [5 empty] | 5 | 9.7
|  | STR |  | N101CS1*3A | 5 | 27
ITC0024 | C | CB | Eaton | EGH3015FFG | 65 | 15 | 480 | 3 | 65kA | 480 | 3 | 3 | 4.8 | 0.33 | (1) (7c) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITC0025 |  | CB |  | EGH3015FFG | 65 | 15 | [5 empty] | 5 | 7.6
|  | STR |  | N101CS1*3A | 5 | 27
ITC0026 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
ITC0027 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITC0028 | C | CB | Eaton | EGH3035FFG | 65 | 35 | 200 | 3 | 65kA | 200 | 3 | 5 | 17.5 | 0.33 | (1) (7c) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITC0029 |  | CB |  | EGH3035FFG | 65 | 35 | [5 empty] | 7.5 | 25.3
|  | STR |  | N101CS1*3A | 5 | 27
ITC0030 | C | CB | Eaton | EGH3035FFG | 65 | 35 | 208 | 3 | 65kA | 208 | 3 | 5 | 16.7 | 0.33 | (1) (7c) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITC0031 |  | CB |  | EGH3035FFG | 65 | 35 | [5 empty] | 7.5 | 24.2
|  | STR |  | N101CS1*3A | 5 | 27
ITC0032 | C | CB | Eaton | EGH3035FFG | 65 | 35 | 240 | 3 | 65kA | 240 | 3 | 5 | 15.2 | 0.33 | (1) (7c) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITC0033 |  | CB |  | EGH3035FFG | 65 | 35 | [5 empty] | 7.5 | 22
|  | STR |  | N101CS1*3A | 5 | 27
ITC0034 | C | CB | Eaton | EGH3020FFG | 65 | 20 | 380 | 3 | 65kA | 380 | 3 | 7.5 | 14 | 0.33 | (1) (7c) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITC0035 |  | CB |  | EGH3035FFG | 65 | 35 | [5 empty] | 10 | 18
|  | STR |  | N101CS1*3A | 5 | 27
ITC0036 | C | CB | Eaton | EGH3015FFG | 65 | 15 | 480 | 3 | 65kA | 460 | 3 | 7.5 | 11 | 0.33 | (1) (7c) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITC0037 |  | CB |  | EGH3020FFG | 65 | 20 | [5 empty] | 10 | 14
|  | STR |  | N101CS1*3A | 5 | 27
ITC0038 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
ITC0039 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITC0040 | C | CB | Eaton | EGH3050FFG | 65 | 50 | 200 | 3 | 65kA | 200 | 3 | 10 | 32.2 | 0.695 | (1) (7c) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101DS2*3A | 5 | 45
ITC0041 |  | CB | Eaton | EGH3050FFG | 65 | 50 | 208 | 3 | 65kA | 208 | 3 | 10 | 30.8
|  | STR |  | N101DS2*3A | 5 | 45
ITC0042 |  | CB | Eaton | EGH3050FFG | 65 | 50 | 240 | 3 | 65kA | 240 | 3 | 10 | 28 | 0.695 | (1) (7c) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101DS2*3A | 5 | 45
ITC0043 |  | CB |  | EGH3070FFG | 65 | 70 | [5 empty] | 15 | 42
|  | STR |  | N101DS2*3A | 5 | 45
ITC0044 | C | CB | Eaton | EGH3050FFG | 65 | 50 | 380 | 3 | 65kA | 380 | 3 | 15 | 27 | 0.695 | (1) (7a) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101DS2*3A | 5 | 45
ITC0045 |  | CB |  | EGH3070FFG | 65 | 70 | [5 empty] | 20 | 34 |  | (1) (7c)
|  | STR |  | N101DS2*3A | 5 | 45
ITC0046 |  | CB |  | EGH3080FFG | 65 | 80 | [5 empty] | 25 | 44
|  | STR |  | N101DS2*3A | 5 | 45
ITC0047 | C | CB | Eaton | EGH3050FFG | 65 | 50 | 480 | 3 | 65kA | 460 | 3 | 15 | 21 | 0.695 | (1) (7a) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101DS2*3A | 5 | 45
ITC0048 |  | CB |  | EGH3060FFG | 65 | 60 | [5 empty] | 20 | 27
|  | STR |  | N101DS2*3A | 5 | 45
ITC0049 |  | CB |  | EGH3080FFG | 65 | 80 | [5 empty] | 25 | 34 |  | (1) (7c)
|  | STR |  | N101DS2*3A | 5 | 45
ITC0050 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
ITC0051 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITC0052 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITC0053 | C | CB | Eaton | EGH3090FFG | 65 | 90 | 200 | 3 | 65kA | 200 | 3 | 15 | 48.3 | 0.695 | (1) (7e) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES3*3A | 5 | 90
ITC0054 |  | CB |  | EGH3100FFG | 65 | 100 | [5 empty] | 20 | 62.1
|  | STR |  | N101ES3*3A | 5 | 90
ITC0055 |  | CB |  | EGH3125FFG | 65 | 125 | [5 empty] | 25 | 78.2
|  | STR |  | N101ES3*3A | 5 | 90
ITC0056 | C | CB | Eaton | JGH3090FAG | 65 | 90 | 200 | 3 | 100kA | 200 | 3 | 15 | 48.3 | 0.695 | (1) (7e) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES3*3A | 5 | 90
ITC0057 |  | CB |  | JGH3100FAG | 65 | 100 | [5 empty] | 20 | 62.1
|  | STR |  | N101ES3*3A | 5 | 90
ITC0058 |  | CB |  | JGH3125FAG | 65 | 125 | [5 empty] | 25 | 78.2
|  | STR |  | N101ES3*3A | 5 | 90
ITC0059 | C | CB | Eaton | EGH3070FFG | 65 | 70 | 208 | 3 | 65kA | 208 | 3 | 15 | 46.2 | 0.695 | (1) (7e) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES3*3A | 5 | 90
ITC0060 |  | CB |  | EGH3090FFG | 65 | 90 | [5 empty] | 20 | 59.4
|  | STR |  | N101ES3*3A | 5 | 90
ITC0061 |  | CB |  | EGH3125FFG | 65 | 125 | [5 empty] | 25 | 74.8
|  | STR |  | N101ES3*3A | 5 | 90
ITC0062 | C | CB | Eaton | JGH3070FAG | 65 | 70 | 208 | 3 | 100kA | 208 | 3 | 15 | 46.2 | 0.695 | (1) (7e) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES3*3A | 5 | 90
ITC0063 |  | CB |  | JGH3090FAG | 65 | 90 | [5 empty] | 20 | 59.4
|  | STR |  | N101ES3*3A | 5 | 90
ITC0064 |  | CB |  | JGH3125FAG | 65 | 125 | [5 empty] | 25 | 74.8
|  | STR |  | N101ES3*3A | 5 | 90
ITC0065 | C | CB | Eaton | EGH3090FFG | 65 | 90 | 240 | 3 | 65kA | 230 | 3 | 20 | 54 | 0.695 | (1) (7e) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES3*3A | 5 | 90
ITC0066 |  | CB |  | EGH3125FFG | 65 | 125 | [5 empty] | 25 | 68
|  | STR |  | N101ES3*3A | 5 | 90
ITC0067 |  | CB |  | EGH3125FFG | 65 | 125 | [5 empty] | 30 | 88
|  | STR |  | N101ES3*3A | 5 | 90
ITC0068 | C | CB | Eaton | JGH3090FAG | 65 | 90 | 240 | 3 | 100kA | 230 | 3 | 20 | 54 | 0.695 | (1) (7e) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES3*3A | 5 | 90
ITC0069 |  | CB |  | JGH3125FAG | 65 | 125 | [5 empty] | 25 | 68
|  | STR |  | N101ES3*3A | 5 | 90
ITC0070 |  | CB |  | JGH3125FAG | 65 | 125 | [5 empty] | 30 | 88
|  | STR |  | N101ES3*3A | 5 | 90
ITC0071 | C | CB | Eaton | EGH3070FFG | 65 | 70 | 380 | 3 | 65kA | 380 | 3 | 30 | 51 | 0.695 | (1) (7e) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES3*3A | 5 | 90
ITC0072 |  | CB |  | EGH3090FFG | 65 | 90 | [5 empty] | 40 | 66
|  | STR |  | N101ES3*3A | 5 | 90
ITC0073 |  | CB |  | EGH3125FFG | 65 | 125 | [5 empty] | 50 | 83
|  | STR |  | N101ES3*3A | 5 | 90
ITC0074 | C | CB | Eaton | JGH3070FAG | 65 | 70 | 380 | 3 | 100kA | 380 | 3 | 30 | 51 | 0.695 | (1) (7e) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES3*3A | 5 | 90
ITC0075 |  | CB |  | JGH3090FAG | 65 | 90 | [5 empty] | 40 | 66
|  | STR |  | N101ES3*3A | 5 | 90
ITC0076 |  | CB |  | JGH3125FAG | 65 | 125 | [5 empty] | 50 | 83
|  | STR |  | N101ES3*3A | 5 | 90
ITC0077 | C | CB | Eaton | EGH3100FFG | 65 | 100 | 480 | 3 | 65kA | 460 | 3 | 30 | 40 | 0.695 | (1) (7c) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES3*3A | 5 | 90
ITC0078 |  | CB |  | EGH3125FFG | 65 | 125 | [5 empty] | 40 | 52 |  | (1) (7e)
|  | STR |  | N101ES3*3A | 5 | 90
ITC0079 |  | CB |  | JGH3150FAG | 65 | 150 | [5 empty] | 50 | 65
|  | STR |  | N101ES3*3A | 5 | 90
ITC0080 | C | CB | Eaton | JGH3100FAG | 65 | 100 | 480 | 3 | 100kA | 460 | 3 | 30 | 40 | 0.695 | (1) (7c) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES3*3A | 5 | 90
ITC0081 |  | CB |  | JGH3125FAG | 65 | 125 | [5 empty] | 40 | 52 |  | (1) (7e)
|  | STR |  | N101ES3*3A | 5 | 90
ITC0082 |  | CB |  | JGH3150FAG | 65 | 150 | [5 empty] | 50 | 65
|  | STR |  | N101ES3*3A | 5 | 90
ITC0083 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
ITC0084 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITC0085 |  | - |  | - | - | - | [5 empty] | - | - |  | -
|  | - |  | - | - | -
ITC0086 | C | CB | Eaton | JGH3150FAG | 65 | 150 | 200 | 3 | 65kA | 200 | 3 | 30 | 92 | 0.695 | (1) (7f) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES4*3A | 10 | 135
ITC0087 |  | CB |  | JGH3175FAG | 65 | 175 | [5 empty] | 40 | 120
|  | STR |  | N101ES4*3A | 10 | 135
ITC0088 | C | CB | Eaton | KDC3150 | 100 | 150 | 200 | 3 | 100kA | 200 | 3 | 30 | 92 | 1.06 | (1) (7f) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES4*3A | 10 | 135
ITC0089 |  | CB |  | KDC3175 | 100 | 175 | [5 empty] | 40 | 120
|  | STR |  | N101ES4*3A | 10 | 135
ITC0090 | C | CB | Eaton | JGH3150FAG | 65 | 150 | 208 | 3 | 65kA | 208 | 3 | 30 | 88 | 0.695 | (1) (7f) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES4*3A | 10 | 135
ITC0091 |  | CB |  | JGH3175FAG | 65 | 175 | [5 empty] | 40 | 114
|  | STR |  | N101ES4*3A | 10 | 135
ITC0092 | C | CB | Eaton | KDC3150 | 100 | 150 | 208 | 3 | 100kA | 208 | 3 | 30 | 88 | 1.06 | (1) (7f) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES4*3A | 10 | 135
ITC0093 |  | CB |  | KDC3175 | 100 | 175 | [5 empty] | 40 | 114
|  | STR |  | N101ES4*3A | 10 | 135
ITC0094 | C | CB | Eaton | JGH3150FAG | 65 | 150 | 240 | 3 | 65kA | 230 | 3 | 40 | 104 | 0.695 | (1) (7f) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES4*3A | 10 | 135
ITC0095 |  | CB |  | JGH3250FAG | 65 | 250 | [5 empty] | 50 | 130
|  | STR |  | N101ES4*3A | 10 | 135
ITC0096 | C | CB | Eaton | KDC3150 | 100 | 150 | 240 | 3 | 100kA | 230 | 3 | 40 | 104 | 1.06 | (1) (7f) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES4*3A | 10 | 135
ITC0097 |  | CB |  | KDC3250 | 100 | 250 | [5 empty] | 50 | 130
|  | STR |  | N101ES4*3A | 10 | 135
ITC0098 | C | CB | Eaton | JGH3150FAG | 65 | 150 | 380 | 3 | 65kA | 380 | 3 | 60 | 103 | 0.695 | (1) (7f) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES4*3A | 10 | 135
ITC0099 |  | CB |  | JGH3250FAG | 65 | 250 | [5 empty] | 75 | 128
|  | STR |  | N101ES4*3A | 10 | 135
ITC0100 | C | CB | Eaton | KDC3150 | 100 | 150 | 380 | 3 | 100kA | 380 | 3 | 60 | 103 | 1.06 | (1) (7f) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES4*3A | 10 | 135
ITC0101 |  | CB |  | KDC3250 | 100 | 250 | [5 empty] | 75 | 128
|  | STR |  | N101ES4*3A | 10 | 135
ITC0102 | C | CB | Eaton | JGH3250FAG | 65 | 250 | 480 | 3 | 65kA | 460 | 3 | 60 | 77 | 1.06 | (1) (7e) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES4*3A | 10 | 135
ITC0103 |  | CB |  | JGH3250FAG | 65 | 250 | [5 empty] | 75 | 96 |  | (1) (7f)
|  | STR |  | N101ES4*3A | 10 | 135
ITC0104 |  | CB |  | HKD3300 | 65 | 300 | [5 empty] | 100 | 124
|  | STR |  | N101ES4*3A | 10 | 135
ITC0105 | C | CB | Eaton | KDC3250 | 100 | 250 | 480 | 3 | 100kA | 460 | 3 | 60 | 77 | 1.06 | (1) (7e) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES4*3A | 10 | 135
ITC0106 |  | CB |  | KDC3250 | 100 | 250 | [5 empty] | 75 | 96 |  | (1) (7f)
|  | STR |  | N101ES4*3A | 10 | 135
ITC0107 |  | CB |  | KDC3300 | 100 | 300 | [5 empty] | 100 | 124
|  | STR |  | N101ES4*3A | 10 | 135
ITC0108 |  | CB |  | KDC3400 | 100 | 400 | [5 empty] | 100 | 124
|  | STR |  | N101ES4*3A | 10 | 135
ITC0109 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
ITC0110 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITC0111 |  | - |  | - | - | - | [5 empty] | - | - |  | -
|  | - |  | - | - | -
ITC0112 | C | CB | Eaton | HKD3250 | 65 | 250 | 200 | 3 | 65kA | 200 | 3 | 50 | 150 | 1.78 | (1) (7j) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101FS5*3A | 10 | 270
ITC0113 |  | CB |  | HKD3250 | 65 | 250 | [5 empty] | 60 | 177
|  | STR |  | N101FS5*3A | 10 | 270
ITC0114 |  | CB |  | HKD3350 | 65 | 350 | [5 empty] | 75 | 221
|  | STR |  | N101FS5*3A | 10 | 270
ITC0115 | C | CB | Eaton | KDC3250 | 100 | 250 | 200 | 3 | 100kA | 200 | 3 | 50 | 150 | 1.78 | (1) (7j) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101FS5*3A | 10 | 270
ITC0116 |  | CB |  | KDC3250 | 100 | 250 | [5 empty] | 60 | 177
|  | STR |  | N101FS5*3A | 10 | 270
ITC0117 |  | CB |  | KDC3350 | 100 | 350 | [5 empty] | 75 | 221
|  | STR |  | N101FS5*3A | 10 | 270
ITC0118 | C | CB | Eaton | HKD3200 | 65 | 200 | 208 | 3 | 65kA | 208 | 3 | 50 | 143 | 2.15 | (1) (7j) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101FS5*3A | 10 | 270
ITC0119 |  | CB |  | HKD3250 | 65 | 250 | [5 empty] | 60 | 169
|  | STR |  | N101FS5*3A | 10 | 270
ITC0120 |  | CB |  | HKD3350 | 65 | 350 | [5 empty] | 75 | 211
|  | STR |  | N101FS5*3A | 10 | 270
ITC0121 | C | CB | Eaton | KDC3200 | 100 | 200 | 208 | 3 | 100kA | 208 | 3 | 50 | 143 | 2.15 | (1) (7j) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101FS5*3A | 10 | 270
ITC0122 |  | CB |  | KDC3250 | 100 | 250 | [5 empty] | 60 | 169
|  | STR |  | N101FS5*3A | 10 | 270
ITC0123 |  | CB |  | KDC3350 | 100 | 350 | [5 empty] | 75 | 211
|  | STR |  | N101FS5*3A | 10 | 270
ITC0124 | C | CB | Eaton | HKD3250 | 65 | 250 | 240 | 3 | 65kA | 230 | 3 | 60 | 154 | 2.15 | (1) (7j) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101FS5*3A | 10 | 270
ITC0125 |  | CB |  | HKD3300 | 65 | 300 | [5 empty] | 75 | 192
|  | STR |  | N101FS5*3A | 10 | 270
ITC0126 |  | CB |  | KDC3400 | 65 | 400 |  |  | 100kA |  |  | 100 | 248
|  | STR |  | N101FS5*3A | 10 | 270
ITC0127 | C | CB | Eaton | KDC3250 | 100 | 250 | 240 | 3 | 100kA | 230 | 3 | 60 | 154 | 2.15 | (1) (7j) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101FS5*3A | 10 | 270
ITC0128 |  | CB |  | KDC3300 | 100 | 300 | [5 empty] | 75 | 192
|  | STR |  | N101FS5*3A | 10 | 270
ITC0129 |  | CB |  | KDC3400 | 100 | 400 | [5 empty] | 100 | 248
|  | STR |  | N101FS5*3A | 10 | 270
ITC0130 | C | CB | Eaton | HKD3250 | 65 | 250 | 380 | 3 | 65kA | 380 | 3 | 100 | 165 | 2.15 | (1) (7j) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101FS5*3A | 10 | 270
ITC0131 |  | CB |  | HKD3300 | 65 | 300 | [5 empty] | 125 | 208
|  | STR |  | N101FS5*3A | 10 | 270
ITC0132 |  | CB |  | KDC3400 | 65 | 400 | [5 empty] | 150 | 240
|  | STR |  | N101FS5*3A | 10 | 270
ITC0133 | C | CB | Eaton | KDC3250 | 100 | 250 | 380 | 3 | 100kA | 380 | 3 | 100 | 165 | 2.15 | (1) (7j) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101FS5*3A | 10 | 270
ITC0134 |  | CB |  | KDC3300 | 100 | 300 | [5 empty] | 125 | 208
|  | STR |  | N101FS5*3A | 10 | 270
ITC0135 |  | CB |  | KDC3400 | 100 | 400 | [5 empty] | 150 | 240
|  | STR |  | N101FS5*3A | 10 | 270
ITC0136 | C | CB | Eaton | HKD3250 | 65 | 250 | 480 | 3 | 65kA | 460 | 3 | 125 | 156 | 2.15 | (1) (7j) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101FS5*3A | 10 | 270
ITC0137 |  | CB |  | HKD3300 | 65 | 300 | [5 empty] | 150 | 180
|  | STR |  | N101FS5*3A | 10 | 270
ITC0138 |  | CB |  | HKD3400 | 65 | 400 | [5 empty] | 200 | 240
|  | STR |  | N101FS5*3A | 10 | 270
ITC0139 |  | CB |  | HLD3400 | 65 | 400 | [5 empty] | 200 | 240
|  | STR |  | N101FS5*3A | 10 | 270
ITC0140 | C | CB | Eaton | KDC3250 | 100 | 250 | 480 | 3 | 100kA | 460 | 3 | 125 | 156 | 2.15 | (1) (7j) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101FS5*3A | 10 | 270
ITC0141 |  | CB |  | KDC3300 | 100 | 300 | [5 empty] | 150 | 180
|  | STR |  | N101FS5*3A | 10 | 270
ITC0142 |  | CB |  | KDC3400 | 100 | 400 | [5 empty] | 200 | 240
|  | STR |  | N101FS5*3A | 10 | 270
ITC0143 |  | CB |  | KDC3400 | 100 | 400 | [5 empty] | 200 | 240
|  | STR |  | N101FS5*3A | 10 | 270
ITC0144 | C | CB | Eaton | HKD3400 | 35 | 400 | 600 | 3 | 25kA | 575 | 3 | 200 | 192 | 2.15 | (1) (7j) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101FS5*3A | 10 | 270
ITC0145 |  | CB |  | HLD3400 | 35 | 400 |  |  | 35kA |  |  | 200 | 192
|  | STR |  | N101FS5*3A | 10 | 270
ITC0146 | C | CB | Eaton | KDC3400 | 100 | 400 | 600 | 3 | 50kA | 575 | 3 | 200 | 192 | 2.15 | (1) (7j) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101FS5*3A | 10 | 270
ITC0147 |  | CB |  | KDC3400 | 100 | 400 | [5 empty] | 200 | 192
|  | STR |  | N101FS5*3A | 10 | 270
ITC0148 | C | CB | Eaton | EGH3015FFG | 65 | 15 | 200 | 3 | 65kA | 200 | 3 | 1 | 4.8 | 0.695 | (1) (7a) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITC0149 |  | CB |  | EGH3020FFG | 65 | 20 | [5 empty] | 1.5 | 6.9
|  | STR |  | N501CS1*3A | 5 | 27
ITC0150 | C | CB | Eaton | EGH3015FFG | 65 | 15 | 208 | 3 | 65kA | 208 | 3 | 1 | 4.6 | 0.695 | (1) (7a) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITC0151 |  | CB |  | EGH3020FFG | 65 | 20 | [5 empty] | 1.5 | 6.6
|  | STR |  | N501CS1*3A | 5 | 27
ITC0152 | C | CB | Eaton | EGH3015FFG | 65 | 15 | 240 | 3 | 65kA | 230 | 3 | 1 | 4.2 | 0.695 | (1) (7a) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITC0153 |  | CB |  | EGH3015FFG | 65 | 15 | [5 empty] | 1.5 | 6
|  | STR |  | N501CS1*3A | 5 | 27
ITC0154 | C | CB | Eaton | EGH3015FFG | 65 | 15 | 380 | 3 | 65kA | 380 | 3 | 2 | 4.3 | 0.695 | (1) (7a) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITC0155 |  | CB |  | EGH3015FFG | 65 | 15 | [5 empty] | 3 | 6.1
|  | STR |  | N501CS1*3A | 5 | 27
ITC0156 | C | CB | Eaton | EGH3015FFG | 65 | 15 | 480 | 3 | 65kA | 460 | 3 | 3 | 4.8 | 0.695 | (1) (7a) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITC0157 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
ITC0158 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITC0159 |  | - |  | - | - | - | [5 empty] | - | - |  |  |  | -
|  | - |  | - | - | -
ITC0160 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITC0161 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITC0162 | C | CB | Eaton | EGH3020FFG | 65 | 20 | 200 | 3 | 65kA | 200 | 3 | 2 | 7.8 | 0.695 | (1) (7a) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITC0163 |  | CB |  | EGH3020FFG | 65 | 20 | [5 empty] | 3 | 11
|  | STR |  | N501CS1*3A | 5 | 27
ITC0164 | C | CB | Eaton | EGH3020FFG | 65 | 20 | 208 | 3 | 65kA | 208 | 3 | 2 | 7.5 | 0.695 | (1) (7a) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITC0165 |  | CB |  | EGH3025FFG | 65 | 25 | [5 empty] | 3 | 10.6
|  | STR |  | N501CS1*3A | 5 | 27
ITC0166 | C | CB | Eaton | EGH3020FFG | 65 | 20 | 240 | 3 | 65kA | 240 | 3 | 2 | 6.8 | 0.695 | (1) (7a) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITC0167 |  | CB |  | EGH3025FFG | 65 | 25 | [5 empty] | 3 | 9.6
|  | STR |  | N501CS1*3A | 5 | 27
ITC0168 | C | CB | Eaton | EGH3015FFG | 65 | 15 | 380 | 3 | 65kA | 380 | 3 | 2 | 4.3 | 0.695 | (1) (7a) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITC0169 |  | CB |  | EGH3015FFG | 65 | 15 | [5 empty] | 3 | 6.1
|  | STR |  | N501CS1*3A | 5 | 27
ITC0170 |  | CB |  | EGH3025FFG | 65 | 25 | [5 empty] | 5 | 9.7
|  | STR |  | N501CS1*3A | 5 | 27
ITC0171 | C | CB | Eaton | EGH3015FFG | 65 | 15 | 480 | 3 | 65kA | 480 | 3 | 3 | 4.8 | 0.695 | (1) (7a) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITC0172 |  | CB |  | EGH3020FFG | 65 | 20 | [5 empty] | 5 | 7.6
|  | STR |  | N501CS1*3A | 5 | 27
ITC0173 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
ITC0174 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITC0175 | C | CB | Eaton | EGH3035FFG | 65 | 35 | 200 | 3 | 65kA | 200 | 3 | 5 | 17.5 | 0.695 | (1) (7a) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITC0176 |  | CB |  | EGH3050FFG | 65 | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | N501CS1*3A | 5 | 27
ITC0177 | C | CB | Eaton | EGH3035FFG | 65 | 35 | 208 | 3 | 65kA | 208 | 3 | 5 | 16.7 | 0.695 | (1) (7a) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITC0178 |  | CB |  | EGH3050FFG | 65 | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | N501CS1*3A | 5 | 27
ITC0179 | C | CB | Eaton | EGH3035FFG | 65 | 35 | 240 | 3 | 65kA | 240 | 3 | 5 | 15.2 | 0.695 | (1) (7a) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITC0180 |  | CB |  | EGH3050FFG | 65 | 50 | [5 empty] | 7.5 | 22
|  | STR |  | N501CS1*3A | 5 | 27
ITC0181 | C | CB | Eaton | EGH3020FFG | 65 | 20 | 380 | 3 | 65kA | 380 | 3 | 7.5 | 14 | 0.695 | (1) (7a) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITC0183 |  | CB |  | EGH3035FFG | 65 | 35 | [5 empty] | 10 | 18
|  | STR |  | N501CS1*3A | 5 | 27
ITC0184 | C | CB | Eaton | EGH3015FFG | 65 | 15 | 480 | 3 | 65kA | 460 | 3 | 7.5 | 11 | 0.695 | (1) (7a) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITC0185 |  | CB |  | EGH3020FFG | 65 | 20 | [5 empty] | 10 | 14
|  | STR |  | N501CS1*3A | 5 | 27
ITC0186 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
ITC0187 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITC0188 | C | CB | Eaton | EGH3050FFG | 65 | 50 | 200 | 3 | 65kA | 200 | 3 | 10 | 32.2 | 1.05 | (1) (7c) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501DS2*3A | 5 | 45
ITC0189 |  | CB | Eaton | EGH3050FFG | 65 | 50 | 208 | 3 | 65kA | 208 | 3 | 10 | 30.8
|  | STR |  | N501DS2*3A | 5 | 45
ITC0190 |  | CB | Eaton | EGH3050FFG | 65 | 50 | 240 | 3 | 65kA | 240 | 3 | 10 | 28 | 1.05 | (1) (7c) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501DS2*3A | 5 | 45
ITC0191 |  | CB |  | EGH3070FFG | 65 | 70 | [5 empty] | 15 | 42
|  | STR |  | N501DS2*3A | 5 | 45
ITC0192 | C | CB | Eaton | EGH3050FFG | 65 | 50 | 380 | 3 | 65kA | 380 | 3 | 15 | 27 | 1.05 | (1) (7a) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501DS2*3A | 5 | 45
ITC0193 |  | CB |  | EGH3070FFG | 65 | 70 | [5 empty] | 20 | 34 |  | (1) (7c)
|  | STR |  | N501DS2*3A | 5 | 45
ITC0194 |  | CB |  | EGH3080FFG | 65 | 80 | [5 empty] | 25 | 44
|  | STR |  | N501DS2*3A | 5 | 45
ITC0195 | C | CB | Eaton | EGH3050FFG | 65 | 50 | 480 | 3 | 65kA | 460 | 3 | 15 | 21 | 1.05 | (1) (7a) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501DS2*3A | 5 | 45
ITC0196 |  | CB |  | EGH3060FFG | 65 | 60 | [5 empty] | 20 | 27
|  | STR |  | N501DS2*3A | 5 | 45
ITC0197 |  | CB |  | EGH3080FFG | 65 | 80 | [5 empty] | 25 | 34 |  | (1) (7a)
|  | STR |  | N501DS2*3A | 5 | 45
ITC0198 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
ITC0199 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITC0200 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITC0201 | C | CB | Eaton | EGH3090FFG | 65 | 90 | 200 | 3 | 65kA | 200 | 3 | 15 | 48.3 | 1.05 | (1) (7e) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES3*3A | 5 | 90
ITC0202 |  | CB |  | EGH3100FFG | 65 | 100 | [5 empty] | 20 | 62.1
|  | STR |  | N501ES3*3A | 5 | 90
ITC0203 |  | CB |  | EGH3125FFG | 65 | 125 | [5 empty] | 25 | 78.2
|  | STR |  | N501ES3*3A | 5 | 90
ITC0204 | C | CB | Eaton | JGH3090FAG | 65 | 90 | 200 | 3 | 100kA | 200 | 3 | 15 | 48.3 | 1.05 | (1) (7e) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES3*3A | 5 | 90
ITC0205 |  | CB |  | JGH3100FAG | 65 | 100 | [5 empty] | 20 | 62.1
|  | STR |  | N501ES3*3A | 5 | 90
ITC0206 |  | CB |  | JGH3125GAF | 65 | 125 | [5 empty] | 25 | 78.2
|  | STR |  | N501ES3*3A | 5 | 90
ITC0207 | C | CB | Eaton | EGH3070FFG | 65 | 70 | 208 | 3 | 65kA | 208 | 3 | 15 | 46.2 | 1.05 | (1) (7e) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES3*3A | 5 | 90
ITC0208 |  | CB |  | EGH3090FFG | 65 | 90 | [5 empty] | 20 | 59.4
|  | STR |  | N501ES3*3A | 5 | 90
ITC0209 |  | CB |  | EGH3125FFG | 65 | 125 | [5 empty] | 25 | 74.8
|  | STR |  | N501ES3*3A | 5 | 90
ITC0210 | C | CB | Eaton | JGH3070FAG | 65 | 70 | 208 | 3 | 100kA | 208 | 3 | 15 | 46.2 | 1.05 | (1) (7e) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES3*3A | 5 | 90
ITC0211 |  | CB |  | JGH3090FAG | 65 | 90 | [5 empty] | 20 | 59.4
|  | STR |  | N501ES3*3A | 5 | 90
ITC0212 |  | CB |  | JGH3125FAG | 65 | 125 | [5 empty] | 25 | 74.8
|  | STR |  | N501ES3*3A | 5 | 90
ITC0213 | C | CB | Eaton | EGH3090FFG | 65 | 90 | 240 | 3 | 65kA | 230 | 3 | 20 | 54 | 1.05 | (1) (7e) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES3*3A | 5 | 90
ITC0214 |  | CB |  | EGH3125FFG | 65 | 125 | [5 empty] | 25 | 68
|  | STR |  | N501ES3*3A | 5 | 90
ITC0215 |  | CB |  | EGH3125FFG | 65 | 125 | [5 empty] | 30 | 88
|  | STR |  | N501ES3*3A | 5 | 90
ITC0216 | C | CB | Eaton | JGH3090FAG | 65 | 90 | 240 | 3 | 100kA | 230 | 3 | 20 | 54 | 1.05 | (1) (7e) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES3*3A | 5 | 90
ITC0217 |  | CB |  | JGH3125FAG | 65 | 125 | [5 empty] | 25 | 68
|  | STR |  | N501ES3*3A | 5 | 90
ITC0218 |  | CB |  | JGH3215FAG | 65 | 125 | [5 empty] | 30 | 88
|  | STR |  | N501ES3*3A | 5 | 90
ITC0219 | C | CB | Eaton | EGH3070FFG | 65 | 70 | 380 | 3 | 65kA | 380 | 3 | 30 | 51 | 1.05 | (1) (7e) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES3*3A | 5 | 90
ITC0220 |  | CB |  | EGH3090FFG | 65 | 90 | [5 empty] | 40 | 66
|  | STR |  | N501ES3*3A | 5 | 90
ITC0221 |  | CB |  | EGH3125FFG | 65 | 125 | [5 empty] | 50 | 83
|  | STR |  | N501ES3*3A | 5 | 90
ITC0222 | C | CB | Eaton | JGH3070FAG | 65 | 70 | 380 | 3 | 100kA | 380 | 3 | 30 | 51 | 1.05 | (1) (7e) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES3*3A | 5 | 90
ITC0223 |  | CB |  | JGH3090FAG | 65 | 90 | [5 empty] | 40 | 66
|  | STR |  | N501ES3*3A | 5 | 90
ITC0224 |  | CB |  | JGH3125FAG | 65 | 125 | [5 empty] | 50 | 83
|  | STR |  | N501ES3*3A | 5 | 90
ITC0225 | C | CB | Eaton | EGH3100FFG | 65 | 100 | 480 | 3 | 65kA | 460 | 3 | 30 | 40 | 1.05 | (1) (7c) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES3*3A | 5 | 90
ITC0226 |  | CB |  | EGH3125FFG | 65 | 125 | [5 empty] | 40 | 52 |  | (1) (7e)
|  | STR |  | N501ES3*3A | 5 | 90
ITC0227 |  | CB |  | JGH3150FAG | 65 | 150 | [5 empty] | 50 | 65
|  | STR |  | N501ES3*3A | 5 | 90
ITC0228 | C | CB | Eaton | JGH3100FAG | 65 | 100 | 480 | 3 | 100kA | 460 | 3 | 30 | 40 | 1.05 | (1) (7c) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES3*3A | 5 | 90
ITC0229 |  | CB |  | JGH3125FAG | 65 | 125 | [5 empty] | 40 | 52 |  | (1) (7e)
|  | STR |  | N501ES3*3A | 5 | 90
ITC0230 |  | CB |  | JGH3150FAG | 65 | 150 | [5 empty] | 50 | 65
|  | STR |  | N501ES3*3A | 5 | 90
ITC0231 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
ITC0232 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITC0233 |  | - |  | - | - | - | [5 empty] | - | - |  | -
|  | - |  | - | - | -
ITC0234 | C | CB | Eaton | JGH3150FAG | 65 | 150 | 200 | 3 | 65kA | 200 | 3 | 30 | 92 | 1.05 | (1) (7f) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES4*3A | 10 | 135
ITC0235 |  | CB |  | JGH3175FAG | 65 | 175 | [5 empty] | 40 | 120
|  | STR |  | N501ES4*3A | 10 | 135
ITC0236 | C | CB | Eaton | KDC3150 | 65 | 150 | 200 | 3 | 100kA | 200 | 3 | 30 | 92 | 1.05 | (1) (7f) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES4*3A | 10 | 135
ITC0237 |  | CB |  | KDC3175 | 65 | 175 | [5 empty] | 40 | 120
|  | STR |  | N501ES4*3A | 10 | 135
ITC0238 | C | CB | Eaton | JGH3150FAG | 65 | 150 | 208 | 3 | 65kA | 208 | 3 | 30 | 88 | 1.05 | (1) (7f) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES4*3A | 10 | 135
ITC0239 |  | CB |  | JGH3175FAG | 65 | 175 | [5 empty] | 40 | 114
|  | STR |  | N501ES4*3A | 10 | 135
ITC0240 | C | CB | Eaton | KDC3150 | 65 | 150 | 208 | 3 | 100kA | 208 | 3 | 30 | 88 | 1.05 | (1) (7f) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES4*3A | 10 | 135
ITC0241 |  | CB |  | KDC3175 | 65 | 175 | [5 empty] | 40 | 114
|  | STR |  | N501ES4*3A | 10 | 135
ITC0242 | C | CB | Eaton | JGH3150FAG | 65 | 150 | 240 | 3 | 65kA | 230 | 3 | 40 | 104 | 1.05 | (1) (7f) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES4*3A | 10 | 135
ITC0243 |  | CB |  | JGH3250FAG | 65 | 250 | [5 empty] | 50 | 130
|  | STR |  | N501ES4*3A | 10 | 135
ITC0244 | C | CB | Eaton | KDC3150 | 65 | 150 | 240 | 3 | 100kA | 230 | 3 | 40 | 104 | 1.05 | (1) (7f) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES4*3A | 10 | 135
ITC0245 |  | CB |  | KDC3250 | 65 | 250 | [5 empty] | 50 | 130
|  | STR |  | N501ES4*3A | 10 | 135
ITC0246 | C | CB | Eaton | JGH3150FAG | 65 | 150 | 380 | 3 | 65kA | 380 | 3 | 60 | 103 | 1.05 | (1) (7f) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES4*3A | 10 | 135
ITC0247 |  | CB |  | JGH3250FAG | 65 | 250 | [5 empty] | 75 | 128
|  | STR |  | N501ES4*3A | 10 | 135
ITC0248 | C | CB | Eaton | KDC3150 | 65 | 150 | 380 | 3 | 100kA | 380 | 3 | 60 | 103 | 1.05 | (1) (7f) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES4*3A | 10 | 135
ITC0249 |  | CB |  | KDC3250 | 65 | 250 | [5 empty] | 75 | 128
|  | STR |  | N501ES4*3A | 10 | 135
ITC0250 | C | CB | Eaton | JGH3250FAG | 65 | 250 | 480 | 3 | 65kA | 460 | 3 | 60 | 77 | 1.05 | (1) (7e) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES4*3A | 10 | 135
ITC0251 |  | CB |  | JGH3250FAG | 65 | 250 | [5 empty] | 75 | 96 |  | (1) (7f)
|  | STR |  | N501ES4*3A | 10 | 135
ITC0252 |  | CB |  | HKD3300 | 65 | 300 | [5 empty] | 100 | 124 | 1.78
|  | STR |  | N501ES4*3A | 10 | 135
ITC0253 |  | CB |  | KDC3400 | 65 | 400 |  |  | 100kA |  |  | 100 | 124
|  | STR |  | N501ES4*3A | 10 | 135
ITC0254 | C | CB | Eaton | KDC3250 | 65 | 250 | 480 | 3 | 100kA | 460 | 3 | 60 | 77 | 1.05 | (1) (7e) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES4*3A | 10 | 135
ITC0255 |  | CB |  | KDC3250 | 65 | 250 | [5 empty] | 75 | 96 |  | (1) (7f)
|  | STR |  | N501ES4*3A | 10 | 135
ITC0256 |  | CB |  | KDC3300 | 65 | 300 | [5 empty] | 100 | 124 | 1.78
|  | STR |  | N501ES4*3A | 10 | 135
ITC0257 |  | CB |  | KDC3400 | 65 | 400 | [5 empty] | 100 | 124
|  | STR |  | N501ES4*3A | 10 | 135
ITC0258 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
ITC0259 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITC0260 |  | - |  | - | - | - | [5 empty] | - | - |  | -
|  | - |  | - | - | -
ITC0261 | C | CB | Eaton | HKD3250 | 65 | 250 | 200 | 3 | 65kA | 200 | 3 | 50 | 150 | 2.5 | (1) (7j) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501FS5*3A | 10 | 270
ITC0262 |  | CB |  | HKD3250 | 65 | 250 | [5 empty] | 60 | 177
|  | STR |  | N501FS5*3A | 10 | 270
ITC0263 |  | CB |  | HKD3350 | 65 | 350 | [5 empty] | 75 | 221
|  | STR |  | N501FS5*3A | 10 | 270
ITC0264 | C | CB | Eaton | KDC3250 | 65 | 250 | 200 | 3 | 100kA | 200 | 3 | 50 | 150 | 2.5 | (1) (7j) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501FS5*3A | 10 | 270
ITC0265 |  | CB |  | KDC3250 | 65 | 250 | [5 empty] | 60 | 177
|  | STR |  | N501FS5*3A | 10 | 270
ITC0266 |  | CB |  | KDC3350 | 65 | 350 | [5 empty] | 75 | 221
|  | STR |  | N501FS5*3A | 10 | 270
ITC0267 | C | CB | Eaton | HKD3200 | 65 | 200 | 208 | 3 | 65kA | 208 | 3 | 50 | 143 | 2.5 | (1) (7j) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501FS5*3A | 10 | 270
ITC0268 |  | CB |  | HKD3250 | 65 | 250 | [5 empty] | 60 | 169
|  | STR |  | N501FS5*3A | 10 | 270
ITC0269 |  | CB |  | HKD3350 | 65 | 350 | [5 empty] | 75 | 211
|  | STR |  | N501FS5*3A | 10 | 270
ITC0270 | C | CB | Eaton | KDC3200 | 65 | 200 | 208 | 3 | 100kA | 208 | 3 | 50 | 143 | 2.5 | (1) (7j) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501FS5*3A | 10 | 270
ITC0271 |  | CB |  | KDC3250 | 65 | 250 | [5 empty] | 60 | 169
|  | STR |  | N501FS5*3A | 10 | 270
ITC0272 |  | CB |  | KDC3350 | 65 | 350 | [5 empty] | 75 | 211
|  | STR |  | N501FS5*3A | 10 | 270
ITC0273 | C | CB | Eaton | HKD3250 | 65 | 250 | 240 | 3 | 65kA | 230 | 3 | 60 | 154 | 2.5 | (1) (7j) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501FS5*3A | 10 | 270
ITC0274 |  | CB |  | HKD3300 | 65 | 300 | [5 empty] | 75 | 192
|  | STR |  | N101FS5*3A | 10 | 270
ITC0275 |  | CB |  | KDC3400 | 65 | 400 | [5 empty] | 100 | 248
|  | STR |  | N501FS5*3A | 10 | 270
ITC0276 | C | CB | Eaton | KDC3250 | 65 | 250 | 240 | 3 | 100kA | 230 | 3 | 60 | 154 | 2.5 | (1) (7j) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501FS5*3A | 10 | 270
ITC0277 |  | CB |  | KDC3300 | 65 | 300 | [5 empty] | 75 | 192
|  | STR |  | N101FS5*3A | 10 | 270
ITC0278 |  | CB |  | KDC3400 | 65 | 400 | [5 empty] | 100 | 248
|  | STR |  | N501FS5*3A | 10 | 270
ITC0279 | C | CB | Eaton | HKD3250 | 65 | 250 | 380 | 3 | 65kA | 380 | 3 | 100 | 165 | 2.5 | (1) (7j) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501FS5*3A | 10 | 270
ITC0280 |  | CB |  | HKD3300 | 65 | 300 | [5 empty] | 125 | 208
|  | STR |  | N501FS5*3A | 10 | 270
ITC0281 |  | CB |  | KDC3400 | 65 | 400 | [5 empty] | 150 | 240
|  | STR |  | N501FS5*3A | 10 | 270
ITC0282 | C | CB | Eaton | KDC3250 | 65 | 250 | 380 | 3 | 100kA | 380 | 3 | 100 | 165 | 2.5 | (1) (7j) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501FS5*3A | 10 | 270
ITC0283 |  | CB |  | KDC3300 | 65 | 300 | [5 empty] | 125 | 208
|  | STR |  | N501FS5*3A | 10 | 270
ITC0284 |  | CB |  | KDC3400 | 65 | 400 | [5 empty] | 150 | 240
|  | STR |  | N501FS5*3A | 10 | 270
ITC0285 | C | CB | Eaton | HKD3250 | 65 | 250 | 480 | 3 | 65kA | 460 | 3 | 125 | 156 | 2.5 | (1) (7j) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501FS5*3A | 10 | 270
ITC0286 |  | CB |  | HKD3300 | 65 | 300 | [5 empty] | 150 | 180
|  | STR |  | N501FS5*3A | 10 | 270
ITC0287 |  | CB |  | HKD3400 | 65 | 400 | [5 empty] | 200 | 240
|  | STR |  | N501FS5*3A | 10 | 270
ITC0288 |  | CB |  | KDC3400 | 65 | 400 | [5 empty] | 200 | 240
|  | STR |  | N101FS5*3A | 10 | 270
ITC0289 | C | CB | Eaton | KDC3250 | 65 | 250 | 480 | 3 | 100kA | 460 | 3 | 125 | 156 | 2.5 | (1) (7j) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501FS5*3A | 10 | 270
ITC0290 |  | CB |  | KDC3300 | 65 | 300 | [5 empty] | 150 | 180
|  | STR |  | N501FS5*3A | 10 | 270
ITC0291 |  | CB |  | KDC3400 | 65 | 400 | [5 empty] | 200 | 240
|  | STR |  | N501FS5*3A | 10 | 270
ITC0292 |  | CB |  | KDC3400 | 65 | 400 | [5 empty] | 200 | 240
|  | STR |  | N101FS5*3A | 10 | 270
ITC0293 | C | - | Eaton | - | - | - | 600 | 3 | - | 575 | 3 | - | - | 2.5 | - | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | - |  | - | - | -
ITC0294 |  | - |  | - | - | - | [5 empty] | - | - |  | (1) (7j)
|  | - |  | - | - | -
ITC0295 |  | CB |  | HKD3400 | 35 | 400 |  |  | 25kA |  |  | 200 | 192
|  | STR |  | N501FS5*3A | 10 | 270
ITC0296 |  | CB |  | HLD3400 | 35 | 400 |  |  | 35kA |  |  | 200 | 192
|  | STR |  | N501FS5*3A | 10 | 270
ITC0297 | C | CB | Eaton | KDC3200 | 65 | 200 | 600 | 3 | 50kA | 575 | 3 | 125 | 125 | 2.5 | (1) (7f) | E176513 Vol.1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501FS5*3A | 10 | 270
ITC0298 |  | CB |  | KDC3200 | 65 | 200 | [5 empty] | 150 | 144 |  | (1) (7j)
|  | STR |  | N501FS5*3A | 10 | 270
ITC0299 |  | CB |  | KDC3300 | 35 | 300 | [5 empty] | 200 | 192
|  | STR |  | N501FS5*3A | 10 | 270
Conditions of Aceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = Additional Conditions of Acceptability may be specified in the individual Tables.
(7) See Table 7 for internal wiring between load side of short circuit protective device & line side of starter.
Table 7 - Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
| Wire Code | Wire Size | Wire Code | Wire Size
| 7a | 12 awg. | 7j | 4/0 awg.
| 7b | 10 awg. | 7k | 250kcml
| 7c | 8 awg. | 7l | 350kcml
| 7d | 6 awg. | 7m | 4/0 awg. (3)
| 7e | 4 awg. | 7n | 4/0 awg. (4)
| 7f | 2 awg. | 7p | 250kcml (2)
| 7g | 1/0 awg. | 7r | 350kcml (3)
| 7h | 2/0 awg. | 7s | 4/0 awg. (2)

## IT-EM Type D
Issued: 2006-05-18
Last Revised: 2006-05-18
Combination Motor Controllers for use in Industrial Control Panels
ID Number | Combination Type | Individual Component | [6 empty] | Combination SCCR | [5 empty] | Conditions of Acceptability | Combination Starter UL File | Motor Contol Center UL File
|  | Component Type | Manufacturer | Partial Catalog No. | Ratings |  |  |  | SCCR kA | Volts | Phase | Hp | NEC FLC | Min. Enclosure Volume (cu. ft.)
[5 empty] | SCCR kA | Max. Amps | Volts | No. Poles
ITD0001 | D | ICB | Eaton | HMCPE007C0C | - | 7 | 200 | 3 | 100kA | 200 | 3 | 1/2 | 2.5 | 0.332 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITD0002 |  | ICB |  | HMCPE007C0C | - | 7 | [5 empty] | 3/4 | 3.7
|  | STR |  | N101CS1*3A | 5 | 27
ITD0003 |  | ICB |  | HMCPE007C0C | - | 7 | [5 empty] | 1 | 4.8
|  | STR |  | N101CS1*3A | 5 | 27
ITD0004 |  | ICB |  | HMCPE015E0C | - | 15 | [5 empty] | 1.5 | 6.9
|  | STR |  | N101CS1*3A | 5 | 27
ITD0005 | D | ICB | Eaton | HMCPE007C0C | - | 7 | 208 | 3 | 100kA | 208 | 3 | 1/2 | 2.4 | 0.332 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITD0006 |  | ICB |  | HMCPE007C0C | - | 7 | [5 empty] | 3/4 | 3.5
|  | STR |  | N101CS1*3A | 5 | 27
ITD0007 |  | ICB |  | HMCPE007C0C | - | 7 | [5 empty] | 1 | 4.6
|  | STR |  | N101CS1*3A | 5 | 27
ITD0008 |  | ICB |  | HMCPE015E0C | - | 15 | [5 empty] | 1.5 | 6.6
|  | STR |  | N101CS1*3A | 5 | 27
ITD0009 | D | ICB | Eaton | HMCPE007C0C | - | 7 | 240 | 3 | 100kA | 230 | 3 | 1/2 | 2.2 | 0.332 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITD0010 |  | ICB |  | HMCPE007C0C | - | 7 | [5 empty] | 3/4 | 3.2
|  | STR |  | N101CS1*3A | 5 | 27
ITD0011 |  | ICB |  | HMCPE007C0C | - | 7 | [5 empty] | 1 | 4.2
|  | STR |  | N101CS1*3A | 5 | 27
ITD0012 |  | ICB |  | HMCPE015E0C | - | 15 | [5 empty] | 1.5 | 6
|  | STR |  | N101CS1*3A | 5 | 27
ITD0013 | D | ICB | Eaton | HMCPE003A0C | - | 3 | 380 | 3 | 100kA | 380 | 3 | 1/2 | 1.3 | 0.332 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITD0014 |  | ICB |  | HMCPE003A0C | - | 3 | [5 empty] | 3/4 | 1.8
|  | STR |  | N101CS1*3A | 5 | 27
ITD0015 |  | ICB |  | HMCPE007C0C | - | 7 | [5 empty] | 1 | 2.3
|  | STR |  | N101CS1*3A | 5 | 27
ITD0016 |  | ICB |  | HMCPE007C0C | - | 7 | [5 empty] | 1.5 | 3.3
|  | STR |  | N101CS1*3A | 5 | 27
ITD0017 | D | ICB | Eaton | HMCPE003A0C | - | 3 | 480 | 3 | 100kA | 460 | 3 | 1/2 | 1.1 | 0.332 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITD0018 |  | ICB |  | HMCPE003A0C | - | 3 | [5 empty] | 3/4 | 1.6
|  | STR |  | N101CS1*3A | 5 | 27
ITD0019 |  | ICB |  | HMCPE007C0C | - | 7 | [5 empty] | 1 | 2.1
|  | STR |  | N101CS1*3A | 5 | 27
ITD0020 |  | ICB |  | HMCPE007C0C | - | 7 | [5 empty] | 1.5 | 3
|  | STR |  | N101CS1*3A | 5 | 27
ITD0021 |  | ICB |  | HMCPE007C0C | - | 7 | [5 empty] | 2 | 3.4
|  | STR |  | N101CS1*3A | 5 | 27
ITD0022 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
ITD0023 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITD0024 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITD0025 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITD0026 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITD0027 | D | ICB | Eaton | HMCPE015E0C | - | 15 | 200 | 3 | 100kA | 200 | 3 | 1 | 4.8 | 0.332 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITD0028 |  | ICB |  | HMCPE015E0C | - | 15 | [5 empty] | 2 | 7.8
|  | STR |  | N101CS1*3A | 5 | 27
ITD0029 |  | ICB |  | HMCPE015E0C | - | 15 | [5 empty] | 3 | 11
|  | STR |  | N101CS1*3A | 5 | 27
ITD0030 | D | ICB | Eaton | HMCPE015E0C | - | 15 | 208 | 3 | 100kA | 208 | 3 | 1 | 4.6 | 0.332 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITD0031 |  | ICB |  | HMCPE015E0C | - | 15 | [5 empty] | 2 | 7.5
|  | STR |  | N101CS1*3A | 5 | 27
ITD0032 |  | ICB |  | HMCPE030E0C | - | 30 | [5 empty] | 3 | 10.6
|  | STR |  | N101CS1*3A | 5 | 27
ITD0033 | D | ICB | Eaton | HMCPE007C0C | - | 7 | 240 | 3 | 100kA | 240 | 3 | 1 | 4.2 | 0.332 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITD0034 |  | ICB |  | HMCPE015E0C | - | 15 | [5 empty] | 2 | 6.8
|  | STR |  | N101CS1*3A | 5 | 27
ITD0035 |  | ICB |  | HMCPE030E0C | - | 30 | [5 empty] | 3 | 9.6
|  | STR |  | N101CS1*3A | 5 | 27
ITD0036 | D | ICB | Eaton | HMCPE007C0C | - | 7 | 380 | 3 | 100kA | 380 | 3 | 2 | 4.3 | 0.332 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITD0037 |  | ICB |  | HMCPE015E0C | - | 15 | [5 empty] | 3 | 6.1
|  | STR |  | N101CS1*3A | 5 | 27
ITD0038 |  | ICB |  | HMCPE030E0C | - | 30 | [5 empty] | 5 | 9.7
|  | STR |  | N101CS1*3A | 5 | 27
ITD0039 | D | ICB | Eaton | HMCPE003A0C | - | 3 | 480 | 3 | 100kA | 480 | 3 | 2 | 2.1 | 0.332 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITD0040 |  | ICB |  | HMCPE007C0C | - | 7 | [5 empty] | 3 | 4.8
|  | STR |  | N101CS1*3A | 5 | 27
ITD0041 |  | ICB |  | HMCPE015E0C | - | 15 | [5 empty] | 5 | 6.1
|  | STR |  | N101CS1*3A | 5 | 27
ITD0042 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
ITD0043 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITD0044 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITD0045 | D | ICB | Eaton | HMCPE030H1C | - | 30 | 200 | 3 | 100kA | 200 | 3 | 3 | 11 | 0.332 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITD0046 |  | ICB |  | HMCPE030H1C | - | 30 | [5 empty] | 5 | 17.5
|  | STR |  | N101CS1*3A | 5 | 27
ITD0047 |  | ICB |  | HMCPE030H1C | - | 30 | [5 empty] | 7.5 | 25.3
|  | STR |  | N101CS1*3A | 5 | 27
ITD0048 | D | ICB | Eaton | HMCPE030H1C | - | 30 | 208 | 3 | 100kA | 208 | 3 | 3 | 11 | 0.332 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITD0049 |  | ICB |  | HMCPE030H1C | - | 30 | [5 empty] | 5 | 17.5
|  | STR |  | N101CS1*3A | 5 | 27
ITD0050 |  | ICB |  | HMCPE030H1C | - | 30 | [5 empty] | 7.5 | 25.3
|  | STR |  | N101CS1*3A | 5 | 27
ITD0051 | D | ICB | Eaton | HMCPE030H1C | - | 30 | 240 | 3 | 100kA | 230 | 3 | 3 | 9.6 | 0.332 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITD0052 |  | ICB |  | HMCPE030H1C | - | 30 | [5 empty] | 5 | 15.2
|  | STR |  | N101CS1*3A | 5 | 27
ITD0053 |  | ICB |  | HMCPE030H1C | - | 30 | [5 empty] | 7.5 | 22
|  | STR |  | N101CS1*3A | 5 | 27
ITD0054 | D | ICB | Eaton | HMCPE015E0C | - | 15 | 380 | 3 | 100kA | 380 | 3 | 5 | 9.7 | 0.332 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITD0055 |  | ICB |  | HMCPE030H1C | - | 30 | [5 empty] | 7.5 | 14
|  | STR |  | N101CS1*3A | 5 | 27
ITD0056 |  | ICB |  | HMCPE030H1C | - | 30 | [5 empty] | 10 | 18
|  | STR |  | N101CS1*3A | 5 | 27
ITD0057 | D | ICB | Eaton | HMCPE015E0C | - | 15 | 480 | 3 | 100kA | 460 | 3 | 5 | 7.6 | 0.332 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101CS1*3A | 5 | 27
ITD0058 |  | ICB |  | HMCPE030H1C | - | 30 | [5 empty] | 7.5 | 11
|  | STR |  | N101CS1*3A | 5 | 27
ITD0059 |  | ICB |  | HMCPE030H1C | - | 30 | [5 empty] | 10 | 14
|  | STR |  | N101CS1*3A | 5 | 27
ITD0060 | D | - | Eaton | - | - | - | 600 | 3 | - | 575 | 3 | - | - | 0.332 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | - |  | - | - | -
ITD0061 |  | ICB |  | HMCPS030*** | - | 30 |  |  | 50Ka |  |  | 7.5 | 9
|  | STR |  | N101CS1*3A | 5 | 18
ITD0062 |  | ICB |  | HMCPS030*** | - | 30 | [5 empty] | 10 | 11
|  | STR |  | N101CS1*3A | 5 | 18
ITD0063 | D | ICB | Eaton | HMCPE050E0C | - | 50 | 200 | 3 | 100kA | 200 | 3 | 10 | 32.2 | 0.332 | (1) (5) (7c) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101NDS2*3A | 5 | 45
ITD0064 |  | ICB |  | HMCPE050E0C | - | 50 | 208 | 3 | 100kA | 208 | 3 | 10 | 30.8 | 0.332 | (1) (5) (7c) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101NDS2*3A | 5 | 45
ITD0065 |  | ICB |  | HMCPE050E0C | - | 50 | 240 | 3 | 100kA | 240 | 3 | 10 | 28 | 0.332 | (1) (5) (7c) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101NDS2*3A | 5 | 45
ITD0066 |  | ICB |  | HMCPE070M2C | - | 70 | [5 empty] | 15 | 42
|  | STR |  | N101NDS2*3A | 5 | 45
ITD0067 | D | ICB | Eaton | HMCPE050E0C | - | 50 | 380 | 3 | 100kA | 380 | 3 | 15 | 27 | 0.332 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101NDS2*3A | 5 | 45
ITD0068 |  | ICB |  | HMCPE050E0C | - | 50 | [5 empty] | 20 | 34 |  | (1) (5) (7c)
|  | STR |  | N101NDS2*3A | 5 | 45
ITD0069 |  | ICB |  | HMCPE070M2C | - | 70 | [5 empty] | 25 | 44
|  | STR |  | N101NDS2*3A | 5 | 45
ITD0070 | D | ICB | Eaton | HMCPE050E0C | - | 50 | 480 | 3 | 100kA | 460 | 3 | 15 | 21 | 0.332 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101NDS2*3A | 5 | 45
ITD0071 |  | ICB |  | HMCPE050E0C | - | 50 | [5 empty] | 20 | 27
|  | STR |  | N101NDS2*3A | 5 | 45
ITD0072 |  | ICB |  | HMCPE050E0C | - | 50 | [5 empty] | 25 | 34 |  | (1) (5) (7c)
|  | STR |  | N101NDS2*3A | 5 | 45
ITD0073 | D | - | Eaton | - | - | - | 600 | 3 | - | 460 | 3 | - | - | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | - |  | - | - | -
ITD0074 |  | ICB |  | HMCPS050*** | - | 50 |  |  | 50kA |  |  | 20 | 22
|  | STR |  | N101NDS2*3A | 5 | 45
ITD0075 |  | ICB |  | HMCPS050*** | - | 50 | [5 empty] | 25 | 27
|  | STR |  | N101NDS2*3A | 5 | 45
ITD0076 | D | ICB | Eaton | HMCPE100R3C | - | 100 | 200 | 3 | 100kA | 200 | 3 | 15 | 48.3 | 0.695 | (1) (5) (7e) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES3*3A | 5 | 90
ITD0077 |  | ICB |  | HMCPE100R3C | - | 100 | [5 empty] | 20 | 62.1
|  | STR |  | N101ES3*3A | 5 | 90
ITD0078 |  | ICB |  | HMCPE100T3C | - | 100 | [5 empty] | 25 | 78.4
|  | STR |  | N101ES3*3A | 5 | 90
ITD0079 | D | ICB | Eaton | HMCPE070M2C | - | 70 | 208 | 3 | 100kA | 208 | 3 | 15 | 46.2 | 0.695 | (1) (5) (7e) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES3*3A | 5 | 90
ITD0080 |  | ICB |  | HMCPE100R3C | - | 100 | [5 empty] | 20 | 59.4
|  | STR |  | N101ES3*3A | 5 | 90
ITD0081 |  | ICB |  | HMCPE100T3C | - | 100 | [5 empty] | 25 | 74.8
|  | STR |  | N101ES3*3A | 5 | 90
ITD0082 | D | ICB | Eaton | HMCPE100R3C | - | 100 | 240 | 3 | 100kA | 230 | 3 | 20 | 54 | 0.695 | (1) (5) (7e) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES3*3A | 5 | 90
ITD0083 |  | ICB |  | HMCPE100R3C | - | 100 | [5 empty] | 25 | 68
|  | STR |  | N101ES3*3A | 5 | 90
ITD0084 |  | ICB |  | HMCPE100T3C | - | 100 | [5 empty] | 30 | 80
|  | STR |  | N101ES3*3A | 5 | 90
ITD0085 | D | ICB | Eaton | HMCPE070M2C | - | 70 | 380 | 3 | 100kA | 380 | 3 | 30 | 51 | 0.695 | (1) (5) (7e) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES3*3A | 5 | 90
ITD0086 |  | ICB |  | HMCPE100R3C | - | 100 | [5 empty] | 40 | 66
|  | STR |  | N101ES3*3A | 5 | 90
ITD0087 |  | ICB |  | HMCPE100T3C | - | 100 | [5 empty] | 50 | 83
|  | STR |  | N101ES3*3A | 5 | 90
ITD0088 | D | ICB | Eaton | HMCPE100R3C | - | 100 | 480 | 3 | 100kA | 460 | 3 | 30 | 40 | 0.695 | (1) (5) (7c) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES3*3A | 5 | 90
ITD0089 |  | ICB |  | HMCPE100R3C | - | 100 | [5 empty] | 40 | 52 |  | (1) (5) (7e)
|  | STR |  | N101ES3*3A | 5 | 90
ITD0090 |  | ICB |  | HMCPE100R3C | - | 100 | [5 empty] | 50 | 65
|  | STR |  | N101ES3*3A | 5 | 90
ITD0091 | D | - | Eaton | - | - | - | 600 | 3 | - | 575 | 3 | - | - | 0.695 | - | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | - |  | - | - | -
ITD0092 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITD0093 |  | - |  | - | - | - | [5 empty] | 50 | 52 |  | (1) (5) (7e)
|  | - |  | - | - | -
ITD0094 |  | ICB |  | HMCP150*** | - | 150 |  |  | 50Ka
|  | STR |  | N101ES3*3A | 5 | 90
ITD0095 | D | ICB | Eaton | HMCPJ250W5L | - | 250 | 200 | 3 | 100kA | 200 | 3 | 30 | 92 | 0.695 | (1) (5) (7f) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES4*3A | 10 | 135
ITD0096 |  | ICB |  | HMCPJ250W5L | - | 250 | [5 empty] | 40 | 120
|  | STR |  | N101ES4*3A | 10 | 135
ITD0097 | D | ICB | Eaton | HMCPJ250G5L | - | 250 | 208 | 3 | 100kA | 208 | 3 | 30 | 88 | 0.695 | (1) (5) (7f) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES4*3A | 10 | 135
ITD0098 |  | ICB |  | HMCPJ250K5L | - | 250 | [5 empty] | 40 | 114
|  | STR |  | N101ES4*3A | 10 | 135
ITD0099 | D | ICB | Eaton | HMCPJ250J5L | - | 250 | 240 | 3 | 100kA | 230 | 3 | 40 | 104 | 0.695 | (1) (5) (7f) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES4*3A | 10 | 135
ITD0100 |  | ICB |  | HMCPJ250L5L | - | 250 | [5 empty] | 50 | 130
|  | STR |  | N101ES4*3A | 10 | 135
ITD0101 | D | ICB | Eaton | HMCPJ250J5L | - | 250 | 380 | 3 | 100kA | 380 | 3 | 60 | 103 | 0.695 | (1) (5) (7f) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES4*3A | 10 | 135
ITD0102 |  | ICB |  | HMCPJ250K5L | - | 250 | [5 empty] | 75 | 128
|  | STR |  | N101ES4*3A | 10 | 135
ITD0103 | D | ICB | Eaton | HMCPJ250F5L | - | 250 | 480 | 3 | 100kA | 480 | 3 | 60 | 77 | 0.695 | (1) (5) (7e) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101ES4*3A | 10 | 135
ITD0104 |  | ICB |  | HMCPJ250J5L | - | 250 | [5 empty] | 75 | 96 |  | (1) (5) (7f)
|  | STR |  | N101ES4*3A | 10 | 135
ITD0105 |  | ICB |  | HMCPJ250K5L | - | 250 | [5 empty] | 100 | 124
|  | ICB |  | N101ES4*3A | 10 | 135
ITD0106 | D | - | Eaton | - | - | - | 600 | 3 | - | 575 | 3 | - | - | 0.695 | - | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | - |  | - | - | -
ITD0107 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITD0108 |  | - |  | - | - | - | [5 empty] | 100 | 99 |  | (1) (5) (7f)
|  | - |  | - | - | -
ITD0109 |  | ICB |  | HMCP150*** | - | 150 |  |  | 50kA
|  | STR |  | N101ES4*3A | 10 | 135
ITD0110 | D | ICB | Eaton | HMCPJ250W5L | - | 250 | 200 | 3 | 100kA | 200 | 3 | 50 | 150 | 1.78 | (1) (50 (7j) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101FS5*3A | 10 | 270
ITD0111 |  | ICB |  | HMCP400X5C | - | 400 | [5 empty] | 60 | 177
|  | STR |  | N101FS5*3A | 10 | 270
ITD0112 |  | ICB |  | HMCP400X5C | - | 400 | [5 empty] | 75 | 221
|  | ICB |  | N101FS5*3A | 10 | 270
ITD0113 | D | ICB | Eaton | HMCPJ250W5L | - | 250 | 208 | 3 | 100kA | 208 | 3 | 50 | 143 | 1.78 | (1) (50 (7j) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101FS5*3A | 10 | 270
ITD0114 |  | ICB |  | HMCP400X5C | - | 400 | [5 empty] | 60 | 169
|  | STR |  | N101FS5*3A | 10 | 270
ITD0115 |  | ICB |  | HMCP400X5C | - | 400 | [5 empty] | 75 | 211
|  | ICB |  | N101FS5*3A | 10 | 270
ITD0116 | D | ICB | Eaton | HMCPJ250W5L | - | 250 | 240 | 3 | 100kA | 230 | 3 | 60 | 154 | 1.78 | (1) (50 (7j) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101FS5*3A | 10 | 270
ITD0117 |  | ICB |  | HMCP400X5C | - | 400 | [5 empty] | 75 | 192
|  | STR |  | N101FS5*3A | 10 | 270
ITD0118 |  | ICB |  | HMCP600L6W | - | 600 | [5 empty] | 100 | 248
|  | ICB |  | N101FS5*3A | 10 | 270
ITD0119 | D | ICB | Eaton | HMCP400X5C | - | 400 | 380 | 3 | 100kA | 380 | 3 | 100 | 165 | 1.78 | (1) (50 (7j) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101FS5*3A | 10 | 270
ITD0120 |  | ICB |  | HMCP400X5C | - | 400 | [5 empty] | 125 | 208
|  | STR |  | N101FS5*3A | 10 | 270
ITD0121 |  | ICB |  | HMCP400X5C | - | 400 | [5 empty] | 150 | 240
|  | ICB |  | N101FS5*3A | 10 | 270
ITD0122 | D | ICB | Eaton | HMCPJ250W5L | - | 250 | 480 | 3 | 100kA | 460 | 3 | 125 | 156 | 1.78 | (1) (50 (7j) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101FS5*3A | 10 | 270
ITD0123 |  | ICB |  | HMCP400X5C | - | 400 | [5 empty] | 150 | 180
|  | STR |  | N101FS5*3A | 10 | 270
ITD0124 |  | ICB |  | HMCP400X5C | - | 400 | [5 empty] | 200 | 240
|  | ICB |  | N101FS5*3A | 10 | 270
ITD0125 | D | ICB | Eaton | HMCPJ250K5L | - | 250 | 600 | 3 | 50kA | 575 | 3 | 125 | 125 | 1.78 | (1) (5) (7f) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N101FS5*3A | 10 | 270
ITD0126 |  | ICB |  | HMCPJ250W5L | - | 250 | [5 empty] | 150 | 144 |  | (1) (5) (7f)
|  | STR |  | N101FS5*3A | 10 | 270
ITD0127 |  | ICB |  | HMCP400X5C | - | 400 | [5 empty] | 200 | 192
|  | ICB |  | N101FS5*3A | 10 | 270
ITD0128 | D | ICB | Eaton | HMCPE007C0C | - | 7 | 200 | 3 | 100kA | 200 | 3 | 1/2 | 2.5 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITD0129 |  | ICB |  | HMCPE007C0C | - | 7 | [5 empty] | 3/4 | 3.7
|  | STR |  | N501CS1*3A | 5 | 27
ITD0130 |  | ICB |  | HMCPE007C0C | - | 7 | [5 empty] | 1 | 4.8
|  | STR |  | N501CS1*3A | 5 | 27
ITD0131 |  | ICB |  | HMCPE015E0C | - | 15 | [5 empty] | 1.5 | 6.9
|  | STR |  | N501CS1*3A | 5 | 27
ITD0132 | D | ICB | Eaton | HMCPE007C0C | - | 7 | 208 | 3 | 100kA | 208 | 3 | 1/2 | 2.4 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITD0133 |  | ICB |  | HMCPE007C0C | - | 7 | [5 empty] | 3/4 | 3.5
|  | STR |  | N501CS1*3A | 5 | 27
ITD0134 |  | ICB |  | HMCPE007C0C | - | 7 | [5 empty] | 1 | 4.6
|  | STR |  | N501CS1*3A | 5 | 27
ITD0135 |  | ICB |  | HMCPE015E0C | - | 15 | [5 empty] | 1.5 | 6.6
|  | STR |  | N501CS1*3A | 5 | 27
ITD0136 | D | ICB | Eaton | HMCPE007C0C | - | 7 | 240 | 3 | 100kA | 230 | 3 | 1/2 | 2.2 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITD0137 |  | ICB |  | HMCPE007C0C | - | 7 | [5 empty] | 3/4 | 3.2
|  | STR |  | N501CS1*3A | 5 | 27
ITD0138 |  | ICB |  | HMCPE007C0C | - | 7 | [5 empty] | 1 | 4.2
|  | STR |  | N501CS1*3A | 5 | 27
ITD0139 |  | ICB |  | HMCPE015E0C | - | 15 | [5 empty] | 1.5 | 6
|  | STR |  | N501CS1*3A | 5 | 27
ITD0140 | D | ICB | Eaton | HMCPE003A0C | - | 3 | 380 | 3 | 100kA | 380 | 3 | 1/2 | 1.3 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITD0141 |  | ICB |  | HMCPE003A0C | - | 3 | [5 empty] | 3/4 | 1.8
|  | STR |  | N501CS1*3A | 5 | 27
ITD0142 |  | ICB |  | HMCPE007C0C | - | 7 | [5 empty] | 1 | 2.3
|  | STR |  | N501CS1*3A | 5 | 27
ITD0143 |  | ICB |  | HMCPE007C0C | - | 7 | [5 empty] | 1.5 | 3.3
|  | STR |  | N501CS1*3A | 5 | 27
ITD0144 | D | ICB | Eaton | HMCPE003A0C | - | 3 | 480 | 3 | 100kA | 460 | 3 | 1/2 | 1.1 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITD0145 |  | ICB |  | HMCPE003A0C | - | 3 | [5 empty] | 3/4 | 1.6
|  | STR |  | N501CS1*3A | 5 | 27
ITD0146 |  | ICB |  | HMCPE007C0C | - | 7 | [5 empty] | 1 | 2.1
|  | STR |  | N501CS1*3A | 5 | 27
ITD0147 |  | ICB |  | HMCPE007C0C | - | 7 | [5 empty] | 1.5 | 3
|  | STR |  | N501CS1*3A | 5 | 27
ITD0148 |  | ICB |  | HMCPE007C0C | - | 7 | [5 empty] | 2 | 3.4
|  | STR |  | N501CS1*3A | 5 | 27
ITD0149 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
ITD0150 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITD0151 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITD0152 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITD0153 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITD0154 | D | ICB | Eaton | HMCPE015E0C | - | 15 | 200 | 3 | 100kA | 200 | 3 | 1 | 4.8 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITD0155 |  | ICB |  | HMCPE015E0C | - | 17 | [5 empty] | 2 | 7.8
|  | STR |  | N501CS1*3A | 5 | 27
ITD0156 |  | ICB |  | HMCPE015E0C | - | 15 | [5 empty] | 3 | 11
|  | STR |  | N501CS1*3A | 5 | 27
ITD0157 | D | ICB | Eaton | HMCPE015E0C | - | 15 | 208 | 3 | 100kA | 208 | 3 | 1 | 4.6 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITD0158 |  | ICB |  | HMCPE015E0C | - | 15 | [5 empty] | 2 | 7.5
|  | STR |  | N501CS1*3A | 5 | 27
ITD0159 |  | ICB |  | HMCPE015E0C | - | 30 | [5 empty] | 3 | 10.6
|  | STR |  | N501CS1*3A | 5 | 27
ITD0160 | D | ICB | Eaton | HMCPE007C0C | - | 7 | 240 | 3 | 100kA | 240 | 3 | 1 | 4.2 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITD0161 |  | ICB |  | HMCPE015E0C | - | 15 | [5 empty] | 2 | 6.8
|  | STR |  | N501CS1*3A | 5 | 27
ITD0162 |  | ICB |  | HMCPE015E0C | - | 30 | [5 empty] | 3 | 9.6
|  | STR |  | N501CS1*3A | 5 | 27
ITD0163 | D | ICB | Eaton | HMCPE007C0C | - | 7 | 380 | 3 | 100kA | 380 | 3 | 2 | 4.3 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITD0164 |  | ICB |  | HMCPE015E0C | - | 15 | [5 empty] | 3 | 6.1
|  | STR |  | N501CS1*3A | 5 | 18
ITD0165 |  | ICB |  | HMCPE015E0C | - | 30 | [5 empty] | 5 | 9.7
|  | STR |  | N501CS1*3A | 5 | 27
ITD0166 | D | ICB | Eaton | HMCPE003A0C | - | 3 | 480 | 3 | 100kA | 480 | 3 | 2 | 2.1 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITD0167 |  | ICB |  | HMCPE007C0C | - | 7 | [5 empty] | 3 | 4.8
|  | STR |  | N501CS1*3A | 5 | 18
ITD0168 |  | ICB |  | HMCPE015E0C | - | 15 | [5 empty] | 5 | 6.1
|  | STR |  | N501CS1*3A | 5 | 27
ITD0169 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
ITD0170 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITD0171 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITD0172 | D | ICB | Eaton | HMCPE030H1C | - | 30 | 200 | 3 | 100kA | 200 | 3 | 3 | 11 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITD0173 |  | ICB |  | HMCPE030H1C | - | 30 | [5 empty] | 5 | 17.5
|  | STR |  | N501CS1*3A | 5 | 27
ITD0174 |  | ICB |  | HMCPE030H1C | - | 30 | [5 empty] | 7.5 | 25.3
|  | STR |  | N501CS1*3A | 5 | 27
ITD0175 | D | ICB | Eaton | HMCPE030H1C | - | 30 | 208 | 3 | 100kA | 208 | 3 | 3 | 11 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITD0176 |  | ICB |  | HMCPE030H1C | - | 30 | [5 empty] | 5 | 17.5
|  | STR |  | N501CS1*3A | 5 | 27
ITD0177 |  | ICB |  | HMCPE030H1C | - | 30 | [5 empty] | 7.5 | 25.3
|  | STR |  | N501CS1*3A | 5 | 27
ITD0178 | D | ICB | Eaton | HMCPE030H1C | - | 30 | 240 | 3 | 100kA | 230 | 3 | 3 | 9.6 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITD0179 |  | ICB |  | HMCPE030H1C | - | 30 | [5 empty] | 5 | 15.2
|  | STR |  | N501CS1*3A | 5 | 27
ITD0180 |  | ICB |  | HMCPE030H1C | - | 30 | [5 empty] | 7.5 | 22
|  | STR |  | N501CS1*3A | 5 | 27
ITD0181 | D | ICB | Eaton | HMCPE015E0C | - | 15 | 380 | 3 | 100kA | 380 | 3 | 5 | 9.7 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITD0182 |  | ICB |  | HMCPE030H1C | - | 30 | [5 empty] | 7.5 | 14
|  | STR |  | N501CS1*3A | 5 | 27
ITD0183 |  | ICB |  | HMCPE030H1C | - | 30 | [5 empty] | 10 | 18
|  | STR |  | N501CS1*3A | 5 | 27
ITD0184 | D | ICB | Eaton | HMCPE015E0C | - | 15 | 480 | 3 | 100kA | 460 | 3 | 5 | 7.6 | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501CS1*3A | 5 | 27
ITD0185 |  | ICB |  | HMCPE030H1C | - | 30 | [5 empty] | 7.5 | 11
|  | STR |  | N501CS1*3A | 5 | 27
ITD0186 |  | ICB |  | HMCPE030H1C | - | 30 | [5 empty] | 10 | 14
|  | STR |  | N501CS1*3A | 5 | 27
ITD0187 | D | - | Eaton | - | - | - | 600 | 3 | - | 575 | 3 | - | - | 0.695 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | - |  | - | - | -
ITD0188 |  | ICB |  | HMCPE030H1C | - | 30 |  |  | 50KA |  |  | 7.5 | 9
|  | STR |  | N501CS1*3A | 5 | 18
ITD0189 |  | ICB |  | HMCPE030H1C | - | 30 | [5 empty] | 10 | 11
|  | STR |  | N501CS1*3A | 5 | 18
ITD0190 | D | ICB | Eaton | HMCPE050E0C | - | 50 | 200 | 3 | 100kA | 200 | 3 | 10 | 32.2 | 1.05 | (1) (5) (7c) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501NDS2*3A | 5 | 45
ITD0191 |  | ICB |  | HMCPE050E0C | - | 50 | 208 | 3 | 100kA | 208 | 3 | 10 | 30.8 | 1.05 | (1) (5) (7c) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501NDS2*3A | 5 | 45
ITD0192 |  | ICB |  | HMCPE050E0C | - | 50 | 240 | 3 | 100kA | 240 | 3 | 10 | 28 | 1.05 | (1) (5) (7c) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501NDS2*3A | 5 | 45
ITD0193 |  | ICB |  | HMCPE070M2C | - | 70 | [5 empty] | 15 | 42
|  | STR |  | N501NDS2*3A | 5 | 45
ITD0194 | D | ICB | Eaton | HMCPE050E0C | - | 50 | 380 | 3 | 100kA | 380 | 3 | 15 | 27 | 1.05 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501NDS2*3A | 5 | 45
ITD0195 |  | ICB |  | HMCPE050E0C | - | 50 | [5 empty] | 20 | 34 |  | (1) (5) (7c)
|  | STR |  | N501NDS2*3A | 5 | 45
ITD0196 |  | ICB |  | HMCPE070M2C | - | 70 | [5 empty] | 25 | 44
|  | STR |  | N501NDS2*3A | 5 | 45
ITD0197 | D | ICB | Eaton | HMCPE050E0C | - | 50 | 480 | 3 | 100kA | 460 | 3 | 15 | 21 | 1.05 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501NDS2*3A | 5 | 45
ITD0198 |  | ICB |  | HMCPE050E0C | - | 50 | [5 empty] | 20 | 27
|  | STR |  | N501NDS2*3A | 5 | 45
ITD0199 |  | ICB |  | HMCPE050E0C | - | 50 | [5 empty] | 25 | 34 |  | (1) (5) (7c)
|  | STR |  | N501NDS2*3A | 5 | 45
ITD0200 | D | - | Eaton | - | - | - | 600 | 3 | - | 460 | 3 | - | - | 1.05 | (1) (5) (7a) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | - |  | - | - | -
ITD0201 |  | ICB |  | HMCPS050*** | - | 50 |  |  | 50Ka |  |  | 20 | 22
|  | STR |  | N501NDS2*3A | 5 | 45
ITD0202 |  | ICB |  | HMCPS050*** | - | 50 | [5 empty] | 25 | 27
|  | STR |  | N501NDS2*3A | 5 | 45
ITD0203 | D | ICB | Eaton | HMCPE100R3C | - | 100 | 200 | 3 | 100kA | 200 | 3 | 15 | 48.3 | 1.05 | (1) (5) (7e) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES3*3A | 5 | 90
ITD0204 |  | ICB |  | HMCPE100R3C | - | 100 | [5 empty] | 20 | 62.1
|  | STR |  | N501ES3*3A | 5 | 90
ITD0205 |  | ICB |  | HMCPE100T3C | - | 100 | [5 empty] | 25 | 78.4
|  | STR |  | N501ES3*3A | 5 | 90
ITD0206 | D | ICB | Eaton | HMCPE070M2C | - | 70 | 208 | 3 | 100kA | 208 | 3 | 15 | 46.2 | 1.05 | (1) (5) (7e) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES3*3A | 5 | 90
ITD0207 |  | ICB |  | HMCPE100R3C | - | 100 | [5 empty] | 20 | 59.4
|  | STR |  | N501ES3*3A | 5 | 90
ITD0208 |  | ICB |  | HMCPE100T3C | - | 100 | [5 empty] | 25 | 74.8
|  | STR |  | N501ES3*3A | 5 | 90
ITD0209 | D | ICB | Eaton | HMCPE100R3C | - | 100 | 240 | 3 | 100kA | 230 | 3 | 20 | 54 | 1.05 | (1) (5) (7e) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES3*3A | 5 | 90
ITD0210 |  | ICB |  | HMCPE100R3C | - | 100 | [5 empty] | 25 | 68
|  | STR |  | N501ES3*3A | 5 | 90
ITD0211 |  | ICB |  | HMCPE100T3C | - | 100 | [5 empty] | 30 | 80
|  | STR |  | N501ES3*3A | 5 | 90
ITD0212 | D | ICB | Eaton | HMCPE070M2C | - | 70 | 380 | 3 | 100kA | 380 | 3 | 30 | 51 | 1.05 | (1) (5) (7e) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES3*3A | 5 | 90
ITD0213 |  | ICB |  | HMCPE100R3C | - | 100 | [5 empty] | 40 | 66
|  | STR |  | N501ES3*3A | 5 | 90
ITD0214 |  | ICB |  | HMCPE100T3C | - | 100 | [5 empty] | 50 | 83
|  | STR |  | N501ES3*3A | 5 | 90
ITD0215 | D | ICB | Eaton | HMCPE100R3C | - | 100 | 480 | 3 | 100kA | 460 | 3 | 30 | 32 | 1.05 | (1) (5) (7c) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES3*3A | 5 | 90
ITD0216 |  | ICB |  | HMCPE100R3C | - | 100 | [5 empty] | 40 | 41
|  | STR |  | N501ES3*3A | 5 | 90
ITD0217 |  | ICB |  | HMCPE100R3C | - | 100 | [5 empty] | 50 | 52 |  | (1) (5) (7e)
|  | STR |  | N501ES3*3A | 5 | 90
ITD0218 | D | - | Eaton | - | - | - | 600 | 3 | - | 575 | 3 | - | - | 1.05 | - | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | - |  | - | - | -
ITD0219 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITD0220 |  | - |  | - | - | - | [5 empty] | 50 | 52 |  | (1) (5) (7e)
|  | - |  | - | - | -
ITD0221 |  | ICB |  | HMCP150*** |  | 150 |  |  | 50Ka
|  | STR |  | N501ES3*3A | 5 | 90
ITD0222 | D | ICB | Eaton | HMCPJ250W5L | - | 250 | 200 | 3 | 100kA | 200 | 3 | 30 | 92 | 1.05 | (1) (5) (7f) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES4*3A | 10 | 135
ITD0223 |  | ICB |  | HMCPJ250W5L | - | 250 | [5 empty] | 40 | 120
|  | STR |  | N501ES4*3A | 10 | 135
ITD0224 | D | ICB | Eaton | HMCPJ250G5L | - | 250 | 208 | 3 | 100kA | 208 | 3 | 30 | 88 | 1.05 | (1) (5) (7f) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES4*3A | 10 | 135
ITD0225 |  | ICB |  | HMCPJ250K5L | - | 250 | [5 empty] | 40 | 114
|  | STR |  | N501ES4*3A | 10 | 135
ITD0226 | D | ICB | Eaton | HMCPJ250J5L | - | 250 | 240 | 3 | 100kA | 230 | 3 | 40 | 104 | 1.05 | (1) (5) (7f) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES4*3A | 10 | 135
ITD0227 |  | ICB |  | HMCPJ250L5L | - | 250 | [5 empty] | 50 | 130
|  | STR |  | N501ES4*3A | 10 | 135
ITD0228 | D | ICB | Eaton | HMCPJ250J5L | - | 250 | 380 | 3 | 100kA | 380 | 3 | 60 | 103 | 1.05 | (1) (5) (7f) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES4*3A | 10 | 135
ITD0229 |  | ICB |  | HMCPJ250K5L | - | 250 | [5 empty] | 75 | 128
|  | STR |  | N501ES4*3A | 10 | 135
ITD0230 | D | ICB | Eaton | HMCPJ250F5L | - | 250 | 480 | 3 | 100kA | 480 | 3 | 60 | 77 | 1.05 | (1) (5) (7e) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501ES4*3A | 10 | 135
ITD0231 |  | ICB |  | HMCPJ250J5L | - | 250 | [5 empty] | 75 | 96 |  | (1) (5) (7f)
|  | STR |  | N501ES4*3A | 10 | 135
ITD0232 |  | ICB |  | HMCPJ250K5L | - | 250 | [5 empty] | 100 | 124
|  | ICB |  | N501ES4*3A | 10 | 135
ITD0233 | D | - | Eaton | - | - | - | 600 | 3 | - | 575 | 3 | - | - | 1.05 | - | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | - |  | - | - | -
ITD0234 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
ITD0235 |  | - |  | - | - | - | [5 empty] | 100 | 99 |  | (1) (5) (7f)
|  | - |  | - | - | -
ITD0236 |  | ICB |  | HMCP150*** | - | 150 |  |  | 50KA
|  | STR |  | N501ES4*3A | 10 | 135
ITD0237 | D | ICB | Eaton | HMCPJ250W5L | - | 250 | 200 | 3 | 100kA | 200 | 3 | 50 | 150 | 2.5 | (1) (5) (7j) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501FS5*3A | 10 | 270
ITD0238 |  | ICB |  | HMCP400X5C | - | 400 | [5 empty] | 60 | 177
|  | STR |  | N501FS5*3A | 10 | 270
ITD0239 |  | ICB |  | HMCP400X5C | - | 400 | [5 empty] | 75 | 221
|  | ICB |  | N501FS5*3A | 10 | 270
ITD0240 | D | ICB | Eaton | HMCPJ250W5L | - | 250 | 208 | 3 | 100kA | 208 | 3 | 50 | 143 | 2.5 | (1) (5) (7j) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501FS5*3A | 10 | 270
ITD0241 |  | ICB |  | HMCP400X5C | - | 400 | [5 empty] | 60 | 169
|  | STR |  | N501FS5*3A | 10 | 270
ITD0242 |  | ICB |  | HMCP400X5C | - | 400 | [5 empty] | 75 | 211
|  | ICB |  | N501FS5*3A | 10 | 270
ITD0243 | D | ICB | Eaton | HMCPJ250W5L | - | 250 | 240 | 3 | 100kA | 230 | 3 | 60 | 154 | 2.5 | (1) (5) (7j) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501FS5*3A | 10 | 270
ITD0244 |  | ICB |  | HMCP400X5C | - | 400 | [5 empty] | 75 | 192
|  | STR |  | N501FS5*3A | 10 | 270
ITD0245 |  | ICB |  | HMCP600L6W | - | 600 | [5 empty] | 100 | 248
|  | ICB |  | N501FS5*3A | 10 | 270
ITD0246 | D | ICB | Eaton | HMCP400X5C | - | 400 | 380 | 3 | 100kA | 380 | 3 | 100 | 165 | 2.5 | (1) (5) (7j) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501FS5*3A | 10 | 270
ITD0247 |  | ICB |  | HMCP400X5C | - | 400 | [5 empty] | 125 | 208
|  | STR |  | N501FS5*3A | 10 | 270
ITD0248 |  | ICB |  | HMCP400X5C | - | 400 | [5 empty] | 150 | 240
|  | ICB |  | N501FS5*3A | 10 | 270
ITD0249 | D | ICB | Eaton | HMCPJ250W5L | - | 250 | 480 | 3 | 100kA | 460 | 3 | 125 | 156 | 2.5 | (1) (5) (7j) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501FS5*3A | 10 | 270
ITD0250 |  | ICB |  | HMCP400X5C | - | 400 | [5 empty] | 150 | 180
|  | STR |  | N501FS5*3A | 10 | 270
ITD0251 |  | ICB |  | HMCP400X5C | - | 400 | [5 empty] | 200 | 240
|  | ICB |  | N501FS5*3A | 10 | 270
ITD0252 | D | ICB | Eaton | HMCPJ250K5L | - | 250 | 600 | 3 | 50kA | 575 | 3 | 125 | 125 | 2.5 | (1) (5) (7f) | E176513 Vol. 1 Sec. 3 | E47048 Vol. 2 Sec. 2
|  | STR |  | N501FS5*3A | 10 | 270
ITD0253 |  | ICB |  | HMCPJ250W5L | - | 250 | [5 empty] | 150 | 144 |  | (1) (5) (7j)
|  | STR |  | N501FS5*3A | 10 | 270
ITD0254 |  | ICB |  | HMCP400X5C | - | 400 | [5 empty] | 200 | 192
|  | ICB |  | N501FS5*3A | 10 | 270
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = Additional Conditions of Acceptability may be specified in the individual Tables.
(7) See table (7) for internal wiring between load side of short circuit protective device & line side of starter.
Table 7 - Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
| Wire Code | Wire Size | Wire Code | Wire Size
| 7a | 12 awg. | 7j | 4/0 awg.
| 7b | 10 awg. | 7k | 250kcml
| 7c | 8 awg. | 7l | 350kcml
| 7d | 6 awg. | 7m | 4/0 awg. (3)
| 7e | 4 awg. | 7n | 4/0 awg. (4)
| 7f | 2 awg. | 7p | 250kcml (2)
| 7g | 1/0 awg. | 7r | 350kcml (3)
| 7h | 2/0 awg. | 7s | 4/0 awg. (2)

## Vacuum Type C
Issued: 2006-05-18
Last Revised: 2006-05-18
Combination Motor Controllers for use in Industrial Control Panels
ID Number | Combination Type | Individual Component | [6 empty] | Combination SCCR | [5 empty] | Conditions of Acceptability | Combination Starter UL File | Motor Control Center UL File
|  | Component Type | Manufacturer | Partial Catalog No. | Ratings |  |  |  | SCCR kA | Volts | Phase | Hp | NEC FLC | Min. Enclosure Volume (cu. ft.)
[5 empty] | SCCR kA | Max. Amps | Volts | No. Poles
VCC001 | C | CB | Eaton | JGH3125FAG | 100 | 125 | 200 | 3 | 65 | 200 | 3 | 25 | 78.2 | 1.42 | (1) (3) (7f) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M4C*** | 10 | 135
VCC002 |  | CB |  | JGH3150FAG | 100 | 150 | [5 empty] | 30 | 92
|  | STR |  | V200M4C*** | 10 | 135
VCC003 |  | CB |  | JGH3175FAG | 100 | 175 | [5 empty] | 40 | 120
|  | STR |  | V200M4C*** | 10 | 135
VCC004 | C | CB | Eaton | JGH3125FAG | 100 | 125 | 230 | 3 | 65 | 230 | 3 | 25 | 68 | 1.42 | (1) (3) (7f) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M4C*** | 10 | 135
VCC005 |  | CB |  | JGH3125FAG | 100 | 125 | [5 empty] | 30 | 80
|  | STR |  | V200M4C*** | 10 | 135
VCC006 |  | CB |  | JGH3150FAG | 100 | 150 | [5 empty] | 40 | 104
|  | STR |  | V200M4C*** | 10 | 135
VCC007 | C | CB | Eaton | JGH3100FAG | 65 | 100 | 460 | 3 | 65 | 460 | 3 | 50 | 65 | 1.42 | (1) (3) (7f) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M4C*** | 10 | 135
VCC008 |  | CB |  | JGH3125FAG | 65 | 125 | [5 empty] | 60 | 77
|  | STR |  | V200M4C*** | 10 | 135
VCC009 |  | CB |  | JGH3150FAG | 65 | 150 | [5 empty] | 75 | 96
|  | STR |  | V200M4C*** | 10 | 135
VCC010 | C | CB | Eaton | JGH3100FAG | 35 | 100 | 575 | 3 | 25 | 575 | 3 | 60 | 62 | 1.42 | (1) (3) (7f) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M4C*** | 10 | 135
VCC011 |  | CB |  | JGH3125FAG | 35 | 125 | [5 empty] | 75 | 77
|  | STR |  | V200M4C*** | 10 | 135
VCC012 |  | CB |  | JGH3150FAG | 35 | 150 | [5 empty] | 100 | 99
|  | STR |  | V200M4C*** | 10 | 135
VCC013 | C | CB | Eaton | JDC3125 | 200 | 125 | 200 | 3 | 100 | 200 | 3 | 25 | 78.2 | 1.42 | (1) (3) (7f) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M4C*** | 10 | 135
VCC014 |  | CB |  | JDC3150 | 200 | 150 | [5 empty] | 30 | 92
|  | STR |  | V200M4C*** | 10 | 135
VCC015 |  | CB |  | JDC3175 | 200 | 175 | [5 empty] | 40 | 120
|  | STR |  | V200M4C*** | 10 | 135
VCC016 | C | CB | Eaton | JDC3125 | 200 | 125 | 230 | 3 | 100 | 230 | 3 | 25 | 68 | 1.42 | (1) (3) (7f) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M4C*** | 10 | 135
VCC017 |  | CB |  | JDC3125 | 200 | 125 | [5 empty] | 30 | 80
|  | STR |  | V200M4C*** | 10 | 135
VCC018 |  | CB |  | JDC3150 | 200 | 150 | [5 empty] | 40 | 104
|  | STR |  | V200M4C*** | 10 | 135
VCC019 | C | CB | Eaton | JDC3100 | 100 | 100 | 460 | 3 | 100 | 460 | 3 | 50 | 65 | 1.42 | (1) (3) (7f) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M4C*** | 10 | 135
VCC020 |  | CB |  | JDC3125 | 100 | 125 | [5 empty] | 60 | 77
|  | STR |  | V200M4C*** | 10 | 135
VCC021 |  | CB |  | JDC3150 | 100 | 150 | [5 empty] | 75 | 96
|  | STR |  | V200M4C*** | 10 | 135
VCC022 | C | CB | Eaton | HJD3125 | 100 | 125 | 200 | 3 | 65 | 200 | 3 | 25 | 78.2 | 1.42 | (1) (3) (7f) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M4C*** | 10 | 135
VCC023 |  | CB |  | HJD3150 | 100 | 150 | [5 empty] | 30 | 92
|  | STR |  | V200M4C*** | 10 | 135
VCC024 |  | CB |  | HJD3175 | 100 | 175 | [5 empty] | 40 | 120
|  | STR |  | V200M4C*** | 10 | 135
VCC025 | C | CB | Eaton | HJD3125 | 100 | 125 | 230 | 3 | 65 | 230 | 3 | 25 | 68 | 1.42 | (1) (3) (7f) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M4C*** | 10 | 135
VCC026 |  | CB |  | HJD3125 | 100 | 125 | [5 empty] | 30 | 80
|  | STR |  | V200M4C*** | 10 | 135
VCC027 |  | CB |  | HJD3150 | 100 | 150 | [5 empty] | 40 | 104
|  | STR |  | V200M4C*** | 10 | 135
VCC028 | C | CB | Eaton | HJD3100 | 65 | 100 | 460 | 3 | 65 | 460 | 3 | 50 | 65 | 1.42 | (1) (3) (7f) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M4C*** | 10 | 135
VCC029 |  | CB |  | HJD3150 | 65 | 125 | [5 empty] | 60 | 77
|  | STR |  | V200M4C*** | 10 | 135
VCC030 |  | CB |  | HJD3150 | 65 | 150 | [5 empty] | 75 | 96
|  | STR |  | V200M4C*** | 10 | 135
VCC031 | C | CB | Eaton | HKD3250 | 100 | 250 | 200 | 3 | 65 | 200 | 3 | 50 | 150 | 2.15 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M5C*** | 10 | 270
VCC032 |  | CB |  | HKD3250 | 100 | 250 | [5 empty] | 60 | 177
|  | STR |  | V200M5C*** | 10 | 270
VCC033 |  | CB |  | HKD3350 | 100 | 350 | [5 empty] | 75 | 221
|  | STR |  | V200M5C*** | 10 | 270
VCC034 | C | CB | Eaton | HKD3250 | 100 | 250 | 230 | 3 | 65 | 230 | 3 | 60 | 154 | 2.15 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M5C*** | 10 | 270
VCC035 |  | CB |  | HKD3300 | 100 | 300 | [5 empty] | 75 | 192
|  | STR |  | V200M5C*** | 10 | 270
VCC036 |  | CB |  | HKD3400 | 100 | 400 | [5 empty] | 100 | 248
|  | STR |  | V200M5C*** | 10 | 270
VCC037 | C | CB | Eaton | HKD3250 | 65 | 250 | 460 | 3 | 65 | 460 | 3 | 125 | 156 | 2.15 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M5C*** | 10 | 270
VCC038 |  | CB |  | HKD3250 | 65 | 250 | [5 empty] | 150 | 180
|  | STR |  | V200M5C*** | 10 | 270
VCC039 |  | CB |  | HKD3350 | 65 | 350 | [5 empty] | 200 | 240
|  | STR |  | V200M5C*** | 10 | 270
VCC040 | C | CB | Eaton | HKD3175 | 35 | 175 | 575 | 3 | 25 | 575 | 3 | 125 | 125 | 2.15 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M5C*** | 10 | 270
VCC041 |  | CB |  | HKD3200 | 35 | 200 | [5 empty] | 150 | 144
|  | STR |  | V200M5C*** | 10 | 270
VCC042 |  | CB |  | HKD3300 | 35 | 300 | [5 empty] | 200 | 192
|  | STR |  | V200M5C*** | 10 | 270
VCC043 | C | CB | Eaton | KDC3250 | 200 | 250 | 200 | 3 | 100 | 200 | 3 | 50 | 150 | 2.15 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M5C*** | 10 | 270
VCC044 |  | CB |  | KDC3250 | 200 | 250 | [5 empty] | 60 | 177
|  | STR |  | V200M5C*** | 10 | 270
VCC045 |  | CB |  | KDC3350 | 200 | 350 | [5 empty] | 75 | 221
|  | STR |  | V200M5C*** | 10 | 270
VCC046 | C | CB | Eaton | KDC3250 | 200 | 250 | 230 | 3 | 100 | 230 | 3 | 60 | 154 | 2.15 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M5C*** | 10 | 270
VCC047 |  | CB |  | KDC3300 | 200 | 300 | [5 empty] | 75 | 192
|  | STR |  | V200M5C*** | 10 | 270
VCC048 |  | CB |  | KDC3400 | 200 | 400 | [5 empty] | 100 | 248
|  | STR |  | V200M5C*** | 10 | 270
VCC049 | C | CB | Eaton | KDC3250 | 100 | 250 | 460 | 3 | 100 | 460 | 3 | 125 | 156 | 2.15 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M5C*** | 10 | 270
VCC050 |  | CB |  | KDC3250 | 100 | 250 | [5 empty] | 150 | 180
|  | STR |  | V200M5C*** | 10 | 270
VCC051 |  | CB |  | KDC3350 | 100 | 350 | [5 empty] | 200 | 240
|  | STR |  | V200M5C*** | 10 | 270
VCC052 | C | CB | Eaton | KDC3175 | 50 | 175 | 575 | 3 | 35 | 575 | 3 | 125 | 125 | 2.15 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M5C*** | 10 | 270
VCC053 |  | CB |  | KDC3200 | 50 | 200 | [5 empty] | 150 | 144
|  | STR |  | V200M5C*** | 10 | 270
VCC054 |  | CB |  | KDC3300 | 50 | 300 | [5 empty] | 200 | 192
|  | STR |  | V200M5C*** | 10 | 270
VCC055 | C | CB | Eaton | HLD3250 | 100 | 250 | 200 | 3 | 65 | 200 | 3 | 50 | 150 | 2.5 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M5C*** | 10 | 270
VCC056 |  | CB |  | HLD3250 | 100 | 250 | [5 empty] | 60 | 177
|  | STR |  | V200M5C*** | 10 | 270
VCC057 |  | CB |  | HLD3350 | 100 | 350 | [5 empty] | 75 | 221
|  | STR |  | V200M5C*** | 10 | 270
VCC058 | C | CB | Eaton | HLD3300 | 100 | 300 | 230 | 3 | 65 | 230 | 3 | 60 | 154 | 2.5 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M5C*** | 10 | 270
VCC059 |  | CB |  | HLD3300 | 100 | 300 | [5 empty] | 75 | 192
|  | STR |  | V200M5C*** | 10 | 270
VCC060 |  | CB |  | HLD3400 | 100 | 400 | [5 empty] | 100 | 248
|  | STR |  | V200M5C*** | 10 | 270
VCC061 | C | CB | Eaton | HLD3300 | 65 | 300 | 460 | 3 | 65 | 460 | 3 | 125 | 156 | 2.5 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M5C*** | 10 | 270
VCC062 |  | CB |  | HLD3300 | 65 | 300 | [5 empty] | 150 | 180
|  | STR |  | V200M5C*** | 10 | 270
VCC063 |  | CB |  | HLD3350 | 65 | 350 | [5 empty] | 200 | 240
|  | STR |  | V200M5C*** | 10 | 270
VCC064 | C | CB | Eaton | HLD3300 | 35 | 300 | 575 | 3 | 35 | 575 | 3 | 125 | 125 | 2.5 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M5C*** | 10 | 270
VCC065 |  | CB |  | HLD3300 | 35 | 300 | [5 empty] | 150 | 144
|  | STR |  | V200M5C*** | 10 | 270
VCC066 |  | CB |  | HLD3300 | 35 | 300 | [5 empty] | 200 | 192
|  | STR |  | V200M5C*** | 10 | 270
VCC067 | C | CB | Eaton | LA3250PR | 200 | 250 | 200 | 3 | 100 | 200 | 3 | 50 | 150 | 2.5 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M5C*** | 10 | 270
VCC068 |  | CB |  | LA3250PR | 200 | 250 | [5 empty] | 60 | 177
|  | STR |  | V200M5C*** | 10 | 270
VCC069 |  | CB |  | LA3350PR | 200 | 350 | [5 empty] | 75 | 221
|  | STR |  | V200M5C*** | 10 | 270
VCC070 | C | CB | Eaton | LA3250PR | 200 | 250 | 230 | 3 | 100 | 230 | 3 | 60 | 154 | 2.5 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M5C*** | 10 | 270
VCC071 |  | CB |  | LA3300PR | 200 | 300 | [5 empty] | 75 | 192
|  | STR |  | V200M5C*** | 10 | 270
VCC072 |  | CB |  | LA3400PR | 200 | 400 | [5 empty] | 100 | 248
|  | STR |  | V200M5C*** | 10 | 270
VCC073 | C | CB | Eaton | LA3250PR | 200 | 250 | 460 | 3 | 100 | 460 | 3 | 125 | 156 | 2.5 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M5C*** | 10 | 270
VCC074 |  | CB |  | LA3250PR | 200 | 250 | [5 empty] | 150 | 180
|  | STR |  | V200M5C*** | 10 | 270
VCC075 |  | CB |  | LA3350PR | 200 | 350 | [5 empty] | 200 | 240
|  | STR |  | V200M5C*** | 10 | 270
VCC076 | C | CB | Eaton | LA3175PR | 200 | 175 | 575 | 3 | 100 | 575 | 3 | 125 | 125 | 2.5 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M5C*** | 10 | 270
VCC077 |  | CB |  | LA3200PR | 200 | 200 | [5 empty] | 150 | 144
|  | STR |  | V200M5C*** | 10 | 270
VCC078 |  | CB |  | LA3300PR | 200 | 300 | [5 empty] | 200 | 192
|  | STR |  | V200M5C*** | 10 | 270
VCC079 | C | CB | Eaton | HLD3400 | 65 | 400 | 200 | 3 | 65 | 200 | 3 | 100 | 285 | 2.87 | (1) (3) (7s) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M6C*** | 18 | 540
VCC080 |  | CB |  | HLD3600 | 65 | 600 | [5 empty] | 125 | 359
|  | STR |  | V200M6C*** | 18 | 540
VCC081 |  | CB |  | HLD3600 | 65 | 600 | [5 empty] | 150 | 414
|  | STR |  | V200M6C*** | 18 | 540
VCC082 | C | CB | Eaton | HLD3500 | 65 | 500 | 230 | 3 | 65 | 230 | 3 | 125 | 312 | 2.87 | (1) (3) (7s) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M6C*** | 18 | 540
VCC083 |  | CB |  | HLD3600 | 65 | 600 | [5 empty] | 150 | 360
|  | STR |  | V200M6C*** | 18 | 540
VCC084 |  | CB |  | HLD3600 | 65 | 600 | [5 empty] | 200 | 480
|  | STR |  | V200M6C*** | 18 | 540
VCC085 | C | CB | Eaton | HLD3600 | 65 | 600 | 460 | 3 | 65 | 460 | 3 | 300 | 361 | 2.87 | (1) (3) (7s) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M6C*** | 18 | 540
VCC086 |  | CB |  | HLD3600 | 65 | 600 | [5 empty] | 350 | 414
|  | STR |  | V200M6C*** | 18 | 540
VCC087 |  | CB |  | HLD3600 | 65 | 600 | [5 empty] | 400 | 477
|  | STR |  | V200M6C*** | 18 | 540
VCC088 | C | CB | Eaton | HLD3500 | 35 | 500 | 575 | 3 | 35 | 575 | 3 | 300 | 289 | 2.87 | (1) (3) (7s) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M6C*** | 18 | 540
VCC089 |  | CB |  | HLD3600 | 35 | 600 | [5 empty] | 350 | 336
|  | STR |  | V200M6C*** | 18 | 540
VCC090 |  | CB |  | HLD3600 | 35 | 600 | [5 empty] | 400 | 382
|  | STR |  | V200M6C*** | 18 | 540
VCC091 | C | CB | Eaton | NB3400P | 200 | 400 | 200 | 3 | 100 | 200 | 3 | 100 | 285 | 3.6 | (1) (3) (7s) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M6C*** | 18 | 540
VCC092 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 125 | 359
|  | STR |  | V200M6C*** | 18 | 540
VCC093 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 150 | 414
|  | STR |  | V200M6C*** | 18 | 540
VCC094 | C | CB | Eaton | NB3500P | 200 | 500 | 230 | 3 | 100 | 230 | 3 | 125 | 312 | 3.6 | (1) (3) (7s) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M6C*** | 18 | 540
VCC095 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 150 | 360
|  | STR |  | V200M6C*** | 18 | 540
VCC096 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 200 | 480
|  | STR |  | V200M6C*** | 18 | 540
VCC097 | C | CB | Eaton | NB3600P | 200 | 600 | 460 | 3 | 100 | 460 | 3 | 300 | 361 | 3.6 | (1) (3) (7s) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M6C*** | 18 | 540
VCC098 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 350 | 414
|  | STR |  | V200M6C*** | 18 | 540
VCC099 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 400 | 477
|  | STR |  | V200M6C*** | 18 | 540
VCC100 | C | CB | Eaton | NB3500P | 200 | 500 | 575 | 3 | 100 | 575 | 3 | 300 | 289 | 3.6 | (1) (3) (7s) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V200M6C*** | 18 | 540
VCC101 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 350 | 336
|  | STR |  | V200M6C*** | 18 | 540
VCC102 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 400 | 382
|  | STR |  | V200M6C*** | 18 | 540
VCC103 | C | CB | Eaton | JGH3125FAG | 100 | 125 | 200 | 3 | 65 | 200 | 3 | 25 | 78.2 | 1.42 | (1) (3) (7f) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M4C*** | 10 | 135
VCC104 |  | CB |  | JGH3150FAG | 100 | 150 | [5 empty] | 30 | 92
|  | STR |  | V210M4C*** | 10 | 135
VCC105 |  | CB |  | JGH3175FAG | 100 | 175 | [5 empty] | 40 | 120
|  | STR |  | V210M4C*** | 10 | 135
VCC106 | C | CB | Eaton | JGH3125FAG | 100 | 125 | 230 | 3 | 65 | 230 | 3 | 25 | 68 | 1.42 | (1) (3) (7f) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M4C*** | 10 | 135
VCC107 |  | CB |  | JGH3125FAG | 100 | 125 | [5 empty] | 30 | 80
|  | STR |  | V210M4C*** | 10 | 135
VCC108 |  | CB |  | JGH3150FAG | 100 | 150 | [5 empty] | 40 | 104
|  | STR |  | V210M4C*** | 10 | 135
VCC109 | C | CB | Eaton | JGH3100FAG | 65 | 100 | 460 | 3 | 65 | 460 | 3 | 50 | 65 | 1.42 | (1) (3) (7f) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M4C*** | 10 | 135
VCC110 |  | CB |  | JGH3125FAG | 65 | 125 | [5 empty] | 60 | 77
|  | STR |  | V210M4C*** | 10 | 135
VCC111 |  | CB |  | JGH3150FAG | 65 | 150 | [5 empty] | 75 | 96
|  | STR |  | V210M4C*** | 10 | 135
VCC112 | C | CB | Eaton | JGH3100FAG | 35 | 100 | 575 | 3 | 25 | 575 | 3 | 60 | 62 | 1.42 | (1) (3) (7f) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M4C*** | 10 | 135
VCC113 |  | CB |  | JGH3125FAG | 35 | 125 | [5 empty] | 75 | 77
|  | STR |  | V210M4C*** | 10 | 135
VCC114 |  | CB |  | JGH3150FAG | 35 | 150 | [5 empty] | 100 | 99
|  | STR |  | V210M4C*** | 10 | 135
VCC115 | C | CB | Eaton | JDC3125 | 200 | 125 | 200 | 3 | 100 | 200 | 3 | 25 | 78.2 | 1.42 | (1) (3) (7f) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M4C*** | 10 | 135
VCC116 |  | CB |  | JDC3150 | 200 | 150 | [5 empty] | 30 | 92
|  | STR |  | V210M4C*** | 10 | 135
VCC117 |  | CB |  | JDC3175 | 200 | 175 | [5 empty] | 40 | 120
|  | STR |  | V210M4C*** | 10 | 135
VCC118 | C | CB | Eaton | JDC3125 | 200 | 125 | 230 | 3 | 100 | 230 | 3 | 25 | 68 | 1.42 | (1) (3) (7f) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M4C*** | 10 | 135
VCC119 |  | CB |  | JDC3125 | 200 | 125 | [5 empty] | 30 | 80
|  | STR |  | V210M4C*** | 10 | 135
VCC120 |  | CB |  | JDC3150 | 200 | 150 | [5 empty] | 40 | 104
|  | STR |  | V210M4C*** | 10 | 135
VCC121 | C | CB | Eaton | JDC3100 | 100 | 100 | 460 | 3 | 100 | 460 | 3 | 50 | 65 | 1.42 | (1) (3) (7f) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M4C*** | 10 | 135
VCC122 |  | CB |  | JDC3125 | 100 | 125 | [5 empty] | 60 | 77
|  | STR |  | V210M4C*** | 10 | 135
VCC123 |  | CB |  | JDC3150 | 100 | 150 | [5 empty] | 75 | 96
|  | STR |  | V210M4C*** | 10 | 135
VCC124 | C | CB | Eaton | HJD3125 | 100 | 125 | 200 | 3 | 65 | 200 | 3 | 25 | 78.2 | 1.42 | (1) (3) (7f) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M4C*** | 10 | 135
VCC125 |  | CB |  | HJD3150 | 100 | 150 | [5 empty] | 30 | 92
|  | STR |  | V210M4C*** | 10 | 135
VCC126 |  | CB |  | HJD3175 | 100 | 175 | [5 empty] | 40 | 120
|  | STR |  | V210M4C*** | 10 | 135
VCC127 | C | CB | Eaton | HJD3125 | 100 | 125 | 230 | 3 | 65 | 230 | 3 | 25 | 68 | 1.42 | (1) (3) (7f) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M4C*** | 10 | 135
VCC128 |  | CB |  | HJD3125 | 100 | 125 | [5 empty] | 30 | 80
|  | STR |  | V210M4C*** | 10 | 135
VCC129 |  | CB |  | HJD3150 | 100 | 150 | [5 empty] | 40 | 104
|  | STR |  | V210M4C*** | 10 | 135
VCC130 | C | CB | Eaton | HJD3100 | 65 | 100 | 460 | 3 | 65 | 460 | 3 | 50 | 65 | 1.42 | (1) (3) (7f) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M4C*** | 10 | 135
VCC131 |  | CB |  | HJD3150 | 65 | 125 | [5 empty] | 60 | 77
|  | STR |  | V210M4C*** | 10 | 135
VCC132 |  | CB |  | HJD3150 | 65 | 150 | [5 empty] | 75 | 96
|  | STR |  | V210M4C*** | 10 | 135
VCC133 | C | CB | Eaton | HKD3250 | 100 | 250 | 200 | 3 | 65 | 200 | 3 | 50 | 150 | 2.15 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M5C*** | 10 | 270
VCC134 |  | CB |  | HKD3250 | 100 | 250 | [5 empty] | 60 | 177
|  | STR |  | V210M5C*** | 10 | 270
VCC135 |  | CB |  | HKD3350 | 100 | 350 | [5 empty] | 75 | 221
|  | STR |  | V210M5C*** | 10 | 270
VCC136 | C | CB | Eaton | HKD3250 | 100 | 250 | 230 | 3 | 65 | 230 | 3 | 60 | 154 | 2.15 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M5C*** | 10 | 270
VCC137 |  | CB |  | HKD3300 | 100 | 300 | [5 empty] | 75 | 192
|  | STR |  | V210M5C*** | 10 | 270
VCC138 |  | CB |  | HKD3400 | 100 | 400 | [5 empty] | 100 | 248
|  | STR |  | V210M5C*** | 10 | 270
VCC139 | C | CB | Eaton | HKD3250 | 65 | 250 | 460 | 3 | 65 | 460 | 3 | 125 | 156 | 2.15 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M5C*** | 10 | 270
VCC140 |  | CB |  | HKD3250 | 65 | 250 | [5 empty] | 150 | 180
|  | STR |  | V210M5C*** | 10 | 270
VCC141 |  | CB |  | HKD3350 | 65 | 350 | [5 empty] | 200 | 240
|  | STR |  | V210M5C*** | 10 | 270
VCC142 | C | CB | Eaton | HKD3175 | 35 | 175 | 575 | 3 | 25 | 575 | 3 | 125 | 125 | 2.15 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M5C*** | 10 | 270
VCC143 |  | CB |  | HKD3200 | 35 | 200 | [5 empty] | 150 | 144
|  | STR |  | V210M5C*** | 10 | 270
VCC144 |  | CB |  | HKD3300 | 35 | 300 | [5 empty] | 200 | 192
|  | STR |  | V210M5C*** | 10 | 270
VCC145 | C | CB | Eaton | KDC3250 | 200 | 250 | 200 | 3 | 100 | 200 | 3 | 50 | 150 | 2.15 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M5C*** | 10 | 270
VCC146 |  | CB |  | KDC3250 | 200 | 250 | [5 empty] | 60 | 177
|  | STR |  | V210M5C*** | 10 | 270
VCC147 |  | CB |  | KDC3350 | 200 | 350 | [5 empty] | 75 | 221
|  | STR |  | V210M5C*** | 10 | 270
VCC148 | C | CB | Eaton | KDC3250 | 200 | 250 | 230 | 3 | 100 | 230 | 3 | 60 | 154 | 2.15 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M5C*** | 10 | 270
VCC149 |  | CB |  | KDC3300 | 200 | 300 | [5 empty] | 75 | 192
|  | STR |  | V210M5C*** | 10 | 270
VCC150 |  | CB |  | KDC3400 | 200 | 400 | [5 empty] | 100 | 248
|  | STR |  | V210M5C*** | 10 | 270
VCC151 | C | CB | Eaton | KDC3250 | 100 | 250 | 460 | 3 | 100 | 460 | 3 | 125 | 156 | 2.15 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M5C*** | 10 | 270
VCC152 |  | CB |  | KDC3250 | 100 | 250 | [5 empty] | 150 | 180
|  | STR |  | V210M5C*** | 10 | 270
VCC153 |  | CB |  | KDC3350 | 100 | 350 | [5 empty] | 200 | 240
|  | STR |  | V210M5C*** | 10 | 270
VCC154 | C | CB | Eaton | KDC3175 | 50 | 175 | 575 | 3 | 35 | 575 | 3 | 125 | 125 | 2.15 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M5C*** | 10 | 270
VCC155 |  | CB |  | KDC3200 | 50 | 200 | [5 empty] | 150 | 144
|  | STR |  | V210M5C*** | 10 | 270
VCC156 |  | CB |  | KDC3300 | 50 | 300 | [5 empty] | 200 | 192
|  | STR |  | V210M5C*** | 10 | 270
VCC157 | C | CB | Eaton | HLD3250 | 100 | 250 | 200 | 3 | 65 | 200 | 3 | 50 | 150 | 2.5 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M5C*** | 10 | 270
VCC158 |  | CB |  | HLD3250 | 100 | 250 | [5 empty] | 60 | 177
|  | STR |  | V210M5C*** | 10 | 270
VCC159 |  | CB |  | HLD3350 | 100 | 350 | [5 empty] | 75 | 221
|  | STR |  | V210M5C*** | 10 | 270
VCC160 | C | CB | Eaton | HLD3300 | 100 | 300 | 230 | 3 | 65 | 230 | 3 | 60 | 154 | 2.5 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M5C*** | 10 | 270
VCC161 |  | CB |  | HLD3300 | 100 | 300 | [5 empty] | 75 | 192
|  | STR |  | V210M5C*** | 10 | 270
VCC162 |  | CB |  | HLD3400 | 100 | 400 | [5 empty] | 100 | 248
|  | STR |  | V210M5C*** | 10 | 270
VCC163 | C | CB | Eaton | HLD3300 | 100 | 300 | 460 | 3 | 65 | 460 | 3 | 125 | 156 | 2.5 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M5C*** | 10 | 270
VCC164 |  | CB |  | HLD3300 | 100 | 300 | [5 empty] | 150 | 180
|  | STR |  | V210M5C*** | 10 | 270
VCC165 |  | CB |  | HLD3350 | 65 | 350 | [5 empty] | 200 | 240
|  | STR |  | V210M5C*** | 10 | 270
VCC166 | C | CB | Eaton | HLD3300 | 35 | 300 | 575 | 3 | 35 | 575 | 3 | 125 | 125 | 2.5 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M5C*** | 10 | 270
VCC167 |  | CB |  | HLD3300 | 35 | 300 | [5 empty] | 150 | 144
|  | STR |  | V210M5C*** | 10 | 270
VCC168 |  | CB |  | HLD3300 | 35 | 300 | [5 empty] | 200 | 192
|  | STR |  | V210M5C*** | 10 | 270
VCC169 | C | CB | Eaton | LA3250PR | 200 | 250 | 200 | 3 | 100 | 200 | 3 | 50 | 150 | 2.5 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M5C*** | 10 | 270
VCC170 |  | CB |  | LA3250PR | 200 | 250 | [5 empty] | 60 | 177
|  | STR |  | V210M5C*** | 10 | 270
VCC171 |  | CB |  | LA3350PR | 200 | 350 | [5 empty] | 75 | 221
|  | STR |  | V210M5C*** | 10 | 270
VCC172 | C | CB | Eaton | LA3250PR | 200 | 250 | 230 | 3 | 100 | 230 | 3 | 60 | 154 | 2.5 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M5C*** | 10 | 270
VCC173 |  | CB |  | LA3300PR | 200 | 300 | [5 empty] | 75 | 192
|  | STR |  | V210M5C*** | 10 | 270
VCC174 |  | CB |  | LA3400PR | 200 | 400 | [5 empty] | 100 | 248
|  | STR |  | V210M5C*** | 10 | 270
VCC175 | C | CB | Eaton | LA3250PR | 200 | 250 | 460 | 3 | 100 | 460 | 3 | 125 | 156 | 2.5 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M5C*** | 10 | 270
VCC176 |  | CB |  | LA3250PR | 200 | 250 | [5 empty] | 150 | 180
|  | STR |  | V210M5C*** | 10 | 270
VCC177 |  | CB |  | LA3350PR | 200 | 350 | [5 empty] | 200 | 240
|  | STR |  | V210M5C*** | 10 | 270
VCC178 | C | CB | Eaton | LA3175PR | 200 | 175 | 575 | 3 | 100 | 575 | 3 | 125 | 125 | 2.5 | (1) (3) (7j) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M5C*** | 10 | 270
VCC179 |  | CB |  | LA3200PR | 200 | 200 | [5 empty] | 150 | 144
|  | STR |  | V210M5C*** | 10 | 270
VCC180 |  | CB |  | LA3300PR | 200 | 300 | [5 empty] | 200 | 192
|  | STR |  | V210M5C*** | 10 | 270
VCC181 | C | CB | Eaton | HLD3400 | 65 | 400 | 200 | 3 | 65 | 200 | 3 | 100 | 285 | 2.87 | (1) (3) (7s) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M6C*** | 18 | 540
VCC182 |  | CB |  | HLD3600 | 65 | 600 | [5 empty] | 125 | 359
|  | STR |  | V210M6C*** | 18 | 540
VCC183 |  | CB |  | HLD3600 | 65 | 600 | [5 empty] | 150 | 414
|  | STR |  | V210M6C*** | 18 | 540
VCC184 | C | CB | Eaton | HLD3500 | 65 | 500 | 230 | 3 | 65 | 230 | 3 | 125 | 312 | 2.87 | (1) (3) (7s) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M6C*** | 18 | 540
VCC185 |  | CB |  | HLD3600 | 65 | 600 | [5 empty] | 150 | 360
|  | STR |  | V210M6C*** | 18 | 540
VCC186 |  | CB |  | HLD3600 | 65 | 600 | [5 empty] | 200 | 480
|  | STR |  | V210M6C*** | 18 | 540
VCC187 | C | CB | Eaton | HLD3600 | 65 | 600 | 460 | 3 | 65 | 460 | 3 | 300 | 361 | 2.87 | (1) (3) (7s) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M6C*** | 18 | 540
VCC188 |  | CB |  | HLD3600 | 65 | 600 | [5 empty] | 350 | 414
|  | STR |  | V210M6C*** | 18 | 540
VCC189 |  | CB |  | HLD3600 | 65 | 600 | [5 empty] | 400 | 477
|  | STR |  | V210M6C*** | 18 | 540
VCC190 | C | CB | Eaton | HLD3500 | 35 | 500 | 575 | 3 | 35 | 575 | 3 | 300 | 289 | 2.87 | (1) (3) (7s) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M6C*** | 18 | 540
VCC191 |  | CB |  | HLD3600 | 35 | 600 | [5 empty] | 350 | 336
|  | STR |  | V210M6C*** | 18 | 540
VCC192 |  | CB |  | HLD3600 | 35 | 600 | [5 empty] | 400 | 382
|  | STR |  | V210M6C*** | 18 | 540
VCC193 | C | CB | Eaton | NB3400P | 200 | 400 | 200 | 3 | 100 | 200 | 3 | 100 | 285 | 3.6 | (1) (3) (7s) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M6C*** | 18 | 540
VCC194 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 125 | 359
|  | STR |  | V210M6C*** | 18 | 540
VCC195 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 150 | 414
|  | STR |  | V210M6C*** | 18 | 540
VCC196 | C | CB | Eaton | NB3500P | 200 | 500 | 230 | 3 | 100 | 230 | 3 | 125 | 312 | 3.6 | (1) (3) (7s) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M6C*** | 18 | 540
VCC197 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 150 | 360
|  | STR |  | V210M6C*** | 18 | 540
VCC198 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 200 | 480
|  | STR |  | V210M6C*** | 18 | 540
VCC199 | C | CB | Eaton | NB3600P | 200 | 600 | 460 | 3 | 100 | 460 | 3 | 300 | 361 | 3.6 | (1) (3) (7s) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M6C*** | 18 | 540
VCC200 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 350 | 414
|  | STR |  | V210M6C*** | 18 | 540
VCC201 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 400 | 477
|  | STR |  | V210M6C*** | 18 | 540
VCC202 | C | CB | Eaton | NB3500P | 200 | 500 | 575 | 3 | 100 | 575 | 3 | 300 | 289 | 3.6 | (1) (3) (7s) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | V210M6C*** | 18 | 540
VCC203 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 350 | 336
|  | STR |  | V210M6C*** | 18 | 540
VCC204 |  | CB |  | NB3600P | 200 | 600 | [5 empty] | 400 | 382
|  | STR |  | V210M6C*** | 18 | 540
VCC205 | C | CB | Eaton | HJD3125 | 100 | 125 | 200 | 3 | 65 | 200 | 3 | 25 | 78.2 | 1.42 | (1) (7f) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | MC |  | V208M4C*** | 10 | 135
VCC206 |  | CB |  | HJD3150 | 100 | 150 | [5 empty] | 30 | 92
|  | MC |  | V208M4C*** | 10 | 135
VCC207 |  | CB |  | HLD3175 | 100 | 175 | [5 empty] | 40 | 120
|  | MC |  | V208M4C*** | 10 | 135
VCC208 | C | CB | Eaton | HJD3125 | 100 | 125 | 230 | 3 | 65 | 230 | 3 | 25 | 68 | 1.42 | (1) (7f) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | MC |  | V208M4C*** | 10 | 135
VCC209 |  | CB |  | HJD3125 | 100 | 125 | [5 empty] | 30 | 80
|  | MC |  | V208M4C*** | 10 | 135
VCC210 |  | CB |  | HJD3150 | 100 | 150 | [5 empty] | 40 | 104
|  | MC |  | V208M4C*** | 10 | 135
VCC211 | C | CB | Eaton | HJD3100 | 65 | 100 | 460 | 3 | 65 | 460 | 3 | 50 | 65 | 1.42 | (1) (7f) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | MC |  | V208M4C*** | 10 | 135
VCC212 |  | CB |  | HJD3125 | 100 | 125 | [5 empty] | 60 | 77
|  | MC |  | V208M4C*** | 10 | 135
VCC213 |  | CB |  | HJD3150 | 100 | 150 | [5 empty] | 75 | 96
|  | MC |  | V208M4C*** | 10 | 135
VCC214 | C | CB | Eaton | HJD3100 | 25 | 100 | 575 | 3 | 25 | 575 | 3 | 60 | 62 | 1.42 | (1) (7f) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | MC |  | V208M4C*** | 10 | 135
VCC215 |  | CB |  | HJD3125 | 100 | 125 | [5 empty] | 75 | 77
|  | MC |  | V208M4C*** | 10 | 135
VCC216 |  | CB |  | HJD3150 | 100 | 150 | [5 empty] | 100 | 99
|  | MC |  | V208M4C*** | 10 | 135
VCC217 | C | CB | Eaton | JDC3125 | 200 | 125 | 200 | 3 | 100 | 200 | 3 | 25 | 78.2 | 1.42 | (1) (7f) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | MC |  | V208M4C*** | 10 | 135
VCC218 |  | CB |  | JCD3150 | 200 | 150 | [5 empty] | 30 | 92
|  | MC |  | V208M4C*** | 10 | 135
VCC219 |  | CB |  | JCDC3175 | 200 | 175 | [5 empty] | 40 | 120
|  | MC |  | V208M4C*** | 10 | 135
VCC220 | C | CB | Eaton | JDC3125 | 200 | 125 | 230 | 3 | 100 | 230 | 3 | 25 | 68 | 1.42 | (1) (7f) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | MC |  | V208M4C*** | 10 | 135
VCC221 |  | CB |  | JDC3125 | 200 | 125 | [5 empty] | 30 | 80
|  | MC |  | V208M4C*** | 10 | 135
VCC222 |  | CB |  | JDC3150 | 200 | 150 | [5 empty] | 40 | 104
|  | MC |  | V208M4C*** | 10 | 135
VCC223 | C | CB | Eaton | JDC3100 | 100 | 100 | 460 | 3 | 100 | 460 | 3 | 50 | 65 | 1.42 | (1) (7f) | E176513 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | MC |  | V208M4C*** | 10 | 135
VCC224 |  | CB |  | JDC3125 | 200 | 125 | [5 empty] | 60 | 77
|  | MC |  | V208M4C*** | 10 | 135
VCC225 |  | CB |  | JDC3150 | 100 | 150 | [5 empty] | 75 | 96
|  | MC |  | V208M4C*** | 10 | 135
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment. (Max. Heater for Size 4 = FH94. Max. Heater for size 5 & 6 = FH33).
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = Install Terminal end Cover TEC2 (6085C42H02) to line side of circuit breaker.
(7) See Table 7 for internal wiring between load side of short circuit protective device & line side of starter.
Table 7 - Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
| Wire Code | Wire Size | Wire Code | Wire Size
| 7a | 12 awg. | 7j | 4/0 awg.
| 7b | 10 awg. | 7k | 250kcml
| 7c | 8 awg. | 7l | 350kcml
| 7d | 6 awg. | 7m | 4/0 awg. (3)
| 7e | 4 awg. | 7n | 4/0 awg. (4)
| 7f | 2 awg. | 7p | 250kcml (2)
| 7g | 1/0 awg. | 7r | 350kcml (3)
| 7h | 2/0 awg. | 7s | 4/0 awg. (2)

## Vacuum Type D
Issued: 2006-05-18
Last Revised: 2014-10-10
Combination Motor Controllers for use in Industrial Control Panels
ID Number | Combination Type | Individual Component | [6 empty] | Combination SCCR | [5 empty] | Conditions of Acceptability | Combination Starter UL File | Motor Control Center UL File
|  | Component Type | Manufacturer | Partial Catalog No. | Ratings |  |  |  | SCCR kA | Volts | Phase | Hp | NEC FLC | Min. Enclosure Volume (cu. ft.)
[5 empty] | SCCR kA | Max. Amps | Volts | No. Poles
VCD001 | D | ICB | Eaton | HMCP150*** | - | 150 | 200 | 3 | 65 | 200 | 3 | 25 | 78.2 | 1.06 | (1) (3) (7f) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | STR |  | V200M4C*** | 10 | 135
VCD002 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 30 | 92
|  | STR |  | V200M4C*** | 10 | 135
VCD003 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 40 | 120
|  | STR |  | V200M4C*** | 10 | 135
VCD004 | D | ICB | Eaton | HMCP150*** | - | 150 | 200 | 3 | 100 | 200 | 3 | 25 | 78.2 | 1.06 | (1) (3) (7f) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | V200M4C*** | 10 | 135
VCD005 | D | ICB | Eaton | HMCP150*** | - | 150 | 200 | 3 | 100 | 200 | 3 | 30 | 92
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | V200M4C*** | 10 | 135
VCD006 | D | ICB | Eaton | HMCP150*** | - | 150 | 200 | 3 | 100 | 200 | 3 | 40 | 120
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | V200M4C*** | 10 | 135
VCD007 | D | ICB | Eaton | HMCP150*** | - | 150 | 230 | 3 | 65 | 230 | 3 | 25 | 68 | 1.06 | (1) (3) (7f) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | STR |  | V200M4C*** | 10 | 135
VCD008 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 30 | 80
|  | STR |  | V200M4C*** | 10 | 135
VCD009 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 40 | 104
|  | STR |  | V200M4C*** | 10 | 135
VCD010 | D | ICB | Eaton | HMCP150*** | - | 150 | 230 | 3 | 100 | 230 | 3 | 25 | 68 | 1.06 | (1) (3) (7f) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | V200M4C*** | 10 | 135
VCD011 | D | ICB | Eaton | HMCP150*** | - | 150 | 230 | 3 | 100 | 230 | 3 | 30 | 80
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | V200M4C*** | 10 | 135
VCD012 | D | ICB | Eaton | HMCP150*** | - | 150 | 230 | 3 | 100 | 230 | 3 | 40 | 104
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | V200M4C*** | 10 | 135
VCD013 | D | ICB | Eaton | HMCP150*** | - | 150 | 460 | 3 | 65 | 460 | 3 | 50 | 65 | 1.06 | (1) (3) (7f) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | STR |  | V200M4C*** | 10 | 135
VCD014 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 60 | 77
|  | STR |  | V200M4C*** | 10 | 135
VCD015 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 75 | 96
|  | STR |  | V200M4C*** | 10 | 135
VCD016 | D | ICB | Eaton | HMCP150*** | - | 150 | 460 | 3 | 100 | 460 | 3 | 50 | 65 | 1.06 | (1) (3) (7f) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | V200M4C*** | 10 | 135
VCD017 | D | ICB | Eaton | HMCP150*** | - | 150 | 460 | 3 | 100 | 460 | 3 | 60 | 77
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | V200M4C*** | 10 | 135
VCD018 | D | ICB | Eaton | HMCP150*** | - | 150 | 460 | 3 | 100 | 460 | 3 | 75 | 96
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | V200M4C*** | 10 | 135
VCD019 | D | ICB | Eaton | HMCP150*** | - | 150 | 575 | 3 | 25 | 575 | 3 | 60 | 62 | 1.06 | (1) (3) (6) (7f) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | STR |  | V200M4C*** | 10 | 135
VCD020 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 75 | 77
|  | STR |  | V200M4C*** | 10 | 135
VCD021 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 100 | 99
|  | STR |  | V200M4C*** | 10 | 135
VCD022 | D | ICB | Eaton | HMCP150*** | - | 150 | 575 | 3 | 100 | 575 | 3 | 60 | 62 | 1.06 | (1) (3) (7f) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | V200M4C*** | 10 | 135
VCD023 | D | ICB | Eaton | HMCP150*** | - | 150 | 575 | 3 | 100 | 575 | 3 | 75 | 77
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | V200M4C*** | 10 | 135
VCD024 | D | ICB | Eaton | HMCP150*** | - | 150 | 575 | 3 | 100 | 575 | 3 | 100 | 99
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | V200M4C*** | 10 | 135
VCD025 | D | ICB | Eaton | HMCP250*** | - | 250 | 200 | 3 | 100 | 200 | 3 | 50 | 150 | 2.15 | (1) (3) (7j) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | STR |  | V200M5C*** | 10 | 270
VCD026 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 60 | 177
|  | STR |  | V200M5C*** | 10 | 270
VCD027 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 75 | 221
|  | STR |  | V200M5C*** | 10 | 270
VCD028 | D | ICB | Eaton | HMCP250*** | - | 250 | 230 | 3 | 100 | 230 | 3 | 60 | 154 | 2.15 | (1) (3) (7j) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | STR |  | V200M5C*** | 10 | 270
VCD029 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 75 | 192
|  | STR |  | V200M5C*** | 10 | 270
VCD030 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 100 | 248
|  | STR |  | V200M5C*** | 10 | 270
VCD031 | D | ICB | Eaton | HMCP250*** | - | 250 | 460 | 3 | 100 | 460 | 3 | 125 | 156 | 2.15 | (1) (3) (7j) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | STR |  | V200M5C*** | 10 | 270
VCD032 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 150 | 180
|  | STR |  | V200M5C*** | 10 | 270
VCD033 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 200 | 240
|  | STR |  | V200M5C*** | 10 | 270
VCD034 | D | ICB | Eaton | HMCP250*** | - | 250 | 575 | 3 | 18 | 575 | 3 | 125 | 125 | 2.15 | (1) (3) (7j) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | STR |  | V200M5C*** | 10 | 270
VCD035 |  | ICB |  | HMCP250*** | - | 250 | [5 empty] | 150 | 144
|  | STR |  | V200M5C*** | 10 | 270
VCD036 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 200 | 192
|  | STR |  | V200M5C*** | 10 | 270
VCD037 | D | ICB | Eaton | HMCP600*** | - | 600 | 200 | 3 | 65 | 200 | 3 | 100 | 285 | 2.87 | (1) (3) (7s) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | STR |  | V200M6C*** | 18 | 540
VCD038 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 125 | 359
|  | STR |  | V200M6C*** | 18 | 540
VCD039 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 150 | 414
|  | STR |  | V200M6C*** | 18 | 540
VCD040 | D | ICB | Eaton | HMCP600*** | - | 600 | 230 | 3 | 65 | 230 | 3 | 125 | 312 | 2.87 | (1) (3) (7s) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | STR |  | V200M6C*** | 18 | 540
VCD041 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 150 | 360
|  | STR |  | V200M6C*** | 18 | 540
VCD042 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 200 | 480
|  | STR |  | V200M6C*** | 18 | 540
VCD043 | D | ICB | Eaton | HMCP600*** | - | 600 | 460 | 3 | 65 | 460 | 3 | 300 | 361 | 2.87 | (1) (3) (7s) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | STR |  | V200M6C*** | 18 | 540
VCD044 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 350 | 414
|  | STR |  | V200M6C*** | 18 | 540
VCD045 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 400 | 477
|  | STR |  | V200M6C*** | 18 | 540
VCD046 | D | ICB | Eaton | HMCP600*** | - | 600 | 575 | 3 | 35 | 575 | 3 | 300 | 289 | 2.87 | (1) (3) (7s) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | STR |  | V200M6C*** | 18 | 540
VCD047 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 350 | 336
|  | STR |  | V200M6C*** | 18 | 540
VCD048 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 400 | 382
|  | STR |  | V200M6C*** | 18 | 540
VCD049 | D | ICB | Eaton | HMCP150*** | - | 150 | 200 | 3 | 65 | 200 | 3 | 25 | 78.2 | 1.06 | (1) (3) (7f) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | STR |  | V210M4C*** | 10 | 135
VCD050 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 30 | 92
|  | STR |  | V210M4C*** | 10 | 135
VCD051 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 40 | 120
|  | STR |  | V210M4C*** | 10 | 135
VCD052 | D | ICB | Eaton | HMCP150*** | - | 150 | 200 | 3 | 100 | 200 | 3 | 25 | 78.2 | 1.06 | (1) (3) (7f) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | V210M4C*** | 10 | 135
VCD053 | D | ICB | Eaton | HMCP150*** | - | 150 | 200 | 3 | 100 | 200 | 3 | 30 | 92
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | V210M4C*** | 10 | 135
VCD054 | D | ICB | Eaton | HMCP150*** | - | 150 | 200 | 3 | 100 | 200 | 3 | 40 | 120
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | V210M4C*** | 10 | 135
VCD055 | D | ICB | Eaton | HMCP150*** | - | 150 | 230 | 3 | 65 | 230 | 3 | 25 | 68 | 1.06 | (1) (3) (7f) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | STR |  | V210M4C*** | 10 | 135
VCD056 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 30 | 80
|  | STR |  | V210M4C*** | 10 | 135
VCD057 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 40 | 104
|  | STR |  | V210M4C*** | 10 | 135
VCD058 | D | ICB | Eaton | HMCP150*** | - | 150 | 230 | 3 | 100 | 230 | 3 | 25 | 68 | 1.06 | (1) (3) (7f) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | V210M4C*** | 10 | 135
VCD059 | D | ICB | Eaton | HMCP150*** | - | 150 | 230 | 3 | 100 | 230 | 3 | 30 | 80
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | V210M4C*** | 10 | 135
VCD060 | D | ICB | Eaton | HMCP150*** | - | 150 | 230 | 3 | 100 | 230 | 3 | 40 | 104
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | V210M4C*** | 10 | 135
VCD061 | D | ICB | Eaton | HMCP150*** | - | 150 | 460 | 3 | 65 | 460 | 3 | 50 | 65 | 1.06 | (1) (3) (7f) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | STR |  | V210M4C*** | 10 | 135
VCD062 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 60 | 77
|  | STR |  | V210M4C*** | 10 | 135
VCD063 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 75 | 96
|  | STR |  | V210M4C*** | 10 | 135
VCD064 | D | ICB | Eaton | HMCP150*** | - | 150 | 460 | 3 | 100 | 460 | 3 | 50 | 65 | 1.06 | (1) (3) (7f) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | V210M4C*** | 10 | 135
VCD065 | D | ICB | Eaton | HMCP150*** | - | 150 | 460 | 3 | 100 | 460 | 3 | 60 | 77
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | V210M4C*** | 10 | 135
VCD066 | D | ICB | Eaton | HMCP150*** | - | 150 | 460 | 3 | 100 | 460 | 3 | 75 | 96
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | V210M4C*** | 10 | 135
VCD067 | D | ICB | Eaton | HMCP150*** | - | 150 | 575 | 3 | 25 | 575 | 3 | 60 | 62 | 1.06 | (1) (3) (6) (7f) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | STR |  | V210M4C*** | 10 | 135
VCD068 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 75 | 77
|  | STR |  | V210M4C*** | 10 | 135
VCD069 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 100 | 99
|  | STR |  | V210M4C*** | 10 | 135
VCD070 | D | ICB | Eaton | HMCP150*** | - | 150 | 575 | 3 | 100 | 575 | 3 | 60 | 62 | 1.06 | (1) (3) (7f) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | V210M4C*** | 10 | 135
VCD071 | D | ICB | Eaton | HMCP150*** | - | 150 | 575 | 3 | 100 | 575 | 3 | 75 | 77
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | V210M4C*** | 10 | 135
VCD072 | D | ICB | Eaton | HMCP150*** | - | 150 | 575 | 3 | 100 | 575 | 3 | 100 | 99
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | V210M4C*** | 10 | 135
VCD073 | D | ICB | Eaton | HMCP250*** | - | 250 | 200 | 3 | 100 | 200 | 3 | 50 | 150 | 2.15 | (1) (3) (7j) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | STR |  | V210M5C*** | 10 | 270
VCD074 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 60 | 177
|  | STR |  | V210M5C*** | 10 | 270
VCD075 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 75 | 221
|  | STR |  | V210M5C*** | 10 | 270
VCD076 | D | ICB | Eaton | HMCP250*** | - | 250 | 230 | 3 | 100 | 230 | 3 | 60 | 154 | 2.15 | (1) (3) (7j) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | STR |  | V210M5C*** | 10 | 270
VCD077 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 75 | 192
|  | STR |  | V210M5C*** | 10 | 270
VCD078 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 100 | 248
|  | STR |  | V210M5C*** | 10 | 270
VCD079 | D | ICB | Eaton | HMCP250*** | - | 250 | 460 | 3 | 100 | 460 | 3 | 125 | 156 | 2.15 | (1) (3) (7j) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | STR |  | V210M5C*** | 10 | 270
VCD080 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 150 | 180
|  | STR |  | V210M5C*** | 10 | 270
VCD081 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 200 | 240
|  | STR |  | V210M5C*** | 10 | 270
VCD082 | D | ICB | Eaton | HMCP250*** | - | 250 | 575 | 3 | 18 | 575 | 3 | 125 | 125 | 2.15 | (1) (3) (7j) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | STR |  | V210M5C*** | 10 | 270
VCD083 |  | ICB |  | HMCP250*** | - | 250 | [5 empty] | 150 | 144
|  | STR |  | V210M5C*** | 10 | 270
VCD084 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 200 | 192
|  | STR |  | V210M5C*** | 10 | 270
VCD085 | D | ICB | Eaton | HMCP600*** | - | 600 | 200 | 3 | 65 | 200 | 3 | 100 | 285 | 2.87 | (1) (3) (7s) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | STR |  | V210M6C*** | 18 | 540
VCD086 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 125 | 359
|  | STR |  | V210M6C*** | 18 | 540
VCD087 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 150 | 414
|  | STR |  | V210M6C*** | 18 | 540
VCD088 | D | ICB | Eaton | HMCP600*** | - | 600 | 230 | 3 | 65 | 230 | 3 | 125 | 312 | 2.87 | (1) (3) (7s) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | STR |  | V210M6C*** | 18 | 540
VCD089 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 150 | 360
|  | STR |  | V210M6C*** | 18 | 540
VCD090 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 200 | 480
|  | STR |  | V210M6C*** | 18 | 540
VCD091 | D | ICB | Eaton | HMCP600*** | - | 600 | 460 | 3 | 65 | 460 | 3 | 300 | 361 | 2.87 | (1) (3) (7s) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | STR |  | V210M6C*** | 18 | 540
VCD092 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 350 | 414
|  | STR |  | V210M6C*** | 18 | 540
VCD093 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 400 | 477
|  | STR |  | V210M6C*** | 18 | 540
VCD094 | D | ICB | Eaton | HMCP600*** | - | 600 | 575 | 3 | 35 | 575 | 3 | 300 | 289 | 2.87 | (1) (3) (7s) | E176513 Vol. 1 Sec. Gen. & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2, Sec. 2
|  | STR |  | V210M6C*** | 18 | 540
VCD095 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 350 | 336
|  | STR |  | V210M6C*** | 18 | 540
VCD096 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 400 | 382
|  | STR |  | V210M6C*** | 18 | 540
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment. (Max. Heater for Size 4 = FH94. Max. Heater for size 5 & 6 = FH33).
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = Install Terminal end Cover TEC2 (6085C42H02) to line side of circuit breaker.
(7) See Table 7 for internal wiring between load side of short circuit protective device & line side of starter.
Table 7 - Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
| Wire Code | Wire Size | Wire Code | Wire Size
| 7a | 12 awg. | 7j | 4/0 awg.
| 7b | 10 awg. | 7k | 250kcml
| 7c | 8 awg. | 7l | 350kcml
| 7d | 6 awg. | 7m | 4/0 awg. (3)
| 7e | 4 awg. | 7n | 4/0 awg. (4)
| 7f | 2 awg. | 7p | 250kcml (2)
| 7g | 1/0 awg. | 7r | 350kcml (3)
| 7h | 2/0 awg. | 7s | 4/0 awg. (2)

## XT - Type D
Issued: 2006-11-07
Last Revised: 2006-11-07
Combination Motor Controllers for use in Industrial Control Panels
ID Number | Combination Type | Individual Component | [6 empty] | Combination SCCR | [5 empty] | Conditions of Acceptability | Combination Starter UL File | Motor Control Center UL File
|  | Component Type | Manufacturer | Partial Catalog No. | Ratings |  |  |  | SCCR kA | Volts | Phase | Hp | NEC FLC | Min. Enclosure Volume (cu. ft.)
[5 empty] | SCCR kA | Max. Amps | Volts | No. Poles
XT001 | D | ICB | EATON | HMCP003*** | - | 3 | 200 | 3 | 35 | 200 | 3 | 0.25 | 1.3 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB1P6B | 5 | 1.6
XT002 | D | ICB | EATON | HMCP003*** | - | 3 |  | 3 | 35 |  | 3 | 0.33333 | 1.5 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB1P6B | 5 | 1.6
XT003 | D | ICB | EATON | HMCP003*** | - | 3 |  | 3 | 35 |  | 3 | 0.5 | 2.5 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB004B | 5 | 4
XT004 | D | ICB | EATON | HMCP007*** | - | 7 |  | 3 | 35 |  | 3 | 0.75 | 3.7 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB004B | 5 | 4
XT005 | D | ICB | EATON | HMCP007*** | - | 7 |  | 3 | 15 |  | 3 | 1 | 4.8 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB006B | 5 | 6
XT006 | D | ICB | EATON | HMCPE015*** | - | 15 |  | 3 | 65 |  | 3 | 1.5 | 6.9 | 1.1 | (1), (2), (3), (5) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB010B | 5 | 10
XT007 | D | ICB | EATON | HMCP003*** | - | 3 | 208 | 3 | 35 | 208 | 3 | 0.25 | 1.2 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB1P6B | 5 | 1.6
XT008 | D | ICB | EATON | HMCP003*** | - | 3 |  | 3 | 35 |  | 3 | 0.33333 | 1.4 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB1P6B | 5 | 1.6
XT009 | D | ICB | EATON | HMCP003*** | - | 3 |  | 3 | 35 |  | 3 | 0.5 | 2.4 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB004B | 5 | 4
XT010 | D | ICB | EATON | HMCP007*** | - | 7 |  | 3 | 35 |  | 3 | 0.75 | 3.5 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB004B | 5 | 4
XT011 | D | ICB | EATON | HMCP007*** | - | 7 |  | 3 | 15 |  | 3 | 1 | 4.6 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB006B | 5 | 6
XT012 | D | ICB | EATON | HMCPE015*** | - | 15 |  | 3 | 65 |  | 3 | 1.5 | 6.6 | 1.1 | (1), (2), (3), (5) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB010B | 5 | 10
XT013 | D | ICB | EATON | HMCP003*** | - | 3 | 230 | 3 | 35 | 230 | 3 | 0.25 | 1 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB1P6B | 5 | 1.6
XT014 | D | ICB | EATON | HMCP003*** | - | 3 |  | 3 | 35 |  | 3 | 0.33333 | 1.2 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB1P6B | 5 | 1.6
XT015 | D | ICB | EATON | HMCP003*** | - | 3 |  | 3 | 35 |  | 3 | 0.5 | 2.2 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB2P4B | 5 | 2.4
XT016 | D | ICB | EATON | HMCP007*** | - | 7 |  | 3 | 35 |  | 3 | 0.75 | 3.2 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB004B | 5 | 4
XT017 | D | ICB | EATON | HMCP007*** | - | 7 |  | 3 | 15 |  | 3 | 1 | 4.2 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB006B | 5 | 6
XT018 | D | ICB | EATON | HMCPE015*** | - | 15 |  | 3 | 65 |  | 3 | 1.5 | 6 | 1.1 | (1), (2), (3),(5) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB010B | 5 | 10
XT019 | D | ICB | EATON | HMCPE015*** | - | 15 |  | 3 | 65 |  | 3 | 2 | 6.8 | 1.1 | (1), (2), (3), (5) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB010B | 5 | 10
XT020 | D | ICB | EATON | HMCP003*** | - | 3 | 460 | 3 | 35 | 460 | 3 | 0.25 | 0.5 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOBP60B | 5 | 0.6
XT021 | D | ICB | EATON | HMCP003*** | - | 3 |  | 3 | 35 |  | 3 | 0.33333 | 0.6 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB001B | 5 | 1
XT022 | D | ICB | EATON | HMCP003*** | - | 3 |  | 3 | 35 |  | 3 | 0.5 | 1.1 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB1P6B | 5 | 1.6
XT023 | D | ICB | EATON | HMCP003*** | - | 3 |  | 3 | 35 |  | 3 | 0.75 | 1.6 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB2P4B | 5 | 2.4
XT024 | D | ICB | EATON | HMCP003*** | - | 3 |  | 3 | 35 |  | 3 | 1 | 2.1 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB2P4B | 5 | 2.4
XT025 | D | ICB | EATON | HMCP003*** | - | 3 |  | 3 | 35 |  | 3 | 1.5 | 3 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB004B | 5 | 4
XT026 | D | ICB | EATON | HMCP007*** | - | 7 |  | 3 | 35 |  | 3 | 2 | 3.4 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB004B | 5 | 4
XT028 | D | ICB | EATON | HMCPE015*** | - | 15 |  | 3 | 65 |  | 3 | 3 | 4.8 | 1.1 | (1), (2), (3), (5) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB006B | 5 | 6
XT029 | D | ICB | EATON | HMCP003*** | - | 3 | 575 | 3 | 35 | 575 | 3 | 0.25 | 0.4 | 1.1 | (1), (2), (3), (4) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOBP40B | 5 | 0.4
XT030 | D | ICB | EATON | HMCP003*** | - | 3 |  | 3 | 35 |  | 3 | 0.33333 | 0.5 | 1.1 | (1), (2), (3), (4) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOBP60B | 5 | 0.6
XT031 | D | ICB | EATON | HMCP003*** | - | 3 |  | 3 | 35 |  | 3 | 0.5 | 0.9 | 1.1 | (1), (2), (3), (4) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB001B | 5 | 1
XT032 | D | ICB | EATON | HMCP003*** | - | 3 |  | 3 | 35 |  | 3 | 0.75 | 1.3 | 1.1 | (1), (2), (3), (4) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB1P6B | 5 | 1.6
XT033 | D | ICB | EATON | HMCP003*** | - | 3 |  | 3 | 35 |  | 3 | 1 | 1.6 | 1.1 | (1), (2), (3), (4) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB1P6B | 5 | 1.6
XT034 | D | ICB | EATON | HMCP007*** | - | 7 |  | 3 | 35 |  | 3 | 1.5 | 2.4 | 1.1 | (1), (2), (3), (4) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB004B | 5 | 4
XT035 | D | ICB | EATON | HMCP007*** | - | 7 |  | 3 | 35 |  | 3 | 2 | 2.7 | 1.1 | (1), (2), (3), (4) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB004B | 5 | 4
XT036 | D | ICB | EATON | HMCP007*** | - | 7 |  | 3 | 35 |  | 3 | 3 | 3.9 | 1.1 | (1), (2), (3), (4) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB004B | 5 | 4
XT037 | D | ICB | EATON | HMCP015*** | - | 15 |  | 3 | 15 |  | 3 | 5 | 6.1 | 1.1 | (1), (2), (3), (4) | E176513 VOL 1 section 5
|  | MC |  | XTCE007B | 5 | 7
|  | OLR |  | XTOB006B | 5 | 6
XT038 | D | ICB | EATON | HMCPE015*** | - | 15 | 200 | 3 | 65 | 200 | 3 | 2 | 7.8 | 1.1 | (1), (2), (3), (5) | E176513 VOL 1 section 5
|  | MC |  | XTCE009B | 5 | 9
|  | OLR |  | XTOB010B | 5 | 10
XT039 | D | ICB | EATON | HMCPE015*** | - | 15 | 208 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1.1 | (1), (2), (3), (5) | E176513 VOL 1 section 5
|  | MC |  | XTCE009B | 5 | 9
|  | OLR |  | XTOB010B | 5 | 10
XT040 | D | ICB | EATON | HMCPE015*** | - | 15 | 230 | 3 | 65 | 230 | 3 | 3 | 9.6 | 1.1 | (1), (2), (3), (5) | E176513 VOL 1 section 5
|  | MC |  | XTCE009B | 5 | 9
|  | OLR |  | XTOB010B | 5 | 10
XT041 | D | ICB | EATON | HMCPE015*** | - | 15 | 460 | 3 | 65 | 460 | 3 | 5 | 7.6 | 1.1 | (1), (2), (3), (5) | E176513 VOL 1 section 5
|  | MC |  | XTCE009B | 5 | 9
|  | OLR |  | XTOB010B | 5 | 10
XT042 | D | ICB | EATON | HMCP015*** | - | 15 | 575 | 3 | 15 | 575 | 3 | 7.5 | 9 | 1.1 | (1), (2), (3), (4) | E176513 VOL 1 section 5
|  | MC |  | XTCE009B | 5 | 9
|  | OLR |  | XTOB010B | 5 | 10
XT043 | D | ICB | EATON | HMCPE015*** | - | 15 | 200 | 3 | 65 | 200 | 3 | 3 | 11 | 1.1 | (1), (2), (3), (5) | E176513 VOL 1 section 5
|  | MC |  | XTCE012B | 5 | 12
|  | OLR |  | XTOB012B | 5 | 12
XT044 | D | ICB | EATON | HMCPE015*** | - | 15 | 208 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1.1 | (1), (2), (3), (5) | E176513 VOL 1 section 5
|  | MC |  | XTCE012B | 5 | 12
|  | OLR |  | XTOB012B | 5 | 12
XT045 | D | ICB | EATON | HMCPE015*** | - | 15 | 230 | 3 | 65 | 230 | 3 | 3 | 9.6 | 1.1 | (1), (2), (3), (5) | E176513 VOL 1 section 5
|  | MC |  | XTCE012B | 5 | 12
|  | OLR |  | XTOB010B | 5 | 10
XT046 | D | ICB | EATON | HMCPE015*** | - | 15 | 460 | 3 | 65 | 460 | 3 | 7.5 | 11 | 1.1 | (1), (2), (3), (5) | E176513 VOL 1 section 5
|  | MC |  | XTCE012B | 5 | 12
|  | OLR |  | XTOB012B | 5 | 12
XT047 | D | ICB | EATON | HMCP015*** | - | 15 | 575 | 3 | 15 | 575 | 3 | 10 | 11 | 1.1 | (1), (2), (3), (4) | E176513 VOL 1 section 5
|  | MC |  | XTCE012B | 5 | 12
|  | OLR |  | XTOB012B | 5 | 12
XT048 | D | ICB | EATON | HMCPE015*** |  | 15 | 200 | 3 | 65 | 200 | 3 | 3 | 11 | 1.1 | (1), (2), (3), (5) | E176513 VOL 1 section 5
|  | MC |  | XTCE015B | 5 | 15.5
|  | OLR |  | XTOB012B | 5 | 12
XT049 | D | ICB | EATON | HMCPE015*** |  | 15 | 208 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1.1 | (1), (2), (3), (5) | E176513 VOL 1 section 5
|  | MC |  | XTCE015B | 5 | 15.5
|  | OLR |  | XTOB012B | 5 | 12
XT050 | D | ICB | EATON | HMCPE030*** |  | 15 | 230 | 3 | 65 | 230 | 3 | 5 | 15.2 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE015B | 5 | 15.5
|  | OLR |  | XTOB016B | 5 | 16
XT051 | D | ICB | EATON | HMCPE030*** |  | 15 | 460 | 3 | 65 | 460 | 3 | 10 | 14 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE015B | 5 | 15.5
|  | OLR |  | XTOB016B | 5 | 16
XT052 | D | ICB | EATON | HMCP015*** |  | 15 | 575 | 3 | 15 | 575 | 3 | 10 | 11 | 1.1 | (1), (2), (3), (4) | E176513 VOL 1 section 5
|  | MC |  | XTCE015B | 5 | 15.5
|  | OLR |  | XTOB012B | 5 | 12
XT053 | D | ICB | EATON | HMCPE030*** | - | 30 | 200 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE018C | 5 | 18
|  | OLR |  | XTOB024C | 5 | 24
XT054 | D | ICB | EATON | HMCPE030*** | - | 15 | 208 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE018C | 5 | 18
|  | OLR |  | XTOB024C | 5 | 24
XT055 | D | ICB | EATON | HMCPE030*** | - | 15 | 230 | 3 | 65 | 230 | 3 | 5 | 15.2 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE018C | 5 | 18
|  | OLR |  | XTOB016C | 5 | 16
XT056 | D | ICB | EATON | HMCPE030*** | - | 15 | 460 | 3 | 65 | 460 | 3 | 10 | 14 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE018C | 5 | 18
|  | OLR |  | XTOB016B | 5 | 16
XT057 | D | ICB | EATON | HMCP030*** | - | 15 | 575 | 3 | 15 | 575 | 3 | 15 | 17 | 1.1 | (1), (2), (3), (4) | E176513 VOL 1 section 5
|  | MC |  | XTCE018C | 5 | 18
|  | OLR |  | XTOB024C | 5 | 24
XT058 | D | ICB | EATON | HMCPE050*** | - | 50 | 200 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE025C | 5 | 25
|  | OLR |  | XTOB032C | 5 | 32
XT059 | D | ICB | EATON | HMCPE050*** | - | 50 | 208 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE025C | 5 | 25
|  | OLR |  | XTOB032C | 5 | 32
XT060 | D | ICB | EATON | HMCPE030*** | - | 30 | 230 | 3 | 65 | 230 | 3 | 7.5 | 22 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE025C | 5 | 25
|  | OLR |  | XTOB024C | 5 | 24
XT061 | D | ICB | EATON | HMCPE030*** | - | 30 | 460 | 3 | 65 | 460 | 3 | 15 | 21 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE025C | 5 | 25
|  | OLR |  | XTOB024C | 5 | 24
XT062 | D | ICB | EATON | HMCP030*** | - | 30 | 575 | 3 | 15 | 575 | 3 | 20 | 22 | 1.1 | (1), (2), (3), (4) | E176513 VOL 1 section 5
|  | MC |  | XTCE025C | 5 | 25
|  | OLR |  | XTOB024C | 5 | 24
XT063 | D | ICB | EATON | HMCPE050*** | - | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE032C | 5 | 32
|  | OLR |  | XTOB032C | 5 | 32
XT064 | D | ICB | EATON | HMCPE050*** | - | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE032C | 5 | 32
|  | OLR |  | XTOB032C | 5 | 32
XT065 | D | ICB | EATON | HMCPE050*** | - | 50 | 230 | 3 | 65 | 230 | 3 | 10 | 28 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE032C | 5 | 32
|  | OLR |  | XTOB032C | 5 | 32
XT066 | D | ICB | EATON | HMCPE050*** | - | 50 | 460 | 3 | 65 | 460 | 3 | 20 | 27 | 1.1 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE032C | 5 | 32
|  | OLR |  | XTOB032C | 5 | 32
XT067 | D | ICB | EATON | HMCP050*** | - | 50 | 575 | 3 | 15 | 575 | 3 | 25 | 27 | 1.1 | (1), (2), (3), (4) | E176513 VOL 1 section 5
|  | MC |  | XTCE032C | 5 | 32
|  | OLR |  | XTOB032C | 5 | 32
XT068 | D | ICB | EATON | HMCPE050*** | - | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 2.8 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE040D | 5 | 40
|  | OLR |  | XTOB040D | 5 | 40
XT069 | D | ICB | EATON | HMCPE050*** | - | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 2.8 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE040D | 5 | 40
|  | OLR |  | XTOB040D | 5 | 40
XT070 | D | ICB | EATON | HMCPE100*** | - | 100 | 230 | 3 | 65 | 230 | 3 | 15 | 42 | 2.8 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE040D | 5 | 40
|  | OLR |  | XTOB057D | 5 | 57
XT071 | D | ICB | EATON | HMCPE050*** | - | 50 | 460 | 3 | 65 | 460 | 3 | 25 | 34 | 2.8 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE040D | 5 | 40
|  | OLR |  | XTOB040D | 5 | 40
XT073 | D | ICB | EATON | HMCPE050*** | - | 50 | 460 | 3 | 65 | 460 | 3 | 30 | 40 | 2.8 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE040D | 5 | 40
|  | OLR |  | XTOB040D | 5 | 40
XT071 | D | ICB | EATON | HMCP050*** | - | 50 | 575 | 3 | 15 | 575 | 3 | 30 | 32 | 10.68 | (1), (2), (3), (4) | E176513 VOL 1 section 5
|  | MC |  | XTCE040D | 5 | 40
|  | OLR |  | XTOB040D | 5 | 40
XT073 | D | ICB | EATON | HMCP100*** | - | 100 | 575 | 3 | 15 | 575 | 3 | 40 | 41 | 10.68 | (1), (2), (3), (4) | E176513 VOL 1 section 5
|  | MC |  | XTCE040D | 5 | 40
|  | OLR |  | XTOB057D | 5 | 57
XT074 | D | ICB | EATON | HMCPE100*** | - | 100 | 200 | 3 | 65 | 200 | 3 | 15 | 48.3 | 2.8 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE050D | 5 | 50
|  | OLR |  | XTOB057D | 5 | 57
XT075 | D | ICB | EATON | HMCPE100*** | - | 100 | 208 | 3 | 65 | 208 | 3 | 15 | 46.2 | 2.8 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE050D | 5 | 50
|  | OLR |  | XTOB057D | 5 | 57
XT076 | D | ICB | EATON | HMCPE100*** | - | 100 | 230 | 3 | 65 | 230 | 3 | 20 | 54 | 2.8 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE050D | 5 | 50
|  | OLR |  | XTOB057D | 5 | 57
XT077 | D | ICB | EATON | HMCPE100*** | - | 100 | 460 | 3 | 65 | 460 | 3 | 40 | 52 | 2.8 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE050D | 5 | 50
|  | OLR |  | XTOB057D | 5 | 57
XT078 | D | ICB | EATON | HMCPJ250*** | - | 250 | 575 | 3 | 35 | 575 | 3 | 50 | 52 | 10.68 | (1), (2), (3), (4) | E176513 VOL 1 section 5
|  | MC |  | XTCE050D | 5 | 50
|  | OLR |  | XTOB057D | 5 | 57
XT079 | D | ICB | EATON | HMCPE100*** | - | 100 | 200 | 3 | 65 | 200 | 3 | 20 | 62.1 | 2.8 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE065D | 5 | 65
|  | OLR |  | XTOB065D | 5 | 65
XT080 | D | ICB | EATON | HMCPE100*** | - | 100 | 208 | 3 | 65 | 208 | 3 | 20 | 59.4 | 2.8 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE065D | 5 | 65
|  | OLR |  | XTOB065D | 5 | 65
XT081 | D | ICB | EATON | HMCPE100*** | - | 100 | 230 | 3 | 65 | 230 | 3 | 25 | 68 | 2.8 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE065D | 5 | 65
|  | OLR |  | XTOB065D | 5 | 65
XT082 | D | ICB | EATON | HMCPE100*** | - | 100 | 460 | 3 | 65 | 460 | 3 | 50 | 65 | 2.8 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE065D | 5 | 65
|  | OLR |  | XTOB065D | 5 | 65
XT083 | D | ICB | EATON | HMCPJ250*** | - | 250 | 575 | 3 | 35 | 575 | 3 | 60 | 62 | 10.68 | (1), (2), (3), (4) | E176513 VOL 1 section 5
|  | MC |  | XTCE065D | 5 | 65
|  | OLR |  | XTOB065D | 5 | 65
XT084 | D | ICB | EATON | HMCPE100*** | - | 100 | 200 | 3 | 65 | 200 | 3 | 25 | 78.2 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE080F | 10 | 115
|  | OLR |  | XTOB100G | 10 | 100
XT085 | D | ICB | EATON | HMCPE100*** | - | 100 | 208 | 3 | 65 | 208 | 3 | 25 | 74.8 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE080F | 10 | 115
|  | OLR |  | XTOB100G | 10 | 100
XT086 | D | ICB | EATON | HMCPE100*** | - | 100 | 230 | 3 | 65 | 230 | 3 | 30 | 80 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE080F | 10 | 115
|  | OLR |  | XTOB100G | 10 | 100
XT087 | D | ICB | EATON | HMCPE100*** | - | 100 | 460 | 3 | 65 | 460 | 3 | 60 | 77 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE080F | 10 | 115
|  | OLR |  | XTOB100G | 10 | 100
XT088 | D | ICB | EATON | HMCPJ250*** | - | 250 | 575 | 3 | 35 | 575 | 3 | 75 | 77 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE080F | 10 | 115
|  | OLR |  | XTOB100G | 10 | 100
XT089 | D | ICB | EATON | HMCPE100*** | - | 100 | 200 | 3 | 65 | 200 | 3 | 25 | 78.2 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE095F | 10 | 115
|  | OLR |  | XTOB100G | 10 | 100
XT090 | D | ICB | EATON | HMCPE100*** | - | 100 | 208 | 3 | 65 | 208 | 3 | 25 | 74.8 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE095F | 10 | 115
|  | OLR |  | XTOB100G | 10 | 100
XT091 | D | ICB | EATON | HMCPJ250*** | - | 250 | 230 | 3 | 65 | 230 | 3 | 40 | 104 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE095F | 10 | 115
|  | OLR |  | XTOB125G | 10 | 125
XT092 | D | ICB | EATON | HMCPJ250*** | - | 250 | 460 | 3 | 65 | 460 | 3 | 75 | 96 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE095F | 10 | 115
|  | OLR |  | XTOB100G | 10 | 100
XT093 | D | ICB | EATON | HMCPJ250*** | - | 250 | 575 | 3 | 35 | 575 | 3 | 100 | 99 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE095F | 10 | 115
|  | OLR |  | XTOB100G | 10 | 100
XT094 | D | ICB | EATON | HMCPJ250*** | - | 250 | 200 | 3 | 65 | 200 | 3 | 30 | 92 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE115G | 10 | 115
|  | OLR |  | XTOB100G | 10 | 100
XT095 | D | ICB | EATON | HMCPJ250*** | - | 250 | 200 | 3 | 65 | 200 | 3 | 40 | 120 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE115G | 10 | 115
|  | OLR |  | XTOB125G | 10 | 125
XT096 | D | ICB | EATON | HMCPJ250*** | - | 250 | 208 | 3 | 65 | 208 | 3 | 30 | 88 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE115G | 10 | 115
|  | OLR |  | XTOB100G | 10 | 100
XT097 | D | ICB | EATON | HMCPJ250*** | - | 250 | 208 | 3 | 65 | 208 | 3 | 40 | 114 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE115G | 10 | 115
|  | OLR |  | XTOB125G | 10 | 125
XT098 | D | ICB | EATON | HMCPJ250*** | - | 250 | 230 | 3 | 35 | 230 | 3 | 50 | 130 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE115G | 10 | 115
|  | OLR |  | XTOB150G | 10 | 150
XT099 | D | ICB | EATON | HMCPJ250*** | - | 250 | 460 | 3 | 35 | 460 | 3 | 100 | 124 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE115G | 10 | 115
|  | OLR |  | XTOB125G | 10 | 125
XT100 | D | ICB | EATON | HMCPJ250*** | - | 250 | 575 | 3 | 35 | 575 | 3 | 125 | 125 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE115G | 10 | 115
|  | OLR |  | XTOB125G | 10 | 125
XT101 | D | ICB | EATON | HMCPJ250*** | - | 250 | 200 | 3 | 65 | 200 | 3 | 40 | 120 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE150G | 10 | 150
|  | OLR |  | XTOB125G | 10 | 125
XT102 | D | ICB | EATON | HMCPJ250*** | - | 250 | 208 | 3 | 65 | 208 | 3 | 40 | 114 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE150G | 10 | 150
|  | OLR |  | XTOB125G | 10 | 125
XT103 | D | ICB | EATON | HMCPJ250*** | - | 250 | 230 | 3 | 65 | 230 | 3 | 60 | 154 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE150G | 10 | 150
|  | OLR |  | XTOB150G | 10 | 150
XT104 | D | ICB | EATON | HMCPJ250*** | - | 250 | 460 | 3 | 65 | 460 | 3 | 125 | 156 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE150G | 10 | 150
|  | OLR |  | XTOB150G | 10 | 150
XT105 | D | ICB | EATON | HMCPJ250*** | - | 250 | 575 | 3 | 35 | 575 | 3 | 125 | 125 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE150G | 10 | 150
|  | OLR |  | XTOB125G | 10 | 125
XT106 | D | ICB | EATON | HMCPJ250*** | - | 250 | 200 | 3 | 65 | 200 | 3 | 50 | 150 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTC E185L | 18 | 185
|  | OLR |  | XTOB160L | 18 | 160
XT107 | D | ICB | EATON | HMCPJ250*** | - | 250 | 208 | 3 | 65 | 208 | 3 | 50 | 143 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTC E185L | 18 | 185
|  | OLR |  | XTOB160L | 18 | 160
XT108 | D | ICB | EATON | HMCPJ250*** | - | 250 | 230 | 3 | 65 | 230 | 3 | 60 | 154 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTC E185L | 18 | 185
|  | OLR |  | XTOB160L | 18 | 160
XT109 | D | ICB | EATON | HMCPJ250*** | - | 250 | 460 | 3 | 65 | 460 | 3 | 125 | 156 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTC E185L | 18 | 185
|  | OLR |  | XTOB160L | 18 | 160
XT110 | D | ICB | EATON | HMCP400*** | - | 400 | 575 | 3 | 35 | 575 | 3 | 150 | 144 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTC E185L | 18 | 185
|  | OLR |  | XTOB160L | 18 | 160
XT111 | D | ICB | EATON | HMCPJ250*** | - | 250 | 200 | 3 | 65 | 200 | 3 | 60 | 177 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE225L | 18 | 225
|  | OLR |  | XTOB220L | 18 | 220
XT112 | D | ICB | EATON | HMCPJ250*** | - | 250 | 208 | 3 | 65 | 208 | 3 | 60 | 169 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE225L | 18 | 225
|  | OLR |  | XTOB220L | 18 | 220
XT113 | D | ICB | EATON | HMCPJ250*** | - | 250 | 230 | 3 | 65 | 230 | 3 | 75 | 192 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE225L | 18 | 225
|  | OLR |  | XTOB220L | 18 | 220
XT114 | D | ICB | EATON | HMCPJ250*** | - | 250 | 460 | 3 | 65 | 460 | 3 | 150 | 180 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE225L | 18 | 225
|  | OLR |  | XTOB220L | 18 | 220
XT115 | D | ICB | EATON | HMCP400*** | - | 400 | 575 | 3 | 35 | 575 | 3 | 200 | 192 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE225L | 18 | 225
|  | OLR |  | XTOB220L | 18 | 220
XT116 | D | ICB | EATON | HMCP400*** | - | 400 | 200 | 3 | 65 | 200 | 3 | 75 | 221 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE250L | 18 | 250
|  | OLR |  | XTOB250L | 18 | 250
XT117 | D | ICB | EATON | HMCP400*** | - | 400 | 208 | 3 | 65 | 208 | 3 | 75 | 211 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE250L | 18 | 250
|  | OLR |  | XTOB250L | 18 | 250
XT118 | D | ICB | EATON | HMCP400*** | - | 400 | 230 | 3 | 65 | 230 | 3 | 100 | 248 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE250L | 18 | 250
|  | OLR |  | XTOB250L | 18 | 250
XT119 | D | ICB | EATON | HMCP400*** | - | 400 | 460 | 3 | 65 | 460 | 3 | 200 | 240 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE250L | 18 | 250
|  | OLR |  | XTOB250L | 18 | 250
XT120 | D | ICB | EATON | HMCP400*** | - | 400 | 575 | 3 | 35 | 575 | 3 | 250 | 242 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE250L | 18 | 250
|  | OLR |  | XTOB250L | 18 | 250
XT121 | D | ICB | EATON | HMCP400*** | - | 400 | 200 | 3 | 25 | 200 | 3 | 100 | 285 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE300M | 18 | 300
|  | OLR |  | XTOT290C3S | 18 | 290
XT122 | D | ICB | EATON | HMCP400*** | - | 400 | 208 | 3 | 25 | 208 | 3 | 100 | 273 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE300M | 18 | 300
|  | OLR |  | XTOT290C3S | 18 | 290
XT123 | D | ICB | EATON | HMCP400*** | - | 400 | 230 | 3 | 25 | 230 | 3 | 125 | 312 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE300M | 18 | 300
|  | OLR |  | XTOT400C3S | 18 | 400
XT124 | D | ICB | EATON | HMCP400*** | - | 400 | 460 | 3 | 25 | 460 | 3 | 250 | 302 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE300M | 18 | 300
|  | OLR |  | XTOT400C3S | 18 | 400
XT125 | D | ICB | EATON | HMCP600*** | - | 600 | 575 | 3 | 25 | 575 | 3 | 300 | 289 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE300M | 18 | 300
|  | OLR |  | XTOT400C3S | 18 | 400
XT126 | D | ICB | EATON | HMCP600*** | - | 600 | 200 | 3 | 25 | 200 | 3 | 125 | 359 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE400M | 18 | 400
|  | OLR |  | XTOT400C3S | 18 | 400
XT127 | D | ICB | EATON | HMCP600*** | - | 600 | 208 | 3 | 25 | 208 | 3 | 125 | 343 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE400M | 18 | 400
|  | OLR |  | XTOT400C3S | 18 | 400
XT128 | D | ICB | EATON | HMCP600*** | - | 600 | 230 | 3 | 25 | 230 | 3 | 150 | 360 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE400M | 18 | 400
|  | OLR |  | XTOT400C3S | 18 | 400
XT129 | D | ICB | EATON | HMCP600*** | - | 400 | 460 | 3 | 25 | 460 | 3 | 300 | 361 | 10.68 | (1), (2), (3) | E176513 VOL 1 section 5
|  | MC |  | XTCE400M | 18 | 400
|  | OLR |  | XTOT400C3S | 18 | 400
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(3) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(4) = When specified, insulation barrier required under the starter as described in report
(5) = Use #12 AWG wire for line and load

## XT Type D #2
Issued: 2010-05-27
Last Revised: 2012-02-07
Database Identification Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Enclosure Volume, cubic inches. Type (1and/or12) | Conditions of Use | Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating
XT141 | D | ICB | EATON | HMCPS015E0C | 480 | 3 | * | 15 | -- | 480 | 3 | 100 | 4.8 | 3 | 8232.3111 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE007B | 480 |  | 5 | 4.8 | 3 | 480
|  | OLR |  | XTOB006BC1 | 480 |  | 5 | 4.8 | 3 | 480
XT142 | D | ICB | EATON | HMCPS030H1C | 480 | 3 | * | 30 | -- | 480 | 3 | 100 | 7.6 | 5 | 8232.3111 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE009B | 480 |  | 5 | 7.6 | 5 | 480
|  | OLR |  | XTOB010BC1 | 480 |  | 5 | 10 | 5 | 480
XT143 | D | ICB | EATON | HMCPS030H1C | 480 | 3 | * | 30 | -- | 480 | 3 | 100 | 11 | 7.5 | 8232.3111 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE012B | 480 |  | 5 | 14 | 10 | 480
|  | OLR |  | XTOB012BC1 | 480 |  | 5 | 12 | 7.5 | 480
XT144 | D | ICB | EATON | HMCPS050K2C | 480 | 3 | * | 50 | -- | 480 | 3 | 100 | 14 | 10 | 8232.3111 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE015B | 480 |  | 5 | 14 | 10 | 480
|  | OLR |  | XTOB016BC1 | 480 |  | 5 | 16 | 10 | 480
XT145 | D | ICB | EATON | HMCPS050K2C | 480 | 3 | * | 50 | -- | 480 | 3 | 100 | 21 | 15 | 13945.6321 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE040D | 480 |  | 5 | 40 | 30 | 480
|  | OLR |  | XTOB040DC1 | 480 |  | 5 | 40 | 30 | 480
XT146 | D | ICB | EATON | HMCPS100R3C | 480 | 3 | * | 100 | -- | 480 | 3 | 100 | 27 | 20 | 13945.6321 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE040D | 480 |  | 5 | 40 | 30 | 480
|  | OLR |  | XTOB040DC1 | 480 |  | 5 | 40 | 30 | 480
XT147 | D | ICB | EATON | HMCPS150(T,U)4C | 480 | 3 | * | 150 | -- | 480 | 3 | 100 | 34 | 25 | 13945.6321 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE040D | 480 |  | 5 | 40 | 30 | 480
|  | OLR |  | XTOB040DC1 | 480 |  | 5 | 40 | 30 | 480
XT148 | D | ICB | EATON | HMCPS150(T,U)4C | 480 | 3 | * | 150 | -- | 480 | 3 | 100 | 40 | 30 | 13945.6321 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE050D | 480 |  | 5 | 52 | 40 | 480
|  | OLR |  | XTOB057DC1 | 480 |  | 5 | 57 | 40 | 480
XT150 | D | ICB | EATON | HMCPS150(T,U)4C | 480 | 3 | * | 150 | -- | 480 | 3 | 100 | 52 | 40 | 13945.6321 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE065D | 480 |  | 5 | 65 | 50 | 480
|  | OLR |  | XTOB065DC1 | 480 |  | 5 | 65 | 50 | 480
XT151 | D | ICB | EATON | HMCPS150(T,U)4C | 480 | 3 | * | 150 | -- | 480 | 3 | 100 | 65 | 50 | 13945.6321 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE072D | 480 |  | 5 | 65 | 50 | 480
|  | OLR |  | XTOB075DC1 | 480 |  | 5 | 75 | 50 | 480
XT152 | D | ICB | EATON | HMCPS150(T,U)4C | 480 | 3 | * | 150 | -- | 480 | 3 | 100 | 77 | 60 | 23889.7795 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE080F | 480 |  | 10 | 77 | 60 | 480
|  | OLR |  | XTOB100GC1 | 480 |  | 10 | 100 | 75 | 480
XT153 | D | ICB | EATON | HMCPS150(T,U)4C | 480 | 3 | * | 150 | -- | 480 | 3 | 100 | 96 | 75 | 23889.7795 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE0115G | 480 |  | 10 | 124 | 100 | 480
|  | OLR |  | XTOB100GC1 | 480 |  | 10 | 100 | 75 | 480
XT154 | D | ICB | EATON | HMCPS150(T,U)4C | 480 | 3 | * | 150 | -- | 480 | 3 | 100 | 96 | 75 | 23889.7795 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE115G | 480 |  | 10 | 124 | 100 | 480
|  | OLR |  | XTOB125GC1 | 480 |  | 10 | 125 | 100 | 480
XT155 | D | ICB | EATON | HMCP250(F,G,J,K,L)5C | 480 | 3 | * | 250 | -- | 480 | 3 | 100 | 96 | 75 | 39341.3405 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE115G | 480 |  | 10 | 124 | 100 | 480
|  | OLR |  | XTOB125GC1 | 480 |  | 10 | 125 | 100 | 480
XT156 | D | ICB | EATON | HMCP250(J,K,L,W)5C | 480 | 3 | * | 250 | -- | 480 | 3 | 100 | 124 | 100 | 39341.3405 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE150G | 480 |  | 10 | 156 | 125 | 480
|  | OLR |  | XTOB150GC1 | 480 |  | 10 | 150 | 100 | 480
XT157 | D | ICB | EATON | HMCP250(K,L,W)5C | 480 | 3 | * | 250 | -- | 480 | 3 | 100 | 156 | 125 | 46071 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE170G | 480 |  | 10 | 156 | 125 | 480
|  | OLR |  | XTOB175GC1 | 480 |  | 10 | 175 | 125 | 480
XT158 | D | ICB | EATON | HMCP250(L,W)5C | 480 | 3 | * | 250 | -- | 480 | 3 | 100 | 180 | 150 | 46071 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE225L | 480 |  | 10 | 270 | 200 | 480
|  | OLR |  | XTOB220LC1 | 480 |  | 10 | 220 | 150 | 480
XT159 | D | ICB | EATON | HMCP400(K,L,W,N,R,X)5C | 480 | 3 | * | 400 | -- | 480 | 3 | 100 | 156 | 125 | 46071 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE185L | 480 |  | 18 | 180 | 150 | 480
|  | OLR |  | XTOB160LC1 | 480 |  | 18 | 160 | 125 | 480
XT160 | D | ICB | EATON | HMCP400(L,W,N,R,X,Y)5C | 480 | 3 | * | 400 | -- | 480 | 3 | 100 | 180 | 150 | 46071 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE225L | 480 |  | 18 | 180 | 150 | 480
|  | OLR |  | XTOB220LC1 | 480 |  | 18 | 220 | 150 | 480
XT161 | D | ICB | EATON | HMCP400(N,R,X,Y)5C | 480 | 3 | * | 400 | -- | 480 | 3 | 100 | 240 | 200 | 76644 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE250L | 480 |  | 18 | 240 | 200 | 480
|  | OLR |  | XTOB250LC1 | 480 |  | 18 | 250 | 200 | 480
XT162 | D | ICB | Eaton | HMCPS150(T,U)4C | 480 | 3 | * | 150 | \ | 480 | 3 | 100 | 34 | 25 | 13946 | 1, 4, 5 | E134360, Vol.1, Sec. 16
|  | MC | Eaton | XTCE040D | 480 |  | 5 | 40 | 30
|  | OLR |  | XTOB040DC1 | 480 |  | 5 | 40 | 30
XT163 | D | ICB | Eaton | HMCPS150(T,U)4C | 480 | 3 | * | 150 | \ | 480 | 3 | 100 | 40 | 30 | 13946 | 1, 4, 5 | E134360, Vol.1, Sec. 16
|  | MC | Eaton | XTCE050D | 480 |  | 5 | 52 | 40
|  | OLR |  | XTOB057DC1 | 480 |  | 5 | 52 | 40
XT164 | D | ICB | Eaton | HMCPS150(T,U)4C | 480 | 3 | * | 150 | \ | 480 | 3 | 100 | 52 | 40 | 13946 | 1, 4, 5 | E134360, Vol.1, Sec. 16
|  | MC | Eaton | XTCE065D | 480 |  | 5 | 65 | 50
|  | OLR |  | XTOB065DC1 | 480 |  | 5 | 52 | 50
XT165 | D | ICB | Eaton | HMCPS150(T,U)4C | 480 | 3 | * | 150 | \ | 480 | 3 | 100 | 65 | 50 | 13946 | 1, 4, 5 | E134360, Vol.1, Sec. 16
|  | MC | Eaton | XTCE072D | 480 |  | 5 | 65 | 50
|  | OLR |  | XTOB075DC1 | 480 |  | 5 | 65 | 50
XT166 | D | ICB | Eaton | HMCPS150(T,U)4C | 480 | 3 | * | 150 | \ | 480 | 3 | 100 | 77 | 60 | 23890 | 1, 4, 5 | E134360, Vol.1, Sec. 16
|  | MC | Eaton | XTCE080F | 480 |  | 10 | 77 | 60
|  | OLR |  | XTOB100GC1 | 480 |  | 10 | 96 | 75
XT167 | D | ICB | Eaton | HMCPS150(T,U)4C | 480 | 3 | * | 150 | \ | 480 | 3 | 100 | 96 | 75 | 23890 | 1, 4, 5 | E134360, Vol.1, Sec. 16
|  | MC | Eaton | XTCE095F | 480 |  | 10 | 96 | 75
|  | OLR |  | XTOB125GC1 | 480 |  | 10 | 96 | 75
XT168 | D | ICB | Eaton | HMCPS150(T,U)4C | 480 | 3 | * | 150 | \ | 480 | 3 | 100 | 124 | 100 | 23890 | 1, 4, 5 | E134360, Vol.1, Sec. 16
|  | MC | Eaton | XTCE150G | 480 |  | 10 | 156 | 125
|  | OLR |  | XTOB150GC1 | 480 |  | 10 | 156 | 125
XT169 | D | ICB | Eaton | HMCP250(F,G,J,K,L)5C | 480 | 3 | * | 250 | \ | 480 | 3 | 100 | 96 | 75 | 39341 | 1, 4, 5 | E134360, Vol.1, Sec. 16
|  | MC | Eaton | XTCE115G | 480 |  | 10 | 124 | 100
|  | OLR |  | XTOB150GC1 | 480 |  | 10 | 156 | 125
XT170 | D | ICB | Eaton | HMCP250(J,K,L,W)5C | 480 | 3 | * | 250 | \ | 480 | 3 | 100 | 124 | 100 | 39341 | 1, 4, 5 | E134360, Vol.1, Sec. 16
|  | MC | Eaton | XTCE150G | 480 |  | 10 | 156 | 125
|  | OLR |  | XTOB150GC1 | 480 |  | 10 | 150 | 125
XT171 | D | ICB | Eaton | HMCP250(K,L,W)5C | 480 | 3 | * | 250 | \ | 480 | 3 | 100 | 156 | 125 | 46071 | 1, 4, 5 | E134360, Vol.1, Sec. 16
|  | MC | Eaton | XTCE170G | 480 |  | 10 | 156 | 125
|  | OLR |  | XTOB175GC1 | 480 |  | 10 | 156 | 125
XT172 | D | ICB | Eaton | HMCP250(L,W)5C | 480 | 3 | * | 250 | \ | 480 | 3 | 100 | 180 | 150 | 46071 | 1, 4, 5 | E134360, Vol.1, Sec. 16
|  | MC | Eaton | XTCE225L | 480 |  | 18 | 180 | 200
|  | OLR |  | XTOB220LC1 | 480 |  | 18 | 180 | 150
XT173 | D | ICB | Eaton | HMCP400(K,L,W,N,R,X)5C | 480 | 3 | * | 400 | \ | 480 | 3 | 100 | 156 | 125 | 46071 | 1, 4, 5 | E134360, Vol.1, Sec. 16
|  | MC | Eaton | XTCE185L | 480 |  | 18 | 180 | 150
|  | OLR |  | XTOB160LC1 | 480 |  | 18 | 156 | 125
XT174 | D | ICB | Eaton | HMCP400(L,W,N,R,X,Y)5C | 480 | 3 | * | 400 | \ | 480 | 3 | 100 | 180 | 150 | 46071 | 1, 4, 5 | E134360, Vol.1, Sec. 16
|  | MC | Eaton | XTCE225L | 480 |  | 18 | 180 | 150
|  | OLR |  | XTOB220LC1 | 480 |  | 18 | 180 | 150
XT175 | D | ICB | Eaton | HMCP400(N,R,X,Y)5C | 480 | 3 | * | 400 | \ | 480 | 3 | 100 | 240 | 200 | 46071 | 1, 4, 5 | E134360, Vol.1, Sec. 16
|  | MC | Eaton | XTCE250L | 480 |  | 18 | 240 | 200 | 480
|  | OLR |  | XTOB250LC1 | 480 |  | 18 | 240 | 200 | 480
XT178 | D | ICB | Eaton | HMCPS150(T,U)4C | 480 | 3 | * | 150 | \ | 480 | 3 | 100 | 34 | 25 | 13946 | 1, 4, 5 | E134360, Vol.1, Sec. 17
|  | MC | Eaton | XTCE040D | 480 |  | 5 | 40 | 30 | 480
|  | OLR |  | XTOB040DC1 | 480 |  | 5 | 40 | 30 | 480
XT179 | D | ICB | Eaton | HMCPS150(T,U)4C | 480 | 3 | * | 150 | \ | 480 | 3 | 100 | 40 | 30 | 13946 | 1, 4, 5 | E134360, Vol.1, Sec. 17
|  | MC | Eaton | XTCE050D | 480 |  | 5 | 52 | 40
|  | OLR |  | XTOB057DC1 | 480 |  | 5 | 52 | 40
XT180 | D | ICB | Eaton | HMCPS150(T,U)4C | 480 | 3 | * | 150 | \ | 480 | 3 | 100 | 52 | 40 | 13946 | 1, 4, 5 | E134360, Vol.1, Sec. 17
|  | MC | Eaton | XTCE065D | 480 |  | 5 | 65 | 50
|  | OLR |  | XTOB065DC1 | 480 |  | 5 | 65 | 50
XT181 | D | ICB | Eaton | HMCPS150(T,U)4C | 480 | 3 | * | 150 | \ | 480 | 3 | 100 | 65 | 50 | 13946 | 1, 4, 5 | E134360, Vol.1, Sec. 17
|  | MC | Eaton | XTCE072D | 480 |  | 5 | 65 | 50
|  | OLR |  | XTOB075DC1 | 480 |  | 5 | 65 | 50
XT182 | D | ICB | Eaton | HMCPS150(T,U)4C | 480 | 3 | * | 150 | \ | 480 | 3 | 100 | 77 | 60 | 23890 | 1, 4, 5 | E134360, Vol.1, Sec. 17
|  | MC | Eaton | XTCE080F | 480 |  | 10 | 77 | 60
|  | OLR |  | XTOB100GC1 | 480 |  | 10 | 96 | 75
XT183 | D | ICB | Eaton | HMCPS150(T,U)4C | 480 | 3 | * | 150 | \ | 480 | 3 | 100 | 96 | 75 | 23890 | 1, 4, 5 | E134360, Vol.1, Sec. 17
|  | MC | Eaton | XTCE095F | 480 |  | 10 | 96 | 75
|  | OLR |  | XTOB125GC1 | 480 |  | 10 | 96 | 75
XT184 | D | ICB | Eaton | HMCPS150(T,U)4C | 480 | 3 | * | 150 | \ | 480 | 3 | 100 | 124 | 100 | 23890 | 1, 4, 5 | E134360, Vol.1, Sec. 17
|  | MC | Eaton | XTCE150G | 480 |  | 10 | 156 | 125
|  | OLR |  | XTOB150GC1 | 480 |  | 10 | 150 | 125
XT185 | D | ICB | Eaton | HMCP250(F,G,J,K,L)5C | 480 | 3 | * | 250 | \ | 480 | 3 | 100 | 96 | 75 | 39341 | 1, 4, 5 | E134360, Vol.1, Sec. 17
|  | MC | Eaton | XTCE115G | 480 |  | 10 | 124 | 100
|  | OLR |  | XTOB150GC1 | 480 |  | 10 | 125 | 125
XT186 | D | ICB | Eaton | HMCP250(J,K,L,W)5C | 480 | 3 | * | 250 | \ | 480 | 3 | 100 | 124 | 100 | 39341 | 1, 4, 5 | E134360, Vol.1, Sec. 17
|  | MC | Eaton | XTCE150G | 480 |  | 10 | 156 | 125
|  | OLR |  | XTOB150GC1 | 480 |  | 10 | 156 | 125
XT187 | D | ICB | Eaton | HMCP250(K,L,W)5C | 480 | 3 | * | 250 | \ | 480 | 3 | 100 | 156 | 125 | 39341 | 1, 4, 5 | E134360, Vol.1, Sec. 17
|  | MC | Eaton | XTCE170G | 480 |  | 10 | 156 | 125
|  | OLR |  | XTOB175GC1 | 480 |  | 10 | 156 | 125
XT188 | D | ICB | Eaton | HMCP250(K,L,W)5C | 480 | 3 | * | 400 | \ | 480 | 3 | 100 | 156 | 125 | 46071 | 1, 4, 5 | E134360, Vol.1, Sec. 17
|  | MC | Eaton | XTCE185L | 480 |  | 18 | 180 | 150
|  | OLR |  | XTOB160LC1 | 480 |  | 18 | 156 | 125
XT189 | D | ICB | Eaton | HMCPS030H1C | 480 | 3 | * | 30 | \ | 480 | 3 | 100 | 11 | 7.5 | 6983 | 1, 4, 5 | E134360, Vol.1, Sec. 19
|  | MC | Eaton | XTCE012B | 480 |  | 5 | 14 | 10
|  | OLR |  | XTOB012BC1 | 480 |  | 5 | 11 | 7.5
XT190 | D | ICB | Eaton | HMCPS050K2C | 480 | 3 | * | 50 | \ | 480 | 3 | 100 | 14 | 10 | 6983 | 1, 4, 5 | E134360, Vol.1, Sec. 19
|  | MC | Eaton | XTCE015B | 480 |  | 5 | 14 | 10
|  | OLR |  | XTOB016BC1 | 480 |  | 5 | 14 | 10
XT191 | D | ICB | Eaton | HMCPS050K2C | 480 | 3 | * | 50 | \ | 480 | 3 | 100 | 14 | 10 | 6983 | 1, 4, 5 | E134360, Vol.1, Sec. 19
|  | MC | Eaton | XTCE040D | 480 |  | 5 | 40 | 30
|  | OLR |  | XTOB040DC1 | 480 |  | 5 | 40 | 30
XT192 | D | ICB | Eaton | HMCPS050K2C | 480 | 3 | * | 50 | \ | 480 | 3 | 100 | 21 | 15 | 6983 | 1, 4, 5 | E134360, Vol.1, Sec. 19
|  | MC | Eaton | XTCE040D | 480 |  | 5 | 40 | 30
|  | OLR |  | XTOB040DC1 | 480 |  | 5 | 40 | 30
XT193 | D | ICB | Eaton | HMCPS100R3C | 480 | 3 | * | 100 | \ | 480 | 3 | 100 | 27 | 20 | 6983 | 1, 4, 5 | E134360, Vol.1, Sec. 19
|  | MC | Eaton | XTCE040D | 480 |  | 5 | 40 | 30
|  | OLR |  | XTOB040DC1 | 480 |  | 5 | 40 | 30
XT194 | D | ICB | Eaton | HMCPS150(T,U)4C | 480 | 3 | * | 150 | \ | 480 | 3 | 100 | 34 | 25 | 6983 | 1, 4, 5 | E134360, Vol.1, Sec. 19
|  | MC | Eaton | XTCE040D | 480 |  | 5 | 40 | 30
|  | OLR |  | XTOB040DC1 | 480 |  | 5 | 40 | 30
XT195 | D | ICB | Eaton | HMCPS150(T,U)4C | 480 | 3 | * | 150 | \ | 480 | 3 | 100 | 40 | 30 | 12751 | 1, 4, 5 | E134360, Vol.1, Sec. 19
|  | MC | Eaton | XTCE050D | 480 |  | 5 | 52 | 40
|  | OLR |  | XTOB057DC1 | 480 |  | 5 | 52 | 40
XT196 | D | ICB | Eaton | HMCPS150(T,U)4C | 480 | 3 | * | 150 | \ | 480 | 3 | 100 | 52 | 40 | 12751 | 1, 4, 5 | E134360, Vol.1, Sec. 19
|  | MC | Eaton | XTCE065D | 480 |  | 5 | 65 | 50
|  | OLR |  | XTOB065DC1 | 480 |  | 5 | 65 | 50
XT197 | D | ICB | Eaton | HMCPS150(T,U)4C | 480 | 3 | * | 150 | \ | 480 | 3 | 100 | 65 | 50 | 12751 | 1, 4, 5 | E134360, Vol.1, Sec. 19
|  | MC | Eaton | XTCE072D | 480 |  | 5 | 65 | 50
|  | OLR |  | XTOB075DC1 | 480 |  | 5 | 65 | 50
XT198 | D | ICB | Eaton | HMCPS150(T,U)4C | 480 | 3 | * | 150 | \ | 480 | 3 | 100 | 77 | 60 | 12751 | 1, 4, 5 | E134360, Vol.1, Sec. 19
|  | MC | Eaton | XTCE080F | 480 |  | 10 | 77 | 60
|  | OLR |  | XTOB100GC1 | 480 |  | 10 | 96 | 75
XT199 | D | ICB | Eaton | HMCPS150(T,U)4C | 480 | 3 | * | 150 | \ | 480 | 3 | 100 | 96 | 75 | 12751 | 1, 4, 5 | E134360, Vol.1, Sec. 19
|  | MC | Eaton | XTCE095F | 480 |  | 10 | 96 | 75
|  | OLR |  | XTOB125GC1 | 480 |  | 10 | 96 | 75
XT200 | D | ICB | Eaton | HMCPS150(T,U)4C | 480 | 3 | * | 150 | \ | 480 | 3 | 100 | 124 | 100 | 12751 | Type 1, 12 only. 1, 4, 5 | E134360, Vol.1, Sec. 19
|  | MC | Eaton | XTCE150G | 480 |  | 10 | 156 | 125
|  | OLR |  | XTOB150GC1 | 480 |  | 10 | 156 | 125
XT201 | D | ICB | Eaton | HMCP250(F,G,J,K,L)5C | 480 | 3 | * | 250 | \ | 480 | 3 | 100 | 96 | 75 | 25381 | Type 1, 12 only. 1, 4, 5 | E134360, Vol.1, Sec. 19
|  | MC | Eaton | XTCE115G | 480 |  | 10 | 124 | 100
|  | OLR |  | XTOB150GC1 | 480 |  | 10 | 156 | 125
XT202 | D | ICB | Eaton | HMCP250(J,K,L,W)5C | 480 | 3 | * | 250 | \ | 480 | 3 | 100 | 124 | 100 | 25381 | Type 1, 12 only. 1, 4, 5 | E134360, Vol.1, Sec. 19
|  | MC | Eaton | XTCE150G | 480 |  | 10 | 156 | 125
|  | OLR |  | XTOB150GC1 | 480 |  | 10 | 156 | 125
XT203 | D | ICB | Eaton | HMCP250(K,L,W)5C | 480 | 3 | * | 250 | \ | 480 | 3 | 100 | 156 | 125 | 25381 | Type 1, 12 only. 1, 4, 5 | E134360, Vol.1, Sec. 19
|  | MC | Eaton | XTCE170G | 480 |  | 10 | 156 | 125
|  | OLR |  | XTOB175GC1 | 480 |  | 10 | 156 | 125
XT204 | D | ICB | Eaton | HMCP250(L,W)5C | 480 | 3 | * | 250 | \ | 480 | 3 | 100 | 180 | 150 | 25381 | Type 1, 12 only. 1, 4, 5 | E134360, Vol.1, Sec. 19
|  | MC | Eaton | XTCE225L | 480 |  | 18 | 270 | 200
|  | OLR |  | XTOB220LC1 | 480 |  | 18 | 180 | 150
XT205 | D | ICB | Eaton | HMCP400(K,L,W,N,R,X)5C | 480 | 3 | * | 400 | \ | 480 | 3 | 100 | 156 | 125 | 46071 | Type 1, 12 only. 1, 4, 5 | E134360, Vol.1, Sec. 19
|  | MC | Eaton | XTCE185L | 480 |  | 18 | 180 | 150
|  | OLR |  | XTOB160LC1 | 480 |  | 18 | 156 | 125
XT206 | D | ICB | Eaton | HMCP400(L,W,N,R,X,Y)5C | 480 | 3 | * | 400 | \ | 480 | 3 | 100 | 180 | 150 | 46071 | Type 1 only. 1, 4, 5 | E134360, Vol.1, Sec. 19
|  | MC | Eaton | XTCE225L | 480 |  | 18 | 180 | 150
|  | OLR |  | XTOB220LC1 | 480 |  | 18 | 180 | 150
XT207 | D | ICB | Eaton | HMCP400(N,R,X,Y)5C | 480 | 3 | * | 400 | \ | 480 | 3 | 100 | 240 | 200 | 46071 | Type 1 only. 1, 4, 5 | E134360, Vol.1, Sec. 19
|  | MC | Eaton | XTCE250L | 480 |  | 18 | 240 | 200
|  | OLR |  | XTOB250LC1 | 480 |  | 18 | 240 | 200
XT208 | D | ICB | EATON | HMCPS050K2C | 480 | 3 | * | 50 | -- | 480 | 3 | 100 | 16 | 10 | 13946 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE040D | 480 |  | 5 | 40 | 30 | 480
|  | OLR |  | XTOB016DC1 | 480 |  | 5 | 16 | 10 | 480
XT209 | D | ICB | EATON | HMCPS050K2C | 480 | 3 | * | 50 | -- | 480 | 3 | 100 | 16 | 10 | 13946 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE040D | 480 |  | 5 | 40 | 30 | 480
|  | OLR |  | XTOB024DC1 | 480 |  | 5 | 24 | 15 | 480
XT210 | D | ICB | EATON | HMCPS150(T,U)4C | 480 | 3 | * | 150 | -- | 480 | 3 | 100 | 130 | 100 | 23890 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE150G | 480 |  | 10 | 156 | 125 | 480
|  | OLR |  | XTOB150GC1 | 480 |  | 10 | 150 | 100 | 480
XT211 | D | ICB | EATON | HMCP250(F,G,J,K,L)5C | 480 | 3 | * | 250 | -- | 480 | 3 | 100 | 96 | 75 | 39341 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE115G | 480 |  | 10 | 124 | 100 | 480
|  | OLR |  | XTOB100GC1 | 480 |  | 10 | 100 | 75 | 480
XT212 | D | ICB | EATON | HMCPS015E0C | 208 | 3 | * | 15 | -- | 208 | 3 | 100 | 4.6 | 1 | 8232.3111 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE007B | 200 |  | 5 | 6.9 | 1.5 | 208
|  | OLR |  | XTOB006BC1 | 208 |  | 5 | 6 | 1.5 | 208
XT213 | D | ICB | EATON | HMCPS030H1C | 208 | 3 | * | 30 | -- | 208 | 3 | 100 | 7.5 | 2 | 8232.3111 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE009B | 200 |  | 5 | 11 | 3 | 208
|  | OLR |  | XTOB010BC1 | 208 |  | 5 | 10 | 2 | 208
XT214 | D | ICB | EATON | HMCPS030H1C | 208 | 3 | * | 30 | -- | 208 | 3 | 100 | 10.6 | 3 | 8232.3111 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE012B | 200 |  | 5 | 11 | 3 | 208
|  | OLR |  | XTOB012BC1 | 208 |  | 5 | 12 | 3 | 208
XT215 | D | ICB | EATON | HMCPS050K2C | 208 | 3 | * | 50 | -- | 208 | 3 | 100 | 10.6 | 3 | 8232.3111 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE015B | 200 |  | 5 | 17.5 | 5 | 208
|  | OLR |  | XTOB016BC1 | 208 |  | 5 | 16 | 5 | 208
XT216 | D | ICB | EATON | HMCPS050K2C | 208 | 3 | * | 50 | -- | 208 | 3 | 100 | 16.7 | 5 | 13945.6321 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE040D | 240 |  | 5 | 42 | 15 | 208
|  | OLR |  | XTOB024DC1 | 208 |  | 5 | 24 | 5 | 208
XT217 | D | ICB | EATON | HMCPS050K2C | 208 | 3 | * | 50 | -- | 208 | 3 | 100 | 24.2 | 7.5 | 13945.6321 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE040D | 240 |  | 5 | 42 | 15 | 208
|  | OLR |  | XTOB040DC1 | 208 |  | 5 | 40 | 10 | 208
XT218 | D | ICB | EATON | HMCPS050K2C | 208 | 3 | * | 50 | -- | 208 | 3 | 100 | 30.8 | 10 | 13945.6321 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE040D | 240 |  | 5 | 42 | 15 | 208
|  | OLR |  | XTOB040DC1 | 208 |  | 5 | 40 | 10 | 208
XT219 | D | ICB | EATON | HMCPS100R3C | 208 | 3 | * | 100 | -- | 208 | 3 | 100 | 30.8 | 10 | 13945.6321 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE040D | 240 |  | 5 | 42 | 15 | 208
|  | OLR |  | XTOB040DC1 | 208 |  | 5 | 40 | 10 | 208
XT220 | D | ICB | EATON | HMCPS150(T,U)4C | 208 | 3 | * | 150 | -- | 208 | 3 | 100 | 46.2 | 15 | 13945.6321 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE050D | 200 |  | 5 | 48.3 | 15 | 208
|  | OLR |  | XTOB057DC1 | 208 |  | 5 | 57 | 15 | 208
XT221 | D | ICB | EATON | HMCPS150(T,U)4C | 208 | 3 | * | 150 | -- | 208 | 3 | 100 | 59.4 | 20 | 13945.6321 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE065D | 200 |  | 5 | 62.1 | 20 | 208
|  | OLR |  | XTOB065DC1 | 208 |  | 5 | 65 | 20 | 208
XT222 | D | ICB | EATON | HMCPS150(T,U)4C | 208 | 3 | * | 150 | -- | 208 | 3 | 100 | 59.4 | 20 | 13945.6321 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE072D | 200 |  | 5 | 62.1 | 20 | 208
|  | OLR |  | XTOB065DC1 | 208 |  | 5 | 65 | 20 | 208
XT223 | D | ICB | EATON | HMCPS150(T,U)4C | 208 | 3 | * | 150 | -- | 208 | 3 | 100 | 74.8 | 25 | 23889.7795 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE080F | 200 |  | 5 | 78.2 | 25 | 208
|  | OLR |  | XTOB100GC1 | 208 |  | 5 | 100 | 30 | 208
XT224 | D | ICB | EATON | HMCPS150(T,U)4C | 208 | 3 | * | 150 | -- | 208 | 3 | 100 | 88 | 30 | 23889.7795 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE0115G | 200 |  | 10 | 120 | 40 | 208
|  | OLR |  | XTOB100GC1 | 208 |  | 10 | 100 | 30 | 208
XT225 | D | ICB | EATON | HMCPS150(T,U)4C | 208 | 3 | * | 250 | -- | 208 | 3 | 100 | 114 | 40 | 23889.7795 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE150G | 200 |  | 10 | 120 | 40 | 208
|  | OLR |  | XTOB125GC1 | 208 |  | 10 | 125 | 40 | 208
XT226 | D | ICB | EATON | HMCP250(G,J,K,L,W)5C | 208 | 3 | * | 250 | -- | 208 | 3 | 100 | 114 | 40 | 39341.3405 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE115G | 200 |  | 10 | 120 | 40 | 208
|  | OLR |  | XTOB125GC1 | 208 |  | 10 | 125 | 40 | 208
XT227 | D | ICB | EATON | HMCP250(J,K,L,W)5C | 208 | 3 | * | 250 | -- | 208 | 3 | 100 | 143 | 50 | 39341.3405 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE150G | 240 |  | 10 | 154 | 60 | 208
|  | OLR |  | XTOB150GC1 | 208 |  | 10 | 150 | 50 | 208
XT228 | D | ICB | EATON | HMCP400(J,K,L,W,N,R)5C | 208 | 3 | * | 400 | -- | 208 | 3 | 100 | 143 | 50 | 46071 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE185L | 240 |  | 10 | 154 | 60 | 208
|  | OLR |  | XTOB160LC1 | 208 |  | 10 | 160 | 50 | 208
XT229 | D | ICB | EATON | HMCP400(N,R,X,Y)5C | 208 | 3 | * | 400 | -- | 208 | 3 | 100 | 211 | 75 | 46071 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE250L | 240 |  | 10 | 248 | 100 | 208
|  | OLR |  | XTOB250LC1 | 208 |  | 10 | 250 | 100 | 208
XT230 | D | ICB | EATON | HMCPS015E0C | 220-240 | 3 | * | 15 | -- | 220-240 | 3 | 100 | 4.2 | 1 | 8232.3111 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE007B | 220-240 |  | 5 | 6.8 | 2 | 220-240
|  | OLR |  | XTOB006BC1 | 220-240 |  | 5 | 6 | 1.5 | 220-240
XT231 | D | ICB | EATON | HMCPS030H1C | 220-240 | 3 | * | 30 | -- | 220-240 | 3 | 100 | 6.8 | 2 | 8232.3111 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE009B | 220-240 |  | 5 | 9.6 | 3 | 220-240
|  | OLR |  | XTOB010BC1 | 220-240 |  | 5 | 10 | 3 | 220-240
XT232 | D | ICB | EATON | HMCPS030H1C | 220-240 | 3 | * | 30 | -- | 220-240 | 3 | 100 | 9.6 | 3 | 8232.3111 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE012B | 220-240 |  | 5 | 9.6 | 3 | 220-240
|  | OLR |  | XTOB012BC1 | 220-240 |  | 5 | 12 | 3 | 220-240
XT233 | D | ICB | EATON | HMCPS050K2C | 220-240 | 3 | * | 50 | -- | 220-240 | 3 | 100 | 9.6 | 3 | 8232.3111 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE015B | 220-240 |  | 5 | 15.2 | 5 | 220-240
|  | OLR |  | XTOB012BC1 | 220-240 |  | 5 | 12 | 3 | 220-240
XT234 | D | ICB | EATON | HMCPS050K2C | 220-240 | 3 | * | 50 | -- | 220-240 | 3 | 100 | 15.2 | 5 | 13945.6321 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE040D | 220-240 |  | 5 | 42 | 15 | 220-240
|  | OLR |  | XTOB016DC1 | 220-240 |  | 5 | 16 | 5 | 220-240
XT235 | D | ICB | EATON | HMCPS050K2C | 220-240 | 3 | * | 50 | -- | 220-240 | 3 | 100 | 22 | 7.5 | 13945.6321 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE040D | 220-240 |  | 5 | 42 | 15 | 220-240
|  | OLR |  | XTOB024DC1 | 220-240 |  | 5 | 24 | 7.5 | 220-240
XT236 | D | ICB | EATON | HMCPS050K2C | 220-240 | 3 | * | 50 | -- | 220-240 | 3 | 100 | 28 | 10 | 13945.6321 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE040D | 220-240 |  | 5 | 42 | 15 | 220-240
|  | OLR |  | XTOB040DC1 | 220-240 |  | 5 | 40 | 10 | 220-240
XT237 | D | ICB | EATON | HMCPS100R3C | 220-240 | 3 | * | 100 | -- | 220-240 | 3 | 100 | 28 | 10 | 13945.6321 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE040D | 220-240 |  | 5 | 42 | 15 | 220-240
|  | OLR |  | XTOB040DC1 | 220-240 |  | 5 | 40 | 10 | 220-240
XT238 | D | ICB | EATON | HMCPS150(T,U)4C | 220-240 | 3 | * | 150 | -- | 220-240 | 3 | 100 | 42 | 15 | 13945.6321 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE050D | 220-240 |  | 5 | 54 | 20 | 220-240
|  | OLR |  | XTOB057DC1 | 220-240 |  | 5 | 57 | 20 | 220-240
XT239 | D | ICB | EATON | HMCPS150(T,U)4C | 220-240 | 3 | * | 150 | -- | 220-240 | 3 | 100 | 54 | 20 | 13945.6321 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE065D | 220-240 |  | 5 | 68 | 25 | 220-240
|  | OLR |  | XTOB065DC1 | 220-240 |  | 5 | 65 | 20 | 220-240
XT240 | D | ICB | EATON | HMCPS150(T,U)4C | 220-240 | 3 | * | 150 | -- | 220-240 | 3 | 100 | 54 | 20 | 13945.6321 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE072D | 220-240 |  | 5 | 68 | 25 | 220-240
|  | OLR |  | XTOB065DC1 | 220-240 |  | 5 | 65 | 20 | 220-240
XT241 | D | ICB | EATON | HMCPS150(T,U)4C | 220-240 | 3 | * | 150 | -- | 220-240 | 3 | 100 | 68 | 25 | 13945.6321 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE072D | 220-240 |  | 5 | 68 | 25 | 220-240
|  | OLR |  | XTOB075DC1 | 220-240 |  | 5 | 75 | 25 | 220-240
XT242 | D | ICB | EATON | HMCPS150(T,U)4C | 220-240 | 3 | * | 150 | -- | 220-240 | 3 | 100 | 68 | 25 | 23889.7795 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE080F | 220-240 |  | 5 | 80 | 30 | 220-240
|  | OLR |  | XTOB070GC1 | 220-240 |  | 5 | 70 | 25 | 220-240
XT243 | D | ICB | EATON | HMCPS150(T,U)4C | 220-240 | 3 | * | 150 | -- | 220-240 | 3 | 100 | 80 | 30 | 23889.7795 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE095F | 220-240 |  | 10 | 104 | 40 | 220-240
|  | OLR |  | XTOB100GC1 | 220-240 |  | 10 | 100 | 30 | 220-240
XT244 | D | ICB | EATON | HMCPS150(T,U)4C | 220-240 | 3 | * | 250 | -- | 220-240 | 3 | 100 | 104 | 40 | 23889.7795 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE150G | 220-240 |  | 10 | 154 | 60 | 220-240
|  | OLR |  | XTOB125GC1 | 220-240 |  | 10 | 125 | 40 | 220-240
XT245 | D | ICB | EATON | HMCP250(G,J,K,L,W)5C | 220-240 | 3 | * | 250 | -- | 220-240 | 3 | 100 | 104 | 40 | 39341.3405 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE115G | 220-240 |  | 10 | 130 | 50 | 220-240
|  | OLR |  | XTOB125GC1 | 220-240 |  | 10 | 125 | 40 | 220-240
XT246 | D | ICB | EATON | HMCP250(J,K,L,W)5C | 220-240 | 3 | * | 250 | -- | 220-240 | 3 | 100 | 130 | 50 | 39341.3405 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE150G | 220-240 |  | 10 | 154 | 60 | 220-240
|  | OLR |  | XTOB150GC1 | 220-240 |  | 10 | 150 | 50 | 220-240
XT247 | D | ICB | EATON | HMCP250(K,L,W)5C | 220-240 | 3 | * | 250 | -- | 220-240 | 3 | 100 | 154 | 60 | 46071 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE170G | 220-240 |  | 10 | 154 | 60 | 220-240
|  | OLR |  | XTOB175GC1 | 220-240 |  | 10 | 175 | 60 | 220-240
XT248 | D | ICB | EATON | HMCP250(L,W)5C | 220-240 | 3 | * | 250 | -- | 220-240 | 3 | 100 | 192 | 75 | 46071 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE225L | 220-240 |  | 10 | 192 | 75 | 220-240
|  | OLR |  | XTOB220LC1 | 220-240 |  | 10 | 220 | 75 | 220-240
XT249 | D | ICB | EATON | HMCP400(G,J,K,L,W,N)5C | 220-240 | 3 | * | 400 | -- | 220-240 | 3 | 100 | 130 | 50 | 46071 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE185L | 220-240 |  | 10 | 154 | 60 | 220-240
|  | OLR |  | XTOB160LC1 | 220-240 |  | 10 | 160 | 60 | 220-240
XT250 | D | ICB | EATON | HMCP400(K,L,W,N,R,X)5C | 220-240 | 3 | * | 400 | -- | 220-240 | 3 | 100 | 154 | 60 | 46071 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE185L | 220-240 |  | 10 | 154 | 60 | 220-240
|  | OLR |  | XTOB160LC1 | 220-240 |  | 10 | 160 | 60 | 220-240
XT251 | D | ICB | EATON | HMCP400(W,N,R,X,Y)5C | 220-240 | 3 | * | 400 | -- | 220-240 | 3 | 100 | 192 | 75 | 46071 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE225L | 220-240 |  | 10 | 192 | 75 | 220-240
|  | OLR |  | XTOB220LC1 | 220-240 |  | 10 | 220 | 75 | 220-240
XT252 | D | ICB | EATON | HMCP400(W,N,R,X,Y)5C | 220-240 | 3 | * | 400 | -- | 220-240 | 3 | 100 | 192 | 75 | 46071 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE250L | 220-240 |  | 10 | 248 | 100 | 220-240
|  | OLR |  | XTOB220LC1 | 220-240 |  | 10 | 220 | 75 | 220-240
XT253 | D | ICB | EATON | HMCP400(N,R,X,Y)5C | 220-240 | 3 | * | 400 | -- | 220-240 | 3 | 100 | 248 | 100 | 76644 | 1, 4, 5 | E134360, Vol.1, Sec. 14
|  | MC |  | XTCE250L | 220-240 |  | 10 | 248 | 100 | 220-240
|  | OLR |  | XTOB250LC1 | 220-240 |  | 10 | 250 | 100 | 220-240
Conditions of Use:
1. All of the specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches. Additional testing is not required when installed in an enclosure having the same or larger volume.
4. Unless otherwise specified, all connections between components are made with insulated wire having an ampacity of 125 percent of the rated motor current and connected to the terminals supplied with the individual components.
5. The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor controllers shall be considered in the end - product application