## Freedom Type C
Issued: 2006-05-18
Last Revised: 2006-05-18
Combination Motor Controllers for use in Industrial Control Panels
ID Number | Combination Type | Individual Component | [6 empty] | Combination SCCR | [5 empty] | Conditions of Acceptability | Combination Starter UL File | Motor Control Center UL File
|  | Component Type | Manufacturer | Partial Catalog No. | Ratings |  |  |  | SCCR kA | Volts | Phase | Hp | NEC FLC | Min. Enclosure Volume (cu. ft.)
[5 empty] | SCCR kA | Max. Amps | Volts | No. Poles
FRC0001 | C | CB | Eaton | HFD3015L | 100 | 15 | 200 | 3 | 65 | 200 | 3 | 1 | 4.8 | 0.332 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16BN0 | 5 | 18
FRC0002 |  | CB |  | HFD3020L | 100 | 20 | [5 empty] | 1.5 | 6.9
|  | STR |  | AN16BN0 | 5 | 18
FRC0003 |  | CB |  | HFD3020L | 100 | 20 | [5 empty] | 2 | 7.8
|  | STR |  | AN16BN0 | 5 | 18
FRC0004 |  | CB |  | HFD3030L | 100 | 30 | [5 empty] | 3 | 11
|  | STR |  | AN16BN0 | 5 | 18
FRC0005 | C | CB | Eaton | HFD3015L | 100 | 15 | 208 | 3 | 65 | 208 | 3 | 1 | 4.6 | 0.332 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16BN0 | 5 | 18
FRC0006 |  | CB |  | HFD3020L | 100 | 20 | [5 empty] | 2 | 7.5
|  | STR |  | AN16BN0 | 5 | 18
FRC0007 |  | CB |  | HFD3020L | 100 | 20 | [5 empty] | 3 | 6.6
|  | STR |  | AN16BN0 | 5 | 18
FRC0008 | C | CB | Eaton | HFD3015L | 100 | 15 | 240 | 3 | 65 | 230 | 3 | 1 | 4.2 | 0.332 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16BN0 | 5 | 18
FRC0009 |  | CB |  | HFD3020L | 100 | 20 | [5 empty] | 2 | 6
|  | STR |  | AN16BN0 | 5 | 18
FRC0010 |  | CB |  | HFD3025L | 100 | 25 | [5 empty] | 3 | 9.6
|  | STR |  | AN16BN0 | 5 | 18
FRC0011 | C | CB | Eaton | HFD3015L | 65 | 15 | 480 | 3 | 65 | 460 | 3 | 3 | 4.8 | 0.332 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16BN0 | 5 | 18
FRC0012 |  | CB |  | HFD3020L | 65 | 20 | [5 empty] | 5 | 7.6
|  | STR |  | AN16BN0 | 5 | 18
FRC0013 | C | CB | Eaton | HFD3015L | 25 | 15 | 600 | 3 | 25 | 575 | 3 | 3 | 3.9 | 0.332 | (1) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16BN0 | 5 | 18
FRC0014 |  | CB |  | HFD3015L | 25 | 15 | [5 empty] | 5 | 6.1
|  | STR |  | AN16BN0 | 5 | 18
FRC0015 | C | CB | Eaton | FDC3015L | 200 | 15 | 200 | 3 | 100 | 200 | 3 | 1 | 4.8 | 0.332 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16BN0 | 5 | 18
FRC0016 |  | CB |  | FDC3020L | 200 | 20 | [5 empty] | 1.5 | 6.9
|  | STR |  | AN16BN0 | 5 | 18
FRC0017 |  | CB |  | FDC3020L | 200 | 20 | [5 empty] | 2 | 7.8
|  | STR |  | AN16BN0 | 5 | 18
FRC0018 |  | CB |  | FDC3030L | 200 | 30 | [5 empty] | 3 | 11
|  | STR |  | AN16BN0 | 5 | 18
FRC0019 | C | CB | Eaton | FDC3015L | 200 | 15 | 208 | 3 | 100 | 208 | 3 | 1 | 4.6 | 0.332 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16BN0 | 5 | 18
FRC0020 |  | CB |  | FDC3020L | 200 | 20 | [5 empty] | 2 | 7.5
|  | STR |  | AN16BN0 | 5 | 18
FRC0021 |  | CB |  | FDC3020L | 200 | 20 | [5 empty] | 3 | 6.6
|  | STR |  | AN16BN0 | 5 | 18
FRC0022 | C | CB | Eaton | FDC3015L | 200 | 15 | 240 | 3 | 100 | 230 | 3 | 1 | 4.2 | 0.332 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16BN0 | 5 | 18
FRC0023 |  | CB |  | FDC3020L | 200 | 20 | [5 empty] | 2 | 6
|  | STR |  | AN16BN0 | 5 | 18
FRC0024 |  | CB |  | FDC3025L | 200 | 25 | [5 empty] | 3 | 9.6
|  | STR |  | AN16BN0 | 5 | 18
FRC0025 | C | CB | Eaton | FDC3015L | 100 | 15 | 480 | 3 | 100 | 460 | 3 | 3 | 4.8 | 0.332 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16BN0 | 5 | 18
FRC0026 |  | CB |  | FDC3020L | 100 | 20 | [5 empty] | 5 | 7.6
|  | STR |  | AN16BN0 | 5 | 18
FRC0027 | C | CB | Eaton | FDC3015L | 35 | 15 | 600 | 3 | 35 | 575 | 3 | 3 | 3.9 | 0.332 | (1) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16BN0 | 5 | 18
FRC0028 |  | CB |  | FDC3015L | 35 | 15 | [5 empty] | 5 | 6.1
|  | STR |  | AN16BN0 | 5 | 18
FRC0029 | C | CB | Eaton | HFD3015L | 100 | 15 | 200 | 3 | 65 | 200 | 3 | 1 | 6.9 | 0.33 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16DN0 | 5 | 27
FRC0030 |  | CB |  | HFD3030L | 100 | 30 | [5 empty] | 3 | 11
|  | STR |  | AN16DN0 | 5 | 27
FRC0031 |  | CB |  | HFD3035L | 100 | 35 | [5 empty] | 5 | 17.5
|  | STR |  | AN16DN0 | 5 | 27
FRC0032 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AN16DN0 | 5 | 27
FRC0033 | C | CB | Eaton | HFD3015L | 100 | 15 | 208 | 3 | 65 | 208 | 3 | 1 | 4.6 | 0.33 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16DN0 | 5 | 27
FRC0034 |  | CB |  | HFD3025L | 100 | 25 | [5 empty] | 3 | 10.6
|  | STR |  | AN16DN0 | 5 | 27
FRC0035 |  | CB |  | HFD3035L | 100 | 35 |  |  |  |  | 3 | 5 | 16.7
|  | STR |  | AN16DN0 | 5 | 27
FRC0036 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | AN16DN0 | 5 | 27
FRC0037 | C | CB | Eaton | HFD3015L | 100 | 15 | 240 | 3 | 65 | 230 | 3 | 1 | 4.2 | 0.33 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16DN0 | 5 | 27
FRC0038 |  | CB |  | HFD3025L | 100 | 25 | [5 empty] | 3 | 9.6
|  | STR |  | AN16DN0 | 5 | 27
FRC0039 |  | CB |  | HFD3035L | 100 | 35 |  |  |  |  | 3 | 5 | 15.2
|  | STR |  | AN16DN0 | 5 | 27
FRC0040 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 22
|  | STR |  | AN16DN0 | 5 | 27
FRC0041 | C | CB | Eaton | HFD3015L | 65 | 15 | 480 | 3 | 65 | 460 | 3 | 3 | 4.8 | 0.33 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16DN0 | 5 | 27
FRC0042 |  | CB |  | HFD3020L | 65 | 20 | [5 empty] | 5 | 7.6
|  | STR |  | AN16DN0 | 5 | 27
FRC0043 |  | CB |  | HFD3030L | 65 | 30 | [5 empty] | 7.5 | 11
|  | STR |  | AN16DN0 | 5 | 27
FRC0044 |  | CB |  | HFD3035L | 65 | 35 | [5 empty] | 10 | 14
|  | STR |  | AN16DN0 | 5 | 27
FRC0045 | C | CB | Eaton | HFD3015L | 25 | 15 | 600 | 3 | 25 | 75 | 3 | 3 | 3.9 | 0.33 | (1) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16DN0 | 5 | 27
FRC0046 |  | CB |  | HFD3015L | 25 | 15 | [5 empty] | 5 | 6.1
|  | STR |  | AN16DN0 | 5 | 27
FRC0047 |  | CB |  | HFD3025L | 25 | 25 | [5 empty] | 7.5 | 9
|  | STR |  | AN16DN0 | 5 | 27
FRC0048 |  | CB |  | HFD3030L | 25 | 30 | [5 empty] | 10 | 11
|  | STR |  | AN16DN0 | 5 | 27
FRC0049 | C | CB | Eaton | FDC3015L | 200 | 15 | 200 | 3 | 100 | 200 | 3 | 1 | 6.9 | 0.33 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16DN0 | 5 | 27
FRC0050 |  | CB |  | FDC3030L | 200 | 30 | [5 empty] | 3 | 11
|  | STR |  | AN16DN0 | 5 | 27
FRC0051 |  | CB |  | FDC3035L | 200 | 35 | [5 empty] | 5 | 17.5
|  | STR |  | AN16DN0 | 5 | 27
FRC0052 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AN16DN0 | 5 | 27
FRC0053 | C | CB | Eaton | FDC3015L | 200 | 15 | 208 | 3 | 100 | 208 | 3 | 1 | 4.6 | 0.33 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16DN0 | 5 | 27
FRC0054 |  | CB |  | FDC3025L | 200 | 25 | [5 empty] | 3 | 10.6
|  | STR |  | AN16DN0 | 5 | 27
FRC0055 |  | CB |  | FDC3035L | 200 | 35 |  |  |  |  | 3 | 5 | 16.7
|  | STR |  | AN16DN0 | 5 | 27
FRC0056 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | AN16DN0 | 5 | 27
FRC0057 | C | CB | Eaton | FDC3015L | 200 | 15 | 240 | 3 | 100 | 230 | 3 | 1 | 4.2 | 0.33 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16DN0 | 5 | 27
FRC0058 |  | CB |  | FDC3025L | 200 | 25 | [5 empty] | 3 | 9.6
|  | STR |  | AN16DN0 | 5 | 27
FRC0059 |  | CB |  | FDC3035L | 200 | 35 |  |  |  |  | 3 | 5 | 15.2
|  | STR |  | AN16DN0 | 5 | 27
FRC0060 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 22
|  | STR |  | AN16DN0 | 5 | 27
FRC0061 | C | CB | Eaton | FDC3015L | 100 | 15 | 480 | 3 | 100 | 460 | 3 | 3 | 4.8 | 0.33 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16DN0 | 5 | 27
FRC0062 |  | CB |  | FDC3020L | 100 | 20 | [5 empty] | 5 | 7.6
|  | STR |  | AN16DN0 | 5 | 27
FRC0063 |  | CB |  | FDC3030L | 100 | 30 | [5 empty] | 7.5 | 11
|  | STR |  | AN16DN0 | 5 | 27
FRC0064 |  | CB |  | FDC3035L | 100 | 35 | [5 empty] | 10 | 14
|  | STR |  | AN16DN0 | 5 | 27
FRC0065 | C | CB | Eaton | FDC3015L | 35 | 15 | 600 | 3 | 35 | 575 | 3 | 3 | 3.9 | 0.33 | (1) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16DN0 | 5 | 27
FRC0066 |  | CB |  | FDC3015L | 35 | 15 | [5 empty] | 5 | 6.1
|  | STR |  | AN16DN0 | 5 | 27
FRC0067 |  | CB |  | FDC3025L | 35 | 25 | [5 empty] | 7.5 | 9
|  | STR |  | AN16DN0 | 5 | 27
FRC0068 |  | CB |  | FDC3030L | 35 | 30 | [5 empty] | 10 | 11
|  | STR |  | AN16DN0 | 5 | 27
FRC0069 | C | CB | Eaton | HFD3015L | 100 | 15 | 600 | 3 | 100 | 575 | 3 | 3 | 3.9 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AN16DN0 | 5 | 27
FRC0070 | C | CB | Eaton | HFD3015L | 100 | 15 | 600 | 3 | 100 | 575 | 3 | 5 | 6.1
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AN16DN0 | 5 | 27
FRC0071 | C | CB | Eaton | HFD3025L | 100 | 25 | 600 | 3 | 100 | 575 | 3 | 7.5 | 9 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AN16DN0 | 5 | 27
FRC0072 | C | CB | Eaton | HFD3030L | 100 | 30 | 600 | 3 | 100 | 575 | 3 | 10 | 11
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AN16DN0 | 5 | 27
FRC0073 | C | CB | Eaton | HFD3035L | 100 | 35 | 200 | 3 | 65 | 200 | 3 | 5 | 17.5 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16GN0 | 5 | 45
FRC0074 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AN16GN0 | 5 | 45
FRC0075 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 10 | 32.2 |  | (1) (3) (7c)
|  | STR |  | AN16GN0 | 5 | 45
FRC0076 | C | CB | Eaton | HFD3035L | 100 | 35 | 208 | 3 | 65 | 208 | 3 | 5 | 16.7 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16GN0 | 5 | 45
FRC0077 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | AN16GN0 | 5 | 45
FRC0078 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 10 | 30.8 |  | (1) (3) (7c)
|  | STR |  | AN16GN0 | 5 | 45
FRC0079 | C | CB | Eaton | HFD3035L | 100 | 35 | 240 | 3 | 65 | 230 | 3 | 7.5 | 22 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16GN0 | 5 | 45
FRC0080 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 10 | 28 |  | (1) (3) (7c)
|  | STR |  | AN16GN0 | 5 | 45
FRC0081 |  | CB |  | HFD3090L | 100 | 90 | [5 empty] | 15 | 42
|  | STR |  | AN16GN0 | 5 | 45
FRC0082 | C | CB | Eaton | HFD3050L | 65 | 50 | 480 | 3 | 65 | 460 | 3 | 15 | 21 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16GN0 | 5 | 45
FRC0083 |  | CB |  | HFD3050L | 65 | 50 | [5 empty] | 20 | 27
|  | STR |  | AN16GN0 | 5 | 45
FRC0084 |  | CB |  | HFD3050L | 65 | 50 | [5 empty] | 25 | 34 |  | (1) (3) (7c)
|  | STR |  | AN16GN0 | 5 | 45
FRC0085 | C | CB | Eaton | HFD3035L | 25 | 35 | 600 | 3 | 25 | 575 | 3 | 15 | 17 | 0.69 | (1) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16GN0 | 5 | 45
FRC0086 |  | CB |  | HFD3050L | 25 | 50 | [5 empty] | 20 | 22
|  | STR |  | AN16GN0 | 5 | 45
FRC0087 |  | CB |  | HFD3050L | 25 | 50 | [5 empty] | 25 | 27
|  | STR |  | AN16GN0 | 5 | 45
FRC0088 | C | CB | Eaton | FDC3035L | 200 | 35 | 200 | 3 | 100 | 200 | 3 | 5 | 17.5 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16GN0 | 5 | 45
FRC0089 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AN16GN0 | 5 | 45
FRC0090 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 10 | 32.2 |  | (1) (3) (7c)
|  | STR |  | AN16GN0 | 5 | 45
FRC0091 | C | CB | Eaton | FDC3035L | 200 | 35 | 208 | 3 | 100 | 208 | 3 | 5 | 16.7 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16GN0 | 5 | 45
FRC0092 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | AN16GN0 | 5 | 45
FRC0093 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 10 | 30.8 |  | (1) (3) (7c)
|  | STR |  | AN16GN0 | 5 | 45
FRC0094 | C | CB | Eaton | FDC3035L | 200 | 35 | 240 | 3 | 100 | 230 | 3 | 7.5 | 22 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16GN0 | 5 | 45
FRC0095 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 10 | 28 |  | (1) (3) (7c)
|  | STR |  | AN16GN0 | 5 | 45
FRC0096 |  | CB |  | FDC3090L | 200 | 90 | [5 empty] | 15 | 42
|  | STR |  | AN16GN0 | 5 | 45
FRC0097 | C | CB | Eaton | FDC3050L | 100 | 50 | 480 | 3 | 100 | 460 | 3 | 15 | 21 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16GN0 | 5 | 45
FRC0098 |  | CB |  | FDC3050L | 100 | 50 | [5 empty] | 20 | 27
|  | STR |  | AN16GN0 | 5 | 45
FRC0099 |  | CB |  | FDC3050L | 100 | 50 | [5 empty] | 25 | 34 |  | (1) (3) (7c)
|  | STR |  | AN16GN0 | 5 | 45
FRC0100 | C | CB | Eaton | FDC3035L | 35 | 35 | 600 | 3 | 35 | 575 | 3 | 15 | 17 | 0.69 | (1) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16GN0 | 5 | 45
FRC0101 |  | CB |  | FDC3050L | 35 | 50 | [5 empty] | 20 | 22
|  | STR |  | AN16GN0 | 5 | 45
FRC0102 |  | CB |  | FDC3050L | 35 | 50 | [5 empty] | 25 | 27
|  | STR |  | AN16GN0 | 5 | 45
FRC0103 | C | CB | Eaton | HFD3035 | 25 | 35 | 600 | 3 | 100 | 575 | 3 | 15 | 17 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AN16GN0 | 5 | 45
FRC0104 | C | CB | Eaton | HFD3050 | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 20 | 22
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AN16GN0 | 5 | 45
FRC0105 | C | CB | Eaton | HFD3050 | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 25 | 27
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AN16GN0 | 5 | 45
FRC0106 | C | CB | Eaton | EGH3035FFG | 100 | 35 | 200 | 3 | 65 | 200 | 3 | 5 | 17.5 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16GN0 | 5 | 45
FRC0107 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AN16GN0 | 5 | 45
FRC0108 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 10 | 32.2
|  | STR |  | AN16GN0 | 5 | 45
FRC0109 | C | CB | Eaton | EGH3035FFG | 100 | 35 | 208 | 3 | 65 | 208 | 3 | 5 | 16.7 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16GN0 | 5 | 45
FRC0110 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | AN16GN0 | 5 | 45
FRC0111 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 10 | 30.8
|  | STR |  | AN16GN0 | 5 | 45
FRC0112 | C | CB | Eaton | EGH3035FFG | 100 | 35 | 240 | 3 | 65 | 230 | 3 | 7.5 | 22 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16GN0 | 5 | 45
FRC0113 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 10 | 28
|  | STR |  | AN16GN0 | 5 | 45
FRC0114 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 15 | 42
|  | STR |  | AN16GN0 | 5 | 45
FRC0115 | C | CB | Eaton | EGH3050FFG | 65 | 50 | 480 | 3 | 65 | 460 | 3 | 15 | 21 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16GN0 | 5 | 45
FRC0116 |  | CB |  | EGH3050FFG | 65 | 50 | [5 empty] | 20 | 27
|  | STR |  | AN16GN0 | 5 | 45
FRC0117 |  | CB |  | EGH3050FFG | 65 | 50 | [5 empty] | 25 | 34
|  | STR |  | AN16GN0 | 5 | 45
FRC0118 | C | CB | Eaton | HFD3090L | 100 | 90 | 200 | 3 | 65 | 200 | 3 | 15 | 48.3 | 1.06 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16KN0 | 5 | 90
FRC0119 |  | CB |  | HFD3100L | 100 | 100 | [5 empty] | 20 | 62.1
|  | STR |  | AN16KN0 | 5 | 90
FRC0120 |  | CB |  | HFD3125L | 100 | 125 | [5 empty] | 25 | 78.2
|  | STR |  | AN16KN0 | 5 | 90
FRC0121 | C | CB | Eaton | HFD3070L | 100 | 70 | 208 | 3 | 65 | 208 | 3 | 15 | 46.2 | 1.06 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16KN0 | 5 | 90
FRC0122 |  | CB |  | HFD3090L | 100 | 90 | [5 empty] | 20 | 59.4
|  | STR |  | AN16KN0 | 5 | 90
FRC0123 |  | CB |  | HFD3125L | 100 | 125 | [5 empty] | 25 | 74.8
|  | STR |  | AN16KN0 | 5 | 90
FRC0124 | C | CB | Eaton | HFD3090L | 100 | 90 | 240 | 3 | 65 | 230 | 3 | 20 | 54 | 1.06 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16KN0 | 5 | 90
FRC0125 |  | CB |  | HFD3125L | 100 | 125 | [5 empty] | 25 | 68
|  | STR |  | AN16KN0 | 5 | 90
FRC0126 |  | CB |  | HFD3125L | 100 | 125 | [5 empty] | 30 | 80
|  | STR |  | AN16KN0 | 5 | 90
FRC0127 | C | CB | Eaton | HFD3060L | 65 | 60 | 480 | 3 | 65 | 460 | 3 | 30 | 40 | 1.06 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16KN0 | 5 | 90
FRC0128 |  | CB |  | HFD3090L | 65 | 90 | [5 empty] | 40 | 52 |  | (1) (3) (7e)
|  | STR |  | AN16KN0 | 5 | 90
FRC0129 |  | CB |  | HFD3100L | 65 | 100 | [5 empty] | 50 | 65
|  | STR |  | AN16KN0 | 5 | 90
FRC0130 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 25 | 575 | 3 | 30 | 32 | 1.06 | (1) (3) (6a) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16KN0 | 5 | 90
FRC0131 |  | CB |  | HFD3060L | 25 | 60 | [5 empty] | 40 | 41 |  | (1) (3) (6b) (7c)
|  | STR |  | AN16KN0 | 5 | 90
FRC0132 |  | CB |  | HFD3090L | 25 | 90 | [5 empty] | 50 | 52 |  | (1) (3) (6b) (7e)
|  | STR |  | AN16KN0 | 5 | 90
FRC0133 | C | CB | Eaton | FDC3090L | 200 | 90 | 200 | 3 | 100 | 200 | 3 | 15 | 48.3 | 1.06 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16KN0 | 5 | 90
FRC0134 |  | CB |  | FDC3100L | 200 | 100 | [5 empty] | 20 | 62.1
|  | STR |  | AN16KN0 | 5 | 90
FRC0135 |  | CB |  | FDC3125L | 200 | 125 | [5 empty] | 25 | 78.2
|  | STR |  | AN16KN0 | 5 | 90
FRC0136 | C | CB | Eaton | FDC3070L | 200 | 70 | 208 | 3 | 100 | 208 | 3 | 15 | 46.2 | 1.06 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16KN0 | 5 | 90
FRC0137 |  | CB |  | FDC3090L | 200 | 90 | [5 empty] | 20 | 59.4
|  | STR |  | AN16KN0 | 5 | 90
FRC0138 |  | CB |  | FDC3125L | 200 | 125 | [5 empty] | 25 | 74.8
|  | STR |  | AN16KN0 | 5 | 90
FRC0139 | C | CB | Eaton | FDC3090L | 200 | 90 | 240 | 3 | 100 | 230 | 3 | 15 | 42 | 1.06 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16KN0 | 5 | 90
FRC0140 |  | CB |  | FDC3125L | 200 | 125 | [5 empty] | 20 | 54 |  | (1) (3) (7e)
|  | STR |  | AN16KN0 | 5 | 90
FRC0141 |  | CB |  | FDC3125L | 200 | 125 | [5 empty] | 25 | 68
|  | STR |  | AN16KN0 | 5 | 90
FRC0142 | C | CB | Eaton | FDC3060L | 100 | 60 | 480 | 3 | 100 | 460 | 3 | 30 | 40 | 1.06 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16KN0 | 5 | 90
FRC0143 |  | CB |  | FDC3090L | 100 | 90 | [5 empty] | 40 | 52 |  | (1) (3) (7e)
|  | STR |  | AN16KN0 | 5 | 90
FRC0144 |  | CB |  | FDC3100L | 100 | 100 | [5 empty] | 50 | 65
|  | STR |  | AN16KN0 | 5 | 90
FRC0145 | C | CB | Eaton | FDC3050L | 35 | 50 | 600 | 3 | 35 | 575 | 3 | 30 | 32 | 1.06 | (1) (3) (6a) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16KN0 | 5 | 90
FRC0146 |  | CB |  | FDC3060L | 35 | 60 | [5 empty] | 40 | 41 |  | (1) (3) (6b) (7c)
|  | STR |  | AN16KN0 | 5 | 90
FRC0147 |  | CB |  | FDC3090L | 35 | 90 | [5 empty] | 50 | 52 |  | (1) (3) (6b) (7e)
|  | STR |  | AN16KN0 | 5 | 90
FRC0148 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 30 | 32 | 1.42 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AN16KN0 | 5 | 90
FRC0149 | C | CB | Eaton | HFD3060L | 25 | 60 | 600 | 3 | 100 | 575 | 3 | 40 | 41 | 1.42 | (1) (3) (7c)
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AN16KN0 | 5 | 90
FRC0150 | C | CB | Eaton | HFD3090L | 25 | 90 | 600 | 3 | 100 | 575 | 3 | 50 | 52 | 1.42 | (1) (3) (7e)
|  | C. Limiter |  | LFD3150R | 200 | 150
|  | STR |  | AN16KN0 | 5 | 90
FRC0151 | C | CB | Eaton | EGH3090FFG | 100 | 90 | 200 | 3 | 65 | 200 | 3 | 15 | 48.3 | 1.06 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16KN0 | 5 | 90
FRC0152 |  | CB |  | EGH3100FFG | 100 | 100 | [5 empty] | 20 | 62.1
|  | STR |  | AN16KN0 | 5 | 90
FRC0153 |  | CB |  | EGH3125FFG | 100 | 125 | [5 empty] | 25 | 78.2
|  | STR |  | AN16KN0 | 5 | 90
FRC0154 | C | CB | Eaton | EGH3070FFG | 100 | 70 | 208 | 3 | 65 | 208 | 3 | 15 | 46.2 | 1.06 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16KN0 | 5 | 90
FRC0155 |  | CB |  | EGH3090FFG | 100 | 90 | [5 empty] | 20 | 59.4
|  | STR |  | AN16KN0 | 5 | 90
FRC0156 |  | CB |  | EGH3125FFG | 100 | 125 | [5 empty] | 25 | 74.8
|  | STR |  | AN16KN0 | 5 | 90
FRC0157 | C | CB | Eaton | EGH3090FFG | 100 | 90 | 240 | 3 | 65 | 230 | 3 | 15 | 42 | 1.06 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16KN0 | 5 | 90
FRC0158 |  | CB |  | EGH3125FFG | 100 | 125 | [5 empty] | 20 | 54 |  | (1) (3) (7e)
|  | STR |  | AN16KN0 | 5 | 90
FRC0159 |  | CB |  | EGH3125FFG | 100 | 125 | [5 empty] | 25 | 68 |  | (1) (3) (7e)
|  | STR |  | AN16KN0 | 5 | 90
FRC0160 | C | CB | Eaton | EGH3060FFG | 65 | 60 | 480 | 3 | 65 | 460 | 3 | 30 | 40 | 1.06 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16KN0 | 5 | 90
FRC0161 |  | CB |  | EGH3090FFG | 65 | 90 | [5 empty] | 40 | 52 |  | (1) (3) (7e)
|  | STR |  | AN16KN0 | 5 | 90
FRC0162 |  | CB |  | EGH3100FFG | 65 | 100 | [5 empty] | 50 | 65
|  | STR |  | AN16KN0 | 5 | 90
FRC0163 | C | CB | Eaton | JGH3125FAG | 100 | 125 | 200 | 3 | 65 | 200 | 3 | 25 | 78.2 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16NN0 | 10 | 135
FRC0164 |  | CB |  | JGH3150FAG | 100 | 150 | [5 empty] | 30 | 92 |  | (1) (3) (7f)
|  | STR |  | AN16NN0 | 10 | 135
FRC0165 |  | CB |  | JGH3175FAG | 100 | 175 | [5 empty] | 40 | 120
|  | STR |  | AN16NN0 | 10 | 135
FRC0166 | C | CB | Eaton | JGH3150FAG | 100 | 150 | 208 | 3 | 65 | 208 | 3 | 30 | 88 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16NN0 | 10 | 135
FRC0167 |  | CB |  | JGH3175FAG | 100 | 175 | [5 empty] | 40 | 114 |  | (1) (3) (7f)
|  | STR |  | AN16NN0 | 10 | 135
FRC0168 |  | CB |  | JGH3200FAG | 100 | 200 | [5 empty] | 50 | 143
|  | STR |  | AN16NN0 | 10 | 135
FRC0169 | C | CB | Eaton | JGH3125FAG | 100 | 125 | 240 | 3 | 65 | 230 | 3 | 30 | 80 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16NN0 | 10 | 135
FRC0170 |  | CB |  | JGH3150FAG | 100 | 150 | [5 empty] | 40 | 104 |  | (1) (3) (7f)
|  | STR |  | AN16NN0 | 10 | 135
FRC0171 |  | CB |  | JGH3200FAG | 100 | 200 | [5 empty] | 50 | 130
|  | STR |  | AN16NN0 | 10 | 135
FRC0172 | C | CB | Eaton | JGH3125FAG | 65 | 125 | 480 | 3 | 65 | 460 | 3 | 60 | 77 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16NN0 | 10 | 135
FRC0173 |  | CB |  | JGH3150FAG | 65 | 150 | [5 empty] | 75 | 96 |  | (1) (3) (7f)
|  | STR |  | AN16NN0 | 10 | 135
FRC0174 |  | CB |  | JGH3175FAG | 65 | 175 | [5 empty] | 100 | 124
|  | STR |  | AN16NN0 | 10 | 135
FRC0175 | C | CB | Eaton | JGH3100FAG | 25 | 100 | 600 | 3 | 25 | 575 | 3 | 60 | 62 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16NN0 | 10 | 135
FRC0176 |  | CB |  | JGH3125FAG | 25 | 125 | [5 empty] | 75 | 77
|  | STR |  | AN16NN0 | 10 | 135
FRC0177 |  | CB |  | JGH3150FAG | 25 | 150 | [5 empty] | 100 | 99 |  | (1) (3) (7f)
|  | STR |  | AN16NN0 | 10 | 135
FRC0178 | C | CB | Eaton | JDC3125 | 200 | 125 | 200 | 3 | 100 | 200 | 3 | 25 | 78.2 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16NN0 | 10 | 135
FRC0179 |  | CB |  | JDC3150 | 200 | 150 | [5 empty] | 30 | 92 |  | (1) (3) (7f)
|  | STR |  | AN16NN0 | 10 | 135
FRC0180 |  | CB |  | JDC3175 | 200 | 175 | [5 empty] | 40 | 120
|  | STR |  | AN16NN0 | 10 | 135
FRC0181 | C | CB | Eaton | JDC3150 | 200 | 150 | 208 | 3 | 100 | 208 | 3 | 25 | 88 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16NN0 | 10 | 135
FRC0182 |  | CB |  | JDC3175 | 200 | 175 | [5 empty] | 40 | 114 |  | (1) (3) (7f)
|  | STR |  | AN16NN0 | 10 | 135
FRC0183 |  | CB |  | JDC3200 | 200 | 200 | [5 empty] | 50 | 143
|  | STR |  | AN16NN0 | 10 | 135
FRC0184 | C | CB | Eaton | JDC3125 | 200 | 125 | 240 | 3 | 100 | 230 | 3 | 30 | 80 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16NN0 | 10 | 135
FRC0185 |  | CB |  | JDC3150 | 200 | 150 | [5 empty] | 40 | 104 |  | (1) (3) (7f)
|  | STR |  | AN16NN0 | 10 | 135
FRC0186 |  | CB |  | JDC3200 | 200 | 200 | [5 empty] | 50 | 130
|  | STR |  | AN16NN0 | 10 | 135
FRC0187 | C | CB | Eaton | JDC3125 | 100 | 125 | 480 | 3 | 100 | 460 | 3 | 60 | 77 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16NN0 | 10 | 135
FRC0188 |  | CB |  | JDC3150 | 100 | 150 | [5 empty] | 75 | 96 |  | (1) (3) (7f)
|  | STR |  | AN16NN0 | 10 | 135
FRC0189 |  | CB |  | JDC3175 | 100 | 175 | [5 empty] | 100 | 124
|  | STR |  | AN16NN0 | 10 | 135
FRC0190 | C | CB | Eaton | JDC3100 | 35 | 100 | 600 | 3 | 35 | 575 | 3 | 60 | 62 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16NN0 | 10 | 135
FRC0191 |  | CB |  | JDC3125 | 35 | 125 | [5 empty] | 75 | 77
|  | STR |  | AN16NN0 | 10 | 135
FRC0192 |  | CB |  | JDC3150 | 35 | 150 | [5 empty] | 100 | 99 |  | (1) (3) (7f)
|  | STR |  | AN16NN0 | 10 | 135
FRC0193 | C | CB | Eaton | LA3100PR | 200 | 100 | 600 | 3 | 100 | 575 | 3 | 60 | 62 | 2.5 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16NN0 | 10 | 135
FRC0194 |  | CB |  | LA3125PR | 200 | 125 | [5 empty] | 75 | 77
|  | STR |  | AN16NN0 | 10 | 135
FRC0195 |  | CB |  | LA3150PR | 200 | 150 | [5 empty] | 100 | 99 |  | (1) (3) (7f)
|  | STR |  | AN16NN0 | 10 | 135
FRC0196 | C | CB | Eaton | HKD3250 | 100 | 250 | 200 | 2 | 65 | 200 | 3 | 50 | 150 | 2.15 | (1) (3) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16SN0 | 10 | 270
FRC0197 |  | CB |  | HKD3350 | 100 | 350 | [5 empty] | 60 | 177
|  | STR |  | AN16SN0 | 10 | 270
FRC0198 |  | CB |  | HKD3400 | 100 | 400 | [5 empty] | 75 | 221
|  | STR |  | AN16SN0 | 10 | 270
FRC0199 | C | CB | Eaton | HKD3200 | 100 | 200 | 208 | 3 | 65 | 208 | 3 | 50 | 143 | 2.15 | (1) (3) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16SN0 | 10 | 270
FRC0200 |  | CB |  | HKD3250 | 100 | 250 | [5 empty] | 60 | 169
|  | STR |  | AN16SN0 | 10 | 270
FRC0201 |  | CB |  | HKD3350 | 100 | 350 | [5 empty] | 75 | 211
|  | STR |  | AN16SN0 | 10 | 270
FRC0202 | C | CB | Eaton | HKD3250 | 100 | 250 | 240 | 3 | 65 | 230 | 3 | 60 | 154 | 2.15 | (1) (3) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16SN0 | 10 | 270
FRC0203 |  | CB |  | HKD3350 | 100 | 350 | [5 empty] | 75 | 192
|  | STR |  | AN16SN0 | 10 | 270
FRC0204 |  | CB |  | HKD3400 | 100 | 400 | [5 empty] | 100 | 248
|  | STR |  | AN16SN0 | 10 | 270
FRC0205 | C | CB | Eaton | HKD3250 | 65 | 250 | 480 | 3 | 65 | 460 | 3 | 125 | 156 | 2.15 | (1) (3) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16SN0 | 10 | 270
FRC0206 |  | CB |  | HKD3250 | 65 | 250 | [5 empty] | 150 | 180
|  | STR |  | AN16SN0 | 10 | 270
FRC0207 |  | CB |  | HKD3350 | 65 | 350 | [5 empty] | 200 | 240
|  | STR |  | AN16SN0 | 10 | 270
FRC0208 | C | CB | Eaton | HKD3175 | 35 | 175 | 600 | 3 | 25 | 575 | 3 | 125 | 125 | 2.15 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16SN0 | 10 | 270
FRC0209 |  | CB |  | HKD3200 | 35 | 200 | [5 empty] | 150 | 144 |  | (1) (3) (7j)
|  | STR |  | AN16SN0 | 10 | 270
FRC0210 |  | CB |  | HLD3300 + | 35 | 300 |  |  | 35 |  |  | 200 | 192
|  | STR |  | AN16SN0 | 10 | 270
FRC0211 | C | CB | Eaton | KDC3250 | 200 | 250 | 200 | 2 | 100 | 200 | 3 | 50 | 150 | 2.15 | (1) (3) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16SN0 | 10 | 270
FRC0212 |  | CB |  | KDC3350 | 200 | 350 | [5 empty] | 60 | 177
|  | STR |  | AN16SN0 | 10 | 270
FRC0213 |  | CB |  | KDC3400 | 200 | 400 | [5 empty] | 75 | 221
|  | STR |  | AN16SN0 | 10 | 270
FRC0214 | C | CB | Eaton | KDC3200 | 200 | 200 | 208 | 3 | 100 | 208 | 3 | 50 | 143 | 2.15 | (1) (3) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16SN0 | 10 | 270
FRC0215 |  | CB |  | KDC3250 | 200 | 250 | [5 empty] | 60 | 169
|  | STR |  | AN16SN0 | 10 | 270
FRC0216 |  | CB |  | KDC3350 | 200 | 350 | [5 empty] | 75 | 211
|  | STR |  | AN16SN0 | 10 | 270
FRC0217 | C | CB | Eaton | KDC3250 | 200 | 250 | 240 | 3 | 100 | 230 | 3 | 60 | 154 | 2.15 | (1) (3) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16SN0 | 10 | 270
FRC0218 |  | CB |  | KDC3350 | 200 | 350 | [5 empty] | 75 | 192
|  | STR |  | AN16SN0 | 10 | 270
FRC0219 |  | CB |  | KDC3400 | 200 | 400 | [5 empty] | 100 | 248
|  | STR |  | AN16SN0 | 10 | 270
FRC0220 | C | CB | Eaton | KDC3250 | 100 | 250 | 480 | 3 | 100 | 460 | 3 | 125 | 156 | 2.15 | (1) (3) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16SN0 | 10 | 270
FRC0221 |  | CB |  | KDC3250 | 100 | 250 | [5 empty] | 150 | 180
|  | STR |  | AN16SN0 | 10 | 270
FRC0222 |  | CB |  | KDC3350 | 100 | 350 | [5 empty] | 200 | 240
|  | STR |  | AN16SN0 | 10 | 270
FRC0223 | C | CB | Eaton | KDC3175 | 50 | 175 | 600 | 3 | 50 | 575 | 3 | 125 | 125 | 2.15 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16SN0 | 10 | 270
FRC0224 |  | CB |  | KDC3200 | 50 | 200 | [5 empty] | 150 | 144 |  | (1) (3) (7j)
|  | STR |  | AN16SN0 | 10 | 270
FRC0225 |  | CB |  | KDC3300 | 50 | 300 | [5 empty] | 200 | 192
|  | STR |  | AN16SN0 | 10 | 270
FRC0226 | C | CB | Eaton | LA3175PR | 200 | 175 | 600 | 3 | 100 | 575 | 3 | 125 | 125 | 2.5 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16SN0 | 10 | 270
FRC0227 |  | CB |  | LA3200PR | 200 | 200 | [5 empty] | 150 | 144 |  | (1) (3) (7j)
|  | STR |  | AN16SN0 | 10 | 270
FRC0228 |  | CB |  | LA3300PR | 200 | 300 | [5 empty] | 200 | 192
|  | STR |  | AN16SN0 | 10 | 270
FRC0229 | C | CB | Eaton | HLD3400 | 100 | 400 | 200 | 3 | 65 | 200 | 3 | 100 | 285 | 3.23 | (1) (3) (7Ss) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16TN0 | 18 | 540
FRC0230 |  | CB |  | HLD3600 | 100 | 600 | [5 empty] | 125 | 359
|  | STR |  | AN16TN0 | 18 | 540
FRC0231 |  | CB |  | HLD3600 | 100 | 600 | [5 empty] | 150 | 414
|  | STR |  | AN16TN0 | 18 | 540
FRC0232 | C | CB | Eaton | HLD3400 | 100 | 400 | 208 | 3 | 65 | 208 | 3 | 100 | 273 | 3.23 | (1) (3) (7Ss) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16TN0 | 18 | 540
FRC0233 |  | CB |  | HLD3600 | 100 | 600 | [5 empty] | 125 | 343
|  | STR |  | AN16TN0 | 18 | 540
FRC0234 |  | CB |  | HLD3600 | 100 | 600 | [5 empty] | 150 | 396
|  | STR |  | AN16TN0 | 18 | 540
FRC0235 | C | CB | Eaton | HLD3500 | 100 | 500 | 240 | 3 | 65 | 230 | 3 | 125 | 312 | 3.23 | (1) (3) (7Ss) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16TN0 | 18 | 540
FRC0236 |  | CB |  | HLD3600 | 100 | 600 | [5 empty] | 150 | 360
|  | STR |  | AN16TN0 | 18 | 540
FRC0237 |  | CB |  | HLD3600 | 100 | 600 | [5 empty] | 200 | 480
|  | STR |  | AN16TN0 | 18 | 540
FRC0238 | C | CB | Eaton | HLD3500 | 65 | 500 | 480 | 3 | 65 | 460 | 3 | 250 | 302 | 3.23 | (1) (3) (7Ss) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16TN0 | 18 | 540
FRC0239 |  | CB |  | HLD3600 | 65 | 600 | [5 empty] | 300 | 361
|  | STR |  | AN16TN0 | 18 | 540
FRC0240 |  | CB |  | HLD3600 | 65 | 600 | [5 empty] | 350 | 414
|  | STR |  | AN16TN0 | 18 | 540
FRC0241 |  | CB |  | HLD3600 | 65 | 600 | [5 empty] | 400 | 477
|  | STR |  | AN16TN0 | 18 | 540
FRC0242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
FRC0243 |  | - |  | - | - | - | [5 empty] | - | - |  | -
|  | - |  | - | - | -
FRC0244 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
FRC0245 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
FRC0246 | C | CB | Eaton | LDC3400 | 200 | 400 | 200 | 3 | 65 | 200 | 3 | 100 | 285 | 3.23 | (1) (3) (7s) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16TN0 | 18 | 540
FRC0247 |  | CB |  | LDC3600 | 200 | 600 | [5 empty] | 125 | 359
|  | STR |  | AN16TN0 | 18 | 540
FRC0248 |  | CB |  | LDC3600 | 200 | 600 | [5 empty] | 150 | 414
|  | STR |  | AN16TN0 | 18 | 540
FRC0249 | C | CB | Eaton | LDC3400 | 200 | 400 | 208 | 3 | 65 | 208 | 3 | 100 | 273 | 3.23 | (1) (3) (7s) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16TN0 | 18 | 540
FRC0250 |  | CB |  | LDC3600 | 200 | 600 | [5 empty] | 125 | 343
|  | STR |  | AN16TN0 | 18 | 540
FRC0251 |  | CB |  | LDC3600 | 200 | 600 | [5 empty] | 150 | 396
|  | STR |  | AN16TN0 | 18 | 540
FRC0252 | C | CB | Eaton | LDC3500 | 200 | 500 | 240 | 3 | 65 | 230 | 3 | 125 | 312 | 3.23 | (1) (3) (7s) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16TN0 | 18 | 540
FRC0253 |  | CB |  | LDC3600 | 200 | 600 | [5 empty] | 150 | 360
|  | STR |  | AN16TN0 | 18 | 540
FRC0254 |  | CB |  | LDC3600 | 200 | 600 | [5 empty] | 200 | 480
|  | STR |  | AN16TN0 | 18 | 540
FRC0255 | C | CB | Eaton | LDC3500 | 100 | 500 | 480 | 3 | 65 | 460 | 3 | 250 | 302 | 3.23 | (1) (3) (7s) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16TN0 | 18 | 540
FRC0256 |  | CB |  | LDC3600 | 100 | 600 | [5 empty] | 300 | 361
|  | STR |  | AN16TN0 | 18 | 540
FRC0257 |  | CB |  | LDC3600 | 100 | 600 | [5 empty] | 350 | 414
|  | STR |  | AN16TN0 | 18 | 540
FRC0258 |  | CB |  | LDC3600 + | 100 | 600 | [5 empty] | 400 | 477
|  | STR |  | AN16TN0 | 18 | 540
FRC0259 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
FRC0260 |  | - |  | - | - | - | [5 empty] | - | - |  | -
|  | - |  | - | - | -
FRC0261 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
FRC0262 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
FRC0263 | C | CB | Eaton | HND312T33W + 12NES1200T | 100 | 1200 | 240 | 3 | 65 | 230 | 3 | 250 | 604 | 22.2 | (1) (3) (7m) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16UN0 | 30 | 810
FRC0264 |  | CB |  | HND312T33W + 12NES1200T | 100 | 1200 | [5 empty] | 300 | 720
|  | STR |  | AN16UN0 | 30 | 810
FRC0265 | C | CB | Eaton | HND312T33W + 12NES1200T | 65 | 1200 | 480 | 3 | 65 | 3 | 3 | 500 | 590 |  | (1) (3) (7m)
|  | STR |  | AN16UN0 | 30 | 810
FRC0266 |  | CB |  | HND312T33W + 12NES1200T | 65 | 1200 | [5 empty] | 600 | 722
|  | STR |  | AN16UN0 | 30 | 810
FRC0267 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
FRC0268 |  | - |  | - | - | - | [5 empty] | - | - |  | -
|  | - |  | - | - | -
FRC0269 | C | CB | Eaton | NDC312T33W + 12NES1200T | 200 | 1200 | 240 | 3 | 65 | 230 | 3 | 250 | 604 | 22.2 | (1) (3) (7m) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16UN0 | 30 | 810
FRC0270 |  | CB |  | NDC312T33W + 12NES1200T | 200 | 1200 | [5 empty] | 300 | 720
|  | STR |  | AN16UN0 | 30 | 810
FRC0271 | C | CB | Eaton | NDC312T33W + 12NES1200T | 100 | 1200 | 480 | 3 | 65 | 3 | 3 | 500 | 590 |  | (1) (3) (7m)
|  | STR |  | AN16UN0 | 30 | 810
FRC0272 |  | CB |  | NDC312T33W + 12NES1200T | 100 | 1200 | [5 empty] | 600 | 722
|  | STR |  | AN16UN0 | 30 | 810
FRC0273 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
FRC0274 |  | - |  | - | - | - | [5 empty] | - | - |  | -
|  | - |  | - | - | -
FRC0275 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
FRC0276 | - | - | - | - | - | - | - | - |  | - | - | - | -
|  | - |  | - | - | -
FRC0277 | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
FRC0278 | C | CB | Eaton | HFD3020L | 100 | 20 | 200 | 3 | 65 | 200 | 3 | 2 | 7.8 | 0.33 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16DNS0 | 5 | 18
FRC0279 |  | CB |  | HFD3030L | 100 | 30 | [5 empty] | 3 | 11
|  | STR |  | AE16DNS0 | 5 | 18
FRC0280 |  | CB |  | HFD3035L | 100 | 35 | [5 empty] | 5 | 17.5
|  | STR |  | AE16DNS0 | 5 | 18
FRC0281 | C | CB | Eaton | HFD3020L | 100 | 20 | 208 | 3 | 65 | 208 | 3 | 2 | 7.5 | 0.33 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16DNS0 | 5 | 18
FRC0282 |  | CB |  | HFD3025L | 100 | 25 | [5 empty] | 3 | 7.6
|  | STR |  | AE16DNS0 | 5 | 18
FRC0283 |  | CB |  | HFD3035L | 100 | 35 | [5 empty] | 5 | 16.7
|  | STR |  | AE16DNS0 | 5 | 18
FRC0284 | C | CB | Eaton | HFD3020L | 100 | 20 | 240 | 3 | 65 | 230 | 3 | 2 | 6.8 | 0.33 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16DNS0 | 5 | 18
FRC0285 |  | CB |  | HFD3025L | 100 | 25 | [5 empty] | 3 | 9.6
|  | STR |  | AE16DNS0 | 5 | 18
FRC0286 |  | CB |  | HFD3035L | 100 | 35 | [5 empty] | 5 | 15.2
|  | STR |  | AE16DN0 | 5 | 18
FRC0287 | C | CB | Eaton | HFD3020L | 65 | 20 | 480 | 3 | 65 | 460 | 3 | 5 | 7.6 | 0.33 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16DNS0 | 5 | 18
FRC0288 |  | CB |  | HFD3030L | 65 | 30 | [5 empty] | 7.5 | 11
|  | STR |  | AE16DNS0 | 5 | 18
FRC0289 |  | CB |  | HFD3035L | 65 | 35 | [5 empty] | 10 | 14
|  | STR |  | AE16DNS0 | 5 | 18
FRC0290 | C | CB | Eaton | HFD3025L | 25 | 25 | 600 | 3 | 25 | 575 | 3 | 7.5 | 9 | 0.33 | (1) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16DNS0 | 5 | 18
FRC0291 |  | CB |  | HFD3030L | 25 | 30 | [5 empty] | 10 | 11
|  | STR |  | AE16DNS0 | 5 | 18
FRC0292 |  | CB |  | HFD3035L | 25 | 35 | [5 empty] | 15 | 17
|  | STR |  | AE16DNS0 | 5 | 18
FRC0293 | C | CB | Eaton | FDC3020L | 200 | 20 | 200 | 3 | 100 | 200 | 3 | 2 | 7.8 | 0.33 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16DNS0 | 5 | 18
FRC0294 |  | CB |  | FDC3030L | 200 | 30 | [5 empty] | 3 | 11
|  | STR |  | AE16DNS0 | 5 | 18
FRC0295 |  | CB |  | FDC3035L | 200 | 35 | [5 empty] | 5 | 17.5
|  | STR |  | AE16DNS0 | 5 | 18
FRC0296 | C | CB | Eaton | FDC3020L | 200 | 20 | 208 | 3 | 100 | 208 | 3 | 2 | 7.5 | 0.33 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16DNS0 | 5 | 18
FRC0297 |  | CB |  | FDC3025L | 200 | 25 | [5 empty] | 3 | 7.6
|  | STR |  | AE16DNS0 | 5 | 18
FRC0298 |  | CB |  | FDC3035L | 200 | 35 | [5 empty] | 5 | 16.7
|  | STR |  | AE16DNS0 | 5 | 18
FRC0299 | C | CB | Eaton | FDC3020L | 200 | 20 | 240 | 3 | 100 | 230 | 3 | 2 | 6.8 | 0.33 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16DNS0 | 5 | 18
FRC0300 |  | CB |  | FDC3025L | 200 | 25 | [5 empty] | 3 | 9.6
|  | STR |  | AE16DNS0 | 5 | 18
FRC0301 |  | CB |  | FDC3035L | 200 | 35 | [5 empty] | 5 | 15.2
|  | STR |  | AE16DNS0 | 5 | 18
FRC0302 | C | CB | Eaton | FDC3020L | 100 | 20 | 480 | 3 | 100 | 460 | 3 | 5 | 7.6 | 0.33 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16DNS0 | 5 | 18
FRC0303 |  | CB |  | FDC3030L | 100 | 30 | [5 empty] | 7.5 | 11
|  | STR |  | AE16DNS0 | 5 | 18
FRC0304 |  | CB |  | FDC3035L | 100 | 35 | [5 empty] | 10 | 14
|  | STR |  | AE16DNS0 | 5 | 18
FRC0305 | C | CB | Eaton | FDC3025L | 35 | 25 | 600 | 3 | 35 | 575 | 3 | 7.5 | 9 | 0.33 | (1) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16DNS0 | 5 | 18
FRC0306 |  | CB |  | FDC3030L | 35 | 30 | [5 empty] | 10 | 11
|  | STR |  | AE16DNS0 | 5 | 18
FRC0307 |  | CB |  | FDC3035L | 35 | 35 | [5 empty] | 15 | 17
|  | STR |  | AE16DNS0 | 5 | 18
FRC0308 | C | CB | Eaton | HFD3030L | 100 | 30 | 200 | 3 | 65 | 200 | 3 | 3 | 11 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16FNS0 | 5 | 32
FRC0309 |  | CB |  | HFD3035L | 100 | 35 | [5 empty] | 5 | 17.5
|  | STR |  | AE16FNS0 | 5 | 32
FRC0310 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AE16FNS0 | 5 | 32
FRC0311 | C | CB | Eaton | HFD3025L | 100 | 25 | 208 | 3 | 65 | 208 | 3 | 5 | 16.7 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16FNS0 | 5 | 32
FRC0312 |  | CB |  | HFD3035L | 100 | 35 | [5 empty] | 7.5 | 22.4
|  | STR |  | AE16FNS0 | 5 | 32
FRC0313 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 10 | 30.8 |  | (1) (3) (7c)
|  | STR |  | AE16FNS0 | 5 | 32
FRC0314 | C | CB | Eaton | HFD3035L | 100 | 35 | 240 | 3 | 65 | 230 | 3 | 5 | 15.2 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16FNS0 | 5 | 32
FRC0315 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 22
|  | STR |  | AE16FNS0 | 5 | 32
FRC0316 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 10 | 28 |  | (1) (3) (7c)
|  | STR |  | AE16FNS0 | 5 | 32
FRC0317 | C | CB | Eaton | HFD3035L | 100 | 35 | 480 | 3 | 65 | 460 | 3 | 10 | 14 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16FNS0 | 5 | 32
FRC0318 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 15 | 21
|  | STR |  | AE16FNS0 | 5 | 32
FRC0319 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 20 | 27
|  | STR |  | AE16FNS0 | 5 | 32
FRC0320 | C | CB | Eaton | HFD3030L | 25 | 30 | 600 | 3 | 25 | 575 | 3 | 10 | 11 | 0.69 | (1) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16FNS0 | 5 | 32
FRC0321 |  | CB |  | HFD3035L | 25 | 35 | [5 empty] | 15 | 17
|  | STR |  | AE16FNS0 | 5 | 32
FRC0322 |  | CB |  | HFC3050 | 25 | 50 | [5 empty] | 20 | 22
|  | STR |  | AE16FNS0 | 5 | 32
FRC0323 |  | CB |  | HFD3050L | 25 | 50 | [5 empty] | 25 | 27
|  | STR |  | AE16FNS0 | 5 | 32
FRC0324 | C | CB | Eaton | FDC3030L | 200 | 30 | 200 | 3 | 100 | 200 | 3 | 3 | 11 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16FNS0 | 5 | 32
FRC0325 |  | CB |  | FDC3035L | 200 | 35 | [5 empty] | 5 | 17.5
|  | STR |  | AE16FNS0 | 5 | 32
FRC0326 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AE16FNS0 | 5 | 32
FRC0327 | C | CB | Eaton | FDC3025L | 200 | 25 | 208 | 3 | 100 | 208 | 3 | 5 | 16.7 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16FNS0 | 5 | 32
FRC0328 |  | CB |  | FDC3035L | 200 | 35 | [5 empty] | 7.5 | 22.4
|  | STR |  | AE16FNS0 | 5 | 32
FRC0329 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 10 | 30.8 |  | (1) (3) (7c)
|  | STR |  | AE16FNS0 | 5 | 32
FRC0330 | C | CB | Eaton | FDC3035L | 200 | 35 | 240 | 3 | 100 | 230 | 3 | 5 | 15.2 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16FNS0 | 5 | 32
FRC0331 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 22
|  | STR |  | AE16FNS0 | 5 | 32
FRC0332 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 10 | 28 |  | (1) (3) (7c)
|  | STR |  | AE16FNS0 | 5 | 32
FRC0333 | C | CB | Eaton | FDC3035L | 200 | 35 | 480 | 3 | 100 | 460 | 3 | 10 | 14 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16FNS0 | 5 | 32
FRC0334 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 15 | 21
|  | STR |  | AE16FNS0 | 5 | 32
FRC0335 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 20 | 27
|  | STR |  | AE16FNS0 | 5 | 32
FRC0336 | C | CB | Eaton | FDC3030L | 35 | 30 | 600 | 3 | 35 | 575 | 3 | 10 | 11 | 0.69 | (1) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16FNS0 | 5 | 32
FRC0337 |  | CB |  | FDC3035L | 35 | 35 | [5 empty] | 15 | 17
|  | STR |  | AE16FNS0 | 5 | 32
FRC0338 |  | CB |  | FDC3050L | 35 | 50 | [5 empty] | 20 | 22
|  | STR |  | AE16FNS0 | 5 | 32
FRC0339 |  | CB |  | FDC3050L | 35 | 50 | [5 empty] | 25 | 27
|  | STR |  | AE16FNS0 | 5 | 32
FRC0340 | C | CB | Eaton | HFD3030L | 25 | 30 | 600 | 3 | 100 | 575 | 3 | 10 | 11 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AE16FNS0 | 5 | 32
FRC0341 | C | CB | Eaton | HFD3035L | 25 | 35 | 600 | 3 | 100 | 575 | 3 | 15 | 17
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AE16FNS0 | 5 | 32
FRC0342 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 20 | 22
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AE16FNS0 | 5 | 32
FRC0343 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 25 | 27
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AE16FNS0 | 5 | 32
FRC0344 | C | CB | Eaton | HFD3030L | 100 | 30 | 200 | 3 | 65 | 200 | 3 | 3 | 11 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16GNS0 | 5 | 37
FRC0345 |  | CB |  | HFD3035L | 100 | 35 | [5 empty] | 5 | 17.5
|  | STR |  | AE16GNS0 | 5 | 37
FRC0346 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AE16GNS0 | 5 | 37
FRC0347 | C | CB | Eaton | HFD3035L | 100 | 35 | 208 | 3 | 65 | 208 | 3 | 5 | 16.7 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16GNS0 | 5 | 37
FRC0348 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | AE16GNS0 | 5 | 37
FRC0349 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 10 | 30.8 |  | (1) (3) (7c)
|  | STR |  | AE16GNS0 | 5 | 37
FRC0350 | C | CB | Eaton | HFD3035L | 100 | 35 | 240 | 3 | 65 | 230 | 3 | 5 | 15.2 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16GNS0 | 5 | 37
FRC0351 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 22
|  | STR |  | AE16GNS0 | 5 | 37
FRC0352 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 10 | 28 |  | (1) (3) (7c)
|  | STR |  | AE16GNS0 | 5 | 37
FRC0353 | C | CB | Eaton | HFD3050L | 65 | 50 | 480 | 3 | 65 | 460 | 3 | 15 | 21 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16GNS0 | 5 | 37
FRC0354 |  | CB |  | HFD3050L | 65 | 50 | [5 empty] | 20 | 27
|  | STR |  | AE16GNS0 | 5 | 37
FRC0355 |  | CB |  | HFD3050L | 65 | 50 | [5 empty] | 25 | 34 |  | (1) (3) (7c)
|  | STR |  | AE16GNS0 | 5 | 37
FRC0356 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 25 | 575 | 3 | 20 | 22 | 0.69 | (1) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16GNS0 | 5 | 37
FRC0357 |  | CB |  | HFD3050L | 25 | 50 | [5 empty] | 25 | 27
|  | STR |  | AE16GNS0 | 5 | 37
FRC0358 |  | CB |  | HFD3050L | 25 | 50 | [5 empty] | 30 | 32 |  | (1) (3) (6a) (7c)
|  | STR |  | AE16GNS0 | 5 | 37
FRC0359 | C | CB | Eaton | FDC3030L | 200 | 30 | 200 | 3 | 100 | 200 | 3 | 3 | 11 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16GNS0 | 5 | 37
FRC0360 |  | CB |  | FDC3035L | 200 | 35 | [5 empty] | 5 | 17.5
|  | STR |  | AE16GNS0 | 5 | 37
FRC0361 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AE16GNS0 | 5 | 37
FRC0362 | C | CB | Eaton | FDC3035L | 200 | 35 | 208 | 3 | 100 | 208 | 3 | 5 | 16.7 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16GNS0 | 5 | 37
FRC0363 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | AE16GNS0 | 5 | 37
FRC0364 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 10 | 30.8 |  | (1) (3) (7c)
|  | STR |  | AE16GNS0 | 5 | 37
FRC0365 | C | CB | Eaton | FDC3035L | 200 | 35 | 240 | 3 | 100 | 230 | 3 | 5 | 15.2 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16GNS0 | 5 | 37
FRC0366 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 22
|  | STR |  | AE16GNS0 | 5 | 37
FRC0367 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 10 | 28 |  | (1) (3) (7c)
|  | STR |  | AE16GNS0 | 5 | 37
FRC0368 | C | CB | Eaton | FDC3050L | 100 | 50 | 480 | 3 | 100 | 460 | 3 | 15 | 21 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16GNS0 | 5 | 37
FRC0369 |  | CB |  | FDC3050L | 100 | 50 | [5 empty] | 20 | 27
|  | STR |  | AE16GNS0 | 5 | 37
FRC0370 |  | CB |  | FDC3050L | 100 | 50 | [5 empty] | 25 | 34 |  | (1) (3) (7c)
|  | STR |  | AE16GNS0 | 5 | 37
FRC0371 | C | CB | Eaton | FDC3050L | 35 | 50 | 600 | 3 | 35 | 575 | 3 | 20 | 22 | 0.69 | (1) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16GNS0 | 5 | 37
FRC0372 |  | CB |  | FDC3050L | 35 | 50 | [5 empty] | 25 | 27
|  | STR |  | AE16GNS0 | 5 | 37
FRC0373 |  | CB |  | FDC3050L | 35 | 50 | [5 empty] | 30 | 32 |  | (1) (3) (6a) (7c)
|  | STR |  | AE16GNS0 | 5 | 37
FRC0374 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 20 | 22 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AE16GNS0 | 5 | 37
FRC0375 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 25 | 27
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AE16GNS0 | 5 | 37
FRC0376 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 30 | 32 |  | (1) (3) (7c)
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AE16GNS0 | 5 | 37
FRC0377 | C | CB | Eaton | HFD3050L | 100 | 50 | 200 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16JNS0 | 5 | 60
FRC0378 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 10 | 32.2 |  | (1) (3) (7c)
|  | STR |  | AE16JNS0 | 5 | 60
FRC0379 |  | CB |  | HFD3090L | 100 | 90 | [5 empty] | 15 | 48.3 |  | (1) (3) (7e)
|  | STR |  | AE16JNS0 | 5 | 60
FRC0380 | C | CB | Eaton | HFD3050L | 100 | 50 | 208 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16JNS0 | 5 | 60
FRC0381 |  | CB |  | HFD3070L | 100 | 70 | [5 empty] | 10 | 30.8 |  | (1) (3) (7c)
|  | STR |  | AE16JNS0 | 5 | 60
FRC0382 |  | CB |  | HFD3090L | 100 | 90 | [5 empty] | 15 | 46.2 |  | (1) (3) (7e)
|  | STR |  | AE16JNS0 | 5 | 60
FRC0383 | C | CB | Eaton | HFD3050L | 100 | 50 | 240 | 3 | 65 | 230 | 3 | 10 | 28 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16JNS0 | 5 | 60
FRC0384 |  | CB |  | HFD3070L | 100 | 70 | [5 empty] | 15 | 42 |  | (1) (3) (7c)
|  | STR |  | AE16JNS0 | 5 | 60
FRC0385 |  | CB |  | HFD3090L | 100 | 90 | [5 empty] | 20 | 54 |  | (1) (3) (7e)
|  | STR |  | AE16JNS0 | 5 | 60
FRC0386 | C | CB | Eaton | HFD3050L | 65 | 50 | 480 | 3 | 65 | 460 | 3 | 25 | 34 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16JNS0 | 5 | 60
FRC0387 |  | CB |  | HFD3060L | 65 | 60 | [5 empty] | 30 | 40 |  | (1) (3) (7c)
|  | STR |  | AE16JNS0 | 5 | 60
FRC0388 |  | CB |  | HFD3090L | 65 | 90 | [5 empty] | 40 | 52 |  | (1) (3) (7e)
|  | STR |  | AE16JNS0 | 5 | 60
FRC0389 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 25 | 575 | 3 | 25 | 27 | 0.69 | (1) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16JNS0 | 5 | 60
FRC0390 |  | CB |  | HFD3050L | 25 | 50 | [5 empty] | 30 | 32 |  | (1) (3) (6a) (7c)
|  | STR |  | AE16JNS0 | 5 | 60
FRC0391 |  | CB |  | HFD3060L | 25 | 60 | [5 empty] | 40 | 41 |  | (1) (3) (6b) (7c)
|  | STR |  | AE16JNS0 | 5 | 60
FRC0392 | C | CB | Eaton | FDC3050L | 200 | 50 | 200 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16JNS0 | 5 | 60
FRC0393 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 10 | 32.2 |  | (1) (3) (7c)
|  | STR |  | AE16JNS0 | 5 | 60
FRC0394 |  | CB |  | FDC3090L | 200 | 90 | [5 empty] | 15 | 48.3
|  | STR |  | AE16JNS0 | 5 | 60
FRC0395 | C | CB | Eaton | FDC3050L | 200 | 50 | 208 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16JNS0 | 5 | 60
FRC0396 |  | CB |  | FDC3070L | 200 | 70 | [5 empty] | 10 | 30.8 |  | (1) (3) (7c)
|  | STR |  | AE16JNS0 | 5 | 60
FRC0397 |  | CB |  | FDC3090L | 200 | 90 | [5 empty] | 15 | 46.2
|  | STR |  | AE16JNS0 | 5 | 60
FRC0398 | C | CB | Eaton | FDC3050L | 200 | 50 | 240 | 3 | 100 | 230 | 3 | 10 | 28 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16JNS0 | 5 | 60
FRC0399 |  | CB |  | FDC3070L | 200 | 70 | [5 empty] | 15 | 42 |  | (1) (3) (7c)
|  | STR |  | AE16JNS0 | 5 | 60
FRC0400 |  | CB |  | FDC3090L | 200 | 90 | [5 empty] | 20 | 54 |  | (1) (3) (7e)
|  | STR |  | AE16JNS0 | 5 | 60
FRC0401 | C | CB | Eaton | FDC3050L | 100 | 50 | 480 | 3 | 100 | 460 | 3 | 25 | 34 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16JNS0 | 5 | 60
FRC0402 |  | CB |  | FDC3060L | 100 | 60 | [5 empty] | 30 | 40 |  | (1) (3) (7c)
|  | STR |  | AE16JNS0 | 5 | 60
FRC0403 |  | CB |  | FDC3090L | 100 | 90 | [5 empty] | 40 | 52 |  | (1) (3) (7e)
|  | STR |  | AE16JNS0 | 5 | 60
FRC0404 | C | CB | Eaton | FDC3050L | 35 | 50 | 600 | 3 | 35 | 575 | 3 | 25 | 27 | 0.69 | (1) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16JNS0 | 5 | 60
FRC0405 |  | CB |  | FDC3060L | 35 | 60 | [5 empty] | 30 | 32 |  | (1) (3) (6a) (7c)
|  | STR |  | AE16JNS0 | 5 | 60
FRC0406 |  | CB |  | FDC3060L | 35 | 60 | [5 empty] | 40 | 41 |  | (1) (3) (6b) (7c)
|  | STR |  | AE16JNS0 | 5 | 60
FRC0407 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 25 | 27 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AE16JNS0 | 5 | 60
FRC0408 | C | CB | Eaton | HFD3060L | 25 | 60 | 600 | 3 | 100 | 575 | 3 | 30 | 32 |  | (1) (3) (7c)
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AE16JNS0 | 5 | 60
FRC0409 | C | CB | Eaton | HFD3060L | 25 | 60 | 600 | 3 | 100 | 575 | 3 | 40 | 41
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AE16JNS0 | 5 | 60
FRC0410 | C | CB | Eaton | EGH3050FFG | 100 | 50 | 200 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16JNS0 | 5 | 60
FRC0411 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 10 | 32.2 |  | (1) (3) (7c)
|  | STR |  | AE16JNS0 | 5 | 60
FRC0412 |  | CB |  | EGH3090FFG | 100 | 90 | [5 empty] | 15 | 48.3
|  | STR |  | AE16JNS0 | 5 | 60
FRC0413 | C | CB | Eaton | EGH3050FFG | 100 | 50 | 208 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16JNS0 | 5 | 60
FRC0414 |  | CB |  | EGH3070FFG | 100 | 70 | [5 empty] | 10 | 30.8 |  | (1) (3) (7c)
|  | STR |  | AE16JNS0 | 5 | 60
FRC0415 |  | CB |  | EGH3090FFG | 100 | 90 | [5 empty] | 15 | 46.2
|  | STR |  | AE16JNS0 | 5 | 60
FRC0416 | C | CB | Eaton | EGH3050FFG | 100 | 50 | 240 | 3 | 65 | 230 | 3 | 10 | 28 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16JNS0 | 5 | 60
FRC0417 |  | CB |  | EGH3070FFG | 100 | 70 | [5 empty] | 15 | 42 |  | (1) (3) (7c)
|  | STR |  | AE16JNS0 | 5 | 60
FRC0418 |  | CB |  | EGH3090FFG | 100 | 90 | [5 empty] | 20 | 54 |  | (1) (3) (7e)
|  | STR |  | AE16JNS0 | 5 | 60
FRC0419 | C | CB | Eaton | EGH3050FFG | 65 | 50 | 480 | 3 | 65 | 460 | 3 | 25 | 34 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16JNS0 | 5 | 60
FRC0420 |  | CB |  | EGH3060FFG | 65 | 60 | [5 empty] | 30 | 40 |  | (1) (3) (7c)
|  | STR |  | AE16JNS0 | 5 | 60
FRC0421 |  | CB |  | EGH3090FFG | 65 | 90 | [5 empty] | 40 | 52 |  | (1) (3) (7e)
|  | STR |  | AE16JNS0 | 5 | 60
FRC0422 | C | CB | Eaton | HFD3050L | 100 | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 0.69 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16KNS0 | 5 | 73
FRC0423 |  | CB |  | HFD3090L | 100 | 90 | [5 empty] | 15 | 48.3 |  | (1) (3) (7e)
|  | STR |  | AE16KNS0 | 5 | 73
FRC0424 |  | CB |  | HFD3090L | 100 | 90 | [5 empty] | 20 | 62.1
|  | STR |  | AE16KNS0 | 5 | 73
FRC0425 | C | CB | Eaton | HFD3050L | 100 | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 0.69 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16KNS0 | 5 | 73
FRC0426 |  | CB |  | HFD3070L | 100 | 70 | [5 empty] | 15 | 46.2 |  | (1) (3) (7e)
|  | STR |  | AE16KNS0 | 5 | 73
FRC0427 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
FRC0428 |  | CB |  | HFD3090L | 100 | 90 | [5 empty] | 20 | 59.4
|  | STR |  | AE16KNS0 | 5 | 73
FRC0429 | C | CB | Eaton | HFD3070L | 100 | 70 | 240 | 3 | 65 | 230 | 3 | 15 | 42 | 0.69 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16KNS0 | 5 | 73
FRC0430 |  | CB |  | HFD3090L | 100 | 90 | [5 empty] | 20 | 54 |  | (1) (3) (7e)
|  | STR |  | AE16KNS0 | 5 | 73
FRC0431 |  | CB |  | HFD3090L | 100 | 90 | [5 empty] | 25 | 68
|  | STR |  | AE16KNS0 | 5 | 73
FRC0432 | C | CB | Eaton | HFD3060L | 65 | 60 | 480 | 3 | 65 | 460 | 3 | 30 | 40 | 0.69 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16KNS0 | 5 | 73
FRC0433 |  | CB |  | HFD3090L | 65 | 90 | [5 empty] | 40 | 52 |  | (1) (3) (7e)
|  | STR |  | AE16KNS0 | 5 | 73
FRC0434 |  | CB |  | HFD3090L | 65 | 90 | [5 empty] | 50 | 65
|  | STR |  | AE16KNS0 | 5 | 73
FRC0435 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 25 | 575 | 3 | 30 | 32 | 0.69 | (1) (3) (6a) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16KNS0 | 5 | 73
FRC0436 |  | CB |  | HFD3090L | 25 | 90 | [5 empty] | 40 | 41 |  | (1) (3) (6b) (7c)
|  | STR |  | AE16KNS0 | 5 | 73
FRC0437 |  | CB |  | HFD3090L | 25 | 90 | [5 empty] | 50 | 52 |  | (1) (3) (6b) (7e)
|  | STR |  | AE16KNS0 | 5 | 73
FRC0438 | C | CB | Eaton | FDC3050L | 200 | 50 | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 0.69 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16KNS0 | 5 | 73
FRC0439 |  | CB |  | FDC3090L | 200 | 90 | [5 empty] | 15 | 48.3 |  | (1) (3) (7e)
|  | STR |  | AE16KNS0 | 5 | 73
FRC0440 |  | CB |  | FDC3090L | 200 | 90 | [5 empty] | 20 | 62.1
|  | STR |  | AE16KNS0 | 5 | 73
FRC0441 | C | CB | Eaton | FDC3050L | 200 | 50 | 208 | 3 | 100 | 208 | 3 | 10 | 30.8 | 0.69 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16KNS0 | 5 | 73
FRC0442 |  | CB |  | FDC3070L | 200 | 70 | [5 empty] | 15 | 46.2 |  | (1) (3) (7e)
|  | STR |  | AE16KNS0 | 5 | 73
FRC0443 |  | CB |  | FDC3090L | 200 | 90 | [5 empty] | 20 | 59.4
|  | STR |  | AE16KNS0 | 5 | 73
FRC0444 | C | CB | Eaton | FDC3070L | 200 | 70 | 240 | 3 | 100 | 230 | 3 | 15 | 42 | 0.69 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16KNS0 | 5 | 73
FRC0445 |  | CB |  | FDC3090L | 200 | 90 | [5 empty] | 20 | 54 |  | (1) (3) (7e)
|  | STR |  | AE16KNS0 | 5 | 73
FRC0446 |  | CB |  | FDC3090L | 200 | 90 | [5 empty] | 25 | 68
|  | STR |  | AE16KNS0 | 5 | 73
FRC0447 | C | CB | Eaton | FDC3060 | 100 | 60 | 480 | 3 | 100 | 460 | 3 | 30 | 40 | 0.69 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16KNS0 | 5 | 73
FRC0448 |  | CB |  | FDC3090L | 100 | 90 | [5 empty] | 40 | 52 |  | (1) (3) (7e)
|  | STR |  | AE16KNS0 | 5 | 73
FRC0449 |  | CB |  | FDC3090L | 100 | 90 | [5 empty] | 50 | 65
|  | STR |  | AE16KNS0 | 5 | 73
FRC0450 | C | CB | Eaton | FDC3050L | 35 | 50 | 600 | 3 | 35 | 575 | 3 | 30 | 32 | 0.69 | (1) (3) (6a) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1
|  | STR |  | AE16KNS0 | 5 | 73
FRC0451 |  | CB |  | FDC3090L | 35 | 90 | [5 empty] | 40 | 41 |  | (1) (3) (6b) (7c)
|  | STR |  | AE16KNS0 | 5 | 73
FRC0452 |  | CB |  | FDC3090L | 35 | 90 | [5 empty] | 50 | 52 |  | (1) (3) (6b) (7e)
|  | STR |  | AE16KNS0 | 5 | 73
FRC0453 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 30 | 32 | 0.69 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AE16KNS0 | 5 | 73
FRC0454 | C | CB | Eaton | HFD3090L | 25 | 90 | 600 | 3 | 100 | 575 | 3 | 40 | 41
|  | C. Limiter |  | LFD3150R | 200 | 90
|  | STR |  | AE16KNS0 | 5 | 73
FRC0455 | C | CB | Eaton | HFD3090L | 25 | 90 | 600 | 3 | 100 | 575 | 3 | 50 | 52 |  | (1) (3) (7e)
|  | C. Limiter |  | LFD3150R | 200 | 150
|  | STR |  | AE16KNS0 | 5 | 73
FRC0456 | C | CB | Eaton | EGH3050FFG | 100 | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 0.69 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16KNS0 | 5 | 73
FRC0457 |  | CB |  | EGH3090FFG | 100 | 90 | [5 empty] | 15 | 48.3 |  | (1) (3) (7e)
|  | STR |  | AE16KNS0 | 5 | 73
FRC0458 |  | CB |  | EGH3090FFG | 100 | 90 | [5 empty] | 20 | 62.1
|  | STR |  | AE16KNS0 | 5 | 73
FRC0459 | C | CB | Eaton | EGH3050FFG | 100 | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 0.69 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16KNS0 | 5 | 73
FRC0460 |  | CB |  | EGH3070FFG | 100 | 70 | [5 empty] | 15 | 46.2 |  | (1) (3) (7e)
|  | STR |  | AE16KNS0 | 5 | 73
FRC0461 |  | CB |  | EGH3090FFG | 100 | 90 | [5 empty] | 20 | 59.4
|  | STR |  | AE16KNS0 | 5 | 73
FRC0462 | C | CB | Eaton | EGH3070FFG | 100 | 70 | 240 | 3 | 65 | 230 | 3 | 15 | 42 | 0.69 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16KNS0 | 5 | 73
FRC0463 |  | CB |  | EGH3090FFG | 100 | 90 | [5 empty] | 20 | 54 |  | (1) (3) (7e)
|  | STR |  | AE16KNS0 | 5 | 73
FRC0464 |  | CB |  | EGH3090FFG | 100 | 90 | [5 empty] | 25 | 68
|  | STR |  | AE16KNS0 | 5 | 73
FRC0465 | C | CB | Eaton | EGH3060FFG | 65 | 60 | 480 | 3 | 65 | 460 | 3 | 30 | 40 | 0.69 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16KNS0 | 5 | 73
FRC0466 |  | CB |  | EGH3090FFG | 65 | 90 | [5 empty] | 40 | 52 |  | (1) (3) (7e)
|  | STR |  | AE16KNS0 | 5 | 73
FRC0467 |  | CB |  | EGH3090FFG | 65 | 90 | [5 empty] | 50 | 65
|  | STR |  | AE16KNS0 | 5 | 73
FRC0468 | C | CB | Eaton | JGH3150FAG | 100 | 150 | 200 | 3 | 65 | 200 | 3 | 25 | 78.2 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16NNS0 | 10 | 140
FRC0469 |  | CB |  | JGH3175FAG | 100 | 175 | [5 empty] | 30 | 92 |  | (1) (3) (7f)
|  | STR |  | AE16NNS0 | 10 | 140
FRC0470 |  | CB |  | JGH3250FAG | 100 | 250 | [5 empty] | 40 | 120
|  | STR |  | AE16NNS0 | 10 | 140
FRC0471 | C | CB | Eaton | JGH3150FAG | 100 | 150 | 208 | 3 | 65 | 208 | 3 | 25 | 74.8 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16NNS0 | 10 | 140
FRC0472 |  | CB |  | JGH3175FAG | 100 | 175 | [5 empty] | 30 | 88
|  | STR |  | AE16NNS0 | 10 | 140
FRC0743 |  | CB |  | JGH3200FAG | 100 | 200 | [5 empty] | 40 | 114 |  | (1) (3) (7f)
|  | STR |  | AE16NNS0 | 10 | 140
FRC0474 | C | CB | Eaton | JGH3125FAG | 100 | 125 | 240 | 3 | 65 | 230 | 3 | 30 | 80 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16NNS0 | 10 | 140
FRC0475 |  | CB |  | JGH3150FAG | 100 | 150 | [5 empty] | 40 | 104 |  | (1) (3) (7f)
|  | STR |  | AE16NNS0 | 10 | 140
FRC0476 |  | CB |  | JGH3200FAG | 100 | 200 | [5 empty] | 50 | 130
|  | STR |  | AE16NNS0 | 10 | 140
FRC0477 | C | CB | Eaton | JGH3125FAG | 65 | 125 | 480 | 3 | 65 | 460 | 3 | 60 | 77 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16NNS0 | 10 | 140
FRC0478 |  | CB |  | JGH3150FAG | 65 | 150 | [5 empty] | 75 | 96 |  | (1) (3) (7f)
|  | STR |  | AE16NNS0 | 10 | 140
FRC0479 |  | CB |  | JGH3175FAG | 65 | 175 | [5 empty] | 100 | 124
|  | STR |  | AE16NNS0 | 10 | 140
FRC0480 | C | CB | Eaton | JGH3125FAG | 25 | 125 | 600 | 3 | 25 | 575 | 3 | 75 | 77 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16NNS0 | 10 | 140
FRC0481 |  | CB |  | JGH3150FAG | 25 | 150 | [5 empty] | 100 | 99 |  | (1) (3) (7f)
|  | STR |  | AE16NNS0 | 10 | 140
FRC0482 |  | CB |  | JGH3175FAG | 25 | 175 | [5 empty] | 125 | 125
|  | STR |  | AE16NNS0 | 10 | 140
FRC0483 | C | CB | Eaton | JDC3150 | 200 | 150 | 200 | 3 | 100 | 200 | 3 | 25 | 78.2 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16NNS0 | 10 | 140
FRC0484 |  | CB |  | JDC3175 | 200 | 175 | [5 empty] | 30 | 92 |  | (1) (3) (7f)
|  | STR |  | AE16NNS0 | 10 | 140
FRC0485 |  | CB |  | JDC3250 | 200 | 250 | [5 empty] | 40 | 120
|  | STR |  | AE16NNS0 | 10 | 140
FRC0486 | C | CB | Eaton | JDC3150 | 200 | 150 | 208 | 3 | 100 | 208 | 3 | 25 | 74.8 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16NNS0 | 10 | 140
FRC0487 |  | CB |  | JDC3175 | 200 | 175 | [5 empty] | 30 | 88
|  | STR |  | AE16NNS0 | 10 | 140
FRC0488 |  | CB |  | JDC3200 | 200 | 200 | [5 empty] | 40 | 114 |  | (1) (3) (7f)
|  | STR |  | AE16NNS0 | 10 | 140
FRC0489 | C | CB | Eaton | JDC3125 | 200 | 125 | 240 | 3 | 100 | 230 | 3 | 30 | 80 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16NNS0 | 10 | 140
FRC0490 |  | CB |  | JDC3150 | 200 | 150 | [5 empty] | 40 | 104 |  | (1) (3) (7f)
|  | STR |  | AE16NNS0 | 10 | 140
FRC0491 |  | CB |  | JDC3200 | 200 | 200 | [5 empty] | 50 | 130
|  | STR |  | AE16NNS0 | 10 | 140
FRC0492 | C | CB | Eaton | JDC3125 | 100 | 125 | 480 | 3 | 100 | 460 | 3 | 60 | 77 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16NNS0 | 10 | 140
FRC0493 |  | CB |  | JDC3150 | 100 | 150 | [5 empty] | 75 | 96 |  | (1) (3) (7f)
|  | STR |  | AE16NNS0 | 10 | 140
FRC0494 |  | CB |  | JDC3175 | 100 | 175 | [5 empty] | 100 | 124
|  | STR |  | AE16NNS0 | 10 | 140
FRC0495 | C | CB | Eaton | JDC3125 | 35 | 125 | 600 | 3 | 35 | 575 | 3 | 75 | 77 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16NNS0 | 10 | 140
FRC0496 |  | CB |  | JDC3150 | 35 | 150 | [5 empty] | 100 | 99 |  | (1) (3) (7f)
|  | STR |  | AE16NNS0 | 10 | 140
FRC0497 |  | CB |  | JDC3175 | 35 | 175 | [5 empty] | 125 | 125
|  | STR |  | AE16NNS0 | 10 | 140
FRC0498 | C | CB | Eaton | LA3125PR | 200 | 125 | 600 | 3 | 100 | 575 | 3 | 75 | 77 | 2.5 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16NNS0 | 10 | 140
FRC0499 |  | CB |  | LA3150PR | 200 | 150 | [5 empty] | 100 | 99 |  | (1) (3) (7f)
|  | STR |  | AE16NNS0 | 10 | 140
FRC0500 |  | CB |  | LA3175PR | 200 | 175 | [5 empty] | 125 | 125
|  | STR |  | AE16NN0 | 10 | 140
FRC0501 | C | CB | Eaton | HFD3015L | 100 | 15 | 200 | 3 | 65 | 200 | 3 | 1 | 4.8 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56BN0 | 5 | 18
FRC0502 |  | CB |  | HFD3020L | 100 | 20 | [5 empty] | 1.5 | 6.9
|  | STR |  | AN56BN0 | 5 | 18
FRC0503 |  | CB |  | HFD3020L | 100 | 20 | [5 empty] | 2 | 7.8
|  | STR |  | AN56BN0 | 5 | 18
FRC0504 |  | CB |  | HFD3030L | 100 | 30 | [5 empty] | 3 | 11
|  | STR |  | AN56BN0 | 5 | 18
FRC0505 | C | CB | Eaton | HFD3015L | 100 | 15 | 208 | 3 | 65 | 208 | 3 | 1 | 4.6 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56BN0 | 5 | 18
FRC0506 |  | CB |  | HFD3020L | 100 | 20 | [5 empty] | 2 | 7.5
|  | STR |  | AN56BN0 | 5 | 18
FRC0507 |  | CB |  | HFD3020L | 100 | 20 | [5 empty] | 3 | 6.6
|  | STR |  | AN56BN0 | 5 | 18
FRC0508 | C | CB | Eaton | HFD3015L | 100 | 15 | 240 | 3 | 65 | 230 | 3 | 1 | 4.2 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56BN0 | 5 | 18
FRC0509 |  | CB |  | HFD3020L | 100 | 20 | [5 empty] | 2 | 6
|  | STR |  | AN56BN0 | 5 | 18
FRC0510 |  | CB |  | HFD3025L | 100 | 25 | [5 empty] | 3 | 9.6
|  | STR |  | AN56BN0 | 5 | 18
FRC0511 | C | CB | Eaton | HFD3015L | 65 | 15 | 480 | 3 | 65 | 460 | 3 | 3 | 4.8 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56BN0 | 5 | 18
FRC0512 |  | CB |  | HFD3020L | 65 | 20 | [5 empty] | 5 | 7.6
|  | STR |  | AN56BN0 | 5 | 18
FRC0513 | C | CB | Eaton | HFD3015L | 25 | 15 | 600 | 3 | 25 | 575 | 3 | 3 | 3.9 | 0.69 | (1) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56BN0 | 5 | 18
FRC0514 |  | CB |  | HFD3015L | 25 | 15 | [5 empty] | 5 | 6.1
|  | STR |  | AN56BN0 | 5 | 18
FRC0515 | C | CB | Eaton | FDC3015L | 200 | 15 | 200 | 3 | 100 | 200 | 3 | 1 | 4.8 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56BN0 | 5 | 18
FRC0516 |  | CB |  | FDC3020L | 200 | 20 | [5 empty] | 1.5 | 6.9
|  | STR |  | AN56BN0 | 5 | 18
FRC0517 |  | CB |  | FDC3020L | 200 | 20 | [5 empty] | 2 | 7.8
|  | STR |  | AN56BN0 | 5 | 18
FRC0518 |  | CB |  | FDC3030L | 200 | 30 | [5 empty] | 3 | 11
|  | STR |  | AN56BN0 | 5 | 18
FRC0519 | C | CB | Eaton | FDC3015L | 200 | 15 | 208 | 3 | 100 | 208 | 3 | 1 | 4.6 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56BN0 | 5 | 18
FRC0520 |  | CB |  | FDC3020L | 200 | 20 | [5 empty] | 2 | 7.5
|  | STR |  | AN56BN0 | 5 | 18
FRC0521 |  | CB |  | FDC3020L | 200 | 20 | [5 empty] | 3 | 6.6
|  | STR |  | AN56BN0 | 5 | 18
FRC0522 | C | CB | Eaton | FDC3015L | 200 | 15 | 240 | 3 | 100 | 230 | 3 | 1 | 4.2 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56BN0 | 5 | 18
FRC0523 |  | CB |  | FDC3020L | 200 | 20 | [5 empty] | 2 | 6
|  | STR |  | AN56BN0 | 5 | 18
FRC0524 |  | CB |  | FDC3025L | 200 | 25 | [5 empty] | 3 | 9.6
|  | STR |  | AN56BN0 | 5 | 18
FRC0525 | C | CB | Eaton | FDC3015L | 100 | 15 | 480 | 3 | 100 | 460 | 3 | 3 | 4.8 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56BN0 | 5 | 18
FRC0526 |  | CB |  | FDC3020L | 100 | 20 | [5 empty] | 5 | 7.6
|  | STR |  | AN56BN0 | 5 | 18
FRC0527 | C | CB | Eaton | FDC3015L | 35 | 15 | 600 | 3 | 35 | 575 | 3 | 3 | 3.9 | 0.69 | (1) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56BN0 | 5 | 18
FRC0528 |  | CB |  | FDC3015L | 35 | 15 | [5 empty] | 5 | 6.1
|  | STR |  | AN56BN0 | 5 | 18
FRC0529 | C | CB | Eaton | HFD3015L | 100 | 15 | 200 | 3 | 65 | 200 | 3 | 1 | 6.9 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56DN0 | 5 | 27
FRC0530 |  | CB |  | HFD3030L | 100 | 30 | [5 empty] | 3 | 11
|  | STR |  | AN56DN0 | 5 | 27
FRC0531 |  | CB |  | HFD3035L | 100 | 35 | [5 empty] | 5 | 17.5
|  | STR |  | AN56DN0 | 5 | 27
FRC0532 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AN56DN0 | 5 | 27
FRC0533 | C | CB | Eaton | HFD3015L | 100 | 15 | 208 | 3 | 65 | 208 | 3 | 1 | 4.6 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56DN0 | 5 | 27
FRC0534 |  | CB |  | HFD3025L | 100 | 25 | [5 empty] | 3 | 10.6
|  | STR |  | AN56DN0 | 5 | 27
FRC0535 |  | CB |  | HFD3035L | 100 | 35 | [5 empty] | 5 | 16.7
|  | STR |  | AN56DN0 | 5 | 27
FRC0536 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | AN56DN0 | 5 | 27
FRC0537 | C | CB | Eaton | HFD3015L | 100 | 15 | 240 | 3 | 65 | 230 | 3 | 1 | 4.2 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56DN0 | 5 | 27
FRC0538 |  | CB |  | HFD3025L | 100 | 25 | [5 empty] | 3 | 9.6
|  | STR |  | AN56DN0 | 5 | 27
FRC0539 |  | CB |  | HFD3035L | 100 | 35 | [5 empty] | 5 | 15.2
|  | STR |  | AN56DN0 | 5 | 27
FRC0540 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 22
|  | STR |  | AN56DN0 | 5 | 27
FRC0541 | C | CB | Eaton | HFD3015L | 65 | 15 | 480 | 3 | 65 | 460 | 3 | 1 | 2.1 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56DN0 | 5 | 27
FRC0542 |  | CB |  | HFD3020L | 65 | 20 | [5 empty] | 3 | 4.8
|  | STR |  | AN56DN0 | 5 | 27
FRC0543 |  | CB |  | HFD3030L | 65 | 30 | [5 empty] | 5 | 7.6
|  | STR |  | AN56DN0 | 5 | 27
FRC0544 |  | CB |  | HFD3035L | 65 | 35 | [5 empty] | 10 | 14
|  | STR |  | AN56DN0 | 5 | 27
FRC0545 | C | - | Eaton | - | - | - | 600 | 3 | 25 | 575 | 3 | - | - | 0.69 | (1) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | - |  | - | - | -
FRC0546 |  | CB |  | HFD3015L | 25 | 15 | [5 empty] | 3 | 3.9
|  | STR |  | AN56DN0 | 5 | 27
FRC0547 |  | CB |  | HFD3025L | 25 | 25 | [5 empty] | 5 | 6.1
|  | STR |  | AN56DN0 | 5 | 27
FRC0548 |  | CB |  | HFD3030L | 25 | 30 | [5 empty] | 10 | 11
|  | STR |  | AN56DN0 | 5 | 27
FRC0549 | C | CB | Eaton | FDC3015L | 200 | 15 | 200 | 3 | 100 | 200 | 3 | 1 | 6.9 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56DN0 | 5 | 27
FRC0550 |  | CB |  | FDC3030L | 200 | 30 | [5 empty] | 3 | 11
|  | STR |  | AN56DN0 | 5 | 27
FRC0551 |  | CB |  | FDC3035L | 200 | 35 | [5 empty] | 5 | 17.5
|  | STR |  | AN56DN0 | 5 | 27
FRC0552 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AN56DN0 | 5 | 27
FRC0553 | C | CB | Eaton | FDC3015L | 200 | 15 | 208 | 3 | 100 | 208 | 3 | 1 | 4.6 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56DN0 | 5 | 27
FRC0554 |  | CB |  | FDC3025L | 200 | 25 | [5 empty] | 3 | 10.6
|  | STR |  | AN56DN0 | 5 | 27
FRC0555 |  | CB |  | FDC3035L | 200 | 35 | [5 empty] | 5 | 16.7
|  | STR |  | AN56DN0 | 5 | 27
FRC0556 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | AN56DN0 | 5 | 27
FRC0557 | C | CB | Eaton | FDC3015L | 200 | 15 | 240 | 3 | 100 | 230 | 3 | 1 | 4.2 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56DN0 | 5 | 27
FRC0558 |  | CB |  | FDC3025L | 200 | 25 | [5 empty] | 3 | 9.6
|  | STR |  | AN56DN0 | 5 | 27
FRC0559 |  | CB |  | FDC3035L | 200 | 35 | [5 empty] | 5 | 15.2
|  | STR |  | AN56DN0 | 5 | 27
FRC0560 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 22
|  | STR |  | AN56DN0 | 5 | 27
FRC0561 | C | - | Eaton | - | - | - | 480 | 3 | 100 | 460 | 3 | - | - | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | - |  | - | - | -
FRC0562 |  | CB |  | FDC3020L | 100 | 20 | [5 empty] | 3 | 4.8
|  | STR |  | AN56DN0 | 5 | 27
FRC0563 |  | CB |  | FDC3030L | 100 | 30 | [5 empty] | 5 | 7.6
|  | STR |  | AN56DN0 | 5 | 27
FRC0564 |  | CB |  | FDC3035L | 100 | 35 | [5 empty] | 10 | 14
|  | STR |  | AN56DN0 | 5 | 27
FRC0565 | C | CB | Eaton | FDC3015L | 35 | 15 | 600 | 3 | 35 | 575 | 3 | 3 | 3.9 | 0.69 | (1) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56DN0 | 5 | 27
FRC0566 |  | CB |  | FDC3015L | 35 | 15 | [5 empty] | 5 | 6.1
|  | STR |  | AN56DN0 | 5 | 27
FRC0567 |  | CB |  | FDC3025L | 35 | 25 | [5 empty] | 7.5 | 9
|  | STR |  | AN56DN0 | 5 | 27
FRC0568 |  | CB |  | FDC3030L | 35 | 30 | [5 empty] | 10 | 11
|  | STR |  | AN56DN0 | 5 | 27
FRC0569 | C | CB | Eaton | HFD3015L | 25 | 15 | 600 | 3 | 100 | 575 | 3 | 3 | 3.9 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AN56DN0 | 5 | 27
FRC0570 | C | CB | Eaton | HFD3015L | 25 | 15 | 600 | 3 | 100 | 575 | 3 | 5 | 6.1
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AN56DN0 | 5 | 27
FRC0571 | C | CB | Eaton | HFD3025L | 25 | 25 | 600 | 3 | 100 | 575 | 3 | 7.5 | 9
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AN56DN0 | 5 | 27
FRC0572 | C | CB | Eaton | HFD3030L | 25 | 30 | 600 | 3 | 100 | 575 | 3 | 10 | 11
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AN56DN0 | 5 | 27
FRC0573 | C | CB | Eaton | HFD3035L | 100 | 35 | 200 | 3 | 65 | 200 | 3 | 5 | 17.5 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56GN0 | 5 | 45
FRC0574 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AN56GN0 | 5 | 45
FRC0575 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 10 | 32.2 |  | (1) (3) (7c)
|  | STR |  | AN56GN0 | 5 | 45
FRC0576 | C | CB | Eaton | HFD3035L | 100 | 35 | 208 | 3 | 65 | 208 | 3 | 5 | 16.7 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56GN0 | 5 | 45
FRC0577 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | AN56GN0 | 5 | 45
FRC0578 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 10 | 30.8 |  | (1) (3) (7c)
|  | STR |  | AN56GN0 | 5 | 45
FRC0579 | C | CB | Eaton | HFD3035L | 100 | 35 | 240 | 3 | 65 | 230 | 3 | 7.5 | 22 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56GN0 | 5 | 45
FRC0580 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 10 | 28 |  | (1) (3) (7c)
|  | STR |  | AN56GN0 | 5 | 45
FRC0581 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 15 | 42
|  | STR |  | AN56GN0 | 5 | 45
FRC0582 | C | CB | Eaton | HFD3050L | 65 | 50 | 480 | 3 | 65 | 460 | 3 | 15 | 21 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56GN0 | 5 | 45
FRC0583 |  | CB |  | HFD3050L | 65 | 50 | [5 empty] | 20 | 27
|  | STR |  | AN56GN0 | 5 | 45
FRC0584 |  | CB |  | HFD3050L | 65 | 50 | [5 empty] | 25 | 34 |  | (1) (3) (7c)
|  | STR |  | AN56GN0 | 5 | 45
FRC0585 | C | CB | Eaton | HFD3035L | 25 | 35 | 600 | 3 | 25 | 575 | 3 | 15 | 17 | 0.69 | (1) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56GN0 | 5 | 45
FRC0586 |  | CB |  | HFD3050L | 25 | 50 | [5 empty] | 20 | 22
|  | STR |  | AN56GN0 | 5 | 45
FRC0587 |  | CB |  | HFD3050L | 25 | 50 | [5 empty] | 25 | 27
|  | STR |  | AN56GN0 | 5 | 45
FRC0588 | C | CB | Eaton | FDC3035L | 100 | 35 | 200 | 3 | 100 | 200 | 3 | 5 | 17.5 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56GN0 | 5 | 45
FRC0589 |  | CB |  | FDC3050L | 100 | 50 | [5 empty] | 7.5 | 25.3 |  | (1) (3) (7c)
|  | STR |  | AN56GN0 | 5 | 45
FRC0590 |  | CB |  | FDC3050L | 100 | 50 | [5 empty] | 10 | 32.2
|  | STR |  | AN56GN0 | 5 | 45
FRC0591 | C | CB | Eaton | FDC3035L | 100 | 35 | 208 | 3 | 100 | 208 | 3 | 5 | 16.7 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56GN0 | 5 | 45
FRC0592 |  | CB |  | FDC3050L | 100 | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | AN56GN0 | 5 | 45
FRC0593 |  | CB |  | FDC3050L | 100 | 50 | [5 empty] | 10 | 30.8 |  | (1) (3) (7c)
|  | STR |  | AN56GN0 | 5 | 45
FRC0594 | C | CB | Eaton | FDC3035L | 100 | 35 | 240 | 3 | 100 | 230 | 3 | 7.5 | 22 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56GN0 | 5 | 45
FRC0595 |  | CB |  | FDC3050L | 100 | 50 | [5 empty] | 10 | 28 |  | (1) (3) (7c)
|  | STR |  | AN56GN0 | 5 | 45
FRC0596 |  | CB |  | FDC3050L | 100 | 50 | [5 empty] | 15 | 42
|  | STR |  | AN56GN0 | 5 | 45
FRC0597 | C | CB | Eaton | FDC3050L | 100 | 50 | 480 | 3 | 100 | 460 | 3 | 15 | 21 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56GN0 | 5 | 45
FRC0598 |  | CB |  | FDC3050L | 100 | 50 | [5 empty] | 20 | 27
|  | STR |  | AN56GN0 | 5 | 45
FRC0599 |  | CB |  | FDC3050L | 100 | 50 | [5 empty] | 25 | 34 |  | (1) (3) (7c)
|  | STR |  | AN56GN0 | 5 | 45
FRC0600 | C | CB | Eaton | FDC3035L | 35 | 35 | 600 | 3 | 35 | 575 | 3 | 15 | 17 | 0.69 | (1) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56GN0 | 5 | 45
FRC0601 |  | CB |  | FDC3050L | 35 | 50 | [5 empty] | 20 | 22
|  | STR |  | AN56GN0 | 5 | 45
FRC0602 |  | CB |  | FDC3050L | 35 | 50 | [5 empty] | 25 | 27
|  | STR |  | AN56GN0 | 5 | 45
FRC0603 | C | CB | Eaton | HFD3035L | 25 | 35 | 600 | 3 | 100 | 575 | 3 | 15 | 17 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AN56GN0 | 5 | 45
FRC0604 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 29 | 22
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AN56GN0 | 5 | 45
FRC0605 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 25 | 27
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AN56GN0 | 5 | 45
FRC0606 | C | CB | Eaton | EGH3035FFG | 100 | 35 | 200 | 3 | 65 | 200 | 3 | 5 | 17.5 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56GN0 | 5 | 45
FRC0607 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 7.5 | 25.3 |  | (1) (3) (7c)
|  | STR |  | AN56GN0 | 5 | 45
FRC0608 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 10 | 32.2
|  | STR |  | AN56GN0 | 5 | 45
FRC0609 | C | CB | Eaton | EGH3035FFG | 100 | 35 | 208 | 3 | 65 | 208 | 3 | 5 | 16.7 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56GN0 | 5 | 45
FRC0610 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | AN56GN0 | 5 | 45
FRC0611 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 10 | 30.8 |  | (1) (3) (7c)
|  | STR |  | AN56GN0 | 5 | 45
FRC0612 | C | CB | Eaton | EGH3035FFG | 100 | 35 | 240 | 3 | 65 | 230 | 3 | 7.5 | 22 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56GN0 | 5 | 45
FRC0613 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 10 | 28 |  | (1) (3) (7c)
|  | STR |  | AN56GN0 | 5 | 45
FRC0614 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 15 | 42
|  | STR |  | AN56GN0 | 5 | 45
FRC0615 | C | CB | Eaton | EGH3050FFG | 65 | 50 | 480 | 3 | 65 | 460 | 3 | 15 | 21 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56GN0 | 5 | 45
FRC0616 |  | CB |  | EGH3050FFG | 65 | 50 | [5 empty] | 20 | 27
|  | STR |  | AN56GN0 | 5 | 45
FRC0617 |  | CB |  | EGH3050FFG | 65 | 50 | [5 empty] | 25 | 34 |  | (1) (3) (7c)
|  | STR |  | AN56GN0 | 5 | 45
FRC0618 | C | CB | Eaton | HFD3090L | 100 | 90 | 200 | 3 | 65 | 200 | 3 | 15 | 48.3 | 1.06 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56KN0 | 5 | 90
FRC0619 |  | CB |  | HFD3100L | 100 | 100 | [5 empty] | 20 | 62.1
|  | STR |  | AN56KN0 | 5 | 90
FRC0620 |  | CB |  | HFD3125L | 100 | 125 | [5 empty] | 25 | 78.2
|  | STR |  | AN56KN0 | 5 | 90
FRC0621 | C | CB | Eaton | HFD3070L | 100 | 70 | 208 | 3 | 65 | 208 | 3 | 15 | 46.2 | 1.06 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56KN0 | 5 | 90
FRC0622 |  | CB |  | HFD3090L | 100 | 90 | [5 empty] | 20 | 59.4
|  | STR |  | AN56KN0 | 5 | 90
FRC0623 |  | CB |  | HFD3125L | 100 | 125 | [5 empty] | 25 | 74.8
|  | STR |  | AN56KN0 | 5 | 90
FRC0624 | C | CB | Eaton | HFD3090L | 100 | 90 | 240 | 3 | 65 | 230 | 3 | 20 | 54 | 1.06 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56KN0 | 5 | 90
FRC0625 |  | CB |  | HFD3125L | 100 | 125 | [5 empty] | 25 | 68
|  | STR |  | AN56KN0 | 5 | 90
FRC0626 |  | CB |  | HFD3125L | 100 | 125 | [5 empty] | 30 | 80
|  | STR |  | AN56KN0 | 5 | 90
FRC0627 | C | CB | Eaton | HFD3060L | 65 | 60 | 480 | 3 | 65 | 460 | 3 | 30 | 40 | 1.06 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56KN0 | 5 | 90
FRC0628 |  | CB |  | HFD3090L | 65 | 90 | [5 empty] | 40 | 52 |  | (1) (3) (7e)
|  | STR |  | AN56KN0 | 5 | 90
FRC0629 |  | CB |  | HFD3100L | 65 | 100 | [5 empty] | 50 | 65
|  | STR |  | AN56KN0 | 5 | 90
FRC0630 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 25 | 575 | 3 | 30 | 32 | 1.06 | (1) (3) (6a) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56KN0 | 5 | 90
FRC0631 |  | CB |  | HFD3060L | 25 | 60 | [5 empty] | 40 | 41 |  | (1) (3) (6b) (7c)
|  | STR |  | AN56KN0 | 5 | 90
FRC0632 |  | CB |  | HFD3090L | 25 | 90 | [5 empty] | 50 | 52 |  | (1) (3) (6b) (7e)
|  | STR |  | AN56KN0 | 5 | 90
FRC0633 | C | CB | Eaton | FDC3090L | 200 | 90 | 200 | 3 | 100 | 200 | 3 | 15 | 48.3 | 1.06 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56KN0 | 5 | 90
FRC0634 |  | CB |  | FDC3100L | 200 | 100 | [5 empty] | 20 | 62.1
|  | STR |  | AN56KN0 | 5 | 90
FRC0635 |  | CB |  | FDC3125L | 200 | 125 | [5 empty] | 25 | 78.2
|  | STR |  | AN56KN0 | 5 | 90
FRC0636 | C | CB | Eaton | FDC3070L | 200 | 70 | 208 | 3 | 100 | 208 | 3 | 15 | 46.2 | 1.06 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56KN0 | 5 | 90
FRC0637 |  | CB |  | FDC3090L | 200 | 90 | [5 empty] | 20 | 59.4
|  | STR |  | AN56KN0 | 5 | 90
FRC0638 |  | CB |  | FDC3125L | 200 | 125 | [5 empty] | 25 | 74.8
|  | STR |  | AN56KN0 | 5 | 90
FRC0639 | C | CB | Eaton | FDC3090L | 200 | 90 | 240 | 3 | 100 | 230 | 3 | 20 | 54 | 1.06 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56KN0 | 5 | 90
FRC0640 |  | CB |  | FDC3125L | 200 | 125 | [5 empty] | 25 | 68
|  | STR |  | AN56KN0 | 5 | 90
FRC0641 |  | CB |  | FDC3125L | 200 | 125 | [5 empty] | 30 | 80
|  | STR |  | AN56KN0 | 5 | 90
FRC0642 | C | CB | Eaton | FDC3060L | 100 | 60 | 480 | 3 | 100 | 460 | 3 | 30 | 40 | 1.06 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56KN0 | 5 | 90
FRC0643 |  | CB |  | FDC3090L | 100 | 90 | [5 empty] | 40 | 52 |  | (1) (3) (7e)
|  | STR |  | AN56KN0 | 5 | 90
FRC0644 |  | CB |  | FDC3100L | 100 | 100 | [5 empty] | 50 | 65
|  | STR |  | AN56KN0 | 5 | 90
FRC0645 | C | CB | Eaton | FDC3050L | 35 | 50 | 600 | 3 | 35 | 575 | 3 | 30 | 32 | 1.06 | (1) (3) (6a) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56KN0 | 5 | 90
FRC0646 |  | CB |  | FDC3060L | 35 | 60 | [5 empty] | 40 | 41 |  | (1) (3) (6b) (7c)
|  | STR |  | AN56KN0 | 5 | 90
FRC0647 |  | CB |  | FDC3090L | 35 | 90 | [5 empty] | 50 | 52 |  | (1) (3) (6b) (7e)
|  | STR |  | AN56KN0 | 5 | 90
FRC0648 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 30 | 32 | 1.42 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AN56KN0 | 5 | 90
FRC0649 | C | CB | Eaton | HFD3060L | 25 | 60 | 600 | 3 | 100 | 575 | 3 | 40 | 41
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AN56KN0 | 5 | 90
FRC0650 | C | CB | Eaton | HFD3090L | 25 | 90 | 600 | 3 | 100 | 575 | 3 | 50 | 52 |  | (1) (3) (7e)
|  | C. Limiter |  | LFD3150R | 200 | 150
|  | STR |  | AN56KN0 | 5 | 90
FRC0651 | C | CB | Eaton | EGH3090FFG | 100 | 90 | 200 | 3 | 65 | 200 | 3 | 15 | 48.3 | 1.06 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56KN0 | 5 | 90
FRC0652 |  | CB |  | EGH3100FFG | 100 | 100 | [5 empty] | 20 | 62.1
|  | STR |  | AN56KN0 | 5 | 90
FRC0653 |  | CB |  | EGH3125FFG | 100 | 125 | [5 empty] | 25 | 78.2
|  | STR |  | AN56KN0 | 5 | 90
FRC0654 | C | CB | Eaton | EGH3070FFG | 100 | 70 | 208 | 3 | 65 | 208 | 3 | 15 | 46.2 | 1.06 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56KN0 | 5 | 90
FRC0655 |  | CB |  | EGH3090FFG | 100 | 90 | [5 empty] | 20 | 59.4
|  | STR |  | AN56KN0 | 5 | 90
FRC0656 |  | CB |  | EGH3215FFG | 100 | 125 | [5 empty] | 25 | 74.8
|  | STR |  | AN56KN0 | 5 | 90
FRC0657 | C | CB | Eaton | EGH3090FFG | 100 | 90 | 240 | 3 | 65 | 230 | 3 | 20 | 54 | 1.06 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56KN0 | 5 | 90
FRC0658 |  | CB |  | EGH3125FFG | 100 | 125 | [5 empty] | 25 | 68
|  | STR |  | AN56KN0 | 5 | 90
FRC0659 |  | CB |  | EGH3125FFG | 100 | 125 | [5 empty] | 30 | 80
|  | STR |  | AN56KN0 | 5 | 90
FRC0660 | C | CB | Eaton | EGH3060FFG | 65 | 60 | 480 | 3 | 65 | 460 | 3 | 30 | 40 | 1.06 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56KN0 | 5 | 90
FRC0661 |  | CB |  | EGH3090FFG | 65 | 90 | [5 empty] | 40 | 52 |  | (1) (3) (7e)
|  | STR |  | AN56KN0 | 5 | 90
FRC0662 |  | CB |  | EGH3100FFG | 65 | 100 | [5 empty] | 50 | 65
|  | STR |  | AN56KN0 | 5 | 90
FRC0663 | C | CB | Eaton | JGH3125FAG | 100 | 125 | 200 | 3 | 65 | 200 | 3 | 25 | 78.2 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56NN0 | 10 | 135
FRC0664 |  | CB |  | JGH3150FAG | 100 | 150 | [5 empty] | 30 | 92 |  | (1) (3) (7f)
|  | STR |  | AN56NN0 | 10 | 135
FRC0665 |  | CB |  | JGH3175FAG | 100 | 175 | [5 empty] | 40 | 120
|  | STR |  | AN56NN0 | 10 | 135
FRC0666 | C | CB | Eaton | JGH3150FAG | 100 | 150 | 208 | 3 | 65 | 208 | 3 | 25 | 88 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56NN0 | 10 | 135
FRC0667 |  | CB |  | JGH3175FAG | 100 | 175 | [5 empty] | 40 | 114 |  | (1) (3) (7f)
|  | STR |  | AN56NN0 | 10 | 135
FRC0668 |  | CB |  | JGH3200FAG | 100 | 200 | [5 empty] | 50 | 143
|  | STR |  | AN56NN0 | 10 | 135
FRC0669 | C | CB | Eaton | JGH3125FAG | 100 | 125 | 240 | 3 | 65 | 230 | 3 | 30 | 80 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56NN0 | 10 | 135
FRC0670 |  | CB |  | JGH3150FAG | 100 | 150 | [5 empty] | 40 | 104 |  | (1) (3) (7f)
|  | STR |  | AN56NN0 | 10 | 135
FRC0671 |  | CB |  | JGH3200FAG | 100 | 200 | [5 empty] | 50 | 130
|  | STR |  | AN56NN0 | 10 | 135
FRC0672 | C | CB | Eaton | JGH3125FAG | 65 | 125 | 480 | 3 | 65 | 460 | 3 | 60 | 77 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56NN0 | 10 | 135
FRC0673 |  | CB |  | JGH3150FAG | 65 | 150 | [5 empty] | 75 | 96 |  | (1) (3) (7f)
|  | STR |  | AN56NN0 | 10 | 135
FRC0674 |  | CB |  | JGH3175FAG | 65 | 175 | [5 empty] | 100 | 124
|  | STR |  | AN56NN0 | 10 | 135
FRC0675 | C | CB | Eaton | JGH3100FAG | 25 | 100 | 600 | 3 | 25 | 575 | 3 | 60 | 62 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56NN0 | 10 | 135
FRC0676 |  | CB |  | JGH3125FAG | 25 | 125 | [5 empty] | 75 | 77
|  | STR |  | AN56NN0 | 10 | 135
FRC0677 |  | CB |  | JGH3150FAG | 25 | 150 | [5 empty] | 100 | 99 |  | (1) (3) (7f)
|  | STR |  | AN56NN0 | 10 | 135
FRC0678 | C | CB | Eaton | JDC3125 | 200 | 125 | 200 | 3 | 100 | 200 | 3 | 25 | 78.2 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56NN0 | 10 | 135
FRC0679 |  | CB |  | JDC3150 | 200 | 150 | [5 empty] | 30 | 92 |  | (1) (3) (7f)
|  | STR |  | AN56NN0 | 10 | 135
FRC0680 |  | CB |  | JDC3175 | 200 | 175 | [5 empty] | 40 | 120
|  | STR |  | AN56NN0 | 10 | 135
FRC0681 | C | CB | Eaton | JDC3150 | 200 | 150 | 208 | 3 | 100 | 208 | 3 | 25 | 88 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56NN0 | 10 | 135
FRC0682 |  | CB |  | JDC3175 | 200 | 175 | [5 empty] | 40 | 114 |  | (1) (3) (7f)
|  | STR |  | AN56NN0 | 10 | 135
FRC0683 |  | CB |  | JDC3200 | 200 | 200 | [5 empty] | 50 | 143
|  | STR |  | AN56NN0 | 10 | 135
FRC0684 | C | CB | Eaton | JDC3125 | 200 | 125 | 240 | 3 | 100 | 230 | 3 | 30 | 80 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56NN0 | 10 | 135
FRC0685 |  | CB |  | JDC3150 | 200 | 150 | [5 empty] | 40 | 104 |  | (1) (3) (7f)
|  | STR |  | AN56NN0 | 10 | 135
FRC0686 |  | CB |  | JDC3200 | 200 | 200 | [5 empty] | 50 | 130
|  | STR |  | AN56NN0 | 10 | 135
FRC0687 | C | CB | Eaton | JDC3125 | 100 | 125 | 480 | 3 | 100 | 460 | 3 | 60 | 77 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56NN0 | 10 | 135
FRC0688 |  | CB |  | JDC3150 | 100 | 150 | [5 empty] | 75 | 96 |  | (1) (3) (7f)
|  | STR |  | AN56NN0 | 10 | 135
FRC0689 |  | CB |  | JDC3175 | 100 | 175 | [5 empty] | 100 | 124
|  | STR |  | AN56NN0 | 10 | 135
FRC0690 | C | CB | Eaton | JDC3100 | 35 | 100 | 600 | 3 | 35 | 575 | 3 | 60 | 62 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56NN0 | 10 | 135
FRC0691 |  | CB |  | JDC3125 | 35 | 125 | [5 empty] | 75 | 77
|  | STR |  | AN56NN0 | 10 | 135
FRC0692 |  | CB |  | JDC3150 | 35 | 150 | [5 empty] | 100 | 99 |  | (1) (3) (7f)
|  | STR |  | AN56NN0 | 10 | 135
FRC0693 | C | CB | Eaton | LA3100PR | 200 | 100 | 600 | 3 | 100 | 575 | 3 | 60 | 62 | 2.5 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56NN0 | 10 | 135
FRC0694 |  | CB |  | LA3125PR | 200 | 125 | [5 empty] | 75 | 77
|  | STR |  | AN56NN0 | 10 | 135
FRC0695 |  | CB |  | LA3150PR | 200 | 150 | [5 empty] | 100 | 99 |  | (1) (3) (7f)
|  | STR |  | AN56NN0 | 10 | 135
FRC0696 | C | CB | Eaton | HKD3250 | 100 | 250 | 200 | 2 | 65 | 200 | 3 | 50 | 150 | 2.15 | (1) (3) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56SN0 | 10 | 270
FRC0697 |  | CB |  | HKD3350 | 100 | 350 | [5 empty] | 60 | 177
|  | STR |  | AN56SN0 | 10 | 270
FRC0698 |  | CB |  | HKD3400 | 100 | 400 | [5 empty] | 75 | 221
|  | STR |  | AN56SN0 | 10 | 270
FRC0699 | C | CB | Eaton | HKD3200 | 100 | 200 | 208 | 3 | 65 | 208 | 3 | 50 | 143 | 2.15 | (1) (3) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56SN0 | 10 | 270
FRC0700 |  | CB |  | HKD3250 | 100 | 250 | [5 empty] | 60 | 169
|  | STR |  | AN56SN0 | 10 | 270
FRC0701 |  | CB |  | HKD3350 | 100 | 350 | [5 empty] | 75 | 211
|  | STR |  | AN56SN0 | 10 | 270
FRC0702 | C | CB | Eaton | HKD3250 | 100 | 250 | 240 | 3 | 65 | 230 | 3 | 60 | 154 | 2.15 | (1) (3) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56SN0 | 10 | 270
FRC0703 |  | CB |  | HKD3350 | 100 | 350 | [5 empty] | 75 | 192
|  | STR |  | AN56SN0 | 10 | 270
FRC0704 |  | CB |  | HKD3400 | 100 | 400 | [5 empty] | 100 | 248
|  | STR |  | AN56SN0 | 10 | 270
FRC0705 | C | CB | Eaton | HKD3250 | 65 | 250 | 480 | 3 | 65 | 460 | 3 | 125 | 156 | 2.15 | (1) (3) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56SN0 | 10 | 270
FRC0706 |  | CB |  | HKD3250 | 65 | 250 | [5 empty] | 150 | 180
|  | STR |  | AN56SN0 | 10 | 270
FRC0707 |  | CB |  | HKD3350 | 65 | 350 | [5 empty] | 200 | 240
|  | STR |  | AN56SN0 | 10 | 270
FRC0708 | C | CB | Eaton | HKD3175 | 35 | 175 | 600 | 3 | 25 | 575 | 3 | 125 | 125 | 2.15 | (1) (3) (7f) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56SN0 | 10 | 270
FRC0709 |  | CB |  | HKD3200 | 35 | 200 | [5 empty] | 150 | 144 |  | (1) (3) (7j)
|  | STR |  | AN56SN0 | 10 | 270
FRC0710 |  | CB |  | HLD3300 | 35 | 300 |  |  | 35 |  |  | 200 | 192
|  | STR |  | AN56SN0 | 10 | 270
FRC0711 | C | CB | Eaton | KDC3250 | 200 | 250 | 200 | 2 | 100 | 200 | 3 | 50 | 150 | 2.15 | (1) (3) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56SN0 | 10 | 270
FRC0712 |  | CB |  | KDC3350 | 200 | 350 | [5 empty] | 60 | 177
|  | STR |  | AN56SN0 | 10 | 270
FRC0713 |  | CB |  | KDC3400 | 200 | 400 | [5 empty] | 75 | 221
|  | STR |  | AN56SN0 | 10 | 270
FRC0714 | C | CB | Eaton | KDC3200 | 200 | 200 | 208 | 3 | 100 | 208 | 3 | 50 | 143 | 2.15 | (1) (3) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56SN0 | 10 | 270
FRC0715 |  | CB |  | KDC3250 | 200 | 250 | [5 empty] | 60 | 169
|  | STR |  | AN56SN0 | 10 | 270
FRC0716 |  | CB |  | KDC3350 | 200 | 350 | [5 empty] | 75 | 211
|  | STR |  | AN56SN0 | 10 | 270
FRC0717 | C | CB | Eaton | KDC3250 | 200 | 250 | 240 | 3 | 100 | 230 | 3 | 60 | 154 | 2.15 | (1) (3) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56SN0 | 10 | 270
FRC0718 |  | CB |  | KDC3350 | 200 | 350 | [5 empty] | 75 | 192
|  | STR |  | AN56SN0 | 10 | 270
FRC0719 |  | CB |  | KDC3400 | 200 | 400 | [5 empty] | 100 | 248
|  | STR |  | AN56SN0 | 10 | 270
FRC0720 | C | CB | Eaton | KDC3250 | 100 | 250 | 480 | 3 | 100 | 460 | 3 | 125 | 156 | 2.15 | (1) (3) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56SN0 | 10 | 270
FRC0721 |  | CB |  | KDC3250 | 100 | 250 | [5 empty] | 150 | 180
|  | STR |  | AN56SN0 | 10 | 270
FRC0722 |  | CB |  | KDC3350 | 100 | 350 | [5 empty] | 200 | 240
|  | STR |  | AN56SN0 | 10 | 270
FRC0723 | C | CB | Eaton | KDC3175 | 50 | 175 | 600 | 3 | 50 | 575 | 3 | 125 | 125 | 2.15 | (1) (3) (7f) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56SN0 | 10 | 270
FRC0724 |  | CB |  | KDC3200 | 50 | 200 | [5 empty] | 150 | 144 |  | (1) (3) (7j)
|  | STR |  | AN56SN0 | 10 | 270
FRC0725 |  | CB |  | KDC3300 | 50 | 300 | [5 empty] | 200 | 192
|  | STR |  | AN56SN0 | 10 | 270
FRC0726 | C | CB | Eaton | LA3175PR | 200 | 175 | 600 | 3 | 100 | 575 | 3 | 125 | 125 | 2.5 | (1) (3) (7f) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56SN0 | 10 | 270
FRC0727 |  | CB |  | LA3200PR | 200 | 200 | [5 empty] | 150 | 144 |  | (1) (3) (7j)
|  | STR |  | AN56SN0 | 10 | 270
FRC0728 |  | CB |  | LA3300PR | 200 | 300 | [5 empty] | 200 | 192
|  | STR |  | AN56SN0 | 10 | 270
FRC0729 | C | CB | Eaton | HLD3400 | 100 | 400 | 200 | 3 | 65 | 200 | 3 | 100 | 285 | 3.23 | (1) (3) (7s) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56TN0 | 18 | 540
FRC0730 |  | CB |  | HLD3600 | 100 | 600 | [5 empty] | 125 | 359
|  | STR |  | AN56TN0 | 18 | 540
FRC0731 |  | CB |  | HLD3600 | 100 | 600 | [5 empty] | 150 | 414
|  | STR |  | AN56TN0 | 18 | 540
FRC0732 | C | CB | Eaton | HLD3400 | 100 | 400 | 208 | 3 | 65 | 208 | 3 | 100 | 273 | 3.23 | (1) (3) (7s) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56TN0 | 18 | 540
FRC0733 |  | CB |  | HLD3600 | 100 | 600 | [5 empty] | 125 | 343
|  | STR |  | AN56TN0 | 18 | 540
FRC0734 |  | CB |  | HLD3600 | 100 | 600 | [5 empty] | 150 | 396
|  | STR |  | AN56TN0 | 18 | 540
FRC0735 | C | CB | Eaton | HLD3500 | 100 | 500 | 240 | 3 | 65 | 230 | 3 | 125 | 312 | 3.23 | (1) (3) (7s) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56TN0 | 18 | 540
FRC0736 |  | CB |  | HLD3600 | 100 | 600 | [5 empty] | 150 | 360
|  | STR |  | AN56TN0 | 18 | 540
FRC0737 |  | CB |  | HLD3600 | 100 | 600 | [5 empty] | 200 | 480
|  | STR |  | AN56TN0 | 18 | 540
FRC0738 | C | CB | Eaton | HLD3500 | 65 | 500 | 480 | 3 | 65 | 460 | 3 | 250 | 302 | 3.23 | (1) (3) (7s) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56TN0 | 18 | 540
FRC0739 |  | CB |  | HLD3600 | 65 | 600 | [5 empty] | 300 | 361
|  | STR |  | AN56TN0 | 18 | 540
FRC0740 |  | CB |  | HLD3600 | 65 | 600 | [5 empty] | 350 | 414
|  | STR |  | AN56TN0 | 18 | 540
FRC0741 |  | CB |  | HLD3600 | 65 | 600 | [5 empty] | 400 | 477
|  | STR |  | AN56TN0 | 18 | 540
FRC0742 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
FRC0743 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
FRC0744 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
FRC0745 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
FRC0746 | C | CB | Eaton | LDC3400 | 200 | 400 | 200 | 3 | 65 | 200 | 3 | 100 | 285 | 3.23 | (1) (3) (7s) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56TN0 | 18 | 540
FRC0747 |  | CB |  | LDC3600 | 200 | 600 | [5 empty] | 125 | 359
|  | STR |  | AN56TN0 | 18 | 540
FRC0748 |  | CB |  | LDC3600 | 200 | 600 | [5 empty] | 150 | 414
|  | STR |  | AN56TN0 | 18 | 540
FRC0749 | C | CB | Eaton | LDC3400 | 200 | 400 | 208 | 3 | 65 | 208 | 3 | 100 | 273 | 3.23 | (1) (3) (7s) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56TN0 | 18 | 540
FRC0750 |  | CB |  | LDC3600 | 200 | 600 | [5 empty] | 125 | 343
|  | STR |  | AN56TN0 | 18 | 540
FRC0751 |  | CB |  | LDC3600 | 200 | 600 | [5 empty] | 150 | 396
|  | STR |  | AN56TN0 | 18 | 540
FRC0752 | C | CB | Eaton | LDC3500 | 200 | 500 | 240 | 3 | 65 | 230 | 3 | 125 | 312 | 3.23 | (1) (3) (7s) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56TN0 | 18 | 540
FRC0753 |  | CB |  | LDC3600 | 200 | 600 | [5 empty] | 150 | 360
|  | STR |  | AN56TN0 | 18 | 540
FRC0754 |  | CB |  | LDC3600 | 200 | 600 | [5 empty] | 200 | 480
|  | STR |  | AN56TN0 | 18 | 540
FRC0755 | C | CB | Eaton | LDC3500 | 100 | 500 | 480 | 3 | 65 | 460 | 3 | 250 | 302 | 3.23 | (1) (3) (7s) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56TN0 | 18 | 540
FRC0756 |  | CB |  | LDC3600 | 100 | 600 | [5 empty] | 300 | 361
|  | STR |  | AN56TN0 | 18 | 540
FRC0757 |  | CB |  | LDC3600 | 100 | 600 | [5 empty] | 350 | 414
|  | STR |  | AN56TN0 | 18 | 540
FRC0758 |  | CB |  | LDC3600 | 100 | 600 | [5 empty] | 400 | 477
|  | STR |  | AN56TN0 | 18 | 540
FRC0759 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
FRC0760 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
FRC0761 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
FRC0762 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
FRC0763 | C | CB | Eaton | HND312T33W + 12NES1200T | 100 | 1200 | 240 | 3 | 65 | 230 | 3 | 250 | 604 | 22.2 | (1) (3) (7m) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56UN0 | 30 | 810
FRC0764 |  | CB |  | HND312T33W + 12NES1200T | 100 | 1200 | [5 empty] | 300 | 720
|  | STR |  | AN56UN0 | 30 | 810
FRC0765 | C | CB | Eaton | HND312T33W + 12NES1200T | 65 | 1200 | 480 | 3 | 65 | 3 | 3 | 500 | 590 | 22.2 | (1) (3) (7m) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56UN0 | 30 | 810
FRC0766 |  | CB |  | HND312T33W + 12NES1200T | 65 | 1200 | [5 empty] | 600 | 722
|  | STR |  | AN56UN0 | 30 | 810
FRC0767 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
FRC0768 |  | - |  | - | - | - | [5 empty] | - | - |  | -
|  | - |  | - | - | -
FRC0769 | C | CB | Eaton | NDC312T33W + 12NES1200T | 200 | 1200 | 240 | 3 | 65 | 230 | 3 | 250 | 604 | 22.2 | (1) (3) (7m) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56UN0 | 30 | 810
FRC0770 |  | CB |  | NDC312T33W + 12NES1200T | 200 | 1200 | [5 empty] | 300 | 720
|  | STR |  | AN56UN0 | 30 | 810
FRC0771 | C | CB | Eaton | NDC312T33W + 12NES1200T | 100 | 1200 | 480 | 3 | 65 | 3 | 3 | 500 | 590 | 22.2 | (1) (3) (7m) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56UN0 | 30 | 810
FRC0772 |  | CB |  | NDC312T33W + 12NES1200T | 100 | 1200 | [5 empty] | 600 | 722
|  | STR |  | AN56UN0 | 30 | 810
FRC0773 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
FRC0774 |  | - |  | - | - | - | [5 empty] | - | - |  | -
|  | - |  | - | - | -
FRC0775 | C | CB | Eaton | HFD3020L | 100 | 20 | 200 | 3 | 65 | 200 | 3 | 2 | 7.8 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56DNS0 | 5 | 18
FRC0776 |  | CB |  | HFD3030L | 100 | 30 | [5 empty] | 3 | 11
|  | STR |  | AE56DNS0 | 5 | 18
FRC0777 |  | CB |  | HFD3035L | 100 | 35 | [5 empty] | 5 | 17.5
|  | STR |  | AE56DNS0 | 5 | 18
FRC0778 | C | CB | Eaton | HFD3020L | 100 | 20 | 208 | 3 | 65 | 208 | 3 | 2 | 7.5 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56DNS0 | 5 | 18
FRC0779 |  | CB |  | HFD3025L | 100 | 25 | [5 empty] | 3 | 7.6
|  | STR |  | AE56DNS0 | 5 | 18
FRC0780 |  | CB |  | HFD3035L | 100 | 35 | [5 empty] | 5 | 16.7
|  | STR |  | AE56DNS0 | 5 | 18
FRC0781 | C | CB | Eaton | HFD3020L | 100 | 20 | 240 | 3 | 65 | 230 | 3 | 2 | 6.8 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56DNS0 | 5 | 18
FRC0782 |  | CB |  | HFD3025L | 100 | 25 | [5 empty] | 3 | 9.6
|  | STR |  | AE56DNS0 | 5 | 18
FRC0783 |  | CB |  | HFD3035L | 100 | 35 | [5 empty] | 5 | 15.2
|  | STR |  | AE56DNS0 | 5 | 18
FRC0784 | C | CB | Eaton | HFD3020L | 65 | 20 | 480 | 3 | 65 | 460 | 3 | 5 | 7.6 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56DNS0 | 5 | 18
FRC0785 |  | CB |  | HFD3030L | 65 | 30 | [5 empty] | 7.5 | 11
|  | STR |  | AE56DNS0 | 5 | 18
FRC0786 |  | CB |  | HFD3035L | 65 | 35 | [5 empty] | 10 | 14
|  | STR |  | AE56DNS0 | 5 | 18
FRC0787 | C | CB | Eaton | HFD3025L | 25 | 25 | 600 | 3 | 25 | 575 | 3 | 7.5 | 9 | 0.69 | (1) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56DNS0 | 5 | 18
FRC0788 |  | CB |  | HFD3030L | 25 | 30 | [5 empty] | 10 | 11
|  | STR |  | AE56DNS0 | 5 | 18
FRC0789 |  | CB |  | HFD3035L | 25 | 35 | [5 empty] | 15 | 17
|  | STR |  | AE56DNS0 | 5 | 18
FRC0790 | C | CB | Eaton | FDC3020L | 200 | 20 | 200 | 3 | 100 | 200 | 3 | 2 | 7.8 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56DNS0 | 5 | 18
FRC0791 |  | CB |  | FDC3030L | 200 | 30 | [5 empty] | 3 | 11
|  | STR |  | AE56DNS0 | 5 | 18
FRC0792 |  | CB |  | FDC3035L | 200 | 35 | [5 empty] | 5 | 17.5
|  | STR |  | AE56DNS0 | 5 | 18
FRC0793 | C | CB | Eaton | FDC3020L | 200 | 20 | 208 | 3 | 100 | 208 | 3 | 2 | 7.5 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56DNS0 | 5 | 18
FRC0794 |  | CB |  | FDC3025L | 200 | 25 | [5 empty] | 3 | 7.6
|  | STR |  | AE56DNS0 | 5 | 18
FRC0795 |  | CB |  | FDC3035L | 200 | 35 | [5 empty] | 5 | 16.7
|  | STR |  | AE56DNS0 | 5 | 18
FRC0796 | C | CB | Eaton | FDC3020L | 200 | 20 | 240 | 3 | 100 | 230 | 3 | 2 | 6.8 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56DNS0 | 5 | 18
FRC0797 |  | CB |  | FDC3025L | 200 | 25 | [5 empty] | 3 | 9.6
|  | STR |  | AE56DNS0 | 5 | 18
FRC0798 |  | CB |  | FDC3035L | 200 | 35 | [5 empty] | 5 | 15.2
|  | STR |  | AE56DNS0 | 5 | 18
FRC0799 | C | CB | Eaton | FDC3020L | 100 | 20 | 480 | 3 | 100 | 460 | 3 | 5 | 7.6 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56DNS0 | 5 | 18
FRC0800 |  | CB |  | FDC3030L | 100 | 30 | [5 empty] | 7.5 | 11
|  | STR |  | AE56DNS0 | 5 | 18
FRC0801 |  | CB |  | FDC3035L | 100 | 35 | [5 empty] | 10 | 14
|  | STR |  | AE56DNS0 | 5 | 18
FRC0802 | C | CB | Eaton | FDC3025L | 35 | 25 | 600 | 3 | 35 | 575 | 3 | 7.5 | 9 | 0.69 | (1) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56DNS0 | 5 | 18
FRC0803 |  | CB |  | FDC3030L | 35 | 30 | [5 empty] | 10 | 11
|  | STR |  | AE56DNS0 | 5 | 18
FRC0804 |  | CB |  | FDC3035L | 35 | 35 | [5 empty] | 15 | 17
|  | STR |  | AE56DNS0 | 5 | 18
FRC0805 | C | CB | Eaton | HFD3030L | 100 | 30 | 200 | 3 | 65 | 200 | 3 | 3 | 11 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56FNS0 | 5 | 32
FRC0806 |  | CB |  | HFD3035L | 100 | 35 | [5 empty] | 5 | 17.5
|  | STR |  | AE56FNS0 | 5 | 32
FRC0807 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AE56FNS0 | 5 | 32
FRC0808 | C | CB | Eaton | HFD3035L | 100 | 35 | 208 | 3 | 65 | 208 | 3 | 5 | 16.7 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56FNS0 | 5 | 32
FRC0809 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 22.4
|  | STR |  | AE56FNS0 | 5 | 32
FRC0810 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 10 | 30.8 |  | (1) (3) (7c)
|  | STR |  | AE56FNS0 | 5 | 32
FRC0811 | C | CB | Eaton | HFD3035L | 100 | 35 | 240 | 3 | 65 | 230 | 3 | 5 | 15.2 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56FNS0 | 5 | 32
FRC0812 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 22
|  | STR |  | AE56FNS0 | 5 | 32
FRC0813 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 10 | 28 |  | (1) (3) (7c)
|  | STR |  | AE56FNS0 | 5 | 32
FRC0814 | C | CB | Eaton | HFD3035L | 65 | 35 | 480 | 3 | 65 | 460 | 3 | 10 | 14 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56FNS0 | 5 | 32
FRC0815 |  | CB |  | HFD3050L | 65 | 50 | [5 empty] | 15 | 21
|  | STR |  | AE56FNS0 | 5 | 32
FRC0816 |  | CB |  | HFD3050L | 65 | 50 | [5 empty] | 20 | 27
|  | STR |  | AE56FNS0 | 5 | 32
FRC0817 | C | CB | Eaton | HFD3035L | 25 | 35 | 600 | 3 | 25 | 575 | 3 | 15 | 17 | 0.69 | (1) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56FNS0 | 5 | 32
FRC0818 |  | CB |  | HFD3050L | 25 | 50 | [5 empty] | 20 | 22
|  | STR |  | AE56FNS0 | 5 | 32
FRC0819 |  | CB |  | HFD3050L | 25 | 50 | [5 empty] | 25 | 27
|  | STR |  | AE56FNS0 | 5 | 32
FRC0820 | C | CB | Eaton | FDC3030L | 200 | 30 | 200 | 3 | 100 | 200 | 3 | 3 | 11 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56FNS0 | 5 | 32
FRC0821 |  | CB |  | FDC3035L | 200 | 35 | [5 empty] | 5 | 17.5
|  | STR |  | AE56FNS0 | 5 | 32
FRC0822 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AE56FNS0 | 5 | 32
FRC0823 | C | CB | Eaton | FDC3035L | 200 | 35 | 208 | 3 | 100 | 208 | 3 | 5 | 16.7 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56FNS0 | 5 | 32
FRC0824 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 22.4
|  | STR |  | AE56FNS0 | 5 | 32
FRC0825 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 10 | 30.8 |  | (1) (3) (7c)
|  | STR |  | AE56FNS0 | 5 | 32
FRC0826 | C | CB | Eaton | FDC3035L | 200 | 35 | 240 | 3 | 100 | 230 | 3 | 5 | 15.2 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56FNS0 | 5 | 32
FRC0827 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 22
|  | STR |  | AE56FNS0 | 5 | 32
FRC0828 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 10 | 28 |  | (1) (3) (7c)
|  | STR |  | AE56FNS0 | 5 | 32
FRC0829 | C | CB | Eaton | FDC3035L | 100 | 35 | 480 | 3 | 100 | 460 | 3 | 10 | 14 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56FNS0 | 5 | 32
FRC0830 |  | CB |  | FDC3050L | 100 | 50 | [5 empty] | 15 | 21
|  | STR |  | AE56FNS0 | 5 | 32
FRC0831 |  | CB |  | FDC3050L | 100 | 50 | [5 empty] | 20 | 27
|  | STR |  | AE56FNS0 | 5 | 32
FRC0832 | C | CB | Eaton | FDC3035L | 35 | 35 | 600 | 3 | 35 | 575 | 3 | 15 | 17 | 0.69 | (1) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56FNS0 | 5 | 32
FRC0833 |  | CB |  | FDC3050L | 35 | 50 | [5 empty] | 20 | 22
|  | STR |  | AE56FNS0 | 5 | 32
FRC0834 |  | CB |  | FDC3050L | 35 | 50 | [5 empty] | 25 | 27
|  | STR |  | AE56FNS0 | 5 | 32
FRC0835 | C | CB | Eaton | HFD3035L | 25 | 35 | 600 | 3 | 100 | 575 | 3 | 15 | 17 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AE56FNS0 | 5 | 32
FRC0836 |  | CB |  | HFD3050L | 25 | 50 | [5 empty] | 20 | 22
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AE56FNS0 | 5 | 32
FRC0837 |  | CB |  | HFD3050L | 25 | 50 | [5 empty] | 25 | 27
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AE56FNS0 | 5 | 32
FRC0838 | C | CB | Eaton | HFD3030L | 100 | 30 | 200 | 3 | 65 | 200 | 3 | 3 | 11 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56GNS0 | 5 | 37
FRC0839 |  | CB |  | HFD3035L | 100 | 35 | [5 empty] | 5 | 17.5
|  | STR |  | AE56GNS0 | 5 | 37
FRC0840 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AE56GNS0 | 5 | 37
FRC0841 | C | CB | Eaton | HFD3035L | 100 | 35 | 208 | 3 | 65 | 208 | 3 | 5 | 16.7 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56GNS0 | 5 | 37
FRC0842 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | AE56GNS0 | 5 | 37
FRC0843 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 10 | 30.8 |  | (1) (3) (7c)
|  | STR |  | AE56GNS0 | 5 | 37
FRC0844 | C | CB | Eaton | HFD3035L | 100 | 35 | 240 | 3 | 65 | 230 | 3 | 5 | 15.2 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56GNS0 | 5 | 37
FRC0845 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 7.5 | 22
|  | STR |  | AE56GNS0 | 5 | 37
FRC0846 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 10 | 28 |  | (1) (3) (7c)
|  | STR |  | AE56GNS0 | 5 | 37
FRC0847 | C | CB | Eaton | HFD3050L | 65 | 50 | 480 | 3 | 65 | 460 | 3 | 15 | 21 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56GNS0 | 5 | 37
FRC0848 |  | CB |  | HFD3050L | 65 | 50 | [5 empty] | 20 | 27
|  | STR |  | AE56GNS0 | 5 | 37
FRC0849 |  | CB |  | HFD3050L | 65 | 50 | [5 empty] | 25 | 34 |  | (1) (3) (7c)
|  | STR |  | AE56GNS0 | 5 | 37
FRC0850 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 25 | 575 | 3 | 20 | 22 | 0.69 | (1) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56GNS0 | 5 | 37
FRC0851 |  | CB |  | HFD3050L | 25 | 50 | [5 empty] | 25 | 27
|  | STR |  | AE56GNS0 | 5 | 37
FRC0852 |  | CB |  | HFD3050L | 25 | 50 | [5 empty] | 30 | 32 |  | (1) (3) (6a) (7c)
|  | STR |  | AE56GNS0 | 5 | 37
FRC0853 | C | CB | Eaton | FDC3030L | 200 | 30 | 200 | 3 | 100 | 200 | 3 | 3 | 11 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56GNS0 | 5 | 37
FRC0854 |  | CB |  | FDC3035L | 200 | 35 | [5 empty] | 5 | 17.5
|  | STR |  | AE56GNS0 | 5 | 37
FRC0855 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AE56GNS0 | 5 | 37
FRC0856 | C | CB | Eaton | FDC3035L | 200 | 35 | 208 | 3 | 100 | 208 | 3 | 5 | 16.7 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56GNS0 | 5 | 37
FRC0857 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | AE56GNS0 | 5 | 37
FRC0858 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 10 | 30.8 |  | (1) (3) (7c)
|  | STR |  | AE56GNS0 | 5 | 37
FRC0859 | C | CB | Eaton | FDC3035L | 200 | 35 | 240 | 3 | 100 | 230 | 3 | 5 | 15.2 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56GNS0 | 5 | 37
FRC0860 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 7.5 | 22
|  | STR |  | AE56GNS0 | 5 | 37
FRC0861 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 10 | 28 |  | (1) (3) (7c)
|  | STR |  | AE56GNS0 | 5 | 37
FRC0862 | C | CB | Eaton | FDC3050L | 100 | 50 | 480 | 3 | 100 | 460 | 3 | 15 | 21 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56GNS0 | 5 | 37
FRC0863 |  | CB |  | FDC3050L | 100 | 50 | [5 empty] | 20 | 27
|  | STR |  | AE56GNS0 | 5 | 37
FRC0864 |  | CB |  | FDC3050L | 100 | 50 | [5 empty] | 25 | 34 |  | (1) (3) (7c)
|  | STR |  | AE56GNS0 | 5 | 37
FRC0865 | C | CB | Eaton | FDC3050L | 35 | 50 | 600 | 3 | 35 | 575 | 3 | 20 | 22 | 0.69 | (1) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56GNS0 | 5 | 37
FRC0866 |  | CB |  | FDC3050L | 35 | 50 | [5 empty] | 25 | 27
|  | STR |  | AE56GNS0 | 5 | 37
FRC0867 |  | CB |  | FDC3050L | 35 | 50 | [5 empty] | 30 | 32 |  | (1) (3) (6a) (7c)
|  | STR |  | AE56GNS0 | 5 | 37
FRC0868 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 20 | 22 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AE56GNS0 | 5 | 37
FRC0869 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 25 | 27
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AE56GNS0 | 5 | 37
FRC0870 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 30 | 32 |  | (1) (3) (7c)
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AE56GNS0 | 5 | 37
FRC0871 | C | CB | Eaton | HFD3050L | 100 | 50 | 200 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56JNS0 | 5 | 60
FRC0872 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 10 | 32.2 |  | (1) (3) (7c)
|  | STR |  | AE56JNS0 | 5 | 60
FRC0873 |  | CB |  | HFD3090L | 100 | 90 | [5 empty] | 15 | 48.3 |  | (1) (3) (7e)
|  | STR |  | AE56JNS0 | 5 | 60
FRC0874 | C | CB | Eaton | HFD3050L | 100 | 50 | 208 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56JNS0 | 5 | 60
FRC0875 |  | CB |  | HFD3050L | 100 | 50 | [5 empty] | 10 | 30.8 |  | (1) (3) (7c)
|  | STR |  | AE56JNS0 | 5 | 60
FRC0876 |  | CB |  | HFD3070L | 100 | 70 | [5 empty] | 15 | 46.2 |  | (1) (3) (7e)
|  | STR |  | AE56JNS0 | 5 | 60
FRC0877 | C | CB | Eaton | HFD3050L | 100 | 50 | 240 | 3 | 65 | 230 | 3 | 10 | 28 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56JNS0 | 5 | 60
FRC0878 |  | CB |  | HFD3070L | 100 | 70 | [5 empty] | 15 | 42 |  | (1) (3) (7c)
|  | STR |  | AE56JNS0 | 5 | 60
FRC0879 |  | CB |  | HFD3090L | 100 | 90 | [5 empty] | 20 | 54 |  | (1) (3) (7e)
|  | STR |  | AE56JNS0 | 5 | 60
FRC0880 | C | CB | Eaton | HFD3050L | 65 | 50 | 480 | 3 | 65 | 460 | 3 | 25 | 34 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56JNS0 | 5 | 60
FRC0881 |  | CB |  | HFD3060L | 65 | 60 | [5 empty] | 30 | 40 |  | (1) (3) (7c)
|  | STR |  | AE56JNS0 | 5 | 60
FRC0882 |  | CB |  | HFD3090L | 65 | 90 | [5 empty] | 40 | 52 |  | (1) (3) (7e)
|  | STR |  | AE56JNS0 | 5 | 60
FRC0883 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 25 | 575 | 3 | 25 | 27 | 0.69 | (1) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56JNS0 | 5 | 60
FRC0884 |  | CB |  | HFD3050L | 25 | 50 | [5 empty] | 30 | 32 |  | (1) (3) (6a) (7c)
|  | STR |  | AE56JNS0 | 5 | 60
FRC0885 |  | CB |  | HFD3060L | 25 | 60 | [5 empty] | 40 | 41 |  | (1) (3) (6b) (7c)
|  | STR |  | AE56JNS0 | 5 | 60
FRC0886 | C | CB | Eaton | FDC3050L | 200 | 50 | 200 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56JNS0 | 5 | 60
FRC0887 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 10 | 32.2 |  | (1) (3) (7c)
|  | STR |  | AE56JNS0 | 5 | 60
FRC0888 |  | CB |  | FDC3090L | 200 | 90 | [5 empty] | 15 | 48.3 |  | (1) (3) (7e)
|  | STR |  | AE56JNS0 | 5 | 60
FRC0889 | C | CB | Eaton | FDC3050L | 200 | 50 | 208 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56JNS0 | 5 | 60
FRC0890 |  | CB |  | FDC3050L | 200 | 50 | [5 empty] | 10 | 30.8 |  | (1) (3) (7c)
|  | STR |  | AE56JNS0 | 5 | 60
FRC0891 |  | CB |  | FDC3070L | 200 | 70 | [5 empty] | 15 | 46.2 |  | (1) (3) (7e)
|  | STR |  | AE56JNS0 | 5 | 60
FRC0892 | C | CB | Eaton | FDC3050L | 200 | 50 | 240 | 3 | 100 | 230 | 3 | 10 | 28 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56JNS0 | 5 | 60
FRC0893 |  | CB |  | FDC3070L | 200 | 70 | [5 empty] | 15 | 42 |  | (1) (3) (7c)
|  | STR |  | AE56JNS0 | 5 | 60
FRC0894 |  | CB |  | FDC3090L | 200 | 90 | [5 empty] | 20 | 54 |  | (1) (3) (7e)
|  | STR |  | AE56JNS0 | 5 | 60
FRC0895 | C | CB | Eaton | FDC3050L | 100 | 50 | 480 | 3 | 100 | 460 | 3 | 25 | 34 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56JNS0 | 5 | 60
FRC0896 |  | CB |  | FDC3060L | 100 | 60 | [5 empty] | 30 | 40 |  | (1) (3) (7c)
|  | STR |  | AE56JNS0 | 5 | 60
FRC0897 |  | CB |  | FDC3090L | 100 | 90 | [5 empty] | 40 | 52 |  | (1) (3) (7e)
|  | STR |  | AE56JNS0 | 5 | 60
FRC0898 | C | CB | Eaton | FDC3050L | 35 | 50 | 600 | 3 | 35 | 575 | 3 | 25 | 27 | 0.69 | (1) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56JNS0 | 5 | 60
FRC0899 |  | CB |  | FDC3050L | 35 | 50 | [5 empty] | 30 | 32 |  | (1) (3) (6a) (7c)
|  | STR |  | AE56JNS0 | 5 | 60
FRC0900 |  | CB |  | FDC3060L | 35 | 60 | [5 empty] | 40 | 41 |  | (1) (3) (6b) (7c)
|  | STR |  | AE56JNS0 | 5 | 60
FRC0901 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 25 | 27 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AE56JNS0 | 5 | 60
FRC0902 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 30 | 32 |  | (1) (3) (7c)
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AE56JNS0 | 5 | 60
FRC0903 | C | CB | Eaton | HFD3060L | 25 | 60 | 600 | 3 | 100 | 575 | 3 | 40 | 41
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AE56JNS0 | 5 | 60
FRC0904 | C | CB | Eaton | EGH3050FFG | 100 | 50 | 200 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56JNS0 | 5 | 60
FRC0905 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 10 | 32.2 |  | (1) (3) (7c)
|  | STR |  | AE56JNS0 | 5 | 60
FRC0906 |  | CB |  | EGH3090FFG | 100 | 90 | [5 empty] | 15 | 48.3 |  | (1) (3) (7e)
|  | STR |  | AE56JNS0 | 5 | 60
FRC0907 | C | CB | Eaton | EGH3050FFG | 100 | 50 | 208 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56JNS0 | 5 | 60
FRC0908 |  | CB |  | EGH3050FFG | 100 | 50 | [5 empty] | 10 | 30.8 |  | (1) (3) (7c)
|  | STR |  | AE56JNS0 | 5 | 60
FRC0909 |  | CB |  | EGH3070FFG | 100 | 70 | [5 empty] | 15 | 46.2 |  | (1) (3) (7e)
|  | STR |  | AE56JNS0 | 5 | 60
FRC0910 | C | CB | Eaton | EGH3050FFG | 100 | 50 | 240 | 3 | 65 | 230 | 3 | 10 | 28 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56JNS0 | 5 | 60
FRC0911 |  | CB |  | EGH3070FFG | 100 | 70 | [5 empty] | 15 | 42 |  | (1) (3) (7c)
|  | STR |  | AE56JNS0 | 5 | 60
FRC0912 |  | CB |  | EGH3090FFG | 100 | 90 | [5 empty] | 20 | 54 |  | (1) (3) (7e)
|  | STR |  | AE56JNS0 | 5 | 60
FRC0913 | C | CB | Eaton | EGH3050FFG | 65 | 50 | 480 | 3 | 65 | 460 | 3 | 25 | 34 | 0.69 | (1) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56JNS0 | 5 | 60
FRC0914 |  | CB |  | EGH3060FFG | 65 | 60 | [5 empty] | 30 | 40 |  | (1) (3) (7c)
|  | STR |  | AE56JNS0 | 5 | 60
FRC0915 |  | CB |  | EGH3090FFG | 65 | 90 | [5 empty] | 40 | 52 |  | (1) (3) (7e)
|  | STR |  | AE56JNS0 | 5 | 60
FRC0916 | C | CB | Eaton | HFD3050L | 100 | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 0.69 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56KNS0 | 5 | 73
FRC0917 |  | CB |  | HFD3090L | 100 | 90 | [5 empty] | 15 | 48.3 |  | (1) (3) (7e)
|  | STR |  | AE56KNS0 | 5 | 73
FRC0918 |  | CB |  | HFD3090L | 100 | 90 | [5 empty] | 20 | 62.1
|  | STR |  | AE56KNS0 | 5 | 73
FRC0919 | C | CB | Eaton | HFD3050L | 100 | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 0.69 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56KNS0 | 5 | 73
FRC0920 |  | CB |  | HFD3070L | 100 | 70 | [5 empty] | 15 | 46.2 |  | (1) (3) (7e)
|  | STR |  | AE56KNS0 | 5 | 73
FRC0921 |  | CB |  | HFD3090L | 100 | 90 | [5 empty] | 20 | 59.4
|  | STR |  | AE56KNS0 | 5 | 73
FRC0922 | C | CB | Eaton | HFD3070L | 100 | 70 | 240 | 3 | 65 | 230 | 3 | 15 | 42 | 0.69 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56KNS0 | 5 | 73
FRC0923 |  | CB |  | HFD3090L | 100 | 90 | [5 empty] | 20 | 54 |  | (1) (3) (7e)
|  | STR |  | AE56KNS0 | 5 | 73
FRC0924 |  | CB |  | HFD3090L | 100 | 90 | [5 empty] | 25 | 68
|  | STR |  | AE56KNS0 | 5 | 73
FRC0925 | C | CB | Eaton | HFD3060L | 65 | 60 | 480 | 3 | 65 | 460 | 3 | 30 | 40 | 0.69 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56KNS0 | 5 | 73
FRC0926 |  | CB |  | HFD3090L | 65 | 90 | [5 empty] | 40 | 52 |  | (1) (3) (7e)
|  | STR |  | AE56KNS0 | 5 | 73
FRC0927 |  | CB |  | HFD3090L | 65 | 90 | [5 empty] | 50 | 65
|  | STR |  | AE56KNS0 | 5 | 73
FRC0928 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 25 | 575 | 3 | 30 | 32 | 0.69 | (1) (3) (6a) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56KNS0 | 5 | 73
FRC0929 |  | CB |  | HFD3060L | 25 | 60 | [5 empty] | 40 | 41 |  | (1) (3) (6b) (7c)
|  | STR |  | AE56KNS0 | 5 | 73
FRC0930 |  | CB |  | HFD3090L | 25 | 90 | [5 empty] | 50 | 52 |  | (1) (3) (6b) (7e)
|  | STR |  | AE56KNS0 | 5 | 73
FRC0931 | C | CB | Eaton | FDC3050L | 200 | 50 | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 0.69 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56KNS0 | 5 | 73
FRC0932 |  | CB |  | FDC3090L | 200 | 90 | [5 empty] | 15 | 48.3 |  | (1) (3) (7e)
|  | STR |  | AE56KNS0 | 5 | 73
FRC0933 |  | CB |  | FDC3090L | 200 | 90 | [5 empty] | 20 | 62.1
|  | STR |  | AE56KNS0 | 5 | 73
FRC0934 | C | CB | Eaton | FDC3050L | 200 | 50 | 208 | 3 | 100 | 208 | 3 | 10 | 30.8 | 0.69 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56KNS0 | 5 | 73
FRC0935 |  | CB |  | FDC3070L | 200 | 70 | [5 empty] | 15 | 46.2 |  | (1) (3) (7e)
|  | STR |  | AE56KNS0 | 5 | 73
FRC0936 |  | CB |  | FDC3090L | 200 | 90 | [5 empty] | 20 | 59.4
|  | STR |  | AE56KNS0 | 5 | 73
FRC0937 | C | CB | Eaton | FDC3070L | 200 | 70 | 240 | 3 | 100 | 230 | 3 | 15 | 42 | 0.69 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56KNS0 | 5 | 73
FRC0938 |  | CB |  | FDC3090L | 200 | 90 | [5 empty] | 20 | 54 |  | (1) (3) (7e)
|  | STR |  | AE56KNS0 | 5 | 73
FRC0939 |  | CB |  | FDC3090L | 200 | 90 | [5 empty] | 25 | 68
|  | STR |  | AE56KNS0 | 5 | 73
FRC0940 | C | CB | Eaton | FC3060L | 65 | 60 | 480 | 3 | 100 | 460 | 3 | 30 | 40 | 0.69 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56KNS0 | 5 | 73
FRC0941 |  | CB |  | FDC3090L | 65 | 90 | [5 empty] | 40 | 52 |  | (1) (3) (7e)
|  | STR |  | AE56KNS0 | 5 | 73
FRC0942 |  | CB |  | FDC3090L | 65 | 90 | [5 empty] | 50 | 65
|  | STR |  | AE56KNS0 | 5 | 73
FRC0943 | C | CB | Eaton | FDC3050L | 35 | 50 | 600 | 3 | 35 | 575 | 3 | 30 | 32 | 0.69 | (1) (3) (6a) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56KNS0 | 5 | 73
FRC0944 |  | CB |  | FDC3060L | 35 | 60 | [5 empty] | 40 | 41 |  | (1) (3) (6b) (7c)
|  | STR |  | AE56KNS0 | 5 | 73
FRC0945 |  | CB |  | FDC3090L | 35 | 90 | [5 empty] | 50 | 52 |  | (1) (3) (6b) (7e)
|  | STR |  | AE56KNS0 | 5 | 73
FRC0946 | C | CB | Eaton | HFD3050L | 25 | 50 | 600 | 3 | 100 | 575 | 3 | 30 | 32 | 0.69 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AE56KNS0 | 5 | 73
FRC0947 | C | CB | Eaton | HFD3060L | 25 | 60 | 600 | 3 | 100 | 575 | 3 | 40 | 41
|  | C. Limiter |  | LFD3070R | 200 | 70
|  | STR |  | AE56KNS0 | 5 | 73
FRC0948 | C | CB | Eaton | HFD3090L | 25 | 90 | 600 | 3 | 100 | 575 | 3 | 50 | 52 |  | (1) (3) (7e)
|  | C. Limiter |  | LFD150R | 200 | 150
|  | STR |  | AE56KNS0 | 5 | 73
FRC0949 | C | CB | Eaton | EGH3050FFG | 100 | 50 | 200 | 3 | 65 | 200 | 3 | 10 | 32.2 | 0.69 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56KNS0 | 5 | 73
FRC0950 |  | CB |  | EGH3090FFG | 100 | 90 | [5 empty] | 15 | 48.3 |  | (1) (3) (7e)
|  | STR |  | AE56KNS0 | 5 | 73
FRC0951 |  | CB |  | EGH3090FFG | 100 | 90 | [5 empty] | 20 | 62.1
|  | STR |  | AE56KNS0 | 5 | 73
FRC0952 | C | CB | Eaton | EGH3050FFG | 100 | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 0.69 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56KNS0 | 5 | 73
FRC0953 |  | CB |  | EGH3070FFG | 100 | 70 | [5 empty] | 15 | 46.2 |  | (1) (3) (7e)
|  | STR |  | AE56KNS0 | 5 | 73
FRC0954 |  | CB |  | EGH3090FFG | 100 | 90 | [5 empty] | 20 | 59.4
|  | STR |  | AE56KNS0 | 5 | 73
FRC0955 | C | CB | Eaton | EGH3070FFG | 100 | 70 | 240 | 3 | 65 | 230 | 3 | 15 | 42 | 0.69 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56KNS0 | 5 | 73
FRC0956 |  | CB |  | EGH3090FFG | 100 | 90 | [5 empty] | 20 | 54 |  | (1) (3) (7e)
|  | STR |  | AE56KNS0 | 5 | 73
FRC0957 |  | CB |  | EGH3090FFG | 100 | 90 | [5 empty] | 25 | 68
|  | STR |  | AE56KNS0 | 5 | 73
FRC0958 | C | CB | Eaton | EGH3060FFG | 65 | 60 | 480 | 3 | 65 | 460 | 3 | 30 | 40 | 0.69 | (1) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56KNS0 | 5 | 73
FRC0959 |  | CB |  | EGH3090FFG | 65 | 90 | [5 empty] | 40 | 52 |  | (1) (3) (7e)
|  | STR |  | AE56KNS0 | 5 | 73
FRC0960 |  | CB |  | EGH3090FFG | 65 | 90 | [5 empty] | 50 | 65
|  | STR |  | AE56KNS0 | 5 | 73
FRC0961 | C | CB | Eaton | JGH3125FAG | 100 | 125 | 200 | 3 | 65 | 200 | 3 | 25 | 78.2 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56NNS0 | 10 | 140
FRC0962 |  | CB |  | JGH3150FAG | 100 | 150 | [5 empty] | 30 | 92 |  | (1) (3) (7f)
|  | STR |  | AE56NNS0 | 10 | 140
FRC0963 |  | CB |  | JGH3175FAG | 100 | 175 | [5 empty] | 40 | 120
|  | STR |  | AE56NNS0 | 10 | 140
FRC0964 | C | CB | Eaton | JGH3125FAG | 100 | 125 | 208 | 3 | 65 | 208 | 3 | 25 | 74.8 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56NNS0 | 10 | 140
FRC0965 |  | CB |  | JGH3150FAG | 100 | 150 | [5 empty] | 30 | 88
|  | STR |  | AE56NNS0 | 10 | 140
FRC0966 |  | CB |  | JGH3175FAG | 100 | 175 | [5 empty] | 40 | 114 |  | (1) (3) (7f)
|  | STR |  | AE56NNS0 | 10 | 140
FRC0967 | C | CB | Eaton | JGH3125FAG | 100 | 125 | 240 | 3 | 65 | 230 | 3 | 30 | 80 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56NNS0 | 10 | 140
FRC0968 |  | CB |  | JGH3150FAG | 100 | 150 | [5 empty] | 40 | 104 |  | (1) (3) (7f)
|  | STR |  | AE56NNS0 | 10 | 140
FRC0969 |  | CB |  | JGH3200FAG | 100 | 200 | [5 empty] | 50 | 130
|  | STR |  | AE56NNS0 | 10 | 140
FRC0970 | C | CB | Eaton | JGH3125FAG | 65 | 125 | 480 | 3 | 65 | 460 | 3 | 60 | 77 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56NNS0 | 10 | 140
FRC0971 |  | CB |  | JGH3150FAG | 65 | 150 | [5 empty] | 75 | 96 |  | (1) (3) (7f)
|  | STR |  | AE56NNS0 | 10 | 140
FRC0972 |  | CB |  | JGH3175FAG | 65 | 175 | [5 empty] | 100 | 124
|  | STR |  | AE56NNS0 | 10 | 140
FRC0973 | C | CB | Eaton | JGH3125FAG | 25 | 125 | 600 | 3 | 25 | 575 | 3 | 75 | 77 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56NNS0 | 10 | 140
FRC0974 |  | CB |  | JGH3150FAG | 25 | 150 | [5 empty] | 100 | 99 |  | (1) (3) (7f)
|  | STR |  | AE56NNS0 | 10 | 140
FRC0975 |  | CB |  | JGH3175FAG | 25 | 175 | [5 empty] | 125 | 125
|  | STR |  | AE56NNS0 | 10 | 140
FRC0976 | C | CB | Eaton | JDC3125 | 200 | 125 | 200 | 3 | 100 | 200 | 3 | 25 | 78.2 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56NNS0 | 10 | 140
FRC0977 |  | CB |  | JDC3150 | 200 | 150 | [5 empty] | 30 | 92 |  | (1) (3) (7f)
|  | STR |  | AE56NNS0 | 10 | 140
FRC0978 |  | CB |  | JDC3175 | 200 | 175 | [5 empty] | 40 | 120
|  | STR |  | AE56NNS0 | 10 | 140
FRC0979 | C | CB | Eaton | JDC3125 | 200 | 125 | 208 | 3 | 100 | 208 | 3 | 25 | 74.8 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56NNS0 | 10 | 140
FRC0980 |  | CB |  | JDC3150 | 200 | 150 | [5 empty] | 30 | 88
|  | STR |  | AE56NNS0 | 10 | 140
FRC0981 |  | CB |  | JDC3175 | 200 | 175 | [5 empty] | 40 | 114 |  | (1) (3) (7f)
|  | STR |  | AE56NNS0 | 10 | 140
FRC0982 | C | CB | Eaton | JDC3125 | 200 | 125 | 240 | 3 | 100 | 230 | 3 | 30 | 80 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56NNS0 | 10 | 140
FRC0983 |  | CB |  | JDC3150 | 200 | 150 | [5 empty] | 40 | 104 |  | (1) (3) (7f)
|  | STR |  | AE56NNS0 | 10 | 140
FRC0984 |  | CB |  | JDC3200 | 200 | 200 | [5 empty] | 50 | 130
|  | STR |  | AE56NNS0 | 10 | 140
FRC0985 | C | CB | Eaton | JDC3125 | 100 | 125 | 480 | 3 | 100 | 460 | 3 | 60 | 77 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56NNS0 | 10 | 140
FRC0986 |  | CB |  | JDC3150 | 100 | 150 | [5 empty] | 75 | 96 |  | (1) (3) (7f)
|  | STR |  | AE56NNS0 | 10 | 140
FRC0987 |  | CB |  | JDC3175 | 100 | 175 | [5 empty] | 100 | 124
|  | STR |  | AE56NNS0 | 10 | 140
FRC0988 | C | CB | Eaton | JDC3125 | 35 | 125 | 600 | 3 | 35 | 575 | 3 | 75 | 77 | 1.42 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56NNS0 | 10 | 140
FRC0989 |  | CB |  | JDC3150 | 35 | 150 | [5 empty] | 100 | 99 |  | (1) (3) (7f)
|  | STR |  | AE56NNS0 | 10 | 140
FRC0990 |  | CB |  | JDC3175 | 35 | 175 | [5 empty] | 125 | 125
|  | STR |  | AE56NNS0 | 10 | 140
FRC0991 | C | CB | Eaton | LA3125PR | 200 | 125 | 600 | 3 | 100 | 575 | 3 | 75 | 77 | 2.5 | (1) (3) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56NNS0 | 10 | 140
FRC0992 |  | CB |  | LA3150PR | 200 | 150 | [5 empty] | 100 | 99 |  | (1) (3) (7f)
|  | STR |  | AE56NNS0 | 10 | 140
FRC0993 |  | CB |  | LA3175PR | 200 | 175 | [5 empty] | 125 | 125
|  | STR |  | AE56NNS0 | 10 | 140
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment. See Table 3.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6a) = Install Terminal End Cover TEC1 (6085C42H01) to line side of circuit breaker.
(6b) = Install Terminal end Cover TEC2 (6085C42H02) to line side of circuit breaker.
(7) See table (7) for internal wiring between load side of short circuit protective device & line side of starter.
Table 7 - Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
| Wire Code | Wire Size | Wire Code | Wire Size
| 7a | 12 awg. | 7j | 4/0 awg.
| 7b | 10 awg. | 7k | 250kcml
| 7c | 8 awg. | 7l | 350kcml
| 7d | 6 awg. | 7m | 4/0 awg. (3)
| 7e | 4 awg. | 7n | 4/0 awg. (4)
| 7f | 2 awg. | 7p | 250kcml (2)
| 7g | 1/0 awg. | 7r | 350kcml (3)
| 7h | 2/0 awg. | 7s | 4/0 awg. (2)
Table 3 - Overload Relay Heater Pack Selection
- Supply Proper Eaton Publication with Panel -
| Publication No. | AN16/AN56 STR. | AE16/AE56 STR.
| 22179 | 00, 0 | A through F
| 22180 | 1, 2 | G through K
| 20104 | 3, 4 | L through N
| 22416 | 5 | -
| 22590 | 6 | -
| 22591 | 7 | -
| 22592 | 8

## Freedom Type D
Issued: 2006-05-18
Last Revised: 2006-05-18
Combination Motor Controllers for use in Industrial Control Panels
ID Number | Combination Type | Individual Component | [6 empty] | Combination SCCR | [5 empty] | Conditions of Acceptability | Combination Starter UL File | Motor Control Center UL File
|  | Component Type | Manufacturer | Partial Catalog No. | Ratings |  |  |  | SCCR kA | Volts | Phase | Hp | NEC FLC | Min. Enclosure Volume (cu. ft.)
[5 empty] | SCCR kA | Max. Amps | Volts | No. Poles
FRD0001 | D | ICB | Eaton | HMCP015*** | - | 15 | 200 | 3 | 100 | 200 | 3 | 2 | 7.8 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16BN0 | 5 | 18
FRD0002 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 3 | 11
|  | STR |  | AN16BN0 | 5 | 18
FRD0003 |  | ICB | Eaton | HMCP015*** | - | 15 | 208 |  |  | 208 |  | 2 | 7.5
|  | STR |  | AN16B0 | 5 | 18
FRD0004 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 3 | 10.6
|  | STR |  | AN16BN0 | 5 | 18
FRD0005 |  | ICB | Eaton | HMCP015*** | - | 15 | 240 |  |  | 230 |  | 2 | 6.8
|  | STR |  | AN16BN0 | 5 | 18
FRD0006 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 3 | 9.6
|  | STR |  | AN16BN0 | 5 | 18
FRD0007 | D | ICB | Eaton | HMCP015*** | - | 15 | 480 | 3 | 100 | 460 | 3 | 3 | 4.8 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16BN0 | 5 | 18
FRD0008 |  | ICB |  | HMCP015*** | - | 15 | [5 empty] | 5 | 7.6
|  | STR |  | AN16BN0 | 5 | 18
FRD0009 |  | ICB |  | HMCP007*** | - | 7 | 600 |  | 50 | 575 |  | 3 | 3.9 |  | (1) (3) (5) (6a) (7a)
|  | STR |  | AN16BN0 | 5 | 18
FRD0010 |  | ICB |  | HMCP015*** | - | 15 | [5 empty] | 5 | 6.1
|  | STR |  | AN16BN0 | 5 | 18
FRD0011 | D | ICB | Eaton | HMCP007*** | - | 7 | 200 | 3 | 100 | 200 | 3 | 1 | 4.8 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16DN0 | 5 | 27
FRD0012 |  | ICB |  | HMCP015*** | - | 15 | [5 empty] | 3 | 11
|  | STR |  | AN16DN0 | 5 | 27
FRD0013 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 5 | 17.5
|  | ICB |  | AN16DN0 | 5 | 27
FRD0014 |  | STR |  | HMCP050*** | - | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AN16DN0 | 5 | 27
FRD0015 | D | ICB | Eaton | HMCP007*** | - | 7 | 208 | 3 | 100 | 208 | 3 | 1 | 4.6 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16DN0 | 5 | 27
FRD0016 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 3 | 10.6
|  | STR |  | AN16DN0 | 5 | 27
FRD0017 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 5 | 16.7
|  | STR |  | AN16DN0 | 5 | 27
FRD0018 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | AN16DN0 | 5 | 27
FRD0019 | D | ICB | Eaton | HMCP007*** | - | 7 | 240 | 3 | 100 | 230 | 3 | 1 | 4.2 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16DN0 | 5 | 27
FRD0020 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 3 | 9.6
|  | STR |  | AN16DN0 | 5 | 27
FRD0021 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 5 | 15.2
|  | STR |  | AN16DN0 | 5 | 27
FRD0022 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 7.5 | 22
|  | STR |  | AN16DN0 | 5 | 27
FRD0023 | D | ICB | Eaton | HMCP007*** | - | 7 | 480 | 3 | 100 | 460 | 3 | 1 | 2.1 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16DN0 | 5 | 27
FRD0024 |  | ICB |  | HMCP007*** | - | 7 | [5 empty] | 3 | 4.8
|  | STR |  | AN16DN0 | 5 | 27
FRD0025 |  | ICB |  | HMCP015*** | - | 15 | [5 empty] | 5 | 7.6
|  | STR |  | AN16DN0 | 5 | 27
FRD0026 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 7.5 | 11
|  | STR |  | AN16DN0 | 5 | 27
FRD0027 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 10 | 14
|  | STR |  | AN16DN0 | 5 | 27
FRD0028 | D | ICB | Eaton | HMCP003*** | - | 3 | 600 | 3 | 50 | 575 | 3 | 1 | 1.7 | 0.33 | (1) (3) (5) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16DN0 | 5 | 27
FRD0029 |  | ICB |  | HMCP007*** | - | 7 | [5 empty] | 3 | 3.9
|  | STR |  | AN16DN0 | 5 | 27
FRD0030 |  | ICB |  | HMCP015*** | - | 15 | [5 empty] | 5 | 6.1
|  | STR |  | AN16DN0 | 5 | 27
FRD0031 |  | ICB |  | HMCP015*** | - | 15 | [5 empty] | 7.5 | 9
|  | STR |  | AN16DN0 | 5 | 27
FRD0032 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 10 | 11
|  | STR |  | AN16DN0 | 5 | 27
FRD0033 | D | ICB | Eaton | HMCP003*** | - | 3 | 600 | 3 | 100 | 575 | 3 | 1 | 1.7 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3003R | - | 3
|  | STR |  | AN16DN0 | 5 | 27
FRD0034 | D | ICB | Eaton | HMCP007*** | - | 7 | 600 | 3 | 100 | 575 | 3 | 3 | 3.9
|  | C. Limiter |  | ELC3007R | - | 7
|  | STR |  | AN16DN0 | 5 | 27
FRD0035 | D | ICB | Eaton | HMCP015*** | - | 15 | 600 | 3 | 100 | 575 | 3 | 5 | 6.1
|  | C. Limiter |  | ELC3015R | - | 15
|  | STR |  | AN16DN0 | 5 | 27
FRD0036 | D | ICB | Eaton | HMCP015*** | - | 15 | 600 | 3 | 100 | 575 | 3 | 7.5 | 9
|  | C. Limiter |  | ELC3015R | - | 15
|  | STR |  | AN16DN0 | 5 | 27
FRD0037 | D | ICB | Eaton | HMCP030*** | - | 30 | 600 | 3 | 100 | 575 | 3 | 10 | 11
|  | C. Limiter |  | ELC3030R | - | 30
|  | STR |  | AN16DN0 | 5 | 27
FRD0038 | D | ICB | Eaton | HMCP050*** | - | 50 | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 0.69 | (1) (3) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16GN0 | 5 | 45
FRD0039 |  | ICB |  | HMCP050*** | - | 50 | 208 |  |  | 208 |  | 10 | 30.8
|  | STR |  | AN16GN0 | 5 | 45
FRD0040 |  | ICB |  | HMCP050*** | - | 50 | 240 |  |  | 230 |  | 10 | 28
|  | STR |  | AN16GN0 | 5 | 45
FRD0041 |  | ICB |  | HMCP070*** | - | 70 | [5 empty] | 15 | 42
|  | STR |  | AN16GN0 | 5 | 45
FRD0042 | D | ICB | Eaton | HMCP050*** | - | 50 | 480 | 3 | 100 | 460 | 3 | 15 | 21 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16GN0 | 5 | 45
FRD0043 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 20 | 27
|  | STR |  | AN16GN0 | 5 | 45
FRD0044 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 25 | 34 |  | (1) (3) (5) (7c)
|  | STR |  | AN16GN0 | 5 | 45
FRD0045 | D | ICB | Eaton | HMCP030*** | - | 30 | 600 | 3 | 50 | 575 | 3 | 15 | 17 | 0.69 | (1) (3) (5) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16GN0 | 5 | 45
FRD0046 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 20 | 22
|  | STR |  | AN16GN0 | 5 | 45
FRD0047 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 25 | 27
|  | STR |  | AN16GN0 | 5 | 45
FRD0048 | D | ICB | Eaton | HMCP030*** | - | 30 | 600 | 3 | 100 | 575 | 3 | 15 | 17 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3030R | - | 30
|  | STR |  | AN16GN0 | 5 | 45
FRD0049 | D | ICB | Eaton | HMCP050*** | - | 50 | 600 | 3 | 100 | 575 | 3 | 20 | 22
|  | C. Limiter |  | ELC3050R | - | 50
|  | STR |  | AN16GN0 | 5 | 45
FRD0050 | D | ICB | Eaton | HMCP050*** | - | 50 | 600 | 3 | 100 | 575 | 3 | 25 | 27
|  | C. Limiter |  | ELC3050R |  | 50
|  | STR |  | AN16GN0 | 5 | 45
FRD0051 | D | ICB | Eaton | HMCP100*** | - | 100 | 200 | 3 | 100 | 200 | 3 | 15 | 48.3 | 1.06 | (1) (3) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16KN0 | 5 | 90
FRD0052 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 20 | 62.1
|  | STR |  | AN16KN0 | 5 | 90
FRD0053 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 25 | 78.2
|  | STR |  | AN16KN0 | 5 | 90
FRD0054 | D | ICB | Eaton | HMCP100*** | - | 100 | 208 | 3 | 100 | 208 | 3 | 15 | 46.2 | 1.06 | (1) (3) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16KN0 | 5 | 90
FRD0055 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 20 | 59.4
|  | STR |  | AN16KN0 | 5 | 90
FRD0056 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 25 | 74.8
|  | STR |  | AN16KN0 | 5 | 90
FRD0057 | D | ICB | Eaton | HMCP100*** | - | 100 | 240 | 3 | 100 | 230 | 3 | 20 | 54 | 1.06 | (1) (3) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16KN0 | 5 | 90
FRD0058 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 25 | 68
|  | STR |  | AN16KN0 | 5 | 90
FRD0059 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 30 | 80
|  | STR |  | AN16KN0 | 5 | 90
FRD0060 | D | ICB | Eaton | HMCP100*** | - | 100 | 480 | 3 | 100 | 460 | 3 | 30 | 40 | 1.06 | (1) (3) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16KN0 | 5 | 90
FRD0061 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 40 | 52 |  | (1) (3) (5) (7e)
|  | STR |  | AN16KN0 | 5 | 90
FRD0062 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 50 | 65
|  | STR |  | AN16KN0 | 5 | 90
FRD0063 | D | ICB | Eaton | HMCP050*** | - | 50 | 600 | 3 | 50 | 575 | 3 | 30 | 32 | 1.06 | (1) (3) (5) 6b) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16KN0 | 5 | 90
FRD0064 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 40 | 41
|  | STR |  | AN16KN0 | 5 | 90
FRD0065 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 50 | 52 |  | (1) (3) (5) (6b) (7e)
|  | STR |  | AN16KN0 | 5 | 90
FRD0066 | D | ICB | Eaton | HMCP050*** | - | 50 | 600 | 3 | 100 | 575 | 3 | 30 | 32 | 1.42 | (1) (3) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3050R | - | 50
|  | STR |  | AN16KN0 | 5 | 90
FRD0067 | D | ICB | Eaton | HMCP100*** | - | 100 | 600 | 3 | 100 | 575 | 3 | 40 | 41
|  | C. Limiter |  | ELC3100R | - | 100
|  | STR |  | AN16KN0 | 5 | 90
FRD0068 | D | ICB | Eaton | HMCP100*** | - | 100 | 600 | 3 | 100 | 575 | 3 | 50 | 52 |  | (1) (3) (5) (7e)
|  | C. Limiter |  | ELC3100R | - | 100
|  | STR |  | AN16KN0 | 5 | 90
FRD0069 | D | ICB | Eaton | HMCP150*** | - | 150 | 200 | 3 | 100 | 200 | 3 | 30 | 92 | 1.42 | (1) (3) (5) (7f) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16NN0 | 10 | 135
FRD0070 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 40 | 120
|  | STR |  | AN16NN0 | 10 | 135
FRD0071 | D | ICB | Eaton | HMCP150*** | - | 150 | 208 | 3 | 100 | 208 | 3 | 30 | 88 | 1.42 | (1) (3) (5) (7f) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16NN0 | 10 | 135
FRD0072 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 40 | 114
|  | STR |  | AN16NN0 | 10 | 135
FRD0073 | D | ICB | Eaton | HMCP150*** | - | 150 | 240 | 3 | 100 | 230 | 3 | 40 | 104 | 1.42 | (1) (3) (5) (7f) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16NN0 | 10 | 135
FRD0074 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 50 | 130
|  | STR |  | AN16NN0 | 10 | 135
FRD0075 | D | ICB | Eaton | HMCP150*** | - | 150 | 480 | 3 | 100 | 460 | 3 | 60 | 77 | 1.42 | (1) (3) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16NN0 | 10 | 135
FRD0076 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 75 | 96 |  | (1) (3) (5) (7f)
|  | STR |  | AN16NN0 | 10 | 135
FRD0077 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 100 | 124
|  | STR |  | AN16NN0 | 10 | 135
FRD0078 | D | ICB | Eaton | HMCPS150*** | - | 150 | 600 | 3 | 50 | 575 | 3 | 60 | 62 | 1.42 | (1) (3) (5) (6b) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16NN0 | 10 | 135
FRD0079 |  | ICB |  | HMCPS150*** | - | 150 | [5 empty] | 75 | 77
|  | STR |  | AN16NN0 | 10 | 135
FRD0080 |  | ICB |  | HMCPS150*** | - | 150 | [5 empty] | 100 | 99 |  | (1) (3) (5) (6b) (7f)
|  | STR |  | AN16NN0 | 10 | 135
FRD0081 | D | ICB | Eaton | HMCP150*** | - | 150 | 600 | 3 | 100 | 575 | 3 | 60 | 63 | 1.42 | (1) (3) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | AN16NN0 | 10 | 135
FRD0082 | D | ICB | Eaton | HMCP150*** | - | 150 | 600 | 3 | 100 | 575 | 3 | 75 | 77
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | AN16NN0 | 10 | 135
FRD0083 | D | ICB | Eaton | HMCP150*** | - | 150 | 600 | 3 | 100 | 575 | 3 | 100 | 99 |  | (1) (3) (5) (7e)
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | AN16NN0 | 10 | 135
FRD0084 | D | ICB | Eaton | HMCP250*** | - | 250 | 200 | 3 | 100 | 200 | 3 | 50 | 150 | 2.15 | (1) (3) (5) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16SN0 | 10 | 270
FRD0085 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 60 | 177
|  | STR |  | AN16SN0 | 10 | 270
FRD0086 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 75 | 221
|  | STR |  | AN16SN0 | 10 | 270
FRD0087 | D | ICB | Eaton | HMCP250*** | - | 250 | 208 | 3 | 100 | 208 | 3 | 50 | 143 | 2.15 | (1) (3) (5) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16SN0 | 10 | 270
FRD0088 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 60 | 169
|  | STR |  | AN16SN0 | 10 | 270
FRD0089 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 75 | 211
|  | STR |  | AN16SN0 | 10 | 270
FRD0090 | D | ICB | Eaton | HMCP250*** | - | 250 | 240 | 3 | 100 | 230 | 3 | 60 | 154 | 2.15 | (1) (3) (5) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16SN0 | 10 | 270
FRD0091 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 75 | 192
|  | STR |  | AN16SN0 | 10 | 270
FRD0092 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 100 | 248
|  | STR |  | AN16SN0 | 10 | 270
FRD0093 | D | ICB | Eaton | HMCP250*** | - | 250 | 480 | 3 | 100 | 460 | 3 | 125 | 156 | 2.15 | (1) (3) (5) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16SN0 | 10 | 270
FRD0094 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 150 | 180
|  | STR |  | AN16SN0 | 10 | 270
FRD0095 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 200 | 240
|  | STR |  | AN16SN0 | 10 | 270
FRD0096 | D | ICB | Eaton | HMCP250*** | - | 250 | 600 | 3 | 50 | 575 | 3 | 125 | 125 | 2.15 | (1) (3) (5) (7f) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16SN0 | 10 | 270
FRD0097 |  | ICB |  | HMCP250*** | - | 250 | [5 empty] | 150 | 144 |  | (1) (3) (5) (7j)
|  | STR |  | AN16SN0 | 10 | 270
FRD0098 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 200 | 192
|  | STR |  | AN16SN0 | 10 | 270
FRD0099 | D | ICB | Eaton | HMCP600*** | - | 600 | 200 | 3 | 65 | 200 | 3 | 100 | 285 | 3.23 | (1) (3) (5) (7s) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16TN0 | 18 | 540
FRD0100 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 125 | 359
|  | STR |  | AN16TN0 | 18 | 540
FRD0101 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 150 | 414
|  | STR |  | AN16TN0 | 18 | 540
FRD0102 | D | ICB | Eaton | HMCP600*** | - | 600 | 208 | 3 | 65 | 208 | 3 | 100 | 273 | 3.23 | (1) (3) (5) (7s) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16TN0 | 18 | 540
FRD0103 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 125 | 343
|  | STR |  | AN16TN0 | 18 | 540
FRD0104 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 150 | 396
|  | STR |  | AN16TN0 | 18 | 540
FRD0105 | D | ICB | Eaton | HMCP600*** | - | 600 | 240 | 3 | 65 | 230 | 3 | 125 | 312 | 3.23 | (1) (3) (5) (7s) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16TN0 | 18 | 540
FRD0106 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 150 | 360
|  | STR |  | AN16TN0 | 18 | 540
FRD0107 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 200 | 480
|  | STR |  | AN16TN0 | 18 | 540
FRD0108 | D | ICB | Eaton | HMCP600*** | - | 600 | 480 | 3 | 65 | 460 | 3 | 250 | 302 | 3.23 | (1) (3) (5) (7s) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16TN0 | 18 | 540
FRD0109 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 300 | 361
|  | STR |  | AN16TN0 | 18 | 540
FRD0110 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 350 | 414
|  | STR |  | AN16TN0 | 18 | 540
FRD0111 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 400 | 477
|  | STR |  | AN16TN0 | 18 | 540
FRD0112 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
FRD0113 |  | - |  | - | - | - | [5 empty] | - | - |  | -
|  | - |  | - | - | -
FRD0114 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
FRD0115 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
FRD0116 | D | ICB | Eaton | HMCP12Y8W | - | 1200 | 240 | 3 | 65 | 230 | 3 | 300 | 720 | 22.1 | (1) (3) (5) (7m) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16UN0 | 30 | 810
FRD0117 |  | ICB |  | HMCP12Y8W | - | 1200 | 480 |  |  | 460 |  | 600 | 722
|  | STR |  | AN16UN0 | 30 | 810
FRD0118 |  | - |  | - | - | - | - |  | - | - |  | - | -
|  | - |  | - | - | -
FRD0119 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
FRD0120 |  | - |  | - | - | - | - |  |  | - |  | - | -
|  | - |  | - | - | -
FRD0121 |  | - |  | - | - | - | - |  |  | - |  | - | -
|  | - |  | - | - | -
FRD0122 | D | ICB | Eaton | HMCPE015*** | - | 15 | 200 | 3 | 100 | 200 | 3 | 2 | 7.8 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16BN0 | 5 | 18
|  | STR |  | AN16B0 | 5 | 18
FRD0123 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 3 | 11
|  | STR |  | AN16BN0 | 5 | 18
FRD0124 |  | ICB | Eaton | HMCPE015*** | - | 15 | 208 |  |  | 208 |  | 2 | 7.5
|  | STR |  | AN16B0 | 5 | 18
FRD0125 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 3 | 10.6
|  | STR |  | AN16BN0 | 5 | 18
FRD0126 |  | ICB | Eaton | HMCPE015*** | - | 15 | 240 | 3 | 100 | 230 | 3 | 2 | 6.8
|  | STR |  | AN16BN0 | 5 | 18
FRD0127 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 3 | 9.6
|  | STR |  | AN16BN0 | 5 | 18
FRD0128 | D | ICB | Eaton | HMCPE015*** | - | 15 | 480 |  |  | 460 |  | 3 | 4.8
|  | STR |  | AN16BN0 | 5 | 18
FRD0129 |  | ICB |  | HMCPE015*** | - | 15 | [5 empty] | 5 | 7.6
|  | STR |  | AN16BN0 | 5 | 18
FRD0130 | D | ICB | Eaton | HMCPE007*** | - | 7 | 200 | 3 | 100 | 200 | 3 | 1 | 4.8 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16DN0 | 5 | 27
FRD0131 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 3 | 11
|  | STR |  | AN16DN0 | 5 | 27
FRD0132 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 5 | 17.5
|  | ICB |  | AN16DN0 | 5 | 27
FRD0133 |  | STR |  | HMCPE050*** | - | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AN16DN0 | 5 | 27
FRD0134 | D | ICB | Eaton | HMCPE007*** | - | 7 | 208 | 3 | 100 | 208 | 3 | 1 | 4.6 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16DN0 | 5 | 27
FRD0135 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 3 | 10.6
|  | STR |  | AN16DN0 | 5 | 27
FRD0136 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 5 | 16.7
|  | STR |  | AN16DN0 | 5 | 27
FRD0137 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | AN16DN0 | 5 | 27
FRD0138 | D | ICB | Eaton | HMCPE007*** | - | 7 | 240 | 3 | 100 | 230 | 3 | 1 | 4.2 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16DN0 | 5 | 27
FRD0139 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 3 | 9.6
|  | STR |  | AN16DN0 | 5 | 27
FRD0140 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 5 | 15.2
|  | STR |  | AN16DN0 | 5 | 27
FRD0141 |  | ICB |  | HMCPE030*** | - | 50 | [5 empty] | 7.5 | 22
|  | STR |  | AN16DN0 | 5 | 27
FRD0142 | D | ICB | Eaton | HMCPE007*** | - | 7 | 480 | 3 | 100 | 460 | 3 | 1 | 2.1 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16DN0 | 5 | 27
FRD0143 |  | ICB |  | HMCPE015*** | - | 15 | [5 empty] | 3 | 4.8
|  | STR |  | AN16DN0 | 5 | 27
FRD0144 |  | ICB |  | HMCPE015*** | - | 15 | [5 empty] | 5 | 7.6
|  | STR |  | AN16DN0 | 5 | 27
FRD0145 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 7.5 | 11
|  | STR |  | AN16DN0 | 5 | 27
FRD0146 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 10 | 14
|  | STR |  | AN16DN0 | 5 | 27
FRD0147 | D | ICB | Eaton | HMCPE050*** | - | 50 | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16GN0 | 5 | 45
FRD0148 |  | ICB |  | HMCPE050*** | - | 50 | 208 |  |  | 208 |  | 10 | 30.8
|  | STR |  | AN16GN0 | 5 | 45
FRD0149 |  | ICB |  | HMCPE050*** | - | 50 | 240 |  |  | 230 |  | 10 | 28
|  | STR |  | AN16GN0 | 5 | 45
FRD0150 |  | ICB |  | HMCPE070*** | - | 70 | [5 empty] | 15 | 42
|  | STR |  | AN16GN0 | 5 | 45
FRD0151 | D | ICB | Eaton | HMCPE050*** | - | 50 | 480 | 3 | 100 | 460 | 3 | 15 | 21 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16GN0 | 5 | 45
FRD0152 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 20 | 27
|  | STR |  | AN16GN0 | 5 | 45
FRD0153 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 25 | 34 |  | (1) (3) (5) (7c)
|  | STR |  | AN16GN0 | 5 | 45
FRD0154 | D | ICB | Eaton | HMCPE100*** | - | 100 | 200 | 3 | 100 | 200 | 3 | 15 | 48.3 | 1.06 | (1) (3) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16KN0 | 5 | 90
FRD0155 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 20 | 62.1
|  | STR |  | AN16KN0 | 5 | 90
FRD0156 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 25 | 78.2
|  | STR |  | AN16KN0 | 5 | 90
FRD0157 | D | ICB | Eaton | HMCPE100*** | - | 100 | 208 | 3 | 100 | 208 | 3 | 15 | 46.2 | 1.06 | (1) (3) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16KN0 | 5 | 90
FRD0158 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 20 | 59.4
|  | STR |  | AN16KN0 | 5 | 90
FRD0159 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 25 | 74.8
|  | STR |  | AN16KN0 | 5 | 90
FRD0160 | D | ICB | Eaton | HMCPE100*** | - | 100 | 240 | 3 | 100 | 230 | 3 | 20 | 54 | 1.06 | (1) (3) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16KN0 | 5 | 90
FRD0161 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 25 | 68
|  | STR |  | AN16KN0 | 5 | 90
FRD0162 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 30 | 80
|  | STR |  | AN16KN0 | 5 | 90
FRD0163 | D | ICB | Eaton | HMCPE100*** | - | 100 | 480 | 3 | 100 | 460 | 3 | 30 | 40 | 1.06 | (1) (3) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN16KN0 | 5 | 90
FRD0164 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 40 | 52 |  | (1) (3) (5) (7e)
|  | STR |  | AN16KN0 | 5 | 90
FRD0165 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 50 | 65
|  | STR |  | AN16KN0 | 5 | 90
FRD0166 | D | ICB | Eaton | GMCP003*** | - | 3 | 200 | 3 | 42 | 200 | 3 | 1/2 | 2.5 | 0.47 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE16ASN0 | 5 | 7
FRD0167 | D | ICB | Eaton | GMCP003*** | - | 3 | 208 |  |  | 208 |  | 1/2 | 2.5
|  | STR |  | AE16ASN0 | 5 | 7
FRD0168 | D | ICB | Eaton | GMCP003*** | - | 3 | 240 |  |  | 230 |  | 1/2 | 2.5
|  | STR |  | AE16ASN0 | 5 | 7
FRD0169 | D | ICB | Eaton | GMCP003*** | - | 3 | 480 |  |  | 460 |  | 1 | 2.1
|  | STR |  | AE16ASN0 | 5 | 7
FRD0170 |  | ICB |  | GMCP007*** | - | 7 | [5 empty] | 1.5 | 3
|  | STR |  | AE16ASN0 | 5 | 7
FRD0171 | D | ICB | Eaton | GMCP007*** | - | 7 | 200 | 3 | 42 | 200 | 3 | 3/4 | 3.7 | 0.47 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE16BNS0 | 5 | 12
FRD0172 |  | ICB |  | GMCP007*** | - | 7 | [5 empty] | 1 | 4.8
|  | STR |  | AE16BNS0 | 5 | 12
FRD0173 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 1.5 | 6.9
|  | STR |  | AE16BNS0 | 5 | 12
FRD0174 | D | ICB | Eaton | GMCP007*** | - | 7 | 208 | 3 | 42 | 208 | 3 | 3/4 | 3.5 | 0.47 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE16BNS0 | 5 | 12
FRD0175 |  | ICB |  | GMCP007*** | - | 7 | [5 empty] | 1 | 4.6
|  | STR |  | AE16BNS0 | 5 | 12
FRD0176 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 1.5 | 6.6
|  | STR |  | AE16BNS0 | 5 | 12
FRD0177 | D | ICB | Eaton | GMCP007*** | - | 7 | 240 | 3 | 42 | 230 | 3 | 3/4 | 3.2 | 0.47 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE16BNS0 | 5 | 12
FRD0178 |  | ICB |  | GMCP007*** | - | 7 | [5 empty] | 1 | 4.2
|  | STR |  | AE16BNS0 | 5 | 12
FRD0179 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 1.5 | 6
|  | STR |  | AE16BNS0 | 5 | 12
FRD0180 | D | ICB | Eaton | GMCP007*** | - | 7 | 480 | 3 | 42 | 460 | 3 | 1.5 | 3 | 0.47 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE16BNS0 | 5 | 12
FRD0181 |  | ICB |  | GMCP007*** | - | 7 | [5 empty] | 2 | 3.4
|  | STR |  | AE16BNS0 | 5 | 12
FRD0182 |  | ICB |  | GMCP007*** | - | 7 | [5 empty] | 3 | 4.8
|  | STR |  | AE16BNS0 | 5 | 12
FRD0183 | D | ICB | Eaton | GMCP007*** | - | 7 | 200 | 3 | 42 | 200 | 3 | 1 | 4.8 | 0.47 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE16CNS0 | 5 | 12
FRD0184 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 1.5 | 6.9
|  | STR |  | AE16CNS0 | 5 | 12
FRD0185 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 2 | 7.8
|  | STR |  | AE16CNS0 | 5 | 12
FRD0186 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 3 | 11
|  | STR |  | AE16CNS0 | 5 | 12
FRD0187 | D | ICB | Eaton | GMCP007*** | - | 7 | 208 | 3 | 42 | 208 | 3 | 1 | 4.6 | 0.47 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE16CNS0 | 5 | 12
FRD0188 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 1.5 | 6.6
|  | STR |  | AE16CNS0 | 5 | 12
FRD0189 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 2 | 7.5
|  | STR |  | AE16CNS0 | 5 | 12
FRD0190 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 3 | 10.6
|  | STR |  | AE16CNS0 | 5 | 12
FRD0191 | D | ICB | Eaton | GMCP007*** | - | 7 | 240 | 3 | 42 | 230 | 3 | 1 | 4.2 | 0.47 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE16CNS0 | 5 | 12
FRD0192 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 1.5 | 6
|  | STR |  | AE16CNS0 | 5 | 12
FRD0193 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 2 | 6.8
|  | STR |  | AE16CNS0 | 5 | 12
FRD0194 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 3 | 9.6
|  | STR |  | AE16CNS0 | 5 | 12
FRD0195 | D | ICB | Eaton | GMCP007*** | - | 7 | 480 | 3 | 42 | 460 | 3 | 3 | 4.8 | 0.47 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE16CNS0 | 5 | 12
FRD0196 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 5 | 7.6
|  | STR |  | AE16CNS0 | 5 | 12
FRD0197 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 7.5 | 11
|  | STR |  | AE16CNS0 | 5 | 12
FRD0198 | D | ICB | Eaton | GMCP015*** | - | 15 | 200 | 3 | 42 | 200 | 3 | 2 | 7.8 | 0.47 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE16DNS0 | 5 | 18
FRD0199 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 3 | 11
|  | STR |  | AE16DNS0 | 5 | 18
FRD0200 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 17.5
|  | STR |  | AE16DNS0 | 5 | 18
FRD0201 | D | ICB | Eaton | HMCP015*** | - | 15 | 200 | 3 | 100 | 200 | 3 | 2 | 7.8 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16DNS0 | 5 | 18
FRD0202 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 3 | 11
|  | STR |  | AE16DNS0 | 5 | 18
FRD0203 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 5 | 17.5
|  | STR |  | AE16DNS0 | 5 | 18
FRD0204 | D | ICB | Eaton | GMCP015*** | - | 15 | 208 | 3 | 42 | 208 | 3 | 2 | 7.5 | 0.47 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE16DNS0 | 5 | 18
FRD0205 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 3 | 10.6
|  | STR |  | AE16DNS0 | 5 | 18
FRD0206 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 16.7
|  | STR |  | AE16DNS0 | 5 | 18
FRD0207 | D | ICB | Eaton | HMCP015*** | - | 15 | 208 | 3 | 100 | 208 | 3 | 2 | 7.5 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16DNS0 | 5 | 18
FRD0208 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 3 | 10.6
|  | STR |  | AE16DNS0 | 5 | 18
FRD0209 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 5 | 16.7
|  | STR |  | AE16DNS0 | 5 | 18
FRD0210 | D | ICB | Eaton | GMCP015*** | - | 15 | 240 | 3 | 42 | 230 | 3 | 2 | 6.8 | 0.47 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE16DNS0 | 5 | 18
FRD0211 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 3 | 9.6
|  | STR |  | AE16DNS0 | 5 | 18
FRD0212 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 15.2
|  | STR |  | AE16DNS0 | 5 | 18
FRD0213 | D | ICB | Eaton | HMCP015*** | - | 15 | 240 | 3 | 100 | 230 | 3 | 2 | 6.8 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16DNS0 | 5 | 18
FRD0214 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 3 | 9.6
|  | STR |  | AE16DNS0 | 5 | 18
FRD0215 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 5 | 15.2
|  | STR |  | AE16DNS0 | 5 | 18
FRD0216 | D | ICB | Eaton | GMCP015*** | - | 15 | 480 | 3 | 42 | 460 | 3 | 5 | 7.6 | 0.47 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE16DNS0 | 5 | 18
FRD0217 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 7.5 | 11
|  | STR |  | AE16DNS0 | 5 | 18
FRD0218 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 10 | 14
|  | STR |  | AE16DNS0 | 5 | 18
FRD0219 | D | ICB | Eaton | HMCP015*** | - | 15 | 480 | 3 | 100 | 460 | 3 | 5 | 7.6 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1
|  | STR |  | AE16DNS0 | 5 | 18
FRD0220 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 7.5 | 11
|  | STR |  | AE16DNS0 | 5 | 18
FRD0221 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 10 | 14
|  | STR |  | AE16DNS0 | 5 | 18
FRD0222 | D | ICB | Eaton | HMCP030*** | - | 30 | 600 | 3 | 50 | 575 | 3 | 7.5 | 9 | 0.33 | (1) (3) (5) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1
|  | STR |  | AE16DNS0 | 5 | 18
FRD0223 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 10 | 11
|  | STR |  | AE16DNS0 | 5 | 18
FRD0224 | D | ICB | Eaton | GMCP015*** | - | 15 | 200 | 3 | 42 | 200 | 3 | 2 | 7.8 | 0.47 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE16ENS0 | 5 | 25
FRD0225 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 3 | 11
|  | STR |  | AE16ENS0 | 5 | 25
FRD0226 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 17.5
|  | STR |  | AE16ENS0 | 5 | 25
FRD0227 | D | ICB | Eaton | GMCP015*** | - | 15 | 208 | 3 | 42 | 208 | 3 | 2 | 7.5 | 0.47 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE16ENS0 | 5 | 25
FRD0228 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 3 | 10.6
|  | STR |  | AE16ENS0 | 5 | 25
FRD0229 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 16.7
|  | STR |  | AE16ENS0 | 5 | 25
FRD0230 | D | ICB | Eaton | GMCP015*** | - | 15 | 240 | 3 | 42 | 230 | 3 | 3 | 9.6 | 0.47 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE16ENS0 | 5 | 25
FRD0231 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 15.2
|  | STR |  | AE16ENS0 | 5 | 25
FRD0232 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 7.5 | 22
|  | STR |  | AE16ENS0 | 5 | 25
FRD0233 | D | ICB | Eaton | GMCP015*** | - | 15 | 480 | 3 | 42 | 460 | 3 | 7.5 | 11 | 0.47 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE16ENS0 | 5 | 25
FRD0234 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 10 | 14
|  | STR |  | AE16ENS0 | 5 | 25
FRD0235 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 15 | 21
|  | STR |  | AE16ENS0 | 5 | 25
FRD0236 | D | ICB | Eaton | HMCP030*** | - | 30 | 200 | 3 | 100 | 200 | 3 | 3 | 11 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16FNS0 | 5 | 32
FRD0237 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 5 | 17.5
|  | STR |  | AE16FNS0 | 5 | 32
FRD0238 |  | ICB |  | GMCP050*** | - | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AE16FNS0 | 5 | 32
FRD0239 | D | ICB | Eaton | GMCP030*** | - | 30 | 200 | 3 | 42 | 200 | 3 | 3 | 11 | 0.47 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE16FNS0 | 5 | 32
FRD0240 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 17.5
|  | STR |  | AE16FNS0 | 5 | 32
FRD0241 |  | ICB |  | GMCP050*** | - | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AE16FNS0 | 5 | 32
FRD0242 | D | ICB | Eaton | HMCP030*** | - | 30 | 208 | 3 | 100 | 208 | 3 | 5 | 16.7 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16FNS0 | 5 | 32
FRD0243 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | AE16FNS0 | 5 | 32
FRD0244 | D | ICB | Eaton | GMCP030*** | - | 30 | 208 | 3 | 42 | 208 | 3 | 5 | 16.7 | 0.47 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE16FNS0 | 5 | 32
FRD0245 |  | ICB |  | GMCP050*** | - | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | AE16FNS0 | 5 | 32
FRD0246 |  | ICB |  | GMCP050*** | - | 50 | [5 empty] | 10 | 30.8 |  | (1) (3) (5) (7c)
|  | STR |  | AE16FNS0 | 5 | 32
FRD0247 | D | ICB | Eaton | HMCP030*** | - | 30 | 240 | 3 | 100 | 230 | 3 | 5 | 15.2 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16FNS0 | 5 | 32
FRD0248 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 7.5 | 22
|  | STR |  | AE16FNS0 | 5 | 32
FRD0249 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 10 | 28 |  | (1) (3) (5) (7c)
|  | STR |  | AE16FNS0 | 5 | 32
FRD0250 | D | ICB | Eaton | GMCP030*** | - | 30 | 240 | 3 | 42 | 230 | 3 | 5 | 15.2 | 0.47 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE16FNS0 | 5 | 32
FRD0251 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 7.5 | 22
|  | STR |  | AE16FNS0 | 5 | 32
FRD0252 | D | ICB | Eaton | HMCP030*** | - | 30 | 480 | 3 | 100 | 460 | 3 | 10 | 14 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16FNS0 | 5 | 32
FRD0253 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 15 | 21
|  | STR |  | AE16FNS0 | 5 | 32
FRD0254 | D | ICB | Eaton | GMCP030*** | - | 30 | 480 | 3 | 42 | 460 | 3 | 10 | 14 | 0.47 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE16FNS0 | 5 | 32
FRD0255 |  | ICB |  | GMCP50*** | - | 50 | [5 empty] | 15 | 21
|  | STR |  | AE16FNS0 | 5 | 32
FRD0256 |  | ICB |  | GMCP50*** | - | 50 | [5 empty] | 20 | 27
|  | STR |  | AE16FNS0 | 5 | 32
FRD0257 | D | ICB | Eaton | HMCP030*** | - | 30 | 600 | 3 | 50 | 575 | 3 | 15 | 17 | 0.33 | (1) (3) (5) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16FNS0 | 5 | 32
FRD0258 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 20 | 22
|  | STR |  | AE16FNS0 | 5 | 32
FRD0259 | D | ICB | Eaton | HMCP030*** | - | 30 | 600 | 3 | 100 | 575 | 3 | 15 | 17 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3030R | - | 30
|  | STR |  | AE16FNS0 | 5 | 32
FRD0260 | D | ICB | Eaton | HMCP030*** | - | 30 | 600 | 3 | 100 | 575 | 3 | 20 | 22
|  | C. Limiter |  | ELC3030R | - | 30
|  | STR |  | AE16FNS0 | 5 | 32
FRD0261 | D | ICB | Eaton | HMCP030*** | - | 30 | 200 | 3 | 100 | 200 | 3 | 3 | 11 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16GNS0 | 5 | 37
FRD0262 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 5 | 17.5
|  | STR |  | AE16GNS0 | 5 | 37
FRD0263 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AE16GNS0 | 5 | 37
FRD0264 | D | ICB | Eaton | HMCP030*** | - | 30 | 208 | 3 | 100 | 208 | 3 | 5 | 16.7 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16GNS0 | 5 | 37
FRD0265 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 7.5 | 24.2
|  | STR |  | AE16GNS0 | 5 | 37
FRD0266 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 10 | 30.8 |  | (1) (3) (5) (7c)
|  | STR |  | AE16GNS0 | 5 | 37
FRD0267 | D | ICB | Eaton | HMCP030*** | - | 30 | 240 | 3 | 100 | 230 | 3 | 5 | 15.2 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16GNS0 | 5 | 37
FRD0268 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 7.5 | 22
|  | STR |  | AE16GNS0 | 5 | 37
FRD0269 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 10 | 28 |  | (1) (3) (5) (7c)
|  | STR |  | AE16GNS0 | 5 | 37
FRD0270 | D | ICB | Eaton | HMCP030*** | - | 30 | 480 | 3 | 100 | 460 | 3 | 10 | 14 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16GNS0 | 5 | 37
FRD0271 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 15 | 21
|  | STR |  | AE16GNS0 | 5 | 37
FRD0272 | D | ICB | Eaton | HMCP030*** | - | 30 | 600 | 3 | 50 | 575 | 3 | 15 | 17 | 0.69 | (1) (3) (5 (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16GNS0 | 5 | 37
FRD0273 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 20 | 22
|  | STR |  | AE16GNS0 | 5 | 37
FRD0274 | D | ICB | Eaton | HMCP030*** | - | 30 | 600 | 3 | 100 | 575 | 3 | 15 | 17 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3030R | - | 30
|  | STR |  | AE16GNS0 | 5 | 37
FRD0275 | D | ICB | Eaton | HMCP030*** | - | 30 | 600 | 3 | 100 | 575 | 3 | 20 | 22
|  | C. Limiter |  | ELC3030R | - | 30
|  | STR |  | AE16GNS0 | 5 | 37
FRD0276 | D | ICB | Eaton | HMCP050*** | - | 50 | 200 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16JNS0 | 5 | 60
FRD0277 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 10 | 32.2 |  | (1) (3) (5) (7c)
|  | STR |  | AE16JNS0 | 5 | 60
FRD0278 |  | ICB |  | HMCP070*** | - | 70 | [5 empty] | 15 | 48.3 |  | (1) (3) (5) (7e)
|  | STR |  | AE16JNS0 | 5 | 60
FRD0279 | D | ICB | Eaton | HMCP050*** | - | 50 | 208 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16JNS0 | 5 | 60
FRD0280 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 10 | 30.8 |  | (1) (3) (5) (7c)
|  | STR |  | AE16JNS0 | 5 | 60
FRD0281 |  | ICB |  | HMCP070*** | - | 70 | [5 empty] | 15 | 46.2 |  | (1) (3) (5) (7e)
|  | STR |  | AE16JNS0 | 5 | 60
FRD0282 | D | ICB | Eaton | HMCP050*** | - | 50 | 240 | 3 | 100 | 230 | 3 | 10 | 28 | 0.69 | (1) (3) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16JNS0 | 5 | 60
FRD0283 |  | ICB |  | HMCP070*** | - | 70 | [5 empty] | 15 | 42
|  | STR |  | AE16JNS0 | 5 | 60
FRD0284 |  | ICB |  | HMCP070*** | - | 70 | [5 empty] | 20 | 54 |  | (1) (3) (5) (7e)
|  | STR |  | AE16JNS0 | 5 | 60
FRD0285 | D | ICB | Eaton | HMCP050*** | - | 50 | 480 | 3 | 100 | 460 | 3 | 25 | 34 | 0.69 | (1) (3) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16JNS0 | 5 | 60
FRD0286 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 30 | 40
|  | STR |  | AE16JNS0 | 5 | 60
FRD0287 | D | ICB | Eaton | HMCP050*** | - | 50 | 600 | 3 | 50 | 575 | 3 | 25 | 27 | 0.69 | (1) (3) (5) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16JNS0 | 5 | 60
FRD0288 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 30 | 32 |  | (1) (3) (5) (6b) (7c)
|  | STR |  | AE16JNS0 | 5 | 60
FRD0289 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 40 | 41
|  | STR |  | AE16JNS0 | 5 | 60
FRD0290 | D | ICB | Eaton | HMCP050*** | - | 50 | 600 | 3 | 100 | 575 | 3 | 25 | 27 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3050R | - | 50
|  | STR |  | AE16JNS0 | 5 | 60
FRD0291 | D | ICB | Eaton | HMCP050*** | - | 50 | 600 | 3 | 100 | 575 | 3 | 30 | 32 |  | (1) (3) (5) (7c)
|  | C. Limiter |  | ELC3050R | - | 50
|  | STR |  | AE16JNS0 | 5 | 60
FRD0292 | D | ICB | Eaton | HMCP050*** | - | 50 | 600 | 3 | 100 | 575 | 3 | 40 | 41
|  | C. Limiter |  | ELC3100R | - | 100
|  | STR |  | AE16JNS0 | 5 | 60
FRD0293 | D | ICB | Eaton | HMCP100*** | - | 100 | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 0.69 | (1) (3) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16KNS0 | 5 | 73
FRD0294 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 15 | 48.3 |  | (1) (3) (5) (7e)
|  | STR |  | AE16KNS0 | 5 | 73
FRD0295 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 20 | 62.1
|  | STR |  | AE16KNS0 | 5 | 73
FRD0296 | D | ICB | Eaton | HMCP050*** | - | 50 | 208 | 3 | 100 | 208 | 3 | 10 | 30.8 | 0.69 | (1) (3) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16KNS0 | 5 | 73
FRD0297 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 15 | 46.2 |  | (1) (3) (5) (7e)
|  | STR |  | AE16KNS0 | 5 | 73
FRD0298 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 20 | 59.4
|  | STR |  | AE16KNS0 | 5 | 73
FRD0299 | D | ICB | Eaton | HMCP070*** | - | 70 | 240 | 3 | 100 | 230 | 3 | 15 | 42 | 0.69 | (1) (3) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16KNS0 | 5 | 73
FRD0300 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 20 | 54 |  | (1) (3) (5) (7e)
|  | STR |  | AE16KNS0 | 5 | 73
FRD0301 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 25 | 68
|  | STR |  | AE16KNS0 | 5 | 73
FRD0302 | D | ICB | Eaton | HMCP100*** | - | 100 | 480 | 3 | 100 | 460 | 3 | 30 | 40 | 0.69 | (1) (3) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16KNS0 | 5 | 73
FRD0303 |  | ICB |  | HMCP100 | - | 100 | [5 empty] | 40 | 52 |  | (1) (3) (5) (7e)
|  | STR |  | AE16KNS0 | 5 | 73
FRD0304 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 50 | 65
|  | STR |  | AE16KNS0 | 5 | 73
FRD0305 | D | ICB | Eaton | HMCP050*** | - | 50 | 600 | 3 | 50 | 575 | 3 | 30 | 32 | 0.69 | (1) (3) (5) (6b) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16KNS0 | 5 | 73
FRD0306 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 40 | 41 |  | (1) (3) (5) (6b) (7e)
|  | STR |  | AE16KNS0 | 5 | 73
FRD0307 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 50 | 52
|  | STR |  | AE16KNS0 | 5 | 73
FRD0308 | D | ICB | Eaton | HMCP050*** | - | 50 | 600 | 3 | 100 | 575 | 3 | 30 | 32 | 0.69 | (1) (3) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3050R | - | 50
|  | STR |  | AE16KNS0 | 5 | 73
FRD0309 | D | ICB | Eaton | HMCP100*** | - | 100 | 600 | 3 | 100 | 575 | 3 | 40 | 41 |  | (1) (3) (5) (7e)
|  | C. Limiter |  | ELC3100R | - | 100
|  | STR |  | AE16KNS0 | 5 | 73
FRD0310 | D | ICB | Eaton | HMCP100*** | - | 100 | 600 | 3 | 100 | 575 | 3 | 50 | 52
|  | C. Limiter |  | ELC3100R | - | 100
|  | STR |  | AE16KNS0 | 5 | 73
FRD0311 | D | ICB | Eaton | HMCP100*** | - | 100 | 200 | 3 | 100 | 200 | 3 | 20 | 62.1 | 1.42 | (1) (3) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16NNS0 | 10 | 140
FRD0312 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 25 | 78.2 |  | (1) (3) (5) (7f)
|  | STR |  | AE16NNS0 | 10 | 140
FRD0313 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 30 | 92
|  | STR |  | AE16NNS0 | 10 | 140
FRD0314 | D | ICB | Eaton | HMCP150*** | - | 150 | 208 | 3 | 100 | 208 | 3 | 25 | 74.8 | 1.42 | (1) (3) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16NNS0 | 10 | 140
FRD0315 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 30 | 88 |  | (1) (3) (5) (7f)
|  | STR |  | AE16NNS0 | 10 | 140
FRD0316 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 40 | 114
|  | STR |  | AE16NNS0 | 10 | 140
FRD0317 | D | ICB | Eaton | HMCP150*** | - | 150 | 240 | 3 | 100 | 230 | 3 | 30 | 80 | 1.42 | (1) (3) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16NNS0 | 10 | 140
FRD0318 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 40 | 104 |  | (1) (3) (5) (7f)
|  | STR |  | AE16NNS0 | 10 | 140
FRD0319 |  | ICB |  | HMCP250 | - | 250 | [5 empty] | 50 | 130
|  | STR |  | AE16NNS0 | 10 | 140
FRD0320 | D | ICB | Eaton | HMCP150*** | - | 150 | 480 | 3 | 100 | 460 | 3 | 60 | 77 | 1.42 | (1) (3) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16NNS0 | 10 | 140
FRD0321 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 75 | 96 |  | (1) (3) (5) (7f)
|  | STR |  | AE16NNS0 | 10 | 140
FRD0322 |  | ICB |  | HMCP150 | - | 150 | [5 empty] | 100 | 124
|  | STR |  | AE16NNS0 | 10 | 140
FRD0323 | D | ICB | Eaton | HMCPS150*** | - | 150 | 600 | 3 | 50 | 575 | 3 | 75 | 77 | 1.42 | (1) (3) (5) (6b) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16NNS0 | 10 | 140
FRD0324 |  | ICB |  | HMCPS150*** | - | 150 | [5 empty] | 100 | 99 |  | (1) (3) (5) (6b) (7f)
|  | STR |  | AE16NNS0 | 10 | 140
FRD0325 |  | ICB |  | HMCPS150*** | - | 150 | [5 empty] | 125 | 125
|  | STR |  | AE16NNS0 | 10 | 140
FRD0326 | D | ICB | Eaton | HMCP150*** | - | 150 | 600 | 3 | 100 | 575 | 3 | 75 | 77 | 1.42 | (1) (3) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | AE16NNS0 | 10 | 140
FRD0327 | D | ICB | Eaton | HMCP150*** | - | 150 | 600 | 3 | 100 | 575 | 3 | 100 | 99 |  | (1) (3) (5) (7e)
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | AE16NNS0 | 10 | 140
FRD0328 | D | ICB | Eaton | HMCP150*** | - | 150 | 600 | 3 | 100 | 575 | 3 | 125 | 125
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | AE16NNS0 | 10 | 140
FRD0329 | D | ICB | Eaton | HMCPE015*** | - | 15 | 200 | 3 | 100 | 200 | 3 | 2 | 7.8 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16DNS0 | 5 | 18
FRD0330 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 3 | 11
|  | STR |  | AE16DNS0 | 5 | 18
FRD0331 | D | ICB | Eaton | HMCPE015 | - | 15 | 208 | 3 | 100 | 208 | 3 | 2 | 7.5 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16DNS0 | 5 | 18
FRD0332 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 3 | 10.6
|  | STR |  | AE16DNS0 | 5 | 18
FRD0333 | D | ICB | Eaton | HMCPE015*** | - | 15 | 240 | 3 | 100 | 230 | 3 | 2 | 6.8 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16DNS0 | 5 | 18
FRD0334 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 3 | 9.6
|  | STR |  | AE16DNS0 | 5 | 18
FRD0335 | D | ICB | Eaton | HMCPE015*** | - | 15 | 480 | 3 | 100 | 460 | 3 | 5 | 7.6 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16DNS0 | 5 | 18
FRD0336 |  | ICB |  | HMCPE015*** | - | 15 | [5 empty] | 7.5 | 11
|  | STR |  | AE16DNS0 | 5 | 18
FRD0337 | D | ICB | Eaton | HMCPE030*** | - | 30 | 200 | 3 | 100 | 200 | 3 | 3 | 11 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16FNS0 | 5 | 32
FRD0338 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 5 | 17.5
|  | STR |  | AE16FNS0 | 5 | 32
FRD0339 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AE16FN0 | 5 | 32
FRD0340 | D | ICB | Eaton | HMCPE030*** | - | 30 | 208 | 3 | 100 | 208 | 3 | 5 | 16.7 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16FNS0 | 5 | 32
FRD0341 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | AE16FNS0 | 5 | 32
FRD0342 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 10 | 30.8 |  | (1) (3) (5) (7c)
|  | STR |  | AE16FNS0 | 5 | 32
FRD0343 | D | ICB | Eaton | HMCPE030*** | - | 30 | 240 | 3 | 100 | 230 | 3 | 5 | 15.2 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16FNS0 | 5 | 32
FRD0344 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 7.5 | 22
|  | STR |  | AE16FNS0 | 5 | 32
FRD0345 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 10 | 28 |  | (1) (3) (5) (7c)
|  | STR |  | AE16FNS0 | 5 | 32
FRD0346 | D | ICB | Eaton | HMCPE030*** | - | 30 | 480 | 3 | 100 | 460 | 3 | 10 | 14 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16FNS0 | 5 | 32
FRD0347 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 15 | 21
|  | STR |  | AE16FNS0 | 5 | 32
FRD0348 | D | ICB | Eaton | HMCPE030*** | - | 30 | 200 | 3 | 100 | 200 | 3 | 3 | 11 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16FNS0 | 5 | 37
FRD0349 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 5 | 17.5
|  | STR |  | AE16FNS0 | 5 | 37
FRD0350 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AE16FNS0 | 5 | 37
FRD0351 | D | ICB | Eaton | HMCPE030*** | - | 30 | 208 | 3 | 100 | 208 | 3 | 5 | 16.7 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16GNS0 | 5 | 37
FRD0352 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 7.5 | 24.2
|  | STR |  | AE16GNS0 | 5 | 37
FRD0353 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 10 | 30.8 |  | (1) (3) (5) (7c)
|  | STR |  | AE16GNS0 | 5 | 37
FRD0354 | D | ICB | Eaton | HMCPE030*** | - | 30 | 240 | 3 | 100 | 230 | 3 | 5 | 15.2 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16GNS0 | 5 | 37
FRD0355 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 7.5 | 22
|  | STR |  | AE16GNS0 | 5 | 37
FRD0356 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 10 | 28 |  | (1) (3) (5) (7c)
|  | STR |  | AE16GNS0 | 5 | 37
FRD0357 | D | ICB | Eaton | HMCPE030*** | - | 30 | 480 | 3 | 100 | 460 | 3 | 15 | 21 | 0.33 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16GNS0 | 5 | 37
FRD0358 | D | ICB | Eaton | HMCPE050*** | - | 50 | 200 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16JNS0 | 5 | 60
FRD0359 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 10 | 32.2 |  | (1) (3) (5) (7c)
|  | STR |  | AE16JNS0 | 5 | 60
FRD0360 |  | ICB |  | HMCPE070*** | - | 70 | [5 empty] | 15 | 48.3 |  | (1) (3) (5) (7e)
|  | STR |  | AE16JNS0 | 5 | 60
FRD0361 | D | ICB | Eaton | HMCPE050*** | - | 50 | 208 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16JNS0 | 5 | 60
FRD0362 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 10 | 30.8 |  | (1) (3) (5) (7c)
|  | STR |  | AE16JNS0 | 5 | 60
FRD0363 |  | ICB |  | HMCPE070*** | - | 70 | [5 empty] | 15 | 46.2 |  | (1) (3) (5) (7e)
|  | STR |  | AE16JNS0 | 5 | 60
FRD0364 | D | ICB | Eaton | HMCPE050*** | - | 50 | 240 | 3 | 100 | 230 | 3 | 10 | 28 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16JNS0 | 5 | 60
FRD0365 |  | ICB |  | HMCPE070*** | - | 70 | [5 empty] | 15 | 42 |  | (1) (3) (5) (7c)
|  | STR |  | AE16JNS0 | 5 | 60
FRD0366 |  | ICB |  | HMCPE070*** | - | 70 | [5 empty] | 20 | 54 |  | (1) (3) (5) (7e)
|  | STR |  | AE16JNS0 | 5 | 60
FRD0367 | D | ICB | Eaton | HMCPE050*** | - | 50 | 480 | 3 | 100 | 460 | 3 | 25 | 34 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16JNS0 | 5 | 60
FRD0368 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 30 | 40 |  | (1) (3) (5) (7c)
|  | STR |  | AE16JNS0 | 5 | 60
FRD0369 | D | ICB | Eaton | HMCPE100*** | - | 100 | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 0.69 | (1) (3) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16KNS0 | 5 | 73
FRD0370 |  | ICB |  | HMCPE150*** | - | 150 | [5 empty] | 15 | 48.3 |  | (1) (3) (5) (7e)
|  | STR |  | AE16KNS0 | 5 | 73
FRD0371 |  | ICB |  | HMCPE150*** | - | 150 | [5 empty] | 20 | 62.1
|  | STR |  | AE16KNS0 | 5 | 73
FRD0372 | D | ICB | Eaton | HMCPE050*** | - | 50 | 208 | 3 | 100 | 208 | 3 | 10 | 30.8 | 0.69 | (1) (3) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16KNS0 | 5 | 73
FRD0373 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 15 | 46.2 |  | (1) (3) (5) (7e)
|  | STR |  | AE16KNS0 | 5 | 73
FRD0374 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 20 | 59.4
|  | STR |  | AE16KNS0 | 5 | 73
FRD0375 | D | ICB | Eaton | HMCPE070*** | - | 70 | 240 | 3 | 100 | 230 | 3 | 15 | 42 | 0.69 | (1) (3) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16KNS0 | 5 | 73
FRD0376 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 20 | 54 |  | (1) (3) (5) (7e)
|  | STR |  | AE16KNS0 | 5 | 73
FRD0377 |  | ICB |  | HMCPE150*** | - | 150 | [5 empty] | 25 | 68
|  | STR |  | AE16KNS0 | 5 | 73
FRD0378 | D | ICB | Eaton | HMCPE100*** | - | 100 | 480 | 3 | 100 | 460 | 3 | 30 | 40 | 0.69 | (1) (3) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16KNS0 | 5 | 73
FRD0379 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 40 | 52 |  | (1) (3) (5) (7e)
|  | STR |  | AE16KNS0 | 5 | 73
FRD0380 |  | ICB |  | HMCPE150*** | - | 150 | [5 empty] | 50 | 65
|  | STR |  | AE16KNS0 | 5 | 73
FRD0381 | D | ICB | Eaton | GMCP003*** | - | 3 | 200 | 3 | 42 | 200 | 3 | 1/2 | 2.5 | 0.47 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE17ANS0 | 5 | 7
FRD0382 | D | ICB | Eaton | GMCP003*** | - | 3 | 208 | 3 | 42 | 208 | 3 | 1/2 | 2.5 | 0.47 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE17ANS0 | 5 | 7
FRD0383 | D | ICB | Eaton | GMCP003*** | - | 3 | 240 | 3 | 42 | 230 | 3 | 1/2 | 2.5 | 0.47 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE17ANS0 | 5 | 7
FRD0384 | D | ICB | Eaton | GMCP003*** | - | 3 | 480 | 3 | 42 | 460 | 3 | 1 | 2.1 | 0.47 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE17ANS0 | 5 | 7
FRD0385 |  | ICB |  | GMCP007*** | - | 7 | [5 empty] | 1.5 | 3
|  | STR |  | AE17ANS0 | 5 | 7
FRD0386 | D | ICB | Eaton | GMCP007*** | - | 7 | 200 | 3 | 42 | 200 | 3 | 3/4 | 3.7 | 0.47 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE17BNS0 | 5 | 12
FRD0387 |  | ICB |  | GMCP007*** | - | 7 | [5 empty] | 1 | 4.8
|  | STR |  | AE17BNS0 | 5 | 12
FRD0388 | D | ICB | Eaton | GMCP007*** | - | 7 | 208 | 3 | 42 | 208 | 3 | 3/4 | 3.5 | 0.47 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE17BNS0 | 5 | 12
FRD0389 |  | ICB |  | GMCP007*** | - | 7 | [5 empty] | 1 | 4.6
|  | STR |  | AE17BNS0 | 5 | 12
FRD0390 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 1.5 | 6.6
|  | STR |  | AE17BNS0 | 5 | 12
FRD0391 | D | ICB | Eaton | GMCP007*** | - | 7 | 240 | 3 | 42 | 230 | 3 | 3/4 | 3.2 | 0.47 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE17BNS0 | 5 | 12
FRD0392 |  | ICB |  | GMCP007*** | - | 7 | [5 empty] | 1 | 4.2
|  | STR |  | AE17BNS0 | 5 | 12
FRD0393 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 1.5 | 6
|  | STR |  | AE17BNS0 | 5 | 12
FRD0394 | D | ICB | Eaton | GMCP007*** | - | 7 | 480 | 3 | 42 | 460 | 3 | 2 | 3.4 | 0.47 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE17BNS0 | 5 | 12
FRD0395 |  | ICB |  | GMCP007*** | - | 7 | [5 empty] | 3 | 4.8
|  | STR |  | AE17BNS0 | 5 | 12
FRD0396 | D | ICB | Eaton | GMCP007*** | - | 7 | 200 | 3 | 42 | 200 | 3 | 1 | 4.8 | 0.47 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE17CNS0 | 5 | 12
FRD0397 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 1.5 | 6.9
|  | STR |  | AE17CNS0 | 5 | 12
FRD0398 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 2 | 7.8
|  | STR |  | AE17CNS0 | 5 | 12
FRD0399 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 3 | 11
|  | STR |  | AE17CNS0 | 5 | 12
FRD0400 | D | ICB | Eaton | GMCP007*** | - | 7 | 208 | 3 | 42 | 208 | 3 | 1 | 4.6 | 0.47 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE17CNS0 | 5 | 12
FRD0401 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 1.5 | 6.6
|  | STR |  | AE17CNS0 | 5 | 12
FRD0402 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 2 | 7.5
|  | STR |  | AE17CNS0 | 5 | 10
FRD0403 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 3 | 10.6
|  | STR |  | AE17CNS0 | 5 | 12
FRD0404 | D | ICB | Eaton | GMCP015*** | - | 15 | 240 | 3 | 42 | 230 | 3 | 1 | 4.2 | 0.47 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE17CNS0 | 5 | 12
FRD0405 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 1.5 | 6
|  | STR |  | AE17CNS0 | 5 | 12
FRD0406 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 2 | 6.8
|  | STR |  | AE17CNS0 | 5 | 12
FRD0407 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 3 | 9.6
|  | STR |  | AE17CNS0 | 5 | 12
FRD0408 | D | ICB | Eaton | GMCP015*** | - | 15 | 480 | 3 | 42 | 460 | 3 | 3 | 4.8 | 0.47 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE17CNS0 | 5 | 12
FRD0409 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 5 | 7.6
|  | STR |  | AE17CNS0 | 5 | 12
FRD0410 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 7.5 | 11
|  | STR |  | AE17CNS0 | 5 | 12
FRD0411 | D | ICB | Eaton | GMCP015*** | - | 15 | 200 | 3 | 42 | 200 | 3 | 2 | 7.8 | 0.47 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE17DNS0 | 5 | 18
FRD0412 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 3 | 11
|  | STR |  | AE17DNS0 | 5 | 18
FRD0413 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 17.5
|  | STR |  | AE17DNS0 | 5 | 18
FRD0414 | D | ICB | Eaton | GMCP015*** | - | 15 | 208 | 3 | 42 | 208 | 3 | 2 | 7.5 | 0.47 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE17DNS0 | 5 | 18
FRD0415 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 3 | 10.6
|  | STR |  | AE17DNS0 | 5 | 18
FRD0416 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 16.7
|  | STR |  | AE17DNS0 | 5 | 18
FRD0417 | D | ICB | Eaton | GMCP015*** | - | 15 | 240 | 3 | 42 | 230 | 3 | 2 | 6.8 | 0.47 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE17DNS0 | 5 | 18
FRD0418 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 3 | 9.6
|  | STR |  | AE17DNS0 | 5 | 18
FRD0419 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 15.2
|  | STR |  | AE17DNS0 | 5 | 18
FRD0420 | D | ICB | Eaton | GMCP015*** | - | 15 | 480 | 3 | 42 | 460 | 3 | 5 | 7.6 | 0.47 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE17DNS0 | 5 | 18
FRD0421 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 7.5 | 11
|  | STR |  | AE17DNS0 | 5 | 18
FRD0422 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 10 | 14
|  | STR |  | AE17DNS0 | 5 | 18
FRD0423 | D | ICB | Eaton | GMCP015*** | - | 15 | 200 | 3 | 42 | 200 | 3 | 2 | 7.8 | 0.47 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE17ENS0 | 5 | 25
FRD0424 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 3 | 11
|  | STR |  | AE17ENS0 | 5 | 25
FRD0425 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 17.5
|  | STR |  | AE17ENS0 | 5 | 25
FRD0426 | D | ICB | Eaton | GMCP015*** | - | 15 | 208 | 3 | 42 | 208 | 3 | 2 | 7.5 | 0.47 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE17ENS0 | 5 | 25
FRD0427 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 3 | 10.6
|  | STR |  | AE17ENS0 | 5 | 25
FRD0428 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 16.7
|  | STR |  | AE17ENS0 | 5 | 25
FRD0429 | D | ICB | Eaton | GMCP015*** | - | 15 | 240 | 3 | 42 | 230 | 3 | 3 | 9.6 | 0.47 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE17ENS0 | 5 | 25
FRD0430 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 15.2
|  | STR |  | AE17ENS0 | 5 | 25
FRD0431 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 7.5 | 22
|  | STR |  | AE17ENS0 | 5 | 25
FRD0432 | D | ICB | Eaton | GMCP015*** | - | 15 | 480 | 3 | 42 | 460 | 3 | 7.5 | 11 | 0.47 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE17ENS0 | 5 | 25
FRD0433 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 10 | 14
|  | STR |  | AE17ENS0 | 5 | 25
FRD0434 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 15 | 21
|  | STR |  | AE17ENS0 | 5 | 25
FRD0435 | D | ICB | Eaton | GMCP030*** | - | 30 | 200 | 3 | 42 | 200 | 3 | 3 | 11 | 0.47 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE17FNS0 | 5 | 32
FRD0436 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 17.5
|  | STR |  | AE17FNS0 | 5 | 32
FRD0437 |  | ICB |  | GMCP050*** | - | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AE17FNS0 | 5 | 32
FRD0438 | D | ICB | Eaton | GMCP030*** | - | 30 | 208 | 3 | 42 | 208 | 3 | 5 | 16.7 | 0.47 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE17FNS0 | 5 | 32
FRD0439 |  | ICB |  | GMCP050*** | - | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | AE17FNS0 | 5 | 32
FRD0440 |  | ICB |  | GMCP050*** | - | 50 | [5 empty] | 10 | 30.8 |  | (1) (5) (7c)
|  | STR |  | AE17FNS0 | 5 | 32
FRD0441 | D | ICB | Eaton | GMCP030*** | - | 30 | 240 | 3 | 42 | 230 | 3 | 5 | 15.2 | 0.47 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE17FNS0 | 5 | 32
FRD0442 |  | ICB |  | GMCP050*** | - | 50 | [5 empty] | 7.5 | 22
|  | STR |  | AE17FNS0 | 5 | 32
FRD0443 |  | ICB |  | GMCP050*** | - | 50 | [5 empty] | 10 | 28 |  | (1) (5) (7c)
|  | STR |  | AE17FNS0 | 5 | 32
FRD0444 | D | ICB | Eaton | GMCP030*** | - | 30 | 480 | 3 | 42 | 460 | 3 | 10 | 14 | 0.47 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE17FNS0 | 5 | 32
FRD0445 |  | ICB |  | GMCP050*** | - | 50 | [5 empty] | 15 | 21
|  | STR |  | AE17FNS0 | 5 | 32
FRD0446 |  | ICB |  | GMCP050*** | - | 50 | [5 empty] | 20 | 27
|  | STR |  | AE17FNS0 | 5 | 32
FRD0447 | D | ICB | Eaton | HMCP015*** | - | 15 | 200 | 3 | 100 | 200 | 3 | 2 | 7.8 | 0.69 | (1) (5) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56BN0 | 5 | 18
FRD0448 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 3 | 11
|  | STR |  | AN56BN0 | 5 | 18
FRD0449 |  | ICB | Eaton | HMCP015*** | - | 15 | 208 |  |  | 208 |  | 2 | 7.5
|  | STR |  | AN56BN0 | 5 | 18
FRD0450 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 3 | 10.6
|  | STR |  | AN56BN0 | 5 | 18
FRD0451 |  | ICB | Eaton | HMCP015*** | - | 15 | 240 |  |  | 230 |  | 2 | 6.8
|  | STR |  | AN56BN0 | 5 | 18
FRD0452 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 3 | 9.6
|  | STR |  | AN56BN0 | 5 | 18
FRD0453 | D | ICB | Eaton | HMCP015*** | - | 15 | 480 | 3 | 100 | 460 | 3 | 3 | 4.8 | 0.69 | (1) (5) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56BN0 | 5 | 18
FRD0454 |  | ICB |  | HMCP015*** | - | 15 | [5 empty] | 5 | 7.6
|  | STR |  | AN56BN0 | 5 | 18
FRD0455 |  | ICB |  | HMCP007*** | - | 7 | 600 |  | 50 | 575 |  | 3 | 3.9 |  | (1) (3) (5) (6a) (7a)
|  | STR |  | AN56BN0 | 5 | 18
FRD0456 |  | ICB |  | HMCP015*** | - | 15 | [5 empty] | 5 | 6.1
|  | STR |  | AN56BN0 | 5 | 18
FRD0457 | D | ICB | Eaton | HMCP007*** | - | 7 | 200 | 3 | 100 | 200 | 3 | 1 | 4.8 | 0.69 | (1) (5) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56DN0 | 5 | 27
FRD0458 |  | ICB |  | HMCP015*** | - | 15 | [5 empty] | 3 | 11
|  | STR |  | AN56DN0 | 5 | 27
FRD0459 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 5 | 17.5
|  | ICB |  | AN56DN0 | 5 | 27
FRD0460 |  | STR |  | HMCP050*** | - | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AN56DN0 | 5 | 27
FRD0461 | D | ICB | Eaton | HMCP007*** | - | 7 | 208 | 3 | 100 | 208 | 3 | 1 | 4.6 | 0.69 | (1) (5) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56DN0 | 5 | 27
FRD0462 |  | ICB |  | HMCP015*** | - | 15 | [5 empty] | 3 | 10.6
|  | STR |  | AN56DN0 | 5 | 27
FRD0463 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 5 | 16.7
|  | STR |  | AN56DN0 | 5 | 27
FRD0464 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | AN56DN0 | 5 | 27
FRD0465 | D | ICB | Eaton | HMCP007*** | - | 7 | 240 | 3 | 100 | 230 | 3 | 1 | 4.2 | 0.69 | (1) (5) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56DN0 | 5 | 27
FRD0466 |  | ICB |  | HMCP015*** | - | 15 | [5 empty] | 3 | 9.6
|  | STR |  | AN56DN0 | 5 | 27
FRD0467 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 5 | 15.2
|  | STR |  | AN56DN0 | 5 | 27
FRD0468 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 7.5 | 22
|  | STR |  | AN56DN0 | 5 | 27
FRD0469 | D | ICB | Eaton | HMCP007*** | - | 7 | 480 | 3 | 100 | 460 | 3 | 1 | 2.1 | 0.69 | (1) (5) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56DN0 | 5 | 27
FRD0470 |  | ICB |  | HMCP007*** | - | 7 | [5 empty] | 3 | 4.8
|  | STR |  | AN56DN0 | 5 | 27
FRD0471 |  | ICB |  | HMCP015*** | - | 15 | [5 empty] | 5 | 7.6
|  | STR |  | AN56DN0 | 5 | 27
FRD0472 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 7.5 | 11
|  | STR |  | AN56DN0 | 5 | 27
FRD0473 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 10 | 14
|  | STR |  | AN16DN0 | 5 | 27
FRD0474 | D | ICB | Eaton | HMCP003*** | - | 3 | 600 | 3 | 50 | 575 | 3 | 1 | 1.7 | 0.69 | (1) (3) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56DN0 | 5 | 27
FRD0475 |  | ICB |  | HMCP007*** | - | 7 | [5 empty] | 3 | 3.9
|  | STR |  | AN56DN0 | 5 | 27
FRD0476 |  | ICB |  | HMCP015*** | - | 15 | [5 empty] | 5 | 6.1
|  | STR |  | AN56DN0 | 5 | 27
FRD0477 |  | ICB |  | HMCP015*** | - | 15 | [5 empty] | 7.5 | 9
|  | STR |  | AN56DN0 | 5 | 27
FRD0478 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 10 | 11
|  | STR |  | AN56DN0 | 5 | 27
FRD0479 | D | ICB | Eaton | HMCP003*** | - | 3 | 600 | 3 | 100 | 575 | 3 | 1 | 1.7 | 0.69 | (1) (5) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3003R | - | 3
|  | STR |  | AN56DN0 | 5 | 27
FRD0480 | D | ICB | Eaton | HMCP007*** | - | 7 | 600 | 3 | 100 | 575 | 3 | 3 | 3.9
|  | C. Limiter |  | ELC3007R | - | 7
|  | STR |  | AN56DN0 | 5 | 27
FRD0481 | D | ICB | Eaton | HMCP015*** | - | 15 | 600 | 3 | 100 | 575 | 3 | 5 | 6.1
|  | C. Limiter |  | ELC3015R | - | 15
|  | STR |  | AN56DN0 | 5 | 27
FRD0482 | D | ICB | Eaton | HMCP015*** | - | 15 | 600 | 3 | 100 | 575 | 3 | 7.5 | 9
|  | C. Limiter |  | ELC3015R | - | 15
|  | STR |  | AN56DN0 | 5 | 27
FRD0483 | D | ICB | Eaton | HMCP030*** | - | 30 | 600 | 3 | 100 | 575 | 3 | 10 | 11
|  | C. Limiter |  | ELC3030R | - | 30
|  | STR |  | AN56DN0 | 5 | 27
FRD0484 | D | ICB | Eaton | HMCP050*** | - | 50 | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 0.69 | (1) (5) (3) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56GN0 | 5 | 45
FRD0485 |  | ICB |  | HMCP050*** | - | 50 | 208 |  |  | 208 |  | 10 | 30.8
|  | STR |  | AN56GN0 | 5 | 45
FRD0486 |  | ICB |  | HMCP050*** | - | 50 | 240 |  |  | 230 |  | 10 | 28
|  | STR |  | AN56GN0 | 5 | 45
FRD0487 |  | ICB |  | HMCP070*** | - | 70 | [5 empty] | 15 | 42
|  | STR |  | AN56GN0 | 5 | 45
FRD0488 | D | ICB | Eaton | HMCP050*** | - | 50 | 480 | 3 | 100 | 460 | 3 | 15 | 21 | 0.69 | (1) (5) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56GN0 | 5 | 45
FRD0489 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 20 | 27
|  | STR |  | AN56GN0 | 5 | 45
FRD0490 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 25 | 34 |  | (1) (3) (5) (7c)
|  | STR |  | AN56GN0 | 5 | 45
FRD0491 | D | ICB | Eaton | HMCP030*** | - | 30 | 600 | 3 | 50 | 575 | 3 | 15 | 17 | 0.69 | (1) (3) (3) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56GN0 | 5 | 45
FRD0492 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 20 | 22
|  | STR |  | AN56GN0 | 5 | 45
FRD0493 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 25 | 27
|  | STR |  | AN56GN0 | 5 | 45
FRD0494 | D | ICB | Eaton | HMCP030*** | - | 30 | 600 | 3 | 100 | 575 | 3 | 15 | 17 | 0.69 | (1) (5) (3) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ECL3030R | - | 30
|  | STR |  | AN56GN0 | 5 | 45
FRD0495 | D | ICB | Eaton | HMCP050*** | - | 50 | 600 | 3 | 100 | 575 | 3 | 20 | 22
|  | C. Limiter |  | ECL3050R | - | 50
|  | STR |  | AN56GN0 | 5 | 45
FRD0496 | D | ICB | Eaton | HMCP050*** | - | 50 | 600 | 3 | 100 | 575 | 3 | 25 | 27
|  | C. Limiter |  | ECL3050R | - | 50
|  | STR |  | AN56GN0 | 5 | 45
FRD0497 | D | ICB | Eaton | HMCP100*** | - | 100 | 200 | 3 | 100 | 200 | 3 | 15 | 48.3 | 1.06 | (1) (3) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56KN0 | 5 | 90
FRD0498 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 20 | 62.1
|  | STR |  | AN56KN0 | 5 | 90
FRD0499 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 25 | 78.2
|  | STR |  | AN56KN0 | 5 | 90
FRD0500 | D | ICB | Eaton | HMCP100*** | - | 100 | 208 | 3 | 100 | 208 | 3 | 15 | 46.2 | 1.06 | (1) (3) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56KN0 | 5 | 90
FRD0501 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 20 | 59.4
|  | STR |  | AN56KN0 | 5 | 90
FRD0502 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 25 | 74.8
|  | STR |  | AN56KN0 | 5 | 90
FRD0503 | D | ICB | Eaton | HMCP100*** | - | 100 | 240 | 3 | 100 | 230 | 3 | 20 | 54 | 1.06 | (1) (3) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56KN0 | 5 | 90
FRD0504 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 25 | 68
|  | STR |  | AN56KN0 | 5 | 90
FRD0505 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 30 | 80
|  | STR |  | AN56KN0 | 5 | 90
FRD0506 | D | ICB | Eaton | HMCP100*** | - | 100 | 480 | 3 | 100 | 460 | 3 | 30 | 40 | 1.06 | (1) (3) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56KN0 | 5 | 90
FRD0507 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 40 | 52 |  | (1) (3) (5) (7e)
|  | STR |  | AN56KN0 | 5 | 90
FRD0508 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 50 | 65
|  | STR |  | AN56KN0 | 5 | 90
FRD0509 | D | ICB | Eaton | HMCP050*** | - | 50 | 600 | 3 | 50 | 575 | 3 | 30 | 32 | 1.06 | (1) (3) (5) (6b) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56KN0 | 5 | 90
FRD0510 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 40 | 41
|  | STR |  | AN56KN0 | 5 | 90
FRD0511 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 50 | 52 |  | (1) (3) (5) (6b) (7f)
|  | STR |  | AN56KN0 | 5 | 90
FRD0512 | D | ICB | Eaton | HMCP050*** | - | 50 | 600 | 3 | 100 | 575 | 3 | 30 | 32 | 1.42 | (1) (3) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3050R | - | 50
|  | STR |  | AN56KN0 | 5 | 90
FRD0513 | D | ICB | Eaton | HMCP100*** | - | 100 | 600 | 3 | 100 | 575 | 3 | 40 | 41
|  | C. Limiter |  | ECL3100R | - | 100
|  | STR |  | AN56KN0 | 5 | 90
FRD0514 | D | ICB | Eaton | HMCP100*** | - | 100 | 600 | 3 | 100 | 575 | 3 | 50 | 52 |  | (1) (3) (5) (7f)
|  | C. Limiter |  | ECL3100R | - | 100
|  | STR |  | AN56KN0 | 5 | 90
FRD0515 | D | ICB | Eaton | HMCP150*** | - | 150 | 200 | 3 | 100 | 200 | 3 | 30 | 92 | 1.42 | (1) (3) (5) (7f) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56NN0 | 10 | 135
FRD0516 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 40 | 120
|  | STR |  | AN56NN0 | 10 | 135
FRD0517 | D | ICB | Eaton | HMCP150*** | - | 150 | 208 | 3 | 100 | 208 | 3 | 30 | 88 | 1.42 | (1) (3) (5) (7f) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56NN0 | 10 | 135
FRD0518 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 40 | 114 |  | (1) (3) (5) (7f)
|  | STR |  | AN56NN0 | 10 | 135
FRD0519 | D | ICB | Eaton | HMCP150*** | - | 150 | 240 | 3 | 100 | 230 | 3 | 40 | 104 | 1.42 | (1) (3) (5) (7f) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56NN0 | 10 | 135
FRD0520 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 50 | 130
|  | STR |  | AN56NN0 | 10 | 135
FRD0521 | D | ICB | Eaton | HMCP150*** | - | 150 | 480 | 3 | 100 | 460 | 3 | 60 | 77 | 1.42 | (1) (3) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56NN0 | 10 | 135
FRD0522 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 75 | 96 |  | (1) (3) (5) (7f)
|  | STR |  | AN56NN0 | 10 | 135
FRD0523 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 100 | 124
|  | STR |  | AN56NN0 | 10 | 135
FRD0524 | D | ICB | Eaton | HMCPS150*** | - | 150 | 600 | 3 | 50 | 575 | 3 | 60 | 62 | 1.42 | (1) (3) (5) (6b) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56NN0 | 10 | 135
FRD0525 |  | ICB |  | HMCPS150*** | - | 150 | [5 empty] | 75 | 77
|  | STR |  | AN56NN0 | 10 | 135
FRD0526 |  | ICB |  | HMCPS150*** | - | 150 | [5 empty] | 100 | 99 |  | (1) (3) (5) (6b) (7f)
|  | STR |  | AN56NN0 | 10 | 135
FRD0527 | D | ICB | Eaton | HMCP150*** | - | 150 | 600 | 3 | 100 | 575 | 3 | 60 | 62 | 1.42 | (1) (3) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ECL3150R | - | 150
|  | STR |  | AN56NN0 | 10 | 135
FRD0528 | D | ICB | Eaton | HMCP150*** | - | 150 | 600 | 3 | 100 | 575 | 3 | 75 | 77
|  | C. Limiter |  | ECL3150R | - | 150
|  | STR |  | AN56NN0 | 10 | 135
FRD0529 | D | ICB | Eaton | HMCP150*** | - | 150 | 600 | 3 | 100 | 575 | 3 | 100 | 99 |  | (1) (3) (5) (7f)
|  | C. Limiter |  | ECL3150R | - | 150
|  | STR |  | AN56NN0 | 10 | 135
FRD0530 | D | ICB | Eaton | HMCP250*** | - | 250 | 200 | 3 | 100 | 200 | 3 | 50 | 150 | 2.15 | (1) (3) (5) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56SN0 | 10 | 270
FRD0531 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 60 | 177
|  | STR |  | AN56SN0 | 10 | 270
FRD0532 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 75 | 221
|  | STR |  | AN56SN0 | 10 | 270
FRD0533 | D | ICB | Eaton | HMCP250*** | - | 250 | 208 | 3 | 100 | 208 | 3 | 50 | 143 | 2.15 | (1) (3) (5) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56SN0 | 10 | 270
FRD0534 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 60 | 169
|  | STR |  | AN56SN0 | 10 | 270
FRD0535 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 75 | 211
|  | STR |  | AN56SN0 | 10 | 270
FRD0536 | D | ICB | Eaton | HMCP250*** | - | 250 | 240 | 3 | 100 | 230 | 3 | 60 | 154 | 2.15 | (1) (3) (5) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56SN0 | 10 | 270
FRD0537 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 75 | 192
|  | STR |  | AN56SN0 | 10 | 270
FRD0538 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 100 | 248
|  | STR |  | AN56SN0 | 10 | 270
FRD0539 | D | ICB | Eaton | HMCP250*** | - | 250 | 480 | 3 | 100 | 460 | 3 | 125 | 156 | 2.15 | (1) (3) (5) (7j) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56SN0 | 10 | 270
FRD0540 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 150 | 180
|  | STR |  | AN56SN0 | 10 | 270
FRD0541 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 200 | 240
|  | STR |  | AN56SN0 | 10 | 270
FRD0542 | D | ICB | Eaton | HMCP250*** | - | 250 | 600 | 3 | 50 | 575 | 3 | 125 | 125 | 2.15 | (1) (3) (5) (7f) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56SN0 | 10 | 270
FRD0543 |  | ICB |  | HMCP250*** | - | 250 | [5 empty] | 150 | 144 |  | (1) (3) (5) (7j)
|  | STR |  | AN56SN0 | 10 | 270
FRD0544 |  | ICB |  | HMCP400*** | - | 400 | [5 empty] | 200 | 192
|  | STR |  | AN56SN0 | 10 | 270
FRD0545 | D | ICB | Eaton | HMCP600*** | - | 600 | 200 | 3 | 65 | 200 | 3 | 100 | 285 | 3.6 | (1) (3) (5) (7s) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56TN0 | 18 | 540
FRD0546 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 125 | 359
|  | STR |  | AN56TN0 | 18 | 540
FRD0547 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 150 | 414
|  | STR |  | AN56TN0 | 18 | 540
FRD0548 | D | ICB | Eaton | HMCP600*** | - | 600 | 208 | 3 | 65 | 208 | 3 | 100 | 273 | 3.6 | (1) (3) (5) (7s) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56TN0 | 18 | 540
FRD0549 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 125 | 343
|  | STR |  | AN56TN0 | 18 | 540
FRD0550 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 150 | 396
|  | STR |  | AN56TN0 | 18 | 540
FRD0551 | D | ICB | Eaton | HMCP600*** | - | 600 | 240 | 3 | 65 | 230 | 3 | 125 | 312 | 3.6 | (1) (3) (5) (7s) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56TN0 | 18 | 540
FRD0552 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 150 | 360
|  | STR |  | AN56TN0 | 18 | 540
FRD0553 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 200 | 480
|  | STR |  | AN56TN0 | 18 | 540
FRD0554 | D | ICB | Eaton | HMCP600*** | - | 600 | 480 | 3 | 65 | 460 | 3 | 250 | 302 | 3.6 | (1) (3) (5) (7s) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56TN0 | 18 | 540
FRD0555 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 300 | 361
|  | STR |  | AN56TN0 | 18 | 540
FRD0556 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 350 | 414
|  | STR |  | AN56TN0 | 18 | 540
FRD0557 |  | ICB |  | HMCP600*** | - | 600 | [5 empty] | 400 | 477
|  | STR |  | AN56TN0 | 18 | 540
FRD0558 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
FRD0559 |  | - |  | - | - | - | [5 empty] | - | - |  | -
|  | - |  | - | - | -
FRD0560 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
FRD0561 |  | - |  | - | - | - | [5 empty] | - | -
|  | - |  | - | - | -
FRD0562 | D | ICB | Eaton | HMCP12Y8W | - | 1200 | 240 | 3 | 65 | 230 | 3 | 300 | 720 | 22.2 | (1) (3) (5) (7m) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56UN0 | 30 | 810
FRD0563 |  | ICB |  | HMCP12Y8W | - | 1200 | 480 |  |  | 460 |  | 600 | 722
|  | STR |  | AN56UN0 | 30 | 810
FRD0564 |  | - |  | - | - | - | - |  | - | - |  | - | -
|  | - |  | - | - | -
FRD0565 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - |  | - | - | -
FRD0566 |  | - |  | - | - | - | - |  |  | - |  | - | -
|  | - |  | - | - | -
FRD0567 |  | - |  | - | - | - | - |  |  | - |  | - | -
|  | - |  | - | - | -
FRD0568 | D | ICB | Eaton | HMCPE015*** | - | 15 | 200 | 3 | 100 | 200 | 3 | 2 | 7.8 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56BN0 | 5 | 18
FRD0569 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 3 | 11
|  | STR |  | AN56BN0 | 5 | 18
FRD0570 |  | ICB | Eaton | HMCPE015*** | - | 15 | 208 |  |  | 208 |  | 2 | 7.5
|  | STR |  | AN56BN0 | 5 | 18
FRD0571 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 3 | 10.6
|  | STR |  | AN56BN0 | 5 | 18
FRD0572 |  | ICB | Eaton | HMCPE015*** | - | 15 | 240 |  |  | 230 |  | 2 | 6.8
|  | STR |  | AN56BN0 | 5 | 18
FRD0573 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 3 | 9.6
|  | STR |  | AN56BN0 | 5 | 18
FRD0574 | D | ICB | Eaton | HMCPE015*** | - | 15 | 480 | 3 | 100 | 460 | 3 | 3 | 4.8 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56BN0 | 5 | 18
FRD0575 |  | ICB |  | HMCPE015*** | - | 15 | [5 empty] | 5 | 7.6
|  | STR |  | AN56BN0 | 5 | 18
FRD0576 | D | ICB | Eaton | HMCPE007*** | - | 7 | 200 | 3 | 100 | 200 | 3 | 1 | 4.8 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56DN0 | 5 | 27
FRD0577 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 3 | 11
|  | STR |  | AN56DN0 | 5 | 27
FRD0578 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 5 | 17.5
|  | ICB |  | AN56DN0 | 5 | 27
FRD0579 |  | STR |  | HMCPE050*** | - | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AN56DN0 | 5 | 27
FRD0580 | D | ICB | Eaton | HMCPE007*** |  | 7 | 208 | 3 | 100 | 208 | 3 | 1 | 4.6 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56DN0 | 5 | 27
FRD0581 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 3 | 10.6
|  | STR |  | AN56DN0 | 5 | 27
FRD0582 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 5 | 16.7
|  | STR |  | AN56DN0 | 5 | 27
FRD0583 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | AN56DN0 | 5 | 27
FRD0584 | D | ICB | Eaton | HMCPE007*** |  | 7 | 240 | 3 | 100 | 230 | 3 | 1 | 4.2 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56DN0 | 5 | 27
FRD0585 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 3 | 9.6
|  | STR |  | AN56DN0 | 5 | 27
FRD0586 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 5 | 15.2
|  | STR |  | AN56DN0 | 5 | 27
FRD0587 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 7.5 | 22
|  | STR |  | AN56DN0 | 5 | 27
FRD0588 | D | ICB | Eaton | HMCPE007*** | - | 7 | 480 | 3 | 100 | 460 | 3 | 1 | 2.1 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56DN0 | 5 | 27
FRD0589 |  | ICB |  | HMCPE007*** | - | 7 | [5 empty] | 3 | 4.8
|  | STR |  | AN56DN0 | 5 | 27
FRD0590 |  | ICB |  | HMCPE015*** | - | 15 | [5 empty] | 5 | 7.6
|  | STR |  | AN56DN0 | 5 | 27
FRD0591 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 7.5 | 11
|  | STR |  | AN56DN0 | 5 | 27
FRD0592 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 10 | 14
|  | STR |  | AN56DN0 | 5 | 27
FRD0593 | D | ICB | Eaton | HMCPE050*** | - | 50 | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 0.69 | (1) (3) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56GN0 | 5 | 45
FRD0594 |  | ICB |  | HMCPE050*** | - | 50 | 208 |  |  | 208 |  | 10 | 30.8
|  | STR |  | AN56GN0 | 5 | 45
FRD0595 |  | ICB |  | HMCPE050*** | - | 50 | 240 |  |  | 230 |  | 10 | 28
|  | STR |  | AN56GN0 | 5 | 45
FRD0596 |  | ICB |  | HMCPE070*** | - | 70 | [5 empty] | 15 | 42
|  | STR |  | AN56GN0 | 5 | 45
FRD0597 | D | ICB | Eaton | HMCPE050*** | - | 50 | 480 | 3 | 100 | 460 | 3 | 15 | 21 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56GN0 | 5 | 45
FRD0598 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 20 | 27
|  | STR |  | AN56GN0 | 5 | 45
FRD0599 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 25 | 34 |  | (1) (3) (5) (7c)
|  | STR |  | AN56GN0 | 5 | 45
FRD0600 | D | ICB | Eaton | HMCPE100*** | - | 100 | 200 | 3 | 100 | 200 | 3 | 15 | 48.3 | 1.06 | (1) (3) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56KN0 | 5 | 90
FRD0601 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 20 | 62.1
|  | STR |  | AN56KN0 | 5 | 90
FRD0602 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 25 | 78.2
|  | STR |  | AN56KN0 | 5 | 90
FRD0603 | D | ICB | Eaton | HMCPE100*** | - | 100 | 208 | 3 | 100 | 208 | 3 | 15 | 46.2 | 1.06 | (1) (3) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56KN0 | 5 | 90
FRD0604 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 20 | 59.4
|  | STR |  | AN56KN0 | 5 | 90
FRD0605 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 25 | 74.8
|  | STR |  | AN56KN0 | 5 | 90
FRD0606 | D | ICB | Eaton | HMCPE100*** | - | 100 | 240 | 3 | 100 | 230 | 3 | 20 | 54 | 1.06 | (1) (3) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56KN0 | 5 | 90
FRD0607 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 25 | 68
|  | STR |  | AN56KN0 | 5 | 90
FRD0608 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 30 | 80
|  | STR |  | AN56KN0 | 5 | 90
FRD0609 | D | ICB | Eaton | HMCPE100*** | - | 100 | 480 | 3 | 100 | 460 | 3 | 30 | 40 | 1.06 | (1) (3) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AN56KN0 | 5 | 90
FRD0610 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 40 | 52 |  | (1) (3) (5) (7e)
|  | STR |  | AN56KN0 | 5 | 90
FRD0611 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 50 | 65
|  | STR |  | AN56KN0 | 5 | 90
FRD0612 | D | ICB | Eaton | HMCP015*** | - | 15 | 200 | 3 | 100 | 200 | 3 | 2 | 7.8 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56DNS0 | 5 | 18
FRD0613 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 3 | 11
|  | STR |  | AE56DNS0 | 5 | 18
FRD0614 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 5 | 17.5
|  | STR |  | AE56DNS0 | 5 | 18
FRD0615 | D | ICB | Eaton | HMCP015*** | - | 15 | 208 | 3 | 100 | 208 | 3 | 2 | 7.5 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56DNS0 | 5 | 18
FRD0616 |  | ICB |  | HMCP015*** | - | 15 | [5 empty] | 3 | 10.6
|  | STR |  | AE56DNS0 | 5 | 18
FRD0617 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 5 | 16.7
|  | STR |  | AE56DNS0 | 5 | 18
FRD0618 | D | ICB | Eaton | HMCP015*** | - | 15 | 240 | 3 | 100 | 230 | 3 | 2 | 6.8 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56DNS0 | 5 | 18
FRD0619 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 3 | 9.6
|  | STR |  | AE56DNS0 | 5 | 18
FRD0620 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 5 | 15.2
|  | STR |  | AE56DNS0 | 5 | 18
FRD0621 | D | ICB | Eaton | HMCP015*** | - | 15 | 480 | 3 | 100 | 460 | 3 | 5 | 7.6 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56DNS0 | 5 | 18
FRD0622 |  | ICB |  | HMCP015*** | - | 15 | [5 empty] | 7.5 | 11
|  | STR |  | AE56DNS0 | 5 | 18
FRD0623 | D | ICB | Eaton | HMCP015*** | - | 15 | 600 | 3 | 50 | 575 | 3 | 7.5 | 9 | 0.69 | (1) (5) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56DNS0 | 5 | 18
FRD0624 |  | ICB |  | HMCP015*** | - | 15 | [5 empty] | 10 | 11
|  | STR |  | AE56DNS0 | 5 | 18
FRD0625 | D | ICB | Eaton | HMCP030*** | - | 30 | 200 | 3 | 100 | 200 | 3 | 3 | 11 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56FNS0 | 5 | 32
FRD0626 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 5 | 17.5
|  | STR |  | AE56FNS0 | 5 | 32
FRD0627 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AE56FNS0 | 5 | 32
FRD0628 | D | ICB | Eaton | HMCP030*** |  | 30 | 208 | 3 | 100 | 208 | 3 | 3 | 10.6 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56FNS0 | 5 | 32
FRD0629 |  | ICB |  | HMCP030*** |  | 30 | [5 empty] | 5 | 16.7
|  | STR |  | AE56FNS0 | 5 | 32
FRD0630 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | AE56FNS0 | 5 | 32
FRD0631 | D | ICB | Eaton | HMCP030*** | - | 30 | 240 | 3 | 100 | 230 | 3 | 5 | 15.2 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56FNS0 | 5 | 32
FRD0632 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 7.5 | 22
|  | STR |  | AE56FNS0 | 5 | 32
FRD0633 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 10 | 28
|  | STR |  | AE56FNS0 | 5 | 32
FRD0634 | D | ICB | Eaton | HMCP030*** | - | 30 | 480 | 3 | 100 | 460 | 3 | 10 | 14 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56FNS0 | 5 | 32
FRD0635 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 15 | 21
|  | STR |  | AE56FNS0 | 5 | 32
FRD0636 | D | ICB | Eaton | HMCP030*** | - | 30 | 600 | 3 | 50 | 575 | 3 | 15 | 17 | 0.69 | (1) (3) (5) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56FNS0 | 5 | 32
FRD0637 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 20 | 22
|  | STR |  | AE56FNS0 | 5 | 32
FRD0638 | D | ICB | Eaton | HMCP030*** | - | 30 | 600 | 3 | 100 | 575 | 3 | 15 | 17 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ECL3030R | - | 30
|  | STR |  | AE56FNS0 | 5 | 32
FRD0639 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 20 | 22
|  | C. Limiter |  | ECL3030R | - | 30
|  | STR |  | AE56FNS0 | 5 | 32
FRD0640 | D | ICB | Eaton | HMCP030*** | - | 30 | 200 | 3 | 100 | 200 | 3 | 3 | 11 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56GNS0 | 5 | 37
FRD0641 |  | ICB |  | HMCP030*** | - | 30 | [5 empty] | 5 | 17.5
|  | STR |  | AE56GN0 | 5 | 37
FRD0642 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AE56GNS0 | 5 | 37
FRD0643 | D | ICB | Eaton | HMCP030*** | - | 30 | 208 | 3 | 100 | 208 | 3 | 5 | 16.7 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56GNS0 | 5 | 37
FRD0644 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | AE56GNS0 | 5 | 37
FRD0645 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 10 | 30.8 |  | (1) (5) (7c)
|  | STR |  | AE56GNS0 | 5 | 37
FRD0646 | D | ICB | Eaton | HMCP030*** | - | 30 | 240 | 3 | 100 | 230 | 3 | 5 | 15.2 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56GNS0 | 5 | 37
FRD0647 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 7.5 | 22
|  | STR |  | AE56GNS0 | 5 | 37
FRD0648 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 10 | 28 |  | (1) (5) (7c)
|  | STR |  | AE56GNS0 | 5 | 37
FRD0649 | D | ICB | Eaton | HMCP030*** | - | 30 | 480 | 3 | 100 | 460 | 3 | 15 | 21 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56GNS0 | 5 | 37
FRD0650 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 20 | 27
|  | STR |  | AE56GNS0 | 5 | 37
FRD0651 | D | ICB | Eaton | HMCP030*** | - | 30 | 600 | 3 | 50 | 575 | 3 | 20 | 22 | 0.69 | (1) (5) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56GNS0 | 5 | 37
FRD0652 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 25 | 27
|  | STR |  | AE56GNS0 | 5 | 37
FRD0653 | D | ICB | Eaton | HMCP030*** | - | 30 | 600 | 3 | 100 | 575 | 3 | 20 | 22 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3030R | - | 30
|  | STR |  | AE56GNS0 | 5 | 37
FRD0654 | D | ICB | Eaton | HMCP050*** | - | 50 | 600 | 3 | 100 | 575 | 3 | 25 | 27
|  | C. Limiter |  | ELC3050R | - | 50
|  | STR |  | AE56GNS0 | 5 | 37
FRD0655 | D | ICB | Eaton | HMCP050*** | - | 50 | 200 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56JNS0 | 5 | 60
FRD0656 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 10 | 32.2 |  | (1) (5) (7c)
|  | STR |  | AE56JNS0 | 5 | 60
FRD0657 |  | ICB |  | HMCP070*** | - | 70 | [5 empty] | 15 | 48.3 |  | (1) (5) (7e)
|  | STR |  | AE56JNS0 | 5 | 60
FRD0658 | D | ICB | Eaton | HMCP050*** | - | 50 | 208 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56JNS0 | 5 | 60
FRD0659 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 10 | 30.8 |  | (1) (5) (7c)
|  | STR |  | AE56JNS0 | 5 | 60
FRD0660 |  | ICB |  | HMCP070*** | - | 70 | [5 empty] | 15 | 46.2 |  | (1) (5) (7e)
|  | STR |  | AE56JNS0 | 5 | 60
FRD0661 | D | ICB | Eaton | HMCP050*** | - | 50 | 240 | 3 | 100 | 230 | 3 | 10 | 28 | 0.69 | (1) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56JNS0 | 5 | 60
FRD0662 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 15 | 42
|  | STR |  | AE56JNS0 | 5 | 60
FRD0663 |  | ICB |  | HMCP070*** | - | 70 | [5 empty] | 20 | 54 |  | (1) (5) (7e)
|  | STR |  | AE56JNS0 | 5 | 60
FRD0664 | D | ICB | Eaton | HMCP050*** | - | 50 | 480 | 3 | 100 | 460 | 3 | 25 | 34 | 0.69 | (1) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56JNS0 | 5 | 60
FRD0665 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 30 | 40
|  | STR |  | AE56JNS0 | 5 | 60
FRD0666 | D | ICB | Eaton | HMCP050*** | - | 50 | 600 | 3 | 50 | 575 | 3 | 25 | 27 | 0.69 | (1) (5) (6a) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56JNS0 | 5 | 60
FRD0667 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 30 | 32 |  | (1) (5) (6b) (7c)
|  | STR |  | AE56JNS0 | 5 | 60
FRD0668 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 40 | 41
|  | STR |  | AE56JNS0 | 5 | 60
FRD0669 | D | ICB | Eaton | HMCP050*** | - | 50 | 600 | 3 | 100 | 575 | 3 | 25 | 27 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3050R | - | 50
|  | STR |  | AE56JNS0 | 5 | 60
FRD0670 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 30 | 32 |  | (1) (5) (7c)
|  | C. Limiter |  | ELC3050R | - | 50
|  | STR |  | AE56JNS0 | 5 | 50
FRD0671 |  | ICB |  | HMCP050*** | - | 50 | [5 empty] | 40 | 41
|  | C. Limiter |  | ELC3050R | - | 50
|  | STR |  | AE56JNS0 | 5 | 60
FRD0672 | D | ICB | Eaton | HMCP050*** | - | 50 | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 0.69 | (1) (3) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56KNS0 | 5 | 73
FRD0673 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 15 | 48.3 |  | (1) (3) (5) (7e)
|  | STR |  | AE56KNS0 | 5 | 73
FRD0674 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 20 | 62.1
|  | STR |  | AE56KNS0 | 5 | 73
FRD0675 | D | ICB | Eaton | HMCP050*** | - | 50 | 208 | 3 | 100 | 208 | 3 | 10 | 30.8 | 0.69 | (1) (3) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56KNS0 | 5 | 73
FRD0676 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 15 | 46.2 |  | (1) (3) (5) (7e)
|  | STR |  | AE56KNS0 | 5 | 73
FRD0677 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 20 | 59.4
|  | STR |  | AE56KNS0 | 5 | 73
FRD0678 | D | ICB | Eaton | HMCP070*** | - | 70 | 240 | 3 | 100 | 230 | 3 | 15 | 42 | 0.69 | (1) (3) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56KNS0 | 5 | 73
FRD0679 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 20 | 54 |  | (1) (3) (5) (7e)
|  | STR |  | AE56KNS0 | 5 | 73
FRD0680 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 25 | 68
|  | STR |  | AE56KNS0 | 5 | 73
FRD0681 | D | ICB | Eaton | HMCP100*** | - | 100 | 480 | 3 | 100 | 460 | 3 | 30 | 40 | 0.69 | (1) (3) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56KNS0 | 5 | 73
FRD0682 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 40 | 52 |  | (1) (3) (5) (7e)
|  | STR |  | AE56KNS0 | 5 | 73
FRD0683 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 50 | 65
|  | STR |  | AE56KNS0 | 5 | 73
FRD0684 | D | ICB | Eaton | HMCP050*** | - | 50 | 600 | 3 | 50 | 575 | 3 | 30 | 32 | 0.69 | (1) (3) (5) (6b) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56KNS0 | 5 | 73
FRD0685 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 40 | 41
|  | STR |  | AE56KNS0 | 5 | 73
FRD0686 |  | ICB |  | HMCP100*** | - | 100 | [5 empty] | 50 | 52 |  | (1) (3) (5) (6b) (7e)
|  | STR |  | AE56KNS0 | 5 | 73
FRD0687 | D | ICB | Eaton | HMCP050*** | - | 50 | 600 | 3 | 100 | 575 | 3 | 30 | 32 | 0.69 | (1) (3) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3050R | - | 50
|  | STR |  | AE56KNS0 | 5 | 73
FRD0688 | D | ICB | Eaton | HMCP100*** | - | 100 | 600 | 3 | 100 | 575 | 3 | 40 | 41
|  | C. Limiter |  | ELC3100R | - | 100
|  | STR |  | AE56KNS0 | 5 | 73
FRD0689 | D | ICB | Eaton | HMCP100*** | - | 100 | 600 | 3 | 100 | 575 | 3 | 50 | 52 |  | (1) (3) (5) (7e)
|  | C. Limiter |  | ELC3100R | - | 100
|  | STR |  | AE56KNS0 | 5 | 73
FRD0690 | D | ICB | Eaton | HMCP150*** | - | 150 | 200 | 3 | 100 | 200 | 3 | 25 | 78.2 | 1.42 | (1) (3) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56NNS0 | 10 | 140
FRD0691 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 30 | 92 |  | (1) (3) (5) (7f)
|  | STR |  | AE56NNS0 | 10 | 140
FRD0692 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 40 | 128
|  | STR |  | AE56NNS0 | 10 | 140
FRD0693 | D | ICB | Eaton | HMCP150*** | - | 150 | 208 | 3 | 100 | 208 | 3 | 25 | 74.8 | 1.42 | (1) (3) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56NNS0 | 10 | 140
FRD0694 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 30 | 88
|  | STR |  | AE56NNS0 | 10 | 140
FRD0695 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 40 | 114 |  | (1) (3) (5) (7f)
|  | STR |  | AE56NNS0 | 10 | 140
FRD0696 | D | ICB | Eaton | HMCP150*** | - | 150 | 240 | 3 | 100 | 230 | 3 | 30 | 80 | 1.42 | (1) (3) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56NNS0 | 10 | 140
FRD0697 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 40 | 104 |  | (1) (3) (5) (7f)
|  | STR |  | AE56NNS0 | 10 | 140
FRD0698 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 50 | 130
|  | STR |  | AE56NNS0 | 10 | 140
FRD0699 | D | ICB | Eaton | HMCP150*** | - | 150 | 480 | 3 | 100 | 460 | 3 | 60 | 77 | 1.42 | (1) (3) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56NNS0 | 10 | 140
FRD0700 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 75 | 96 |  | (1) (3) (5) (7f)
|  | STR |  | AE56NNS0 | 10 | 140
FRD0701 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 100 | 124
|  | STR |  | AE56NNS0 | 10 | 140
FRD0702 | D | ICB | Eaton | HMCPS150*** | - | 150 | 600 | 3 | 50 | 575 | 3 | 75 | 77 | 1.42 | (1) (3) (5) (6b) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56NNS0 | 10 | 140
FRD0703 |  | ICB |  | HMCPS150*** | - | 150 | [5 empty] | 100 | 99 |  | (1) (3) (5) (6b) (7f)
|  | STR |  | AE56NNS0 | 10 | 140
FRD0704 |  | ICB |  | HMCPS150*** | - | 150 | [5 empty] | 125 | 125
|  | STR |  | AE56NNS0 | 10 | 140
FRD0705 | D | ICB | Eaton | HMCP150*** | - | 150 | 600 | 3 | 100 | 575 | 3 | 75 | 77 | 1.42 | (1) (3) (5) (7e) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | AE56NNS0 | 10 | 140
FRD0706 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 100 | 99 |  | (1) (3) (5) (7f)
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | AE56NNS0 | 10 | 140
FRD0707 |  | ICB |  | HMCP150*** | - | 150 | [5 empty] | 125 | 125
|  | C. Limiter |  | ELC3150R | - | 150
|  | STR |  | AE56NNS0 | 10 | 140
FRD0708 | D | ICB | Eaton | HMCPE015*** | - | 15 | 200 | 3 | 100 | 200 | 3 | 2 | 7.8 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56DNS0 | 5 | 18
FRD0709 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 3 | 11
|  | STR |  | AE56DNS0 | 5 | 18
FRD0710 | D | ICB | Eaton | HMCPE015*** | - | 15 | 208 | 3 | 100 | 208 | 3 | 2 | 7.5 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56DNS0 | 5 | 18
FRD0711 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 3 | 10.6
|  | STR |  | AE56DNS0 | 5 | 18
FRD0712 | D | ICB | Eaton | HMCPE015*** | - | 15 | 240 | 3 | 100 | 230 | 3 | 2 | 6.8 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56DNS0 | 5 | 18
FRD0713 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 3 | 9.6
|  | STR |  | AE56DNS0 | 5 | 18
FRD0714 | D | ICB | Eaton | HMCPE015*** | - | 15 | 480 | 3 | 100 | 460 | 3 | 5 | 7.6 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56DNS0 | 5 | 18
FRD0715 |  | ICB |  | HMCPE015*** | - | 15 | [5 empty] | 7.5 | 11
|  | STR |  | AE56DNS0 | 5 | 18
FRD0716 | D | ICB | Eaton | HMCPE030*** | - | 30 | 200 | 3 | 100 | 200 | 3 | 3 | 11 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56FNS0 | 5 | 32
FRD0717 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 5 | 17.5
|  | STR |  | AE56FNS0 | 5 | 32
FRD0718 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AE56FNS0 | 5 | 32
FRD0719 | D | ICB | Eaton | HMCPE030*** | - | 30 | 208 | 3 | 100 | 208 | 3 | 5 | 16.7 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56FNS0 | 5 | 32
FRD0720 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 7.5 | 24.2
|  | STR |  | AE56FNS0 | 5 | 32
FRD0721 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 10 | 30.8 |  | (1) (5) (7c)
|  | STR |  | AE56FNS0 | 5 | 32
FRD0722 | D | ICB | Eaton | HMCPE030*** | - | 30 | 240 | 3 | 100 | 230 | 3 | 5 | 15.2 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56FNS0 | 5 | 32
FRD0723 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 7.5 | 22
|  | STR |  | AE56FNS0 | 5 | 32
FRD0724 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 10 | 28 |  | (1) (5) (7c)
|  | STR |  | AE56FNS0 | 5 | 32
FRD0725 | D | ICB | Eaton | HMCPE030*** | - | 30 | 480 | 3 | 100 | 460 | 3 | 10 | 14 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56FNS0 | 5 | 32
FRD0726 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 15 | 21
|  | STR |  | AE56FNS0 | 5 | 32
FRD0727 | D | ICB | Eaton | HMCPE030*** | - | 30 | 200 | 3 | 100 | 200 | 3 | 3 | 11 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56GNS0 | 5 | 37
FRD0728 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 5 | 17.5
|  | STR |  | AE56GNS0 | 5 | 37
FRD0729 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AE56GNS0 | 5 | 37
FRD0730 | D | ICB | Eaton | HMCPE030*** | - | 30 | 208 | 3 | 100 | 208 | 3 | 5 | 16.7 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56GNS0 | 5 | 37
FRD0731 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 7.5 | 24.2
|  | STR |  | AE56GNS0 | 5 | 37
FRD0732 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 10 | 30.8 |  | (1) (5) (7c)
|  | STR |  | AE56GNS0 | 5 | 37
FRD0733 | D | ICB | Eaton | HMCPE030*** | - | 30 | 240 | 3 | 100 | 230 | 3 | 5 | 15.2 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56GNS0 | 5 | 37
FRD0734 |  | ICB |  | HMCPE030*** | - | 30 | [5 empty] | 7.5 | 22
|  | STR |  | AE56GNS0 | 5 | 37
FRD0735 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 10 | 28 |  | (1) (5) (7c)
|  | STR |  | AE56GNS0 | 5 | 37
FRD0736 | D | ICB | Eaton | HMCPE030*** | - | 30 | 480 | 3 | 100 | 460 | 3 | 15 | 21 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56GNS0 | 5 | 37
FRD0737 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 20 | 27
|  | STR |  | AE56GNS0 | 5 | 37
FRD0738 | D | ICB | Eaton | HMCPE050*** | - | 50 | 200 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56JNS0 | 5 | 60
FRD0739 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 10 | 32.2 |  | (1) (5) (7c)
|  | STR |  | AE56JNS0 | 5 | 60
FRD0740 |  | ICB |  | HMCPE070*** | - | 70 | [5 empty] | 15 | 48.3 |  | (1) (5) (7e)
|  | STR |  | AE56JNS0 | 5 | 60
FRD0741 | D | ICB | Eaton | HMCPE050*** |  | 50 | 208 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56JNS0 | 5 | 60
FRD0742 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 10 | 30.8 |  | (1) (5) (7c)
|  | STR |  | AE56JNS0 | 5 | 60
FRD0743 |  | ICB |  | HMCPE070*** | - | 70 | [5 empty] | 15 | 46.2 |  | (1) (5) (7e)
|  | STR |  | AE56JNS0 | 5 | 60
FRD0744 | D | ICB | Eaton | HMCPE050*** | - | 50 | 240 | 3 | 100 | 230 | 3 | 10 | 28 | 0.69 | (1) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56JNS0 | 5 | 60
FRD0745 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 15 | 42
|  | STR |  | AE56JNS0 | 5 | 60
FRD0746 |  | ICB |  | HMCPE070*** | - | 70 | [5 empty] | 20 | 54 |  | (1) (5) (7e)
|  | STR |  | AE56JNS0 | 5 | 60
FRD0747 | D | ICB | Eaton | HMCPE050*** | - | 50 | 480 | 3 | 100 | 460 | 3 | 25 | 34 | 0.69 | (1) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56JNS0 | 5 | 60
FRD0748 |  | ICB |  | HMCPE050*** | - | 50 | [5 empty] | 30 | 40
|  | STR |  | AE56JNS0 | 5 | 60
FRD0749 | D | ICB | Eaton | HMCPE100*** | - | 100 | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 0.69 | (1) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56KNS0 | 5 | 73
FRD0750 |  | ICB |  | HMCPE150*** | - | 150 | [5 empty] | 15 | 48.3 |  | (1) (5) (7e)
|  | STR |  | AE56KNS0 | 5 | 73
FRD0751 |  | ICB |  | HMCPE150*** | - | 150 | [5 empty] | 20 | 62.1
|  | STR |  | AE56KNS0 | 5 | 73
FRD0752 | D | ICB | Eaton | HMCPE050*** | - | 50 | 208 | 3 | 100 | 208 | 3 | 10 | 30.8 | 0.69 | (1) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56KNS0 | 5 | 73
FRD0753 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 15 | 46.2 |  | (1) (5) (7e)
|  | STR |  | AE56KNS0 | 5 | 73
FRD0754 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 20 | 59.4
|  | STR |  | AE56KNS0 | 5 | 73
FRD0755 | D | ICB | Eaton | HMCPE070*** | - | 70 | 240 | 3 | 100 | 230 | 3 | 15 | 42 | 0.69 | (1) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56KNS0 | 5 | 73
FRD0756 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 20 | 54 |  | (1) (5) (7e)
|  | STR |  | AE56KNS0 | 5 | 73
FRD0757 |  | ICB |  | HMCPE150*** | - | 150 | [5 empty] | 25 | 68
|  | STR |  | AE56KNS0 | 5 | 73
FRD0758 | D | ICB | Eaton | HMCPE100*** | - | 100 | 480 | 3 | 100 | 460 | 3 | 30 | 40 | 0.69 | (1) (5) (7c) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE56KNS0 | 5 | 73
FRD0759 |  | ICB |  | HMCPE100*** | - | 100 | [5 empty] | 40 | 52 |  | (1) (5) (7e)
|  | STR |  | AE56KNS0 | 5 | 73
FRD0760 |  | ICB |  | HMCPE150*** | - | 150 | [5 empty] | 50 | 65
|  | STR |  | AE56KNS0 | 5 | 73
FRD0761 | D | ICB | Eaton | GMCP003*** | - | 3 | 200 | 3 | 42 | 200 | 3 | 1/2 | 2.5 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE56ANS0 | 5 | 7
FRD0762 | D | ICB | Eaton | GMCP003*** | - | 3 | 208 | 3 | 42 | 208 | 3 | 1/2 | 2.5 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE56ANS0 | 5 | 7
FRD0763 | D | ICB | Eaton | GMCP003*** | - | 3 | 240 | 3 | 42 | 230 | 3 | 1/2 | 2.5 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE56ANS0 | 5 | 7
FRD0764 | D | ICB | Eaton | GMCP003*** | - | 3 | 480 | 3 | 42 | 460 | 3 | 1 | 2.1 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE56ANS0 | 5 | 7
FRD0765 |  | ICB |  | GMCP003*** | - | 3 | [5 empty] | 1.5 | 3
|  | STR |  | AE56ANS0 | 5 | 7
FRD0766 | D | ICB | Eaton | GMCP007*** | - | 7 | 200 | 3 | 42 | 200 | 3 | 3/4 | 3.7 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE56BNS0 | 5 | 10
FRD0767 |  | ICB |  | GMCP007*** | - | 7 | [5 empty] | 1 | 4.8
|  | STR |  | AE56BNS0 | 5 | 10
FRD0768 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 1.5 | 6.9
|  | STR |  | AE56BNS0 | 5 | 10
FRD0769 | D | ICB | Eaton | GMCP007*** | - | 7 | 208 | 3 | 42 | 208 | 3 | 3/4 | 3.5 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE56BNS0 | 5 | 10
FRD0770 |  | ICB |  | GMCP007*** | - | 7 | [5 empty] | 1 | 4.6
|  | STR |  | AE56BNS0 | 5 | 10
FRD0771 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 1.5 | 6.6
|  | STR |  | AE56BNS0 | 5 | 10
FRD0772 | D | ICB | Eaton | GMCP007*** | - | 7 | 240 | 3 | 42 | 230 | 3 | 3/4 | 3.2 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE56BNS0 | 5 | 10
FRD0773 |  | ICB |  | GMCP007*** | - | 7 | [5 empty] | 1 | 4.2
|  | STR |  | AE56BNS0 | 5 | 10
FRD0774 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 1.5 | 6
|  | STR |  | AE56BNS0 | 5 | 10
FRD0775 | D | ICB | Eaton | GMCP007*** | - | 7 | 480 | 3 | 42 | 460 | 3 | 1.5 | 3 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE56BNS0 | 5 | 10
FRD0776 |  | ICB |  | GMCP007*** | - | 7 | [5 empty] | 2 | 3.4
|  | STR |  | AE56BNS0 | 5 | 10
FRD0777 |  | ICB |  | GMCP007*** | - | 7 | [5 empty] | 3 | 4.8
|  | STR |  | AE56BNS0 | 5 | 10
FRD0778 | D | ICB | Eaton | GMCP007*** | - | 7 | 200 | 3 | 42 | 200 | 3 | 1 | 3.7 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE56CNS0 | 5 | 12
FRD0779 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 1.5 | 6.9
|  | STR |  | AE56CNS0 | 5 | 12
FRD0780 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 2 | 7.8
|  | STR |  | AE56CNS0 | 5 | 12
FRD0781 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 3 | 11
|  | STR |  | AE56CNS0 | 5 | 12
FRD0782 | D | ICB | Eaton | GMCP007*** | - | 7 | 208 | 3 | 42 | 208 | 3 | 1 | 4.6 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE56CNS0 | 5 | 12
FRD0783 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 1.5 | 6.6
|  | STR |  | AE56CNS0 | 5 | 12
FRD0784 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 2 | 7.5
|  | STR |  | AE56CNS0 | 5 | 12
FRD0785 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 3 | 9.6
|  | STR |  | AE56CNS0 | 5 | 12
FRD0786 | D | ICB | Eaton | GMCP007*** | - | 7 | 240 | 3 | 42 | 230 | 3 | 1 | 4.2 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE56CNS0 | 5 | 12
FRD0787 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 1.5 | 6
|  | STR |  | AE56CNS0 | 5 | 12
FRD0788 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 2 | 6.8
|  | STR |  | AE56CNS0 | 5 | 12
FRD0789 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 3 | 6.1
|  | STR |  | AE56CNS0 | 5 | 12
FRD0790 | D | ICB | Eaton | GMCP007*** | - | 7 | 480 | 3 | 42 | 460 | 3 | 3 | 4.8 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE56CNS0 | 5 | 12
FRD0791 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 5 | 7.6
|  | STR |  | AE56CNS0 | 5 | 12
FRD0792 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 7.5 | 11
|  | STR |  | AE56CNS0 | 5 | 12
FRD0793 | D | ICB | Eaton | GMCP015*** | - | 15 | 200 | 3 | 42 | 200 | 3 | 2 | 7.8 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE56DNS0 | 5 | 18
FRD0794 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 3 | 11
|  | STR |  | AE56DNS0 | 5 | 18
FRD0795 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 17.5
|  | STR |  | AE56DNS0 | 5 | 18
FRD0796 | D | ICB | Eaton | GMCP015*** | - | 15 | 208 | 3 | 42 | 208 | 3 | 2 | 7.5 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE56DNS0 | 5 | 18
FRD0797 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 3 | 10.6
|  | STR |  | AE56DNS0 | 5 | 18
FRD0798 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 16.7
|  | STR |  | AE56DNS0 | 5 | 18
FRD0799 | D | ICB | Eaton | GMCP015*** | - | 15 | 240 | 3 | 42 | 230 | 3 | 2 | 6.6 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE56DNS0 | 5 | 18
FRD0800 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 3 | 9.6
|  | STR |  | AE56DNS0 | 5 | 18
FRD0801 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 15.2
|  | STR |  | AE56DNS0 | 5 | 18
FRD0802 | D | ICB | Eaton | GMCP015*** | - | 15 | 480 | 3 | 42 | 460 | 3 | 5 | 7.6 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE56DNS0 | 5 | 18
FRD0803 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 7.5 | 11
|  | STR |  | AE56DNS0 | 5 | 18
FRD0804 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 10 | 14
|  | STR |  | AE56DNS0 | 5 | 18
FRD0805 | D | ICB | Eaton | GMCP015*** | - | 15 | 200 | 3 | 42 | 200 | 3 | 2 | 7.8 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE56ENS0 | 5 | 25
FRD0806 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 3 | 11
|  | STR |  | AE56ENS0 | 5 | 25
FRD0807 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 17
|  | STR |  | AE56ENS0 | 5 | 25
FRD0808 | D | ICB | Eaton | GMCP015*** | - | 15 | 208 | 3 | 42 | 208 | 3 | 2 | 7.5 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE56ENS0 | 5 | 25
FRD0809 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 3 | 10.6
|  | STR |  | AE56ENS0 | 5 | 25
FRD0810 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 16.7
|  | STR |  | AE56ENS0 | 5 | 25
FRD0811 | D | ICB | Eaton | GMCP015*** | - | 15 | 240 | 3 | 42 | 230 | 3 | 3 | 9.6 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE56ENS0 | 5 | 25
FRD0812 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 15.2
|  | STR |  | AE56ENS0 | 5 | 25
FRD0813 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 7.5 | 22
|  | STR |  | AE56ENS0 | 5 | 25
FRD0814 | D | ICB | Eaton | GMCP015*** | - | 15 | 480 | 3 | 42 | 460 | 3 | 7.5 | 11 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE56ENS0 | 5 | 25
FRD0815 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 10 | 14
|  | STR |  | AE56ENS0 | 5 | 25
FRD0816 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 15 | 21
|  | STR |  | AE56ENS0 | 5 | 25
FRD0817 | D | ICB | Eaton | GMCP030*** | - | 30 | 200 | 3 | 42 | 200 | 3 | 3 | 11 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE56FNS0 | 5 | 32
FRD0818 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 17.5
|  | STR |  | AE56FNS0 | 5 | 32
FRD0819 |  | ICB |  | GMCP050*** | - | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AE56FNS0 | 5 | 32
FRD0820 | D | ICB | Eaton | GMCP030*** | - | 30 | 208 | 3 | 42 | 208 | 3 | 3 | 10.6 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE56FNS0 | 5 | 32
FRD0821 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 16.7
|  | STR |  | AE56FNS0 | 5 | 32
FRD0822 |  | ICB |  | GMCP050*** | - | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | AE56FNS0 | 5 | 32
FRD0823 | D | ICB | Eaton | GMCP030*** | - | 30 | 240 | 3 | 42 | 230 | 3 | 5 | 15.2 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE56FNS0 | 5 | 32
FRD0824 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 7.5 | 22
|  | STR |  | AE56FNS0 | 5 | 32
FRD0825 |  | ICB |  | GMCP050*** | - | 50 | [5 empty] | 10 | 28
|  | STR |  | AE56FNS0 | 5 | 32
FRD0826 | D | ICB | Eaton | GMCP030*** | - | 30 | 480 | 3 | 42 | 460 | 3 | 10 | 14 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE56FNS0 | 5 | 32
FRD0827 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 15 | 21
|  | STR |  | AE56FNS0 | 5 | 32
FRD0828 |  | ICB |  | GMCP050*** | - | 50 | [5 empty] | 20 | 27
|  | STR |  | AE56FNS0 | 5 | 32
FRD0829 | D | ICB | Eaton | GMCP003*** | - | 3 | 200 | 3 | 42 | 200 | 3 | 1/2 | 2.5 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE57ANS0 | 5 | 7
FRD0830 | D | ICB | Eaton | GMCP003*** | - | 3 | 208 | 3 | 42 | 208 | 3 | 1/2 | 2.5 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE57ANS0 | 5 | 7
FRD0831 | D | ICB | Eaton | GMCP003*** | - | 3 | 240 | 3 | 42 | 230 | 3 | 1/2 | 2.5 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE57ANS0 | 5 | 7
FRD0832 | D | ICB | Eaton | GMCP003*** | - | 3 | 480 | 3 | 42 | 460 | 3 | 1 | 2.1 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE57ANS0 | 5 | 7
FRD0833 |  | ICB |  | GMCP007*** | - | 7 | [5 empty] | 1.5 | 3
|  | STR |  | AE57ANS0 | 5 | 7
FRD0834 | D | ICB | Eaton | GMCP007*** |  | 7 | 200 | 3 | 42 | 200 | 3 | 3/4 | 3.7 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE57BNS0 | 5 | 12
FRD0835 |  | ICB |  | GMCP007*** | - | 7 | [5 empty] | 1 | 4.8
|  | STR |  | AE57BNS0 | 5 | 12
FRD0836 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 1.5 | 6.9
|  | STR |  | AE57BNS0 | 5 | 12
FRD0837 | D | ICB | Eaton | GMCP007*** | - | 7 | 208 | 3 | 42 | 208 | 3 | 3/4 | 3.5 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE57BNS0 | 5 | 12
FRD0838 |  | ICB |  | GMCP007*** | - | 7 | [5 empty] | 1 | 4.6
|  | STR |  | AE57BNS0 | 5 | 12
FRD0839 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 1.5 | 6.6
|  | STR |  | AE57BNS0 | 5 | 12
FRD0840 | D | ICB | Eaton | GMCP007*** | - | 7 | 240 | 3 | 42 | 230 | 3 | 3/4 | 3.2 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE57BNS0 | 5 | 12
FRD0841 |  | ICB |  | GMCP007*** | - | 7 | [5 empty] | 1 | 4.2
|  | STR |  | AE57BNS0 | 5 | 12
FRD0842 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 1.5 | 6
|  | STR |  | AE57BNS0 | 5 | 12
FRD0843 | D | ICB | Eaton | GMCP007*** | - | 7 | 480 | 3 | 42 | 460 | 3 | 1.5 | 3 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE57BNS0 | 5 | 12
FRD0844 |  | ICB |  | GMCP007*** | - | 7 | [5 empty] | 2 | 3.4
|  | STR |  | AE57BNS0 | 5 | 12
FRD0845 |  | ICB |  | GMCP007*** | - | 7 | [5 empty] | 3 | 4.8
|  | STR |  | AE57BNS0 | 5 | 12
FRD0846 | D | ICB | Eaton | GMCP007*** | - | 7 | 200 | 3 | 42 | 200 | 3 | 1 | 4.8 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE57CNS0 | 5 | 12
FRD0847 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 1.5 | 6.9
|  | STR |  | AE57CNS0 | 5 | 12
FRD0848 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 2 | 7.8
|  | STR |  | AE57CNS0 | 5 | 12
FRD0849 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 3 | 11
|  | STR |  | AE57CNS0 | 5 | 12
FRD0850 | D | ICB | Eaton | GMCP007*** | - | 7 | 208 | 3 | 42 | 208 | 3 | 1 | 4.6 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE57CNS0 | 5 | 12
FRD0851 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 1.5 | 6.6
|  | STR |  | AE57CNS0 | 5 | 12
FRD0852 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 2 | 7.5
|  | STR |  | AE57CNS0 | 5 | 12
FRD0853 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 3 | 10.6
|  | STR |  | AE57CNS0 | 5 | 12
FRD0854 | D | ICB | Eaton | GMCP007*** | - | 7 | 240 | 3 | 42 | 230 | 3 | 1 | 4.2 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE57CNS0 | 5 | 12
FRD0855 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 1.5 | 6
|  | STR |  | AE57CNS0 | 5 | 12
FRD0856 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 2 | 6.8
|  | STR |  | AE57CNS0 | 5 | 12
FRD0857 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 3 | 9.6
|  | STR |  | AE57CNS0 | 5 | 12
FRD0858 | D | ICB | Eaton | GMCP007*** | - | 7 | 480 | 3 | 42 | 460 | 3 | 3 | 4.8 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE57CNS0 | 5 | 12
FRD0859 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 5 | 7.6
|  | STR |  | AE57CNS0 | 5 | 12
FRD0860 |  | ICB |  | GMCP015*** | - | 15 | [5 empty] | 7.5 | 11
|  | STR |  | AE57CNS0 | 5 | 12
FRD0861 | D | ICB | Eaton | GMCP015*** | - | 15 | 200 | 3 | 42 | 200 | 3 | 2 | 7.8 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE57DNS0 | 5 | 18
FRD0862 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 3 | 11
|  | STR |  | AE57DNS0 | 5 | 18
FRD0863 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 17.5
|  | STR |  | AE57DNS0 | 5 | 18
FRD0864 | D | ICB | Eaton | GMCP015*** | - | 15 | 208 | 3 | 42 | 208 | 3 | 2 | 7.5 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE57DNS0 | 5 | 18
FRD0865 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 3 | 10.6
|  | STR |  | AE57DNS0 | 5 | 18
FRD0866 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 16.7
|  | STR |  | AE57DNS0 | 5 | 18
FRD0867 | D | ICB | Eaton | GMCP015*** | - | 15 | 240 | 3 | 42 | 230 | 3 | 2 | 6.8 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE57DNS0 | 5 | 18
FRD0868 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 3 | 9.6
|  | STR |  | AE57DNS0 | 5 | 18
FRD0869 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 15.2
|  | STR |  | AE57DNS0 | 5 | 18
FRD0870 | D | ICB | Eaton | GMCP015*** | - | 15 | 480 | 3 | 42 | 460 | 3 | 5 | 7.6 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE57DNS0 | 5 | 18
FRD0871 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 7.5 | 11
|  | STR |  | AE57DNS0 | 5 | 18
FRD0872 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 10 | 14
|  | STR |  | AE57DNS0 | 5 | 18
FRD0873 | D | ICB | Eaton | GMCP015*** | - | 15 | 200 | 3 | 42 | 200 | 3 | 2 | 7.8 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE57ENS0 | 5 | 25
FRD0874 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 3 | 11
|  | STR |  | AE57ENS0 | 5 | 25
FRD0875 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 17.5
|  | STR |  | AE57ENS0 | 5 | 25
FRD0876 | D | ICB | Eaton | GMCP015*** | - | 15 | 208 | 3 | 42 | 208 | 3 | 2 | 7.5 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE57ENS0 | 5 | 25
FRD0877 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 3 | 10.6
|  | STR |  | AE57ENS0 | 5 | 25
FRD0878 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 16.7
|  | STR |  | AE57ENS0 | 5 | 25
FRD0879 | D | ICB | Eaton | GMCP015*** | - | 15 | 240 | 3 | 42 | 230 | 3 | 3 | 9.6 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE57ENS0 | 5 | 25
FRD0880 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 15.2
|  | STR |  | AE57ENS0 | 5 | 25
FRD0881 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 7.5 | 22
|  | STR |  | AE57ENS0 | 5 | 25
FRD0882 | D | ICB | Eaton | GMCP015*** | - | 15 | 480 | 3 | 42 | 460 | 3 | 7.5 | 11 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE57ENS0 | 5 | 25
FRD0883 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 10 | 14
|  | STR |  | AE57ENS0 | 5 | 25
FRD0884 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 15 | 21
|  | STR |  | AE57ENS0 | 5 | 25
FRD0885 | D | ICB | Eaton | GMCP030*** | - | 30 | 200 | 3 | 42 | 200 | 3 | 3 | 11 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE57FNS0 | 5 | 32
FRD0886 |  | ICB |  | GMCP030*** | - | 30 | [5 empty] | 5 | 17.5
|  | STR |  | AE57FNS0 | 5 | 32
FRD0887 |  | ICB |  | GMCP050*** | - | 50 | [5 empty] | 7.5 | 25.3
|  | STR |  | AE57FNS0 | 5 | 32
FRD0888 | D | ICB | Eaton | GMCP030*** | - | 30 | 208 | 3 | 42 | 208 | 3 | 5 | 16.7 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE57FNS0 | 5 | 32
FRD0889 |  | ICB |  | GMCP050*** | - | 50 | [5 empty] | 7.5 | 24.2
|  | STR |  | AE57FNS0 | 5 | 32
FRD0890 |  | ICB |  | GMCP050*** | - | 50 | [5 empty] | 10 | 30.8 |  | (1) (5) (7c)
|  | STR |  | AE57FNS0 | 5 | 32
FRD0891 | D | ICB | Eaton | GMCP030*** | - | 30 | 240 | 3 | 42 | 230 | 3 | 5 | 15.2 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE57FNS0 | 5 | 32
FRD0892 |  | ICB |  | GMCP050*** | - | 50 | [5 empty] | 7.5 | 22
|  | STR |  | AE57FNS0 | 5 | 32
FRD0893 |  | ICB |  | GMCP050*** | - | 50 | [5 empty] | 10 | 28 |  | (1) (5) (7c)
|  | STR |  | AE57FNS0 | 5 | 32
FRD0894 | D | ICB | Eaton | GMCP030*** | - | 30 | 480 | 3 | 42 | 460 | 3 | 10 | 14 | 0.69 | (1) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | -
|  | STR |  | AE57FNS0 | 5 | 32
FRD0895 |  | ICB |  | GMCP050*** | - | 50 | [5 empty] | 15 | 21
|  | STR |  | AE57FNS0 | 5 | 32
FRD0896 |  | ICB |  | GMCP050*** | - | 50 | [5 empty] | 20 | 27
|  | STR |  | AE57FNS0 | 5 | 32
FRD0897 | D | ICB | Eaton | HMCP030*** | - | 30 | 208 | 3 | 100 | 208 | 3 | 3 | 10.6 | 0.69 | (1) (3) (5) (7a) | E176513 Vol. 1 Sec. General & E176513 Vol. 1 Sec. 1 | E47048 Vol. 2 Sec. 2
|  | STR |  | AE16FNS0 | 5 | 32
FRD0898 |  | ICB |  | HMCPE030*** | - | 30 | 200 | 3 | 100 | 200 | 3 | 5 | 17.5 | 0.69 | (1) (3) (5) (7a)
|  | STR |  | AE56DNS0 | 5 | 18
FRD0899 |  | ICB |  | HMCPE030*** | - | 30 | 208 | 3 | 100 | 208 | 3 | 5 | 16.7 | 0.69 | (1) (3) (5) (7a)
|  | STR |  | AE56DNS0 | 5 | 18
FRD0900 |  | ICB |  | HMCPE030*** | - | 30 | 240 | 3 | 100 | 240 | 3 | 5 | 15.2 | 0.69 | (1) (3) (5) (7a)
|  | STR |  | AE56DNS0 | 5 | 18
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment. See Table 3
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6a) = Install Terminal End Cover TEC1 (6085C42H01) to line side of circuit breaker.
(6b) = Install Terminal end Cover TEC2 (6085C42H02) to line side of circuit breaker.
(7) See table (7) for internal wiring between load side of short circuit protective device & line side of starter.
Table 7 - Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
| Wire Code | Wire Size | Wire Code | Wire Size
| 7a | 12 awg. | 7j | 4/0 awg.
| 7b | 10 awg. | 7k | 250kcml
| 7c | 8 awg. | 7l | 350kcml
| 7d | 6 awg. | 7m | 4/0 awg. (3)
| 7e | 4 awg. | 7n | 4/0 awg. (4)
| 7f | 2 awg. | 7p | 250kcml (2)
| 7g | 1/0 awg. | 7r | 350kcml (3)
| 7h | 2/0 awg. | 7s | 4/0 awg. (2)
Table 3 - Overload Relay Heater Pack Selection
- Supply Proper Eaton Publication with Panel -
| Publication No. | AN16/AN56 STR. | AE16/AE56 STR. | AE17/AE57 STR.
| 22179 | 00, 0 | A through F | Does not Apply
| 22180 | 1, 2 | G through K
| 20104 | 3, 4 | L through N
| 22416 | 5 | -
| 22590 | 6 | -
| 22591 | 7 | -
| 22592 | 8

## FdmC440 Sz 00 Type D MCOLR
Eaton "Type D" Combination Motor Controllers | [18 empty] | Issue Date: 2014-01-21
Freedom style contactors with C440 Solid State Overload Relays
Database Identification Number | Listed Combination Motor Controller Information |  | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings
| UL File Number | Volume / Section (Vol#).(Sec#) |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating | Enclosure Volume, cubic inches | Conditions of Use | Other References
FdmC440-NEMA00-D-1.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-1.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-1.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-1.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-2.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-2.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-2.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-2.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-3.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-3.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-3.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-3.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-4.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-4.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-4.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-4.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-5.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-5.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-5.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-5.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-6.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-6.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-6.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-6.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-7.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-7.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-7.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-7.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-8.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-8.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-8.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-8.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-9.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-9.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-9.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-9.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-10.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-10.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-10.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-10.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-11.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-11.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-11.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-11.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-12.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-12.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-12.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-12.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-13.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-13.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-13.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-13.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-14.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-14.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-14.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-14.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-15.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-15.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-15.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-15.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-16.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-16.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-16.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-16.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-17.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-17.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-17.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-17.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-18.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-18.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-18.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-18.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-19.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-19.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-19.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-19.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-20.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-20.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-20.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-20.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-21.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-21.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-21.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-21.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-22.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-22.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-22.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-22.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-23.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-23.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-23.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-23.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-24.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-24.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-24.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-24.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-25.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-25.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-25.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-25.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-26.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-26.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-26.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-26.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-27.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-27.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-27.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-27.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-28.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-28.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-28.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-28.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-29.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-29.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-29.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-29.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-30.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-30.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-30.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-30.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-31.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-31.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-31.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-31.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-32.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-32.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-32.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-32.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-33-01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-33.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-33.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-33.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-34.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-34.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-34.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-34.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-35.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-35.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-35.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-35.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-36.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-36.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-36.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-36.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-38.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-38.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-38.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-38.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-39.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-39.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-39.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-39.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-40.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-40.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-40.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-40.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-41.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-41.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-41.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-41.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-42.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-42.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-42.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-42.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-43.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-43.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-43.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-43.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-44.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-44.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-44.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-44.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-45.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-45.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-45.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-45.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-46.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-46.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-46.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-46.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-47.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-47.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-47.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-47.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-48.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-48.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-48.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-48.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-49.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-49.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-49.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-49.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-51.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-51.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-51.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-51.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-52.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-52.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-52.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-52.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-53.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-53.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-53.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-53.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-54.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-54.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-54.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-54.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-55.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-55.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-55.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-55.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-56.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-56.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-56.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-56.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-57.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-57.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-57.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-57.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-58.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-58.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-58.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-58.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-59.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-59.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-59.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-59.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-60.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-60.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-60.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-60.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-61.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-61.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-61.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-61.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-62.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-62.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-62.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-62.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-64.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-64.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-64.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-64.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-65.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-65.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-65.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-65.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-66.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-66.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-66.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-66.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-67.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-67.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-67.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-67.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-68.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-68.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-68.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-68.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-69.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-69.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-69.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-69.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-70.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-70.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-70.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-70.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-71.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-71.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-71.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-71.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-72.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-72.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-72.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-72.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-73.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-73.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-73.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-73.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-74.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-74.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-74.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-74.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-75.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-75.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-75.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-75.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-77.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-77.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-77.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-77.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-78.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-78.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-78.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-78.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-79.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-79.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-79.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-79.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-80.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-80.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-80.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-80.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-81.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-81.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-81.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-81.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-82.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-82.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-82.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-82.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-83.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-83.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-83.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-83.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-84.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-84.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-84.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-84.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-85.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-85.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-85.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-85.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-86.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-86.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-86.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-86.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-87.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-87.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-87.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-87.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 208 | 3 | 5 | 6.6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-88.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-88.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF00 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-88.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-88.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA00-D-89.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF00 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-89.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF00 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-89.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-89.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-90.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF00 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-90.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF00 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-90.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-90.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-91.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF00 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-91.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF00 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-91.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-91.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-92.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF00 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-92.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF00 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-92.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-92.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-93.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF00 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-93.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF00 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-93.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-93.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-94.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF00 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-94.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF00 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-94.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-94.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-95.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF00 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-95.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF00 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-95.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-95.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-96.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF00 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-96.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF00 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-96.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA00-D-96.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55AN3*B | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
Conditions of Use:
1. All of the specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches. Additional testing is not required when installed in an enclosure having the same or larger volume.
5. The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor controllers shall be considered in the end - product application
6. Connections between components are made with insulated wire that is sized per the table below:
| Freedom Contactor Size | Minimum Wire Size from Breaker to Contactor (AWG) |  | Minimum Length (inches)
| OO (A Frame) | 14 |  | 15
| Note 1: | * notes the one or two digit code for the selection of the magnet coil voltage of the motor controller.

## FdmC440 Sz 0 Type D MCOLR
Eaton "Type D" Combination Motor Controllers | [18 empty] | Issue Date: 2014-01-21
Freedom style contactors with C440 Solid State Overload Relays
Database Identification Number | Listed Combination Motor Controller Information |  | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings
| UL File Number | Volume / Section (Vol#).(Sec#) |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating | Enclosure Volume, cubic inches | Conditions of Use | Other References
FdmC440-NEMA0-D-1.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-1.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-1.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-1.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-2.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-2.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-2.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-2.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-3.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-3.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-3.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-3.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-4.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-4.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-4.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-4.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-5.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-5.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-5.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-5.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-6.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-6.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-6.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-6.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-7.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-7.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-7.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-7.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-8.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-8.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-8.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-8.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-9.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-9.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-9.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-9.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-10.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-10.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-10.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-10.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-11.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-11.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-11.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-11.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-12.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-12.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-12.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-12.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-13.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-13.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-13.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-13.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-14.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-14.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-14.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-14.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-15.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-15.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-15.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-15.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-16.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-16.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-16.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-16.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-17.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-17.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-17.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-17.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-18.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-18.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-18.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-18.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-19.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-19.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-19.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-19.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-20.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-20.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-20.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-20.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-21.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-21.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-21.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-21.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-22.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-22.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-22.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-22.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-23.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-23.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-23.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-23.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-24.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-24.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-24.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-24.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-25.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-25.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-25.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-25.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-26.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-26.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-26.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-26.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-27.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-27.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-27.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-27.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-28.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-28.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-28.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-28.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-29.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-29.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-29.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-29.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-30.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-30.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-30.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-30.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-31.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-31.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-31.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-31.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-32.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-32.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-32.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-32.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-33.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-33.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-33.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-33.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-34.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-34.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-34.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-34.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-35.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-35.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-35.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-35.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-36.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-36.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-36.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-36.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-37.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-37.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-37.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-37.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-38.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-38.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-38.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-38.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-39.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-39.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-39.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-39.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-40.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-40.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-40.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-40.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-41.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-41.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-41.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-41.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-42.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-42.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-42.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-42.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-43.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-43.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-43.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-43.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-44.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-44.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-44.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-44.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-45.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-45.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-45.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-45.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-46.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-46.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-46.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-46.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-47.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-47.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-47.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-47.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-48.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-48.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-48.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-48.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-49.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-49.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-49.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-49.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-50.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-50.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-50.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-50.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-51.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-51.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-51.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-51.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-52.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-52.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-52.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-52.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-53.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-53.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-53.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-53.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-54.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-54.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-54.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-54.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-55.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-55.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-55.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-55.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-56.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-56.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-56.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-56.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-57.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-57.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-57.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-57.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-58.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-58.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-58.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-58.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-59.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-59.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-59.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-59.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-60.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-60.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-60.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-60.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-61.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-61.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-61.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-61.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-62.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-62.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-62.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-62.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-63.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-63.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-63.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-63.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-64.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-64.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-64.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-64.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-65.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-65.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-65.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-65.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-66.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-66.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-66.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-66.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-67.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-67.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-67.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-67.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-68.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-68.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-68.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-68.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-69.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-69.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-69.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-69.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-70.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-70.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-70.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-70.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-71.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-71.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-71.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-71.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-72.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-72.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-72.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-72.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-73.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-73.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-73.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-73.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-74.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-74.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-74.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-74.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-75.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-75.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-75.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-75.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-76.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-76.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-76.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-76.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-77.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-77.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-77.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-77.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-78.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-78.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-78.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-78.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-79.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-79.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-79.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-79.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-80.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-80.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-80.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-80.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-81.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-81.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-81.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-81.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-82.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-82.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-82.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-82.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-83.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-83.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-83.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-83.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-84.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-84.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-84.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-84.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-85.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-85.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-85.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-85.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-86.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-86.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-86.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-86.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-87.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-87.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-87.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-87.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-88.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-88.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-88.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-88.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-89.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-89.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-89.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-89.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-90.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-90.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-90.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-90.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-91.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-91.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-91.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-91.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-92.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-92.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF0 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-92.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-92.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA0-D-93.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-93.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-93.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-93.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-94.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-94.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-94.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-94.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-95.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-95.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-95.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-95.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-96.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-96.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-96.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-96.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-97.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-97.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-97.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-97.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-98.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-98.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-98.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-98.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-99.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-99.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-99.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-99.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-100.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-100.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-100.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-100.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-101.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-101.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-101.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-101.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-102.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-102.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-102.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-102.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-103.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-103.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-103.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-103.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-104.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-104.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-104.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-104.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-105.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-105.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-105.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-105.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-106.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-106.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-106.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-106.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-107.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-107.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-107.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-107.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-108.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-108.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-108.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-108.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-109.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-109.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-109.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-109.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-110.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-110.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-110.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-110.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-111.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-111.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-111.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-111.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-112.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-112.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-112.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-112.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-113.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-113.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-113.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-113.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-114.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-114.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-114.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-114.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-115.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-115.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-115.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-115.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-116.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-116.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-116.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-116.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-117.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-117.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-117.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-117.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-118.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-118.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-118.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-118.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-119.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-119.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-119.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-119.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-120.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-120.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-120.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-120.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-121.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-121.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-121.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-121.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-122.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-122.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-122.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-122.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-123.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-123.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-123.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-123.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-124.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-124.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-124.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-124.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-125.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-125.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-125.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-125.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-126.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-126.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-126.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-126.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-127.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-127.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-127.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-127.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-128.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-128.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-128.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-128.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-129.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-129.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-129.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-129.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-130.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-130.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-130.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-130.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-131.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-131.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-131.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-131.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-132.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-132.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-132.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-132.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-133.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-133.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-133.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-133.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-134.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-134.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-134.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-134.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-135.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-135.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-135.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-135.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-136.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-136.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-136.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-136.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-137.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-137.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-137.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-137.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-138.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-138.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-138.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-138.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-139.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-139.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-139.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-139.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-140.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-140.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-140.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-140.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-141.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-141.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-141.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-141.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-142.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-142.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-142.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-142.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-143.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-143.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-143.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-143.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-144.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-144.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-144.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-144.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-145.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-145.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-145.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-145.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-146.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-146.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-146.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-146.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-147.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-147.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-147.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-147.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-148.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-148.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-148.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-148.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-149.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-149.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-149.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-149.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-150.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-150.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-150.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-150.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-151.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-151.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-151.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-151.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-152.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-152.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-152.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-152.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-153.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-153.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-153.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-153.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-154.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-154.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-154.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-154.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-155.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-155.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-155.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-155.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-156.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-156.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-156.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-156.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-157.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-157.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-157.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-157.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-158.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-158.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-158.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-158.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-159.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-159.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-159.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-159.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-160.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-160.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-160.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-160.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-161.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-161.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-161.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-161.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-162.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-162.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-162.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-162.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-163.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-163.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-163.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-163.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-164.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-164.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-164.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-164.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-165.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-165.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-165.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-165.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-166.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-166.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-166.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-166.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-167.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-167.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-167.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-167.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-168.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-168.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-168.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-168.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-169.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-169.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-169.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-169.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-170.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-170.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-170.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-170.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-171.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-171.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-171.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-171.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-172.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-172.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-172.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-172.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-173.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-173.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-173.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-173.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-174.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-174.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-174.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-174.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-175.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-175.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-175.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-175.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-176.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-176.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-176.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-176.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-177.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-177.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-177.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-177.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-178.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-178.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-178.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-178.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-179.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-179.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-179.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-179.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-180.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-180.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-180.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-180.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-181.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-181.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-181.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-181.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-182.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-182.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-182.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-182.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-183.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-183.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-183.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-183.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-184.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-184.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-184.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-184.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-185.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-185.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-185.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-185.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-186.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-186.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-186.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-186.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-187.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-187.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-187.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-187.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-188.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-188.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-188.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-188.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-189.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-189.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-189.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-189.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-190.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-190.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-190.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-190.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-191.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-191.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-191.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-191.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-192.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-192.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-192.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-192.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-193.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-193.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-193.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-193.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-194.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-194.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-194.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-194.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-195.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-195.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-195.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-195.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-196.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-196.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-196.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-196.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-197.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-197.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-197.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-197.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-198.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-198.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-198.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-198.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-199.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-199.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-199.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-199.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-200.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-200.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-200.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-200.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-201.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-201.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-201.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-201.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-202.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-202.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-202.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-202.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-203.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-203.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-203.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-203.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-204.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-204.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-204.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-204.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-205.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-205.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-205.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-205.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-206.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-206.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-206.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-206.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-207.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-207.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-207.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-207.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-208.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-208.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-208.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-208.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-209.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-209.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-209.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-209.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-210.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-210.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF0 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-210.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-210.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA0-D-211.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF0 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA0-D-211.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF0 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA0-D-211.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA0-D-211.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA0-D-212.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF0 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA0-D-212.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF0 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA0-D-212.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA0-D-212.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA0-D-213.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF0 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA0-D-213.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF0 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA0-D-213.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA0-D-213.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA0-D-214.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF0 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA0-D-214.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF0 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA0-D-214.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA0-D-214.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55BN3*B | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
Conditions of Use:
1. All of the specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches. Additional testing is not required when installed in an enclosure having the same or larger volume.
5. The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor controllers shall be considered in the end - product application
6. Connections between components are made with insulated wire that is sized per the table below:
| Freedom Contactor Size | Minimum Wire Size from Breaker to Contactor (AWG) |  | Minimum Length (inches)
| 0 (B Frame) | 10 |  | 14
| Note 1: | * notes the one or two digit code for the selection of the magnet coil voltage of the motor controller.

## FdmC440 Sz 1 Type D MCOLR
Eaton "Type D" Combination Motor Controllers | [18 empty] | Issue Date: 2014-01-21
Freedom style contactors with C440 Solid State Overload Relays
Database Identification Number | Listed Combination Motor Controller Information |  | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings
| UL File Number | Volume / Section (Vol#).(Sec#) |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating | Enclosure Volume, cubic inches | Conditions of Use | Other References
FdmC440-NEMA1-D-1.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-1.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-1.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-1.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-2.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-2.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-2.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-2.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-3.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-3.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-3.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-3.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-4.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-4.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-4.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-4.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-5.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-5.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-5.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-5.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-6.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-6.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-6.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-6.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-7.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-7.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-7.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-7.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-8.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-8.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-8.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-8.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-9.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-9.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-9.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-9.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-10.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-10.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-10.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-10.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-11.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-11.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-11.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-11.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-12.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-12.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-12.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-12.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-13.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-13.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-13.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-13.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-14.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-14.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-14.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-14.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-15.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-15.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-15.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-15.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-16.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-16.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-16.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-16.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-17.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-17.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-17.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-17.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-18.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-18.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-18.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-18.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-19.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-19.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-19.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-19.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-20.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-20.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-20.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-20.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-21.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-21.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-21.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-21.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-22.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-22.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-22.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-22.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-23.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-23.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-23.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-23.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-24.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-24.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-24.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-24.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-25.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-25.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-25.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-25.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-26.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-26.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-26.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-26.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-27.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-27.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-27.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-27.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-28.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-28.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-28.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-28.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-29.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-29.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-29.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-29.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-30.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-30.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-30.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-30.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-31.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-31.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-31.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-31.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-32.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-32.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-32.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-32.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-33.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-33.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-33.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-33.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-34.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-34.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-34.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-34.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-35.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-35.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-35.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-35.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-36.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-36.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-36.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-36.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-37.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-37.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-37.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-37.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-38.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-38.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-38.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-38.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-39.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-39.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-39.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-39.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-40.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-40.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-40.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-40.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-41.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-41.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-41.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-41.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-42.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-42.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-42.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-42.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-43.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-43.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-43.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-43.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-44.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-44.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-44.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-44.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-45.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-45.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-45.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-45.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-46.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-46.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-46.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-46.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-47.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-47.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-47.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-47.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-48.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-48.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-48.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-48.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-49.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-49.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-49.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-49.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-50.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-50.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-50.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-50.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-51.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-51.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-51.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-51.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-52.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-52.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-52.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-52.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-53.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-53.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-53.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-53.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-54.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-54.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-54.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-54.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-55.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-55.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-55.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-55.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-56.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-56.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-56.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-56.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-57.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-57.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-57.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-57.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-58.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-58.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-58.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-58.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-59.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-59.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-59.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-59.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-60.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-60.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-60.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-60.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-61.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-61.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-61.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-61.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-62.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-62.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-62.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-62.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-63.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-63.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-63.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-63.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-64.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-64.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-64.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-64.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-65.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-65.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-65.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-65.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-66.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-66.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-66.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-66.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-67.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-67.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-67.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-67.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-68.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-68.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-68.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-68.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-69.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-69.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-69.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-69.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-70.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-70.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-70.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-70.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-71.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-71.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-71.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-71.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-72.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-72.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-72.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-72.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-73.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-73.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-73.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-73.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-74.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-74.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-74.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-74.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-75.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-75.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-75.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-75.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-76.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-76.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-76.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-76.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-77.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-77.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-77.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-77.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-78.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-78.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-78.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-78.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-79.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-79.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-79.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-79.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-80.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-80.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-80.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-80.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-81.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-81.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-81.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-81.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-82.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-82.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-82.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-82.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-83.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-83.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-83.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-83.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-84.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-84.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-84.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-84.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-85.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-85.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-85.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-85.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-86.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-86.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-86.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-86.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-87.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-87.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-87.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-87.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-88.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-88.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-88.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-88.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-89.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-89.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-89.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-89.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-90.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-90.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-90.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-90.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-91.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-91.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-91.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-91.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-92.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-92.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF1 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-92.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-92.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA1-D-93.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-93.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-93.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-93.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-94.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-94.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-94.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-94.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-95.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-95.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-95.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-95.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-96.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-96.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-96.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-96.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-97.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-97.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-97.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-97.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-98.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-98.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-98.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-98.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-99.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-99.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-99.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-99.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-100.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-100.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-100.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-100.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-101.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-101.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-101.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-101.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-102.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-102.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-102.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-102.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-103.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-103.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-103.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-103.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-104.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-104.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-104.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-104.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-105.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-105.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-105.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-105.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-106.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-106.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-106.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-106.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-107.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-107.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-107.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-107.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-108.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-108.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-108.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-108.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-109.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-109.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-109.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-109.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-110.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-110.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-110.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-110.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-111.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-111.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-111.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-111.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-112.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-112.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-112.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-112.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-113.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-113.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-113.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-113.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-114.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-114.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-114.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-114.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-115.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-115.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-115.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-115.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-116.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-116.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-116.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-116.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-117.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-117.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-117.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-117.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-118.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-118.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-118.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-118.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-119.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-119.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-119.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-119.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-120.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-120.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-120.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-120.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-121.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-121.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-121.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-121.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-122.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-122.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-122.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-122.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-123.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-123.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-123.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-123.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-124.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-124.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-124.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-124.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-125.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-125.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-125.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-125.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-126.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-126.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-126.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-126.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-127.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-127.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-127.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-127.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-128.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-128.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-128.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-128.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-129.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-129.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-129.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-129.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-130.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-130.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-130.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-130.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-131.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-131.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-131.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-131.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-132.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-132.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-132.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-132.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-133.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-133.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-133.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-133.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-134.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-134.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-134.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-134.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-135.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-135.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-135.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-135.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-136.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-136.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-136.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-136.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-137.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-137.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-137.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-137.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-138.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-138.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-138.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-138.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-139.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-139.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-139.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-139.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-140.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-140.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-140.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-140.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-141.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-141.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-141.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-141.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-142.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-142.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-142.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-142.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-143.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-143.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-143.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-143.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-144.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-144.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-144.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-144.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-145.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-145.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-145.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-145.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-146.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-146.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-146.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-146.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-147.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-147.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-147.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-147.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-148.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-148.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-148.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-148.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-149.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-149.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-149.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-149.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-150.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-150.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-150.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-150.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-151.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-151.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-151.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-151.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-152.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-152.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-152.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-152.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-153.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-153.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-153.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-153.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-154.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-154.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-154.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-154.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-155.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-155.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-155.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-155.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-156.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-156.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-156.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-156.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-157.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-157.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-157.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-157.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-158.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-158.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-158.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-158.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-159.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-159.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-159.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-159.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-160.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-160.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-160.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-160.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-161.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-161.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-161.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-161.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-162.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-162.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-162.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-162.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-163.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-163.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-163.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-163.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-164.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-164.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-164.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-164.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-165.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-165.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-165.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-165.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-166.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-166.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-166.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-166.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-167.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-167.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-167.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-167.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-168.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-168.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-168.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-168.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-169.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-169.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-169.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-169.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-170.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-170.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-170.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-170.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-171.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-171.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-171.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-171.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-172.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-172.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-172.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-172.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-173.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-173.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-173.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-173.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-174.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-174.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-174.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-174.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-175.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-175.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-175.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-175.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-176.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-176.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-176.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-176.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-177.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-177.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-177.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-177.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-178.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-178.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-178.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-178.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-179.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-179.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-179.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-179.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-180.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-180.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-180.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-180.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-181.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-181.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-181.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-181.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-182.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-182.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-182.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-182.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-183.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-183.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-183.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-183.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-184.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-184.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-184.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-184.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-185.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-185.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-185.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-185.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-186.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-186.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-186.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-186.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-187.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-187.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-187.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-187.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-188.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-188.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-188.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-188.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-189.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-189.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-189.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-189.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-190.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-190.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-190.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-190.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-191.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-191.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-191.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-191.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-192.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-192.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-192.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-192.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-193.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-193.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-193.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-193.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-194.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-194.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-194.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-194.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-195.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-195.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-195.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-195.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-196.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-196.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-196.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-196.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-197.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-197.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-197.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-197.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-198.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-198.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-198.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-198.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-199.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-199.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-199.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-199.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-200.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-200.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-200.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-200.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-201.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-201.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-201.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-201.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-202.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-202.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-202.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-202.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-203.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-203.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-203.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-203.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-204.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-204.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-204.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-204.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-205.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-205.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-205.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-205.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-206.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-206.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-206.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-206.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-207.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-207.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-207.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-207.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-208.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-208.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-208.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-208.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-209.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-209.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-209.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-209.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-210.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-210.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-210.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-210.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-211.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-211.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-211.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-211.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-212.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-212.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-212.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-212.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-213.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-213.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-213.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-213.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-214.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-214.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-214.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-214.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-215.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-215.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-215.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-215.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-216.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-216.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-216.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-216.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-217.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-217.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-217.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-217.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-218.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-218.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-218.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-218.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-219.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-219.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-219.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-219.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-220.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-220.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-220.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-220.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-221.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-221.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-221.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-221.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-222.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-222.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-222.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-222.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-223.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-223.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-223.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-223.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-224.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-224.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-224.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-224.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-225.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-225.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-225.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-225.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-226.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-226.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-226.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-226.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-227.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-227.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-227.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-227.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-228.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-228.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-228.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-228.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-229.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-229.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-229.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-229.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-230.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-230.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-230.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-230.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-231.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-231.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-231.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-231.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-232.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-232.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-232.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-232.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-233.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-233.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-233.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-233.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-234.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-234.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-234.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-234.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-235.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-235.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-235.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-235.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-236.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-236.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-236.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-236.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-237.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-237.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-237.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-237.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-238.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-238.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-238.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-238.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-239.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-239.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-239.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-239.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-240.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-240.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-240.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-240.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-241.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-241.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-241.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-241.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-242.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-242.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-242.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-242.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-243.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-243.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-243.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-243.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-244.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-244.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF1 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-244.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-244.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA1-D-245.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-245.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-245.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-245.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-246.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-246.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-246.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-246.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-247.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-247.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-247.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-247.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-248.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-248.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-248.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-248.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-249.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-249.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-249.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-249.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-250.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-250.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-250.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-250.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-251.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-251.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-251.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-251.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-252.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-252.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-252.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-252.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-253.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-253.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-253.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-253.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-254.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-254.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-254.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-254.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-255.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-255.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-255.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-255.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-256.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-256.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-256.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-256.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-257.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-257.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-257.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-257.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-258.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-258.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-258.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-258.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-259.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-259.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-259.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-259.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-260.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-260.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-260.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-260.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-261.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-261.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-261.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-261.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-262.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-262.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-262.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-262.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-263.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-263.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-263.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-263.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-264.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-264.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-264.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-264.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-265.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-265.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-265.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-265.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-266.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-266.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-266.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-266.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-267.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-267.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-267.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-267.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-268.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-268.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-268.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-268.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-269.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-269.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-269.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-269.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-270.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-270.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-270.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-270.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-271.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-271.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-271.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-271.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-272.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-272.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-272.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-272.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-273.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-273.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-273.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-273.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-274.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-274.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-274.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-274.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-275.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-275.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-275.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-275.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-276.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-276.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-276.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-276.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-277.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-277.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-277.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-277.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-278.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-278.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-278.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-278.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-279.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-279.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-279.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-279.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-280.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-280.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-280.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-280.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-281.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-281.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-281.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-281.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-282.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-282.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-282.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-282.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-283.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-283.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-283.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-283.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-284.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-284.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-284.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-284.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-285.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-285.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-285.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-285.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-286.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-286.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-286.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-286.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-287.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-287.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-287.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-287.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-288.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-288.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-288.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-288.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-289.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-289.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-289.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-289.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-290.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-290.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-290.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-290.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-291.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-291.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-291.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-291.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-292.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-292.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-292.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-292.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-293.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-293.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-293.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-293.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-294.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-294.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-294.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-294.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-295.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-295.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-295.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-295.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-296.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-296.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-296.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-296.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-297.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-297.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-297.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-297.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-298.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-298.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-298.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-298.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-299.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-299.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-299.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-299.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-300.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-300.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-300.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-300.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-301.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-301.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-301.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-301.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-302.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-302.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-302.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-302.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-303.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-303.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-303.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-303.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-304.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-304.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-304.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-304.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-305.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-305.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-305.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-305.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-306.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-306.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-306.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-306.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-307.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-307.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-307.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-307.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-308.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-308.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-308.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-308.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-309.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-309.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-309.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-309.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-310.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-310.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-310.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-310.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-311.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-311.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-311.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-311.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-312.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-312.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-312.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-312.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-313.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-313.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-313.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-313.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-314.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-314.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-314.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-314.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-315.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-315.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-315.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-315.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-316.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-316.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-316.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-316.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-317.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-317.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-317.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-317.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-318.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-318.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-318.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-318.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-319.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-319.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-319.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-319.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-320.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-320.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-320.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-320.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-321.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-321.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-321.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-321.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-322.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-322.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-322.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-322.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-323.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-323.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-323.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-323.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-324.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-324.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-324.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-324.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-325.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-325.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-325.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-325.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-326.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-326.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-326.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-326.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-327.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-327.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-327.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-327.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-328.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-328.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-328.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-328.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-329.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-329.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-329.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-329.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-330.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-330.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-330.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-330.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-331.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-331.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-331.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-331.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-332.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-332.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-332.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-332.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-333.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-333.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-333.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-333.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-334.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-334.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-334.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-334.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-335.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-335.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-335.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-335.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-336.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-336.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-336.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-336.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-337.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-337.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-337.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-337.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-338.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-338.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-338.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-338.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-339.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-339.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-339.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-339.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-340.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-340.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-340.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-340.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-341.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-341.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-341.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-341.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-342.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-342.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-342.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-342.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-343.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-343.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-343.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-343.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-344.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-344.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-344.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-344.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-345.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-345.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-345.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-345.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-346.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-346.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-346.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-346.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-347.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-347.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-347.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-347.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-348.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-348.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF1 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-348.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA1-D-348.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55DN3*B | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
Conditions of Use:
1. All of the specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches. Additional testing is not required when installed in an enclosure having the same or larger volume.
5. The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor controllers shall be considered in the end - product application
6. Connections between components are made with insulated wire that is sized per the table below:
| Freedom Contactor Size | Minimum Wire Size from Breaker to Contactor (AWG) |  | Minimum Length (inches)
| 1 (D Frame) | 10 |  | 15
| Note 1: | * notes the one or two digit code for the selection of the magnet coil voltage of the motor controller.

## FdmC440 Sz 2 Type D MCOLR
Eaton "Type D" Combination Motor Controllers | [18 empty] | Issue Date: 2014-01-21
Freedom style contactors with C440 Solid State Overload Relays
Database Identification Number | Listed Combination Motor Controller Information |  | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings
| UL File Number | Volume / Section (Vol#).(Sec#) |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating | Enclosure Volume, cubic inches | Conditions of Use | Other References
FdmC440-NEMA2-D-1.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-1.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-1.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-1.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-2.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-2.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-2.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-2.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-3.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-3.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-3.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-3.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-4.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-4.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-4.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-4.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-5.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-5.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-5.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-5.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-6.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-6.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-6.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-6.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-7.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-7.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-7.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-7.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-8.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-8.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-8.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-8.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-9.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-9.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-9.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-9.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-10.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-10.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-10.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-10.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-11.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-11.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-11.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-11.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-12.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-12.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-12.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-12.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-13.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-13.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-13.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-13.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-14.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-14.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-14.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-14.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-15.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-15.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-15.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-15.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-16.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-16.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-16.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-16.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-17.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-17.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-17.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-17.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-18.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-18.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-18.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-18.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-19.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-19.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-19.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-19.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-20.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-20.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-20.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-20.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-21.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-21.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-21.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-21.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-22.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-22.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-22.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-22.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-23.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-23.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-23.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-23.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-24.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-24.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-24.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-24.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-25.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-25.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-25.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-25.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-26.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-26.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-26.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-26.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-27.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-27.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-27.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-27.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-28.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-28.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-28.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-28.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-29.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-29.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-29.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-29.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-30.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-30.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-30.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-30.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-31.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-31.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-31.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-31.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-32.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-32.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-32.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-32.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-33.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-33.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-33.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-33.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-34.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-34.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-34.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-34.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-35.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-35.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-35.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-35.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-36.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-36.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-36.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-36.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-37.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-37.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-37.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-37.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-38.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-38.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-38.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-38.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-39.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-39.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-39.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-39.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-40.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-40.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-40.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-40.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-41.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-41.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-41.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-41.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-42.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-42.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-42.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-42.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-43.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-43.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-43.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-43.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-44.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-44.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-44.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-44.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-45.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-45.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-45.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-45.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-46.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-46.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-46.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-46.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-47.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-47.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-47.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-47.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-48.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-48.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-48.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-48.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-49.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-49.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-49.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-49.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-50.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-50.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-50.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-50.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-51.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-51.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-51.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-51.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-52.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-52.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-52.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-52.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-53.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-53.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-53.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-53.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-54.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-54.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-54.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-54.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-55.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-55.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-55.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-55.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-56.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-56.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-56.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-56.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-57.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-57.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-57.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-57.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-58.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-58.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-58.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-58.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-59.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-59.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-59.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-59.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-60.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-60.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-60.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-60.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-61.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-61.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-61.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-61.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-62.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-62.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-62.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-62.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-63.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-63.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-63.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-63.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-64.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-64.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-64.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-64.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-65.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-65.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-65.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-65.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-66.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-66.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-66.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-66.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-67.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-67.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-67.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-67.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-68.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-68.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-68.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-68.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-69.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-69.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-69.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-69.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-70.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-70.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-70.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-70.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-71.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-71.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-71.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-71.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-72.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-72.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-72.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-72.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-73.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-73.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-73.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-73.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-74.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-74.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-74.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-74.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-75.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-75.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-75.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-75.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-76.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-76.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-76.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-76.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-77.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-77.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-77.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-77.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-78.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-78.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-78.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-78.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-79.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-79.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-79.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-79.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-80.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-80.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-80.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-80.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-81.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-81.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-81.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-81.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-82.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-82.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-82.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-82.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-83.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-83.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-83.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-83.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-84.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-84.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-84.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-84.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-85.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-85.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-85.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-85.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-86.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-86.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-86.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-86.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-87.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-87.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-87.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-87.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-88.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-88.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-88.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-88.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-89.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-89.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-89.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-89.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-90.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-90.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-90.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-90.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-91.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-91.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-91.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-91.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-92.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-92.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SF2 | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-92.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-92.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
FdmC440-NEMA2-D-93.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-93.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-93.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-93.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-94.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-94.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-94.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-94.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-95.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-95.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-95.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-95.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-96.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-96.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-96.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-96.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-97.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-97.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-97.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-97.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-98.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-98.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-98.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-98.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-99.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-99.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-99.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-99.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-100.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-100.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-100.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-100.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-101.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-101.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-101.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-101.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-102.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-102.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-102.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-102.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-103.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-103.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-103.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-103.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-104.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-104.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-104.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-104.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-105.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-105.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-105.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-105.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-106.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-106.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-106.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-106.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-107.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-107.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-107.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-107.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-108.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-108.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-108.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-108.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-109.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-109.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-109.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-109.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-110.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-110.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-110.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-110.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-111.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-111.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-111.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-111.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-112.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-112.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-112.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-112.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-113.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-113.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-113.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-113.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-114.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-114.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-114.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-114.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-115.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-115.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-115.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-115.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-116.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-116.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-116.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-116.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-117.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-117.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-117.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-117.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-118.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-118.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-118.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-118.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-119.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-119.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-119.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-119.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-120.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-120.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-120.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-120.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-121.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-121.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-121.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-121.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-122.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-122.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-122.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-122.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-123.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-123.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-123.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-123.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-124.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-124.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-124.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-124.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-125.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-125.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-125.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-125.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-126.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-126.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-126.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-126.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-127.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-127.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-127.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-127.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-128.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-128.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-128.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-128.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-129.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-129.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-129.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-129.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-130.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-130.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-130.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-130.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-131.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-131.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-131.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-131.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-132.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-132.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-132.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-132.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-133.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-133.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-133.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-133.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-134.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-134.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-134.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-134.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-135.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-135.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-135.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-135.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-136.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-136.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-136.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-136.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-137.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-137.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-137.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-137.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-138.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-138.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-138.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-138.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-139.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-139.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-139.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-139.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-140.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-140.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-140.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-140.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-141.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-141.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-141.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-141.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-142.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-142.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-142.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-142.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-143.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-143.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-143.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-143.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-144.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-144.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-144.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-144.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-145.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-145.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-145.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-145.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-146.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-146.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-146.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-146.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-147.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-147.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-147.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-147.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-148.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-148.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-148.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-148.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-149.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-149.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-149.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-149.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-150.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-150.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-150.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-150.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-151.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-151.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-151.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-151.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-152.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-152.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-152.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-152.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-153.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-153.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-153.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-153.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-154.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-154.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-154.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-154.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-155.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-155.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-155.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-155.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-156.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-156.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-156.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-156.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-157.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-157.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-157.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-157.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-158.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-158.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-158.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-158.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-159.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-159.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-159.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-159.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-160.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-160.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-160.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-160.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-161.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-161.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-161.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-161.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-162.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-162.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-162.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-162.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-163.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-163.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-163.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-163.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-164.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-164.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-164.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-164.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-165.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-165.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-165.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-165.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-166.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-166.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-166.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-166.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-167.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-167.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-167.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-167.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-168.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-168.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-168.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-168.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-169.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-169.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-169.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-169.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-170.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-170.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-170.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-170.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-171.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-171.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-171.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-171.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-172.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-172.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-172.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-172.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-173.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-173.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-173.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-173.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-174.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-174.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-174.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-174.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-175.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-175.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-175.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-175.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-176.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-176.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-176.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-176.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-177.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-177.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-177.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-177.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-178.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-178.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-178.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-178.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-179.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-179.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-179.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-179.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-180.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-180.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-180.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-180.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-181.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-181.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-181.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-181.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-182.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-182.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-182.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-182.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-183.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-183.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-183.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-183.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-184.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-184.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-184.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-184.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-185.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-185.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-185.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-185.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-186.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-186.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-186.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-186.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-187.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-187.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-187.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-187.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-188.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-188.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-188.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-188.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-189.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-189.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-189.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-189.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-190.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-190.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-190.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-190.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-191.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-191.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-191.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-191.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-192.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-192.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-192.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-192.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-193.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-193.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-193.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-193.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-194.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-194.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-194.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-194.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-195.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-195.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-195.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-195.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-196.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-196.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-196.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-196.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-197.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-197.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-197.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-197.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-198.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-198.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-198.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-198.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-199.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-199.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-199.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-199.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-200.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-200.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-200.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-200.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-201.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-201.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-201.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-201.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-202.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-202.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-202.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-202.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-203.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-203.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-203.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-203.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-204.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-204.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-204.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-204.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-205.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-205.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-205.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-205.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-206.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-206.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-206.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-206.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-207.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-207.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-207.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-207.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-208.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-208.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-208.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-208.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-209.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-209.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-209.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-209.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-210.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-210.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-210.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-210.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-211.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-211.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-211.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-211.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-212.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-212.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-212.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-212.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-213.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-213.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-213.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-213.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-214.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-214.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-214.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-214.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-215.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-215.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-215.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-215.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-216.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-216.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-216.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-216.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-217.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-217.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-217.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-217.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-218.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-218.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-218.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-218.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-219.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-219.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-219.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-219.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-220.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-220.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-220.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-220.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-221.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-221.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-221.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-221.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-222.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-222.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-222.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-222.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-223.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-223.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-223.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-223.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-224.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-224.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-224.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-224.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-225.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-225.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-225.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-225.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-226.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-226.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-226.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-226.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-227.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-227.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-227.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-227.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-228.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-228.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-228.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-228.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-229.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-229.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-229.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-229.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-230.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-230.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-230.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-230.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-231.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-231.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-231.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-231.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-232.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-232.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-232.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-232.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-233.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-233.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-233.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-233.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-234.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-234.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-234.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-234.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-235.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-235.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-235.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-235.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-236.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-236.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-236.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-236.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 200 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-237.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-237.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-237.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-237.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-238.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-238.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-238.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-238.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-239.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-239.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-239.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-239.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 208 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-240.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-240.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-240.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-240.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-241.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-241.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-241.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-241.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 220-240 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-242.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-242.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-242.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-242.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-243.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-243.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-243.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-243.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-244.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-244.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SF2 | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-244.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-244.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A020SAX | 440-480 | 3 | 5 | 20 | -
FdmC440-NEMA2-D-245.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-245.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-245.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-245.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-246.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-246.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-246.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-246.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-247.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-247.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-247.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-247.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-248.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-248.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-248.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-248.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-249.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-249.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-249.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-249.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-250.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-250.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-250.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-250.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-251.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-251.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-251.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-251.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-252.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-252.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-252.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-252.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-253.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-253.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-253.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-253.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-254.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-254.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-254.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-254.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-255.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-255.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-255.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-255.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-256.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-256.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-256.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-256.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-257.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-257.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-257.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-257.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-258.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-258.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-258.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-258.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-259.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-259.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-259.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-259.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-260.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-260.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-260.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-260.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-261.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-261.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-261.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-261.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-262.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-262.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-262.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-262.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-263.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-263.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-263.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-263.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-264.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-264.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-264.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-264.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-265.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-265.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-265.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-265.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-266.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-266.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-266.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-266.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-267.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-267.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-267.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-267.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-268.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-268.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-268.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-268.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-269.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-269.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-269.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-269.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-270.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-270.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-270.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-270.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-271.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-271.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-271.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-271.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-272.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-272.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-272.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-272.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-273.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-273.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-273.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-273.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-274.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-274.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-274.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-274.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-275.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-275.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-275.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-275.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-276.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-276.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-276.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-276.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-277.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-277.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-277.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-277.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-278.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-278.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-278.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-278.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-279.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-279.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-279.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-279.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-280.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-280.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-280.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-280.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-281.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-281.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-281.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-281.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-282.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-282.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-282.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-282.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-283.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-283.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-283.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-283.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-284.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-284.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-284.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-284.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-285.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-285.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-285.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-285.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-286.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-286.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-286.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-286.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-287.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-287.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-287.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-287.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-288.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-288.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-288.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-288.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-289.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-289.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-289.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-289.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-290.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-290.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-290.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-290.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-291.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-291.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-291.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-291.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-292.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-292.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-292.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-292.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-293.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-293.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-293.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-293.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-294.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-294.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-294.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-294.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-295.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-295.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-295.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-295.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-296.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-296.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-296.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-296.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-297.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-297.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-297.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-297.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-298.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-298.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-298.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-298.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-299.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-299.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-299.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-299.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-300.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-300.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-300.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-300.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-301.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-301.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-301.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-301.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-302.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-302.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-302.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-302.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-303.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-303.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-303.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-303.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-304.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-304.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-304.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-304.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-305.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-305.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-305.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-305.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-306.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-306.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-306.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-306.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-307.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-307.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-307.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-307.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-308.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-308.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-308.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-308.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-309.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-309.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-309.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-309.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-310.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-310.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-310.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-310.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-311.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-311.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-311.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-311.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-312.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-312.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-312.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-312.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-313.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-313.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-313.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-313.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-314.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-314.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-314.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-314.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-315.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-315.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-315.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-315.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-316.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-316.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-316.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-316.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-317.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-317.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-317.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-317.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-318.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-318.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-318.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-318.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-319.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-319.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-319.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-319.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-320.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-320.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-320.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-320.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-321.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-321.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-321.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-321.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-322.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-322.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-322.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-322.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-323.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-323.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-323.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-323.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-324.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-324.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-324.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-324.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-325.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-325.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-325.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-325.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-326.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-326.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-326.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-326.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-327.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-327.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-327.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-327.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-328.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-328.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-328.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-328.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-329.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-329.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-329.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-329.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-330.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-330.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-330.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-330.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-331.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-331.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-331.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-331.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-332.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-332.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-332.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-332.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-333.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-333.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-333.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-333.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-334.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-334.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-334.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-334.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-335.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-335.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-335.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-335.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-336.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-336.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-336.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-336.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-337.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-337.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-337.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-337.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-338.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-338.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-338.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-338.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-339.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-339.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-339.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-339.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-340.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-340.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-340.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-340.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-341.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-341.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-341.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-341.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-342.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-342.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-342.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-342.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-343.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-343.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-343.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-343.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-344.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-344.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-344.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-344.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-345.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-345.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-345.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-345.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-346.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-346.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-346.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-346.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-347.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-347.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-347.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-347.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-348.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-348.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-348.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-348.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-349.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-349.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-349.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-349.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-350.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-350.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-350.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-350.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-351.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-351.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-351.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-351.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-352.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-352.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-352.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-352.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-353.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-353.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-353.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-353.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-354.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-354.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-354.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-354.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-355.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-355.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-355.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-355.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-356.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-356.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-356.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-356.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-357.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-357.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-357.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-357.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-358.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-358.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-358.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-358.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-359.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-359.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-359.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-359.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-360.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-360.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-360.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-360.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-361.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-361.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-361.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-361.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-362.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-362.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-362.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-362.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-363.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-363.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-363.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-363.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-364.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-364.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-364.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-364.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-365.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-365.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-365.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-365.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-366.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-366.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-366.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-366.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-367.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-367.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-367.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-367.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-368.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-368.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-368.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-368.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-369.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-369.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-369.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-369.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-370.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-370.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-370.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-370.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-371.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-371.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-371.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-371.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-372.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-372.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-372.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-372.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-373.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-373.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-373.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-373.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-374.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-374.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-374.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-374.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-375.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-375.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-375.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-375.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-376.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-376.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-376.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-376.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-377.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-377.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-377.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-377.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-378.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-378.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-378.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-378.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-379.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-379.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-379.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-379.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-380.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-380.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-380.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-380.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-381.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-381.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-381.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-381.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-382.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-382.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-382.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-382.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-383.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-383.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-383.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-383.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-384.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-384.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-384.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-384.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-385.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-385.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-385.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-385.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-386.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 208 | 3 | - | 70 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-386.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 208 | 3 | - | 70 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-386.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 208 | 3 | - | 70 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-386.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 208 | 3 | - | 70 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-387.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 208 | 3 | - | 70 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-387.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 208 | 3 | - | 70 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-387.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 208 | 3 | - | 70 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-387.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 208 | 3 | - | 70 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-388.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-388.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-388.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-388.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-389.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-389.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-389.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-389.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-390.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-390.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-390.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-390.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-391.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-391.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-391.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-391.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-392.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-392.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-392.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-392.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-393.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-393.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-393.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-393.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-394.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-394.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-394.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-394.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-395.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-395.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-395.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-395.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-396.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-396.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-396.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-396.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 200 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-397.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 208 | 3 | - | 70 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-397.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 208 | 3 | - | 70 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-397.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 208 | 3 | - | 70 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-397.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 208 | 3 | - | 70 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-398.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 208 | 3 | - | 70 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-398.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 208 | 3 | - | 70 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-398.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 208 | 3 | - | 70 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-398.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 208 | 3 | - | 70 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 208 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-399.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-399.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-399.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-399.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-400.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-400.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-400.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-400.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-401.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-401.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-401.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-401.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 220-240 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-402.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-402.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-402.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-402.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-403.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-403.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-403.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-403.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-404.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-404.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SF2 | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-404.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A045SAX | 440-480 | 3 | 5 | 45 | -
FdmC440-NEMA2-D-404.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55GN3*B | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A045SAX | 440-480 | 3 | 5 | 45 | -
Conditions of Use:
1. All of the specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches. Additional testing is not required when installed in an enclosure having the same or larger volume.
5. The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor controllers shall be considered in the end - product application
6. Connections between components are made with insulated wire that is sized per the table below:
| Freedom Contactor Size | Minimum Wire Size from Breaker to Contactor (AWG) |  | Minimum Length (inches)
| 2 (G Frame) | 8 |  | 15
| Note 1: | * notes the one or two digit code for the selection of the magnet coil voltage of the motor controller.

## FdmC440 Sz 3 Type D MCOLR
Eaton "Type D" Combination Motor Controllers | [18 empty] | Issue Date: 2014-01-21
Freedom style contactors with C440 Solid State Overload Relays
Database Identification Number | Listed Combination Motor Controller Information |  | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings
| UL File Number | Volume / Section (Vol#).(Sec#) |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating | Enclosure Volume, cubic inches | Conditions of Use | Other References
FdmC440-NEMA3-D-1.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 25.3 | 7.5 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-1.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 25.3 | 7.5 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-1.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 25.3 | 7.5 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-1.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 25.3 | 7.5 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-2.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 32.2 | 10 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-2.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 32.2 | 10 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-2.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 32.2 | 10 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-2.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 32.2 | 10 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-3.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-3.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-3.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-3.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-4.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-4.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-4.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-4.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-5.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-5.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-5.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-5.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-6.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 30.8 | 10 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-6.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 30.8 | 10 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-6.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 30.8 | 10 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-6.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 30.8 | 10 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-7.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-7.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-7.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-7.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-8.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-8.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-8.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-8.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-9.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-9.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-9.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-9.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-10.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 28 | 10 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-10.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 28 | 10 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-10.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 28 | 10 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-10.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 28 | 10 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-11.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-11.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-11.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-11.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-12.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-12.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-12.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-12.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-13.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-13.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-13.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-13.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-14.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-14.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-14.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-14.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-15.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 27 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-15.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 27 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-15.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 27 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-15.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 27 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-16.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 34 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-16.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 34 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-16.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 34 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-16.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 34 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-17.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-17.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-17.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-17.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-18.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-18.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-18.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-18.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-19.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-19.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-19.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-19.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-20.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 25.3 | 7.5 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-20.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 25.3 | 7.5 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-20.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 25.3 | 7.5 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-20.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 25.3 | 7.5 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-21.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 32.2 | 10 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-21.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 32.2 | 10 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-21.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 32.2 | 10 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-21.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 32.2 | 10 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-22.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-22.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-22.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-22.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-23.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-23.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-23.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-23.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-24.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-24.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-24.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-24.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-25.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 30.8 | 10 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-25.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 30.8 | 10 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-25.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 30.8 | 10 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-25.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 30.8 | 10 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-26.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-26.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-26.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-26.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-27.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-27.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-27.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-27.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-28.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-28.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-28.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-28.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-29.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 28 | 10 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-29.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 28 | 10 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-29.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 28 | 10 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-29.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 28 | 10 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-30.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-30.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-30.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-30.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-31.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-31.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-31.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-31.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-32.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-32.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-32.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-32.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-33.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-33.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-33.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-33.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-34.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 27 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-34.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 27 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-34.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 27 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-34.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 27 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-35.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 34 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-35.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 34 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-35.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 34 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-35.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 34 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-36.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-36.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-36.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-36.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-37.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-37.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-37.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-37.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-38.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-38.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-38.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-38.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-39.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 25.3 | 7.5 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-39.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 25.3 | 7.5 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-39.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 25.3 | 7.5 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-39.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 25.3 | 7.5 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-40.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 32.2 | 10 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-40.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 32.2 | 10 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-40.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 32.2 | 10 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-40.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 32.2 | 10 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-41.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-41.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-41.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-41.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-42.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-42.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-42.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-42.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-43.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-43.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-43.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-43.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-44.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 30.8 | 10 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-44.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 30.8 | 10 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-44.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 30.8 | 10 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-44.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 30.8 | 10 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-45.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-45.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-45.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-45.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-46.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-46.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-46.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-46.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-47.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-47.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-47.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-47.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-48.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 28 | 10 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-48.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 28 | 10 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-48.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 28 | 10 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-48.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 28 | 10 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-49.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-49.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-49.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-49.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-50.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-50.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-50.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-50.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-51.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-51.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-51.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-51.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-52.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-52.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-52.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-52.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-53.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 27 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-53.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 27 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-53.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 27 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-53.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 27 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-54.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 34 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-54.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 34 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-54.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 34 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-54.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 34 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-55.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-55.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-55.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-55.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-56.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-56.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-56.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-56.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-57.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-57.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-57.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-57.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-58.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 25.3 | 7.5 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-58.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 25.3 | 7.5 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-58.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 25.3 | 7.5 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-58.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 25.3 | 7.5 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-59.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 32.2 | 10 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-59.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 32.2 | 10 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-59.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 32.2 | 10 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-59.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 32.2 | 10 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-60.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-60.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-60.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-60.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-61.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-61.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-61.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-61.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-62.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-62.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-62.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-62.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-63.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 30.8 | 10 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-63.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 30.8 | 10 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-63.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 30.8 | 10 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-63.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 30.8 | 10 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-64.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-64.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-64.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-64.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-65.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-65.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-65.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-65.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-66.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-66.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-66.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-66.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-67.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 28 | 10 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-67.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 28 | 10 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-67.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 28 | 10 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-67.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 28 | 10 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-68.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-68.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-68.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-68.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-69.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-69.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-69.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-69.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-70.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-70.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-70.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-70.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-71.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-71.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-71.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-71.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-72.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 27 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-72.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 27 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-72.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 27 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-72.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 27 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-73.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 34 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-73.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 34 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-73.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 34 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-73.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 34 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-74.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-74.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-74.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-74.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-75.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-75.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-75.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-75.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-76.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-76.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-76.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-76.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-77.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-77 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-77 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-77 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-78.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-78 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-78 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-78 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-79.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-79 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-79 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-79 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-80.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-80 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-80 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-80 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-81.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-81 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-81 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-81 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-82.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-82 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-82 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-82 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-83.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-83 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-83 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-83 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-84.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-84 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-84 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-84 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-85.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-85 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-85 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-85 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-86.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-86 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-86 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-86 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-87.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-87 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-87 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-87 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-88.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-88 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-88 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-88 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-89.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-89 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-89 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-89 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-90.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-90.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-90.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-90.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-91.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-91.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-91.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-91.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-92.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-92.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-92.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-92.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-93.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-93.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-93.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-93.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-94.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-94.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-94.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-94.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-95.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-95.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-95.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-95.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-96.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-96.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-96.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-96.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-97.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-97.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-97.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-97.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-98.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-98.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-98.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-98.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-99.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-99.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-99.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-99.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-100.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-100.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-100.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-100.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-101.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-101.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-101.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-101.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-102.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-102.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-102.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-102.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-103.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-103.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-103.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-103.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-104.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-104.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-104.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-104.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-105.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-105.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-105.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-105.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-106.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-106.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-106.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-106.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-107.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-107.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-107.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-107.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-108.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-108.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-108.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-108.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-109.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-109.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-109.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-109.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-110.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-110.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-110.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-110.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-111.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-111.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-111.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-111.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-112.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-112.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-112.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-112.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-113.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-113.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-113.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-113.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-114.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-114.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-114.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-114.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-115.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-115.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-115.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-115.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-116.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-116.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-116.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-116.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-117.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-117.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-117.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-117.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-118.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-118.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-118.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-118.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 200 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-119.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-119.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-119.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-119.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-120.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-120.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-120.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-120.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-121.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-121.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-121.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-121.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 208 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-122.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-122.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-122.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-122.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-123.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-123.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-123.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-123.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-124.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-124.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-124.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-124.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-125.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-125.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-125.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-125.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 220-240 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-126.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-126.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-126.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-126.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-127.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-127.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-127.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-127.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-128.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-128.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SF3 | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-128.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B1A100SAX | 440-480 | 3 | 10 | 100 | -
FdmC440-NEMA3-D-128.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55KN3* | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440B2A100SAX | 440-480 | 3 | 10 | 100 | -
Conditions of Use:
1. All of the specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches. Additional testing is not required when installed in an enclosure having the same or larger volume.
5. The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor controllers shall be considered in the end - product application
6. Connections between components are made with insulated wire that is sized per the table below:
| Freedom Contactor Size | Minimum Wire Size from Breaker to Contactor (AWG) |  | Minimum Length (inches)
| 3 (K Frame) | 4 |  | 18
| Note 1: | * notes the one or two digit code for the selection of the magnet coil voltage of the motor controller.

## FdmC440 Sz 4 Type D MCOLR
Eaton "Type D" Combination Motor Controllers | [18 empty] | Issue Date: 2014-01-21
Freedom style contactors with C440 Solid State Overload Relays
Database Identification Number | Listed Combination Motor Controller Information |  | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings
| UL File Number | Volume / Section (Vol#).(Sec#) |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating | Enclosure Volume, cubic inches | Conditions of Use | Other References
FdmC440-NEMA4-D-1.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-1.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-1.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-1.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-1.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-1.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-2.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-2.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-2.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-2.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-2.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-2.07 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-3.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-3.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-3.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-3.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-3.07 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-3.08 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-4.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-4.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-4.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-4.07 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-4.08 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-4.09 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-5.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-5.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-5.07 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-5.08 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-5.09 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-5.10 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-6.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-6.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-6.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-6.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-6.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-6.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-7.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-7.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-7.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-7.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-7.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-7.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-8.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-8.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-8.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-8.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-8.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-8.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-9.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-9.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-9.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-9.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-9.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-9.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-10.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-10.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-10.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-10.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-10.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-10.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-11.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-11.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-11.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-11.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-11.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-11.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-12.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-12.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-12.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-12.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-12.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-12.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-13.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-13.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-13.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-13.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-13.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-13.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-14.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-14.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-14.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-14.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-14.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-14.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-15.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-15.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-15.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-15.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-15.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-15.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-16.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-16.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-16.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-16.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-16.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-16.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-17.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-17.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-17.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-17.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-17.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-17.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-18.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-18.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-18.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-18.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-18.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-18.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-19.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-19.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-19.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-19.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-19.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-19.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-20.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-20.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-20.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-20.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-20.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-20.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-21.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-21.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-21.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-21.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-21.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-21.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-22.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-22.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-22.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-22.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-22.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-22.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-23.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-23.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-23.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-23.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-23.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-23.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-24.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-24.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-24.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-24.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-24.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-24.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-25.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-25.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-25.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-25.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-25.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-25.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-26.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-26.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-26.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-26.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-26.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-26.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-27.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-27.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-27.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-27.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-27.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-27.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-28.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-28.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-28.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-28.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-28.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-28.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-29.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-29.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-29.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-29.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-29.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-29.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-30.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-30.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-30.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-30.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-30.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-30.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-31.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-31.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-31.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-31.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-31.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-31.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-32.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-32.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-32.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-32.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-32.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-32.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-33.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-33.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-33.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-33.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-33.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-33.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-34.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-34.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-34.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-34.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-34.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-34.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-35.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-35.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-35.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-35.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-35.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-35.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-36.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-36.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-36.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-36.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-36.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-36.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-37.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-37.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-37.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-37.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-37.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-37.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-38.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-38.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-38.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-38.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-38.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-38.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-39.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-39.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-39.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-39.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-39.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-39.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-40.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-40.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-40.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-40.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-40.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-40.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-41.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-41.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-41.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-41.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-41.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-41.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-42.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-42.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-42.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-42.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-42.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-42.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-43.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-43.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-43.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-43.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-43.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-43.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-44.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-44.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-44.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-44.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-44.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-44.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-45.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-45.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-45.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-45.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-45.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-45.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-46.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-46.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-46.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-46.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-46.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-46.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-47.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-47.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-47.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-47.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-47.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-47.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-48.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-48.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-48.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-48.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-48.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-48.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-49.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-49.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-49.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-49.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-49.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-49.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-50.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-50.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-50.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-50.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-50.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-50.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-51.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-51.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-51.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-51.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-51.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-51.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-52.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-52.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-52.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-52.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-52.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-52.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-53.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-53.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-53.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-53.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-53.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-53.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-54.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-54.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-54.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-54.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-54.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-54.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-55.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-55.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-55.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-55.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-55.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-55.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-56.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-56.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-56.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-56.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-56.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-56.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-57.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-57.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-57.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-57.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-57.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-57.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-58.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-58.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-58.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-58.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-58.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-58.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-59.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-59.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-59.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-59.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-59.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-59.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-60.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-60.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-60.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-60.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-60.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-60.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-61.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-61.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-61.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-61.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-61.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-61.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-62.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-62.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-62.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-62.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-62.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-62.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-63.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-63.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-63.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-63.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-63.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-63.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-64.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-64.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-64.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-64.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-64.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-64.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-65.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-65.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-65.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-65.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-65.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-65.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-66.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-66.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-66.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-66.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-66.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-66.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | MC | Eaton | CN15NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-67.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-67.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-67.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-67.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-67.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-67.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-68.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-68.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-68.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-68.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-68.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-68.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-69.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-69.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-69.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-69.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-69.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-69.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-70.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-70.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-70.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-70.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-70.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-70.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-71.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-71.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-71.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-71.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-71.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-71.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-72.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-72.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-72.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-72.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-72.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-72.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-73.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-73.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-73.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-73.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-73.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-73.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-74.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-74.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-74.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-74.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-74.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-74.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-75.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-75.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-75.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-75.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-75.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-75.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-76.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-76.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-76.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-76.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-76.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-76.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-77.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-77.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-77.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-77.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-77.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-77.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-78.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-78.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-78.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-78.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-78.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-78.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-79.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-79.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-79.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-79.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-79.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-79.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-80.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-80.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-80.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-80.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-80.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-80.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-81.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-81.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-81.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-81.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-81.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-81.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-82.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-82.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-82.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-82.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-82.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-82.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-83.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-83.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-83.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-83.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-83.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-83.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-84.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-84.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-84.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-84.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-84.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-84.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-85.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-85.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-85.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-85.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-85.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-85.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-86.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-86.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-86.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-86.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-86.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-86.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-87.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-87.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-87.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-87.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-87.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-87.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-88.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-88.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SF4 | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-88.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-88.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-88.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA4-D-88.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55NN3* | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
Conditions of Use:
1. All of the specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches. Additional testing is not required when installed in an enclosure having the same or larger volume.
5. The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor controllers shall be considered in the end - product application
6. Connections between components are made with insulated wire that is sized per the table below:
| Freedom Contactor Size | Minimum Wire Size from Breaker to Contactor (AWG) |  | Minimum Length (inches)
| 4 (N Frame) | 2 |  | 20
| Note 1: | * notes the one or two digit code for the selection of the magnet coil voltage of the motor controller.

## FdmC440 Sz 5 Type D MCOLR
Eaton "Type D" Combination Motor Controllers | [18 empty] | Issue Date: 2014-01-21
Freedom style contactors with C440 Solid State Overload Relays
Database Identification Number | Listed Combination Motor Controller Information |  | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings
| UL File Number | Volume / Section (Vol#).(Sec#) |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating | Enclosure Volume, cubic inches | Conditions of Use | Other References
FdmC440-NEMA5-D-1.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-1.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-1.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-1.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-2.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-2.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-2.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-2.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-3.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-3.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-3.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-3.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-4.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-4.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-4.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-4.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-5.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-5.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-5.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-5.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-6.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-6.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-6.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-6.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-7.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-7.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-7.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-7.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-8.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-8.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-8.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-8.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-9.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-9.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-9.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-9.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-10.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-10.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-10.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-10.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-11.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-11.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-11.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-11.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-12.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-12.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-12.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-12.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-13.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-13.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-13.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-13.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-14.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-14.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-14.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-14.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-15.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-15.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-15.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-15.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-16.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-16.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-16.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-16.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-17.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-17.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-17.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-17.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-18.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-18.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-18.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-18.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-19.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-19.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-19.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-19.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-20.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-20.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-20.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-20.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-21.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-21.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-21.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-21.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-22.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-22.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-22.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-22.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-23.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-23.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-23.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-23.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-24.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-24.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-24.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-24.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-25.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-25.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-25.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-25.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-26.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-26.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-26.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-26.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-27.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-27.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-27.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-27.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-28.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-28.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-28.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-28.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-29.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-29.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-29.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-29.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-30.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-30.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-30.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-30.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-31.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-31.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-31.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-31.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-32.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-32.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-32.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-32.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-33.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-33.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-33.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-33.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-34.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-34.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-34.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-34.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-35.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-35.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-35.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-35.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-36.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-36.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-36.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-36.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-37.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-37.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-37.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-37.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-38.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-38.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-38.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-38.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-39.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-39.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-39.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-39.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-40.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-40.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-40.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-40.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-41.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-41.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-41.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-41.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-42.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-42.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-42.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-42.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-43.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-43.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-43.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-43.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-44.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-44.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-44.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-44.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-45.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-45.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-45.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-45.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-46.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-46.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-46.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-46.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-47.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-47.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-47.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-47.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-48.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-48.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-48.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-48.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-49.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-49.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-49.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-49.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-50.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-50.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-50.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-50.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-51.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-51.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-51.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-51.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-52.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-52.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-52.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-52.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-53.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-53.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-53.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-53.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-54.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-54.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-54.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-54.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-55.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-55.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-55.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-55.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-56.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-56.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-56.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-56.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-58.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-58.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-58.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-58.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-59.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-59.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-59.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-59.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-60.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-60.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-60.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-60.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-61.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-61.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-61.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-61.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-62.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-62.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-62.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-62.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-63.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-63.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-63.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-63.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-64.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-64.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-64.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-64.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-65.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-65.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-65.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-65.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-66.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-66.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-66.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-66.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-67.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-67.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-67.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-67.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-68.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-68.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-68.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-68.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-69.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-69.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-69.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-69.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-70.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-70.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-70.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-70.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-71.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-71.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-71.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-71.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-72.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-72.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-72.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-72.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-73.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-73.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-73.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-73.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-74.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-74.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-74.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-74.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-75.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-75.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-75.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-75.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-76.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-76.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-76.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-76.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-77.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-77.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-77.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-77.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-78.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-78.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-78.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-78.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-79.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-79.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-79.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-79.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-80.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-80.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-80.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-80.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-81.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-81.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-81.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-81.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-82.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-82.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-82.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-82.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-83.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-83.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-83.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-83.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-84.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-84.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-84.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-84.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-85.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-85.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-85.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-85.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-86.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-86.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-86.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-86.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-87.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-87.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-87.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-87.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-88.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-88.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-88.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-88.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-89.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-89.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-89.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-89.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-90.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-90.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-90.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-90.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-91.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-91.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-91.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-91.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-92.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-92.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-92.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-92.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-93.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-93.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-93.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-93.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-94.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-94.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-94.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-94.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-95.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-95.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-95.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-95.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-96.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-96.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-96.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-96.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-97.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-97.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-97.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-97.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-98.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-98.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-98.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-98.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-99.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-99.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-99.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-99.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-100.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-100.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-100.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-100.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-101.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-101.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-101.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-101.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-102.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-102.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-102.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-102.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-103.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-103.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-103.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-103.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-104.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-104.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-104.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-104.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-105.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-105.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-105.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-105.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-106.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-106.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-106.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-106.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-107.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-107.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-107.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-107.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-108.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-108.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-108.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-108.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-109.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-109.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-109.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-109.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-110.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-110.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-110.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-110.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-111.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-111.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-111.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-111.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-112.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-112.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-112.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-112.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-113.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-113.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-113.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-113.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-114.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-114.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-114.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-114.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-115.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-115.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-115.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-115.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-116.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-116.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-116.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-116.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-117.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-117.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-117.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-117.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-118.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-118.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-118.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-118.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-119.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-119.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-119.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-119.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-120.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-120.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-120.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-120.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-121.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-121.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-121.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-121.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-122.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-122.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-122.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-122.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-123.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-123.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-123.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-123.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-124.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-124.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-124.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-124.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-125.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-125.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-125.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-125.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-126.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-126.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-126.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-126.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-127.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-127.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-127.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-127.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-128.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-128.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-128.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-128.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-129.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-129.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-129.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-129.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-130.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-130.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-130.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-130.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-131.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-131.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-131.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-131.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-132.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-132.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-132.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-132.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-133.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-133.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-133.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-133.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-134.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-134.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-134.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-134.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-135.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-135.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-135.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-135.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-136.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-136.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-136.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-136.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-137.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-137.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-137.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-137.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-138.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-138.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-138.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-138.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-139.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-139.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-139.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-139.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-140.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-140.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-140.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-140.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-141.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-141.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-141.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-141.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-142.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-142.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-142.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-142.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-143.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-143.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-143.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-143.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-144.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-144.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-144.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-144.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-145.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-145.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-145.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-145.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-146.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-146.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-146.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-146.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-147.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-147.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-147.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-147.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-148.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-148.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-148.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-148.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-149.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-149.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-149.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-149.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-150.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-150.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-150.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-150.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-151.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-151.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-151.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-151.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-152.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-152.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-152.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-152.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-153.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-153.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-153.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-153.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-154.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-154.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-154.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-154.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-155.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-155.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-155.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-155.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-156.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-156.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-156.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-156.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-157.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-157.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-157.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-157.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-158.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-158.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-158.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-158.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-159.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-159.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-159.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-159.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-160.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-160.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-160.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-160.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-161.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-161.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-161.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-161.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-162.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-162.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-162.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-162.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-163.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-163.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-163.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-163.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-164.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-164.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-164.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-164.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-165.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-165.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-165.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-165.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-166.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-166.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-166.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-166.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-167.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-167.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-167.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-167.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-168.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-168.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-168.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-168.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-169.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-169.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-169.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-169.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-170.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-170.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-170.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-170.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-171.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-171.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-171.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-171.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-172.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-172.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-172.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-172.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-173.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-173.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-173.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-173.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-174.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-174.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-174.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-174.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-175.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-175.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-175.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-175.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-176.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-176.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-176.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-176.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-177.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-177.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-177.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-177.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-178.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-178.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-178.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-178.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-179.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-179.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-179.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-179.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-180.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-180.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-180.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-180.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-181.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-181.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-181.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-181.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-182.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-182.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-182.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-182.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-183.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-183.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-183.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-183.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-184.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-184.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-184.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-184.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-185.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-185.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-185.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-185.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-186.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-186.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-186.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-186.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-187.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-187.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-187.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-187.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-188.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-188.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-188.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-188.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-189.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-189.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-189.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-189.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-190.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-190.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-190.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-190.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-191.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-191.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-191.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-191.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-192.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-192.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-192.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-192.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-193.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-193.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-193.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-193.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-194.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-194.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-194.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-194.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-195.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-195.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-195.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-195.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-196.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-196.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-196.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-196.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-197.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-197.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-197.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-197.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-198.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-198.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-198.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-198.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-199.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-199.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-199.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-199.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 200 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-200.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-200.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-200.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-200.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-201.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-201.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-201.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-201.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 208 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-202.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-202.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-202.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-202.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-203.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-203.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-203.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-203.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-204.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-204.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-204.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-204.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-205.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-205.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-205.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-205.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-206.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-206.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-206.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-206.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-207.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-207.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-207.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-207.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-208.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-208.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-208.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-208.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-209.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-209.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-209.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-209.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 220-240 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-210.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-210.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-210.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-210.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-211.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-211.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-211.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-211.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-212.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-212.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-212.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-212.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-213.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-213.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SAX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-213.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C1A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-213.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440C2A140SPX | 440-480 | 3 | 10 | 140 | -
FdmC440-NEMA5-D-214.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-214.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-215.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-215.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-216.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-216.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-217.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-217.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-218.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-218.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-219.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-219.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-220.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-220.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-221.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-221.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-222.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-222.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-223.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-223.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-224.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-224.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-225.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-225.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-226.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-226.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-227.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-227.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-228.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-228.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-229.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-229.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-230.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-230.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-231.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-231.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-232.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-232.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-233.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-233.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-234.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-234.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-235.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-235.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-236.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-236.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-237.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-237.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-238.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-238.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-239.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-239.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-240.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-240.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-241.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-241.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-242.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-242.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-243.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-243.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-244.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-244.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-245.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-245.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-246.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-246.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-247.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-247.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-248.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-248.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-249.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-249.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-250.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-250.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-251.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-251.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-252.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-252.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-253.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-253.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-254.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-254.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-255.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-255.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-256.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-256.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-257.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-257.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-258.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-258.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-259.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-259.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-260.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-260.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-261.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-261.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-262.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-262.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-263.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-263.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-264.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-264.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-265.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-265.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-266.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-266.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-267.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-267.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-268.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-268.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-269.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-269.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-270.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-270.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-271.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-271.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-272.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-272.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-273.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-273.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-274.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-274.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-275.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-275.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-276.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-276.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-277.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-277.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-278.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-278.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-279.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-279.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-280.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-280.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-281.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-281.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-282.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-282.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-283.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-283.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-284.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-284.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-285.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-285.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-286.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-286.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-287.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-287.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-288.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-288.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-289.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-289.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-290.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-290.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-291.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-291.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-292.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-292.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-293.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-293.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-294.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-294.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-295.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-295.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-296.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-296.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-297.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-297.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-298.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-298.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-299.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-299.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-300.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-300.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-301.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-301.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-302.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-302.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-303.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-303.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-304.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-304.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-305.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-305.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-306.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-306.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-307.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-307.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-308.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-308.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-309.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-309.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-310.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-310.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-311.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-311.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-312.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-312.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-313.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-313.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-314.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-314.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-315.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-315.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-316.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-316.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-317.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-317.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-318.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-318.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-319.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-319.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-320.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-320.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-321.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-321.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-322.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-322.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-323.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-323.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-324.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-324.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-325.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-325.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-326.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-326.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-327.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-327.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-328.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-328.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-329.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-329.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-330.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-330.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-331.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-331.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-332.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-332.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-333.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-333.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-334.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-334.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-335.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-335.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-336.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-336.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-337.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-337.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-338.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-338.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-339.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-339.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-340.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-340.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-341.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-341.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-342.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-342.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-343.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-343.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-344.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-344.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-345.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-345.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-346.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-346.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-347.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-347.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-348.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-348.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-349.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-349.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-350.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-350.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-351.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-351.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-352.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-352.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-353.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-353.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-354.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-354.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-355.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-355.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-356.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-356.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-357.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-357.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-358.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-358.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-359.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-359.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-360.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-360.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-361.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-361.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-362.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-362.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-363.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-363.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-364.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-364.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-365.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-365.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-366.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-366.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-367.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-367.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-368.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-368.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-369.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-369.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-370.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-370.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-371.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-371.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-372.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-372.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-373.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-373.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-374.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-374.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-375.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-375.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-376.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-376.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-377.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-377.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-378.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-378.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-379.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-379.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-380.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-380.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-381.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-381.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-382.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-382.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-383.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-383.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-384.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-384.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-385.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-385.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-386.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-386.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-387.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-387.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-388.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-388.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-389.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-389.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-390.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-390.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-391.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-391.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-392.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-392.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-393.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-393.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-394.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-394.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-395.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-395.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-396.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-396.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-397.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-397.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-398.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-398.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-399.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-399.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-400.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-400.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-401.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-401.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-402.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-402.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-403.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-403.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-404.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-404.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-405.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-405.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-406.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-406.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-407.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-407.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-408.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-408.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-409.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-409.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-410.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-410.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-411.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-411.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-412.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-412.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-413.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-413.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-414.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-414.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-415.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-415.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-416.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-416.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-417.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-417.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-418.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-418.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-419.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-419.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-420.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-420.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-421.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-421.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-422.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-422.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-423.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-423.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-424.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-424.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-425.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-425.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-426.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-426.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-427.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-427.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-428.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-428.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-429.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-429.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-430.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-430.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-431.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-431.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-432.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-432.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-433.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-433.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-434.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-434.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-435.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-435.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-436.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-436.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-437.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-437.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-438.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-438.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-439.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-439.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-440.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-440.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-441.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-441.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-442.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-442.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-443.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-443.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-444.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-444.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-445.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-445.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-446.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-446.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-447.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-447.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-448.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-448.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-449.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-449.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-450.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-450.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-451.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-451.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-452.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-452.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-453.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-453.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-454.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-454.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-455.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-455.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-456.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-456.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-457.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-457.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-458.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-458.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-459.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-459.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-460.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-460.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-461.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-461.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-462.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-462.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-463.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-463.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-464.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-464.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-465.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-465.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-466.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-466.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-467.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-467.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-468.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-468.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-469.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-469.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-470.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-470.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-471.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-471.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-472.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-472.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-473.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-473.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-474.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-474.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-475.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-475.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-476.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-476.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-477.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-477.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-478.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-478.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-479.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-479.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-480.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-480.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-481.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-481.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-482.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-482.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-483.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-483.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-484.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-484.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-485.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-485.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-486.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-486.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-487.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-487.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-488.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-488.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-489.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-489.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-490.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-490.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-491.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-491.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-492.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-492.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-493.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-493.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-494.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-494.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-495.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-495.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-496.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-496.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-497.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-497.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-498.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-498.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-499.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-499.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-500.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-500.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-501.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-501.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-502.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-502.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-503.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-503.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-504.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-504.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-505.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-505.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-506.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-506.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-507.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-507.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-508.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-508.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-509.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-509.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-510.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-510.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-511.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-511.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-512.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-512.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-513.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-513.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-514.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-514.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-515.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-515.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-516.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-516.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-517.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-517.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-518.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-518.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-519.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-519.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-520.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-520.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-521.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-521.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-522.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-522.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-523.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-523.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-524.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-524.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-525.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-525.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-526.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-526.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-527.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-527.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-528.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-528.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-529.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-529.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-530.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-530.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-531.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-531.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-532.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-532.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-533.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-533.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-534.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-534.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-535.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-535.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-536.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-536.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-537.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-537.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-538.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-538.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-539.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-539.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-540.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-540.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-541.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-541.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-542.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-542.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-543.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-543.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-544.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-544.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-545.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-545.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-546.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-546.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-547.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-547.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-548.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-548.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-549.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-549.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-550.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-550.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-551.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-551.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-552.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-552.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-553.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-553.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-554.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-554.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-555.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-555.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-556.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-556.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-557.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-557.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-558.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-558.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-559.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-559.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-560.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-560.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-561.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-561.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-562.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-562.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-563.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-563.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-564.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-564.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-565.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-565.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-566.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-566.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-567.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-567.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-568.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-568.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-569.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-569.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-570.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-570.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-571.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-571.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-572.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-572.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-573.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-573.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-574.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-574.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-575.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-575.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-576.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-576.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-577.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-577.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-578.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-578.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-579.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-579.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-580.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 200 | 3 | - | 400 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-580.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 200 | 3 | - | 400 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-581.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 200 | 3 | - | 400 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-581.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 200 | 3 | - | 400 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-582.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 200 | 3 | - | 400 | - | 200 | 3 | 65 | 221 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-582.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 200 | 3 | - | 400 | - | 200 | 3 | 65 | 221 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-583.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 208 | 3 | - | 400 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-583.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 208 | 3 | - | 400 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-584.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 208 | 3 | - | 400 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-584.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 208 | 3 | - | 400 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-585.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 208 | 3 | - | 400 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-585.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 208 | 3 | - | 400 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-586.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 220-240 | 3 | - | 400 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-586.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 220-240 | 3 | - | 400 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-587.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 220-240 | 3 | - | 400 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-587.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 220-240 | 3 | - | 400 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-588.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 220-240 | 3 | - | 400 | - | 220-240 | 3 | 65 | 248 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-588.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 220-240 | 3 | - | 400 | - | 220-240 | 3 | 65 | 248 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-589.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 440-480 | 3 | - | 400 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-589.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 440-480 | 3 | - | 400 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-590.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 440-480 | 3 | - | 400 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-590.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 440-480 | 3 | - | 400 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-591.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 440-480 | 3 | - | 400 | - | 440-480 | 3 | 65 | 240 | 200 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-591.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 440-480 | 3 | - | 400 | - | 440-480 | 3 | 65 | 240 | 200 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-592.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 200 | 3 | - | 400 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-592.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 200 | 3 | - | 400 | - | 200 | 3 | 65 | 150 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-593.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 200 | 3 | - | 400 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-593.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 200 | 3 | - | 400 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-594.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 200 | 3 | - | 400 | - | 200 | 3 | 65 | 221 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-594.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 200 | 3 | - | 400 | - | 200 | 3 | 65 | 221 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-595.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 208 | 3 | - | 400 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-595.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 208 | 3 | - | 400 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-596.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 208 | 3 | - | 400 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-596.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 208 | 3 | - | 400 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-597.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 208 | 3 | - | 400 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-597.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 208 | 3 | - | 400 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-598.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 220-240 | 3 | - | 400 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-598.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 220-240 | 3 | - | 400 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-599.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 220-240 | 3 | - | 400 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-599.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 220-240 | 3 | - | 400 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-600.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 220-240 | 3 | - | 400 | - | 220-240 | 3 | 65 | 248 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-600.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 220-240 | 3 | - | 400 | - | 220-240 | 3 | 65 | 248 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-601.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 440-480 | 3 | - | 400 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-601.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 440-480 | 3 | - | 400 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-602.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 440-480 | 3 | - | 400 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-602.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 440-480 | 3 | - | 400 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-603.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 440-480 | 3 | - | 400 | - | 440-480 | 3 | 65 | 240 | 200 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-603.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400R5C | 440-480 | 3 | - | 400 | - | 440-480 | 3 | 65 | 240 | 200 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-604.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 200 | 3 | - | 400 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-604.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 200 | 3 | - | 400 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-605.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 200 | 3 | - | 400 | - | 200 | 3 | 65 | 221 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-605.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 200 | 3 | - | 400 | - | 200 | 3 | 65 | 221 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-606.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 208 | 3 | - | 400 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-606.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 208 | 3 | - | 400 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-607.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 208 | 3 | - | 400 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-607.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 208 | 3 | - | 400 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-608.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 220-240 | 3 | - | 400 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-608.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 220-240 | 3 | - | 400 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-609.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 220-240 | 3 | - | 400 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-609.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 220-240 | 3 | - | 400 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-610.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 220-240 | 3 | - | 400 | - | 220-240 | 3 | 65 | 248 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-610.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 220-240 | 3 | - | 400 | - | 220-240 | 3 | 65 | 248 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-611.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 440-480 | 3 | - | 400 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-611.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 440-480 | 3 | - | 400 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-612.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 440-480 | 3 | - | 400 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-612.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 440-480 | 3 | - | 400 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-613.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 440-480 | 3 | - | 400 | - | 440-480 | 3 | 65 | 240 | 200 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-613.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 440-480 | 3 | - | 400 | - | 440-480 | 3 | 65 | 240 | 200 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-614.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 200 | 3 | - | 400 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-614.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 200 | 3 | - | 400 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-615.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 200 | 3 | - | 400 | - | 200 | 3 | 65 | 221 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-615.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 200 | 3 | - | 400 | - | 200 | 3 | 65 | 221 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-616.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 208 | 3 | - | 400 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-616.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 208 | 3 | - | 400 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-617.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 208 | 3 | - | 400 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-617.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 208 | 3 | - | 400 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-618.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 220-240 | 3 | - | 400 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-618.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 220-240 | 3 | - | 400 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-619.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 220-240 | 3 | - | 400 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-619.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 220-240 | 3 | - | 400 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-620.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 220-240 | 3 | - | 400 | - | 220-240 | 3 | 65 | 248 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-620.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 220-240 | 3 | - | 400 | - | 220-240 | 3 | 65 | 248 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-621.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 440-480 | 3 | - | 400 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-621.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 440-480 | 3 | - | 400 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-622.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 440-480 | 3 | - | 400 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-622.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 440-480 | 3 | - | 400 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-623.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 440-480 | 3 | - | 400 | - | 440-480 | 3 | 65 | 240 | 200 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-623.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP400X5C | 440-480 | 3 | - | 400 | - | 440-480 | 3 | 65 | 240 | 200 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-624.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 200 | 3 | - | 600 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-624.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 200 | 3 | - | 600 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-625.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 200 | 3 | - | 600 | - | 200 | 3 | 65 | 221 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-625.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 200 | 3 | - | 600 | - | 200 | 3 | 65 | 221 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-626.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 208 | 3 | - | 600 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-626.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 208 | 3 | - | 600 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-627.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 208 | 3 | - | 600 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-627.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 208 | 3 | - | 600 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-628.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 208 | 3 | - | 600 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-628.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 208 | 3 | - | 600 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-629.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 220-240 | 3 | - | 600 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-629.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 220-240 | 3 | - | 600 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-630.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 220-240 | 3 | - | 600 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-630.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 220-240 | 3 | - | 600 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-631.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 220-240 | 3 | - | 600 | - | 220-240 | 3 | 65 | 248 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-631.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 220-240 | 3 | - | 600 | - | 220-240 | 3 | 65 | 248 | 100 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-632.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 440-480 | 3 | - | 600 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-632.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 440-480 | 3 | - | 600 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-633.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 440-480 | 3 | - | 600 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-633.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 440-480 | 3 | - | 600 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-634.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 440-480 | 3 | - | 600 | - | 440-480 | 3 | 65 | 240 | 200 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
| E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 440-480 | 3 | - | 600 | - | 440-480 | 3 | 65 | 240 | 200 | 16646 | 1, 5, 6
|  |  |  | MC | Eaton | CN15SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-635.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 200 | 3 | - | 600 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-635.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 200 | 3 | - | 600 | - | 200 | 3 | 65 | 177 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-636.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 200 | 3 | - | 600 | - | 200 | 3 | 65 | 221 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-636.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 200 | 3 | - | 600 | - | 200 | 3 | 65 | 221 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 200 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 200 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-637.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 208 | 3 | - | 600 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-637.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 208 | 3 | - | 600 | - | 208 | 3 | 65 | 143 | 50 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-638.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 208 | 3 | - | 600 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-638.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 208 | 3 | - | 600 | - | 208 | 3 | 65 | 169 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-639.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 208 | 3 | - | 600 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-639.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 208 | 3 | - | 600 | - | 208 | 3 | 65 | 211 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 208 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 208 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-640.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 220-240 | 3 | - | 600 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-640.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 220-240 | 3 | - | 600 | - | 220-240 | 3 | 65 | 154 | 60 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-641.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 220-240 | 3 | - | 600 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-641.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 220-240 | 3 | - | 600 | - | 220-240 | 3 | 65 | 192 | 75 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-642.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 220-240 | 3 | - | 600 | - | 220-240 | 3 | 65 | 248 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-642.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 220-240 | 3 | - | 600 | - | 220-240 | 3 | 65 | 248 | 100 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 220-240 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 220-240 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-643.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 440-480 | 3 | - | 600 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-643.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 440-480 | 3 | - | 600 | - | 440-480 | 3 | 65 | 156 | 125 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-644.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 440-480 | 3 | - | 600 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-644.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 440-480 | 3 | - | 600 | - | 440-480 | 3 | 65 | 180 | 150 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-645.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 440-480 | 3 | - | 600 | - | 440-480 | 3 | 65 | 240 | 200 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A1A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
FdmC440-NEMA5-D-645.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP600L6W | 440-480 | 3 | - | 600 | - | 440-480 | 3 | 65 | 240 | 200 | 16646 | 1, 5, 6
|  |  |  | REVCON | Eaton | CN55SN3* | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1
|  |  |  | OLR | Eaton | C440A2A005SAX | 440-480 | 3 | 5 | 5 | -
|  |  |  | CT KIT | Eaton | ZEB-XCT300 | 440-480 | 3 | - | 300 | - | [7 empty] | See Note 2
Conditions of Use:
1. All of the specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches. Additional testing is not required when installed in an enclosure having the same or larger volume.
5. The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor controllers shall be considered in the end - product application
6. Connections between components are made with insulated wire that is sized per the table below:
| Freedom Contactor Size | Minimum Wire Size from Breaker to Contactor (AWG) | Minimum Length (inches)
| 5 (S Frame) | 250 MCM | 24
| Note 1: | * notes the one or two digit code for the selection of the magnet coil voltage of the motor controller.
| Note 2: | ZEB-XCT300 current transformer package (CT = 300:5)

## FdmC440STR Sz 00 Type D MCOLR
Eaton "Type D" Combination Motor Controllers | [18 empty] | Issue Date: 2014-01-21
Freedom Solid State Starters (C440)
Database Identification Number | Listed Combination Motor Controller Information |  | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings
| UL File Number | Volume / Section (Vol#).(Sec#) |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating | Enclosure Volume, cubic inches | Conditions of Use | Other References
FdmC440STR-NEMA00-D-1.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-1.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-2.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-2.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-3.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-3.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-4.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-4.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-5.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-5.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-6.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-6.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-7.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-7.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-8.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-8.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-9.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-9.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-10.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-10.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-11.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-11.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-12.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-12.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-13.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-13.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-14.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-14.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-15.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-15.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-16.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-16.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-17.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-17.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-18.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-18.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-19.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-19.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-20.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-20.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-21.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-21.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-22.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-22.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-23.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-23.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-24.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-24.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-25.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-25.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-26.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-26.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-27.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-27.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-28.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-28.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-29.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-29.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-30.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-30.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-31.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-31.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-32.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-32.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-33-01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-33.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-34.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-34.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-35.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-35.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-36.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-36.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-38.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-38.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-39.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-39.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-40.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-40.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-41.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-41.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-42.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-42.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-43.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-43.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-44.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-44.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-45.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-45.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-46-01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-46-02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-47.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-47.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-48.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-48.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-49.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-49.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-51.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-51.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-52.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-52.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-53.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-53.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-54.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-54.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-55.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-55.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-56.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-56.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-57.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-57.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-58.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-58.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-59.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-59.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-60.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-60.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-61.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-61.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-62.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-62.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-64.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-64.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-65.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-65.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-66.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-66.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 200 | 3 | 5 | 6.9 | 1.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-67.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-67.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-68.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-68.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-69.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-69.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-70.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-70.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-71.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-71.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-72.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-72.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-73.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-73.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-74.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-74.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-75.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-75.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 440-480 | 3 | 5 | 3.4 | 2 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-77.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-77.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-78.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-78.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-79.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-79.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-80.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-80.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-81.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-81.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-82.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-82.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-83.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-83.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-84.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-84.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-85.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-85.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-86.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-86.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-87.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-87.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-88.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-88.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-89.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E020 | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-89.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G020 | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-90.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E020 | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-90.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G020 | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-91.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E020 | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-91.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G020 | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-92.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E020 | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-92.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G020 | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-93.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E020 | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-93.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G020 | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-94.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5E020 | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-94.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19AN0*5G020 | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-95.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E020 | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-95.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G020 | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-96.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5E020 | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA00-D-96.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59AN0*5G020 | 220-240 | 3 | 5 | 6 | 1.5 | [7 empty] | See Note 1, 2
Conditions of Use:
1. All of the specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches. Additional testing is not required when installed in an enclosure having the same or larger volume.
5. The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor controllers shall be considered in the end - product application
6. Connections between components are made with insulated wire that is sized per the table below:
| Freedom Starter Size | Minimum Wire Size from Breaker to Starter (AWG) |  | Minimum Length (inches)
| OO (A Frame) | 14 |  | 15
| Note 1: | * notes the one or two digit code for the selection of the magnet coil voltage of the motor controller.
| Note 2: | Overload Relay: …5E… = Standard Feature Set; …5G… = Ground Fault Feature Set

## FdmC440STR Sz 0 Type D MCOLR
Eaton "Type D" Combination Motor Controllers | [18 empty] | Issue Date: 2014-01-21
Freedom Solid State Starters (C440)
Database Identification Number | Listed Combination Motor Controller Information |  | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings
| UL File Number | Volume / Section (Vol#).(Sec#) |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating | Enclosure Volume, cubic inches | Conditions of Use | Other References
FdmC440STR-NEMA0-D-1.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-1.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-2.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-2.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-3.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-3.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-4.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-4.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-5.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-5.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-6.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-6.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-7.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-7.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-8.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-8.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-9.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-9.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-10.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-10.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-11.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-11.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-12.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-12.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-13.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-13.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-14.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-14.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-15.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-15.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-16.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-16.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-17.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-17.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-18.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-18.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-19.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-19.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-20.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-20.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-21.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-21.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-22.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-22.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-23.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-23.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-24.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-24.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-25.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-25.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-26.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-26.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-27.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-27.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-28.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-28.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-29.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-29.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-30.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-30.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-31.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-31.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-32.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-32.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-33.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-33.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-34.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-34.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-35.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-35.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-36.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-36.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-37.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-37.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-38.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-38.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-39.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-39.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-40.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-40.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-41.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-41.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-42.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-42.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-43.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-43.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-44.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-44.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-45.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-45.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-46.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-46.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-47.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-47.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-48.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-48.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-49.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-49.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-50.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-50.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-51.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-51.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-52.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-52.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-53.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-53.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-54.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-54.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-55.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-55.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-56.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-56.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-57.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-57.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-58.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-58.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-59.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-59.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-60.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-60.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-61.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-61.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-62.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-62.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-63.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-63.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-64.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-64.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-65.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-65.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-66.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-66.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-67.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-67.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-68.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-68.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-69.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-69.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-70.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-70.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-71.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-71.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-72.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-72.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-73.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-73.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-74.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-74.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-75.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-75.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-76.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-76.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-77.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-77.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-78.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-78.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-79.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-79.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-80.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-80.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-81.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-81.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-82.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-82.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-83.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-83.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-84.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-84.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-85.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-85.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-86.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-86.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-87.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-87.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-88.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-88.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-89.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-89.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-90.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-90.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-91.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-91.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-92.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-92.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-93.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-93.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-94.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-94.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-95.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-95.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-96.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-96.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-97.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-97.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-98.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-98.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-99.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-99.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-99.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-99.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-100.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-100.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-101.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-101.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-102.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-102.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-103.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-103.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-104.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-104.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-105.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-105.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-106.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-106.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-107.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-107.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-108.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-108.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-109.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-109.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-110.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-110.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-111.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-111.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-113.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-113.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-114.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-114.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-115.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-115.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-116.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-116.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-117.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-117.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-118.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-118.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-119.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-119.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-120.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-120.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-121.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-121.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-122.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-122.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-123.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-123.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-124.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-124.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-125.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-125.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-126.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-126.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-127.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-127.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-128.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-128.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-129.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-129.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-130.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-130.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-131.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-131.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-132.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-132.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-133.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-133.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-134.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-134.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-135.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-135.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-136.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-136.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-137.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-137.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-138.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-138.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-139.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-139.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-140.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-140.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-141.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-141.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-142.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-142.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-143.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-143.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-144.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-144.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-145.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-145.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-146.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-146.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-147.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-147.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-148.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-148.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-149.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-149.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-150.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-150.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-151.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-151.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-152.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-152.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-153.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-153.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-154.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-154.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-155.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-155.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-156.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-156.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-157.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-157.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-158.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-158.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-159.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-159.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-160.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-160.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-161.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-161.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-162.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-162.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-163.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-163.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-164.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-164.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-165.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-165.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-166.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-166.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-167.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-167.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-168.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-168.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-169.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-169.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-170.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-170.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-171.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-171.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-172.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-172.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-173.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-173.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-174.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-174.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-175.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-175.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-176.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-176.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-177.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-177.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-178.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-178.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-179.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-179.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-180.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-180.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-181.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-181.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-182.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-182.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-183.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-183.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-184.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-184.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-185.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-185.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-186.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-186.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-187.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-187.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-188.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-188.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-189.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-189.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-190.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-190.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-191.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-191.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-192.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-192.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-193.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-193.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-194.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-194.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-195.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-195.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-196.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-196.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-197.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-197.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-198.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-198.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-199.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-199.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-200.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-200.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-201.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-201.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-202.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-202.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-203.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-203.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-204.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-204.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-205.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-205.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-206.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-206.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 200 | 3 | 5 | 11 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-207.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-207.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-208.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-208.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-209.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-209.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 220-240 | 3 | 5 | 9.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-210.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-210.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G020 | 440-480 | 3 | 5 | 7.6 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-211.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E045 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-211.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G045 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-212.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E045 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-212.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G045 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-213.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5E045 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-213.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19BN0*5G045 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-214.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5E045 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA0-D-214.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59BN0*5G045 | 208 | 3 | 5 | 10.6 | 3 | [7 empty] | See Note 1, 2
Conditions of Use:
1. All of the specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches. Additional testing is not required when installed in an enclosure having the same or larger volume.
5. The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor controllers shall be considered in the end - product application
6. Connections between components are made with insulated wire that is sized per the table below:
| Freedom Starter Size | Minimum Wire Size from Breaker to Starter (AWG) |  | Minimum Length (inches)
| 0 (B Frame) | 10 |  | 14
| Note 1: | * notes the one or two digit code for the selection of the magnet coil voltage of the motor controller.
| Note 2: | Overload Relay: …5E… = Standard Feature Set; …5G… = Ground Fault Feature Set

## FdmC440STR Sz C1 Type D MCOLR
Eaton "Type D" Combination Motor Controllers | [18 empty] | Issue Date: 2014-01-21
Freedom Solid State Starters (C440)
Database Identification Number | Listed Combination Motor Controller Information |  | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings
| UL File Number | Volume / Section (Vol#).(Sec#) |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating | Enclosure Volume, cubic inches | Conditions of Use | Other References
FdmC440STR-NEMAC1-D-1.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-1.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-2.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-2.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-3.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-3.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-4.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-4.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-5.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-5.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-6.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-6.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-7.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-7.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-8.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-8.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-9.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-9.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-10.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-10.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-11.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-11.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-12.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-12.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-13.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-13.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-14.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-14.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-15.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-15.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-16.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-16.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-17.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-17.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-18.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-18.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-19.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-19.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-20.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-20.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-21.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-21.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-22.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-22.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-23.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-23.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-24.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-24.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-25.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-25.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-26.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-26.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-27.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-27.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-28.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-28.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-29.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-29.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-30.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-30.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-31.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-31.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-32.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-32.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-33.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-33.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-34.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-34.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-35.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-35.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-36.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-36.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-37.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-37.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-38.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-38.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-39.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-39.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-40.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-40.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-41.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-41.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-42.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-42.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-43.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-43.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-44.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-44.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-45.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-45.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-46.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-46.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-47.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-47.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-48.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-48.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-49.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-49.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-50.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-50.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-51.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-51.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-52.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-52.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-53.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-53.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-54.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-54.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-55.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-55.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-56.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-56.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-57.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-57.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-58.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-58.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-59.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-59.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-60.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-60.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-61.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-61.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-62.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-62.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-63.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-63.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-64.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-64.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-65.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-65.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-66.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-66.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-67.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-67.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-68.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-68.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-69.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-69.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-70.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-70.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-71.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-71.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-72.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-72.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-73.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-73.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-74.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-74.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-75.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-75.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-76.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-76.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-77.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-77.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-78.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-78.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-79.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-79.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-80.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-80.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-81.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-81.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-82.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-82.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-83.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-83.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-84.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-84.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-85.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-85.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-86.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-86.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-87.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-87.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-88.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-88.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-89.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-89.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-90.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-90.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-91.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-91.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-92.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-92.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-93.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-93.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-94.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-94.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-95.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-95.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-96.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-96.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-97.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-97.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-98.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-98.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-99.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-99.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-100.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-100.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-101.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-101.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-102.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-102.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-103.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-103.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-104.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-104.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-105.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-105.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-106.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-106.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-107.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-107.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-108.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-108.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-109.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-109.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-110.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-110.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-111.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-111.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-112.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-112.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-113.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-113.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-114.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-114.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-115.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-115.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-116.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-116.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-117.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-117.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-118.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-118.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-119.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-119.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-120.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-120.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-121.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-121.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-122.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-122.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-123.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-123.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-124.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-124.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-125.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-125.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-126.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-126.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-127.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-127.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-128.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-128.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-129.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-129.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-130.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-130.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-131.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-131.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-132.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-132.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-133.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-133.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-134.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-134.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-135.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-135.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-136.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-136.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-137.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-137.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-138.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-138.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-139.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-139.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-140.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-140.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-141.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-141.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-142.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-142.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-143.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-143.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-144.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-144.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-145.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-145.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-146.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-146.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-147.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-147.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-148.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-148.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-149.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-149.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-150.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-150.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-151.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-151.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-152.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-152.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-153.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-153.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-154.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-154.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-155.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-155.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-156.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-156.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-157.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-157.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-158.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-158.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-159.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-159.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-160.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-160.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-161.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-161.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-162.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-162.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-163.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-163.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-164.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-164.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-165.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-165.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-166.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-166.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-167.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-167.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-168.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-168.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-169.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-169.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-170.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-170.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-171.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-171.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-172.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-172.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-173.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-173.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-174.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-174.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-175.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-175.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-176.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-176.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-177.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-177.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-178.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-178.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-179.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-179.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-180.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-180.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-181.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-181.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-182.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-182.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-183.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-183.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-184.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-184.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-185.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-185.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-186.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-186.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-187.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-187.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-188.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-188.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-189.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-189.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-190.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-190.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-191.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-191.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-192.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-192.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-193.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-193.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-194.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-194.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-195.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-195.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-196.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-196.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-197.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-197.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-198.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-198.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-199.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-199.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-200.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-200.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-201.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-201.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-202.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-202.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-203.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-203.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-204.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-204.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-205.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-205.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-206.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-206.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-207.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-207.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-208.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-208.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-209.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-209.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-210.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-210.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-211.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-211.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-212.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-212.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-213.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-213.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-214.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-214.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-215.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-215.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-216.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-216.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-217.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-217.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-218.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-218.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-219.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-219.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-220.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-220.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-221.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-221.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-222.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-222.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-223.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-223.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-224.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-224.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-225.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-225.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-226.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-226.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-227.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-227.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-228.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-228.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-229.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-229.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-230.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-230.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-231.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-231.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-232.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-232.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-233.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-233.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-234.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-234.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-235.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-235.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-236.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-236.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-237.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-237.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-238.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-238.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-239.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-239.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-240.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-240.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-241.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-241.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-242.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-242.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-243.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-243.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-244.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-244.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-245.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-245.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-246.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-246.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-247.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-247.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-248.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-248.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-249.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-249.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-250.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-250.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-251.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-251.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-252.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-252.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-253.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-253.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-254.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-254.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-255.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-255.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-256.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-256.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-257.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-257.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-258.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-258.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-259.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-259.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-260.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-260.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-261.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-261.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-262.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-262.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-263.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-263.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-264.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-264.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-265.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-265.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-266.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-266.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-267.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-267.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-268.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-268.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-269.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-269.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-270.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-270.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-271.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-271.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-272.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-272.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-273.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-273.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-274.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-274.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-275.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-275.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-276.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-276.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-277.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-277.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-278.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-278.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-279.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-279.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-280.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-280.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-281.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-281.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-282.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-282.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-283.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-283.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-284.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-284.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-285.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-285.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-286.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-286.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-287.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-287.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-288.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-288.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-289.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-289.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-290.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-290.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-291.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-291.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-292.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-292.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-293.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-293.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-294.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-294.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-295.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-295.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-296.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-296.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-297.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-297.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-298.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-298.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-299.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-299.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-300.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-300.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-301.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-301.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-302.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-302.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-303.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-303.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-304.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-304.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-305.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-305.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-306.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-306.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-307.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-307.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-308.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-308.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-309.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-309.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-310.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-310.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-311.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-311.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-312.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-312.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-313.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-313.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-314.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-314.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-315.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-315.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-316.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-316.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-317.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-317.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-318.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-318.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-319.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-319.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-320.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-320.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-321.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-321.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-322.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-322.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-323.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-323.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-324.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-324.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-325.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-325.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-326.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-326.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-327.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-327.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-328.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-328.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-329.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-329.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-330.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-330.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-331.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-331.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-332.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-332.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-333.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-333.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-334.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-334.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-335.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-335.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-336.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-336.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-337.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-337.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-338.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-338.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-339.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-339.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-340.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-340.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-341.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-341.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19CN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-342.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-342.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-343.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-343.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-344.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-344.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-345.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-345.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-346.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-346.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-347.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-347.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-348.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC1-D-348.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59CN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
Conditions of Use:
1. All of the specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches. Additional testing is not required when installed in an enclosure having the same or larger volume.
5. The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor controllers shall be considered in the end - product application
6. Connections between components are made with insulated wire that is sized per the table below:
| Freedom Starter Size | Minimum Wire Size from Breaker to Starter (AWG) |  | Minimum Length (inches)
| C1 (C Frame) | 10 |  | 15
| Note 1: | * notes the one or two digit code for the selection of the magnet coil voltage of the motor controller.
| Note 2: | Overload Relay: …5E… = Standard Feature Set; …5G… = Ground Fault Feature Set

## FdmC440STR Sz 1 Type D MCOLR
Eaton "Type D" Combination Motor Controllers | [18 empty] | Issue Date: 2014-01-21
Freedom Solid State Starters (C440)
Database Identification Number | Listed Combination Motor Controller Information |  | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings
| UL File Number | Volume / Section (Vol#).(Sec#) |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating | Enclosure Volume, cubic inches | Conditions of Use | Other References
FdmC440STR-NEMA1-D-1.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-1.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-2.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-2.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-3.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-3.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-4.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-4.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-5.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-5.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-6.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-6.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-7.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-7.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-8.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-8.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-9.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-9.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-10.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-10.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-11.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-11.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-12.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-12.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-13.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-13.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-14.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-14.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-15.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-15.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-16.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-16.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-17.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-17.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-18.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-18.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-19.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-19.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-20.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-20.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-21.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-21.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-22.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-22.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-23.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-23.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-24.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-24.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-25.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-25.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-26.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-26.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-27.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-27.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-28.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-28.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-29.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-29.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-30.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-30.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-31.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-31.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-32.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-32.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-33.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-33.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-34.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-34.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-35.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-35.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-36.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-36.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-37.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-37.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-38.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-38.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-39.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-39.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-40.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-40.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-41.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-41.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-42.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-42.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-43.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-43.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-44.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-44.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-45.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-45.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-46.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-46.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-47.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-47.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-48.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-48.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-49.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-49.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-50.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-50.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-51.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-51.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-52.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-52.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-53.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-53.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-54.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-54.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-55.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-55.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-56.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-56.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-57.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-57.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-58.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-58.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-59.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-59.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-60.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-60.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-61.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-61.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-62.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-62.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-63.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-63.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-64.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-64.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-65.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-65.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-66.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-66.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-67.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-67.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-68.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-68.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-69.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-69.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-70.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-70.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-71.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-71.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-72.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-72.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-73.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-73.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-74.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-74.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-75.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-75.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-76.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-76.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-77.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-77.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-78.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-78.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-79.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-79.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-80.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-80.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-81.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-81.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-82.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-82.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-83.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-83.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-84.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-84.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-85.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-85.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-86.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-86.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-87.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-87.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-88.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-88.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-89.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-89.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 200 | 3 | 5 | 4.8 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-90.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-90.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 208 | 3 | 5 | 4.6 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-91.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-91.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 220-240 | 3 | 5 | 4.2 | 1 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-92.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-92.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G005 | 440-480 | 3 | 5 | 4.8 | 3 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-93.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-93.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-94.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-94.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-95.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-95.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-96.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-96.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-97.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-97.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-98.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-98.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-99.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-99.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-100.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-100.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-101.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-101.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-102.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-102.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-103.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-103.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-104.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-104.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-105.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-105.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-106.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-106.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-107.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-107.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-108.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-108.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-109.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-109.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-110.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-110.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-111.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-111.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-112.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-112.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-113.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-113.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-114.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-114.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-115.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-115.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-116.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-116.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-117.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-117.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-118.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-118.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-119.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-119.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-120.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-120.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-121.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-121.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-122.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-122.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-123.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-123.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-124.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-124.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-125.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-125.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-126.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-126.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-127.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-127.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-128.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-128.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-129.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-129.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-130.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-130.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-131.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-131.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-132.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-132.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-133.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-133.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-134.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-134.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-135.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-135.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-136.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-136.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-137.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-137.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-138.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-138.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-139.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-139.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-140.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-140.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-141.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-141.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-142.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-142.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-143.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-143.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-144.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-144.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-145.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-145.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-146.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-146.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-147.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-147.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-148.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-148.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-149.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-149.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-150.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-150.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-151.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-151.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-152.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-152.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-153.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-153.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-154.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-154.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-155.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-155.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-156.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-156.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-157.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-157.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-158.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-158.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-159.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-159.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-160.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-160.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-161.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-161.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-162.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-162.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-163.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-163.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-164.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-164.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-165.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-165.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-166.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-166.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-167.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-167.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-168.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-168.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-169.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-169.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-170.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-170.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-171.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-171.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-172.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-172.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-173.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-173.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-174.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-174.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-175.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-175.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-176.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-176.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-177.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-177.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-178.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-178.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-179.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-179.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-180.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-180.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-181.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-181.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-182.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-182.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-183.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-183.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-184.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-184.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-185.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-185.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-186.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-186.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-187.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-187.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-188.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-188.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-189.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-189.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-190.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-190.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-191.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-191.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-192.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-192.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-193.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-193.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-194.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-194.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-195.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-195.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-196.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-196.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-197.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-197.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-198.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-198.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-199.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-199.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-200.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-200.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-201.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-201.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-202.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-202.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-203.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-203.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-204.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-204.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-205.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-205.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-206.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-206.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-207.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-207.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-208.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-208.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-209.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-209.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-210.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-210.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-211.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-211.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-212.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-212.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-213.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-213.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-214.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-214.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-215.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-215.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-216.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-216.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-217.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-217.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-218.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-218.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-219.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-219.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-220.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-220.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-221.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-221.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-222.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-222.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-223.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-223.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-224.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-224.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-225.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-225.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-226.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-226.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-227.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-227.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-228.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-228.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-229.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-229.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-230.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-230.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-231.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-231.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-232.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-232.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-233.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-233.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-234.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-234.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-235.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-235.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-236.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-236.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 200 | 3 | 5 | 17.5 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-237.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-237.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-238.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-238.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-239.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-239.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 208 | 3 | 5 | 16.7 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-240.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-240.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-241.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-241.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 220-240 | 3 | 5 | 15.2 | 5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-242.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-242.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-243.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-243.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-244.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-244.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G020 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-245.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-245.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-246.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-246.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-247.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-247.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-248.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-248.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-249.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-249.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-250.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-250.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-251.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-251.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-252.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-252.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-253.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-253.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-254.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-254.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-255.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-255.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-256.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-256.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-257.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-257.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-258.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-258.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-259.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-259.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-260.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-260.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-261.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-261.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-262.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-262.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-263.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-263.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-264.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-264.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-265.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-265.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-266.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-266.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-267.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-267.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-268.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-268.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-269.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-269.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-270.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-270.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-271.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-271.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-272.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-272.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-273.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-273.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-274.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-274.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-275.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-275.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-276.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-276.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-277.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-277.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-278.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-278.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-279.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-279.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-280.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-280.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-281.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-281.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-282.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-282.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-283.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-283.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-284.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-284.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-285.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-285.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-286.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-286.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-287.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-287.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-288.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-288.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-289.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-289.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-290.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-290.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-291.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-291.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-292.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-292.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-293.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-293.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-294.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-294.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-295.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-295.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-296.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-296.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-297.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-297.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-298.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-298.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-299.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-299.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-300.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-300.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-301.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-301.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-302.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-302.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-303.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-303.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-304.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-304.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-305.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-305.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-306.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-306.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-307.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-307.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-308.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-308.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-309.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-309.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-310.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-310.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-311.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-311.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-312.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-312.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-313.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-313.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-314.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-314.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-315.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-315.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-316.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-316.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-317.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-317.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-318.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-318.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-319.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-319.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-320.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-320.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-321.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-321.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-322.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-322.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-323.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-323.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-324.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-324.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-325.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-325.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-326.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-326.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-327.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-327.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-328.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-328.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-329.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-329.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-330.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-330.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-331.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-331.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-332.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-332.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-333.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-333.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-334.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-334.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-335.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-335.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-336.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-336.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-337.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-337.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-338.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-338.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-339.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-339.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-340.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-340.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-341.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-341.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19DN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-342.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-342.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-343.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-343.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 200 | 3 | 5 | 25.3 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-344.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-344.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-345.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-345.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 208 | 3 | 5 | 24.2 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-346.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-346.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-347.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-347.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 220-240 | 3 | 5 | 22 | 7.5 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-348.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5E045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA1-D-348.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59DN0*5G045 | 440-480 | 3 | 5 | 14 | 10 | [7 empty] | See Note 1, 2
Conditions of Use:
1. All of the specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches. Additional testing is not required when installed in an enclosure having the same or larger volume.
5. The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor controllers shall be considered in the end - product application
6. Connections between components are made with insulated wire that is sized per the table below:
| Freedom Starter Size | Minimum Wire Size from Breaker to Starter (AWG) |  | Minimum Length (inches)
| 1 (D Frame) | 10 |  | 15
| Note 1: | * notes the one or two digit code for the selection of the magnet coil voltage of the motor controller.
| Note 2: | Overload Relay: …5E… = Standard Feature Set; …5G… = Ground Fault Feature Set

## FdmC440STR Sz 2 Type D MCOLR
Eaton "Type D" Combination Motor Controllers | [18 empty] | Issue Date: 2014-01-21
Freedom Solid State Starters (C440)
Database Identification Number | Listed Combination Motor Controller Information |  | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings
| UL File Number | Volume / Section (Vol#).(Sec#) |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating | Enclosure Volume, cubic inches | Conditions of Use | Other References
FdmC440STR-NEMA2-D-1.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19GN0*5E005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-1.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19GN0*5G005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-2.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19GN0*5E005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-2.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19GN0*5G005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-3.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19GN0*5E005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-3.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19GN0*5G005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-4.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-4.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-5.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-5.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-6.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-6.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | STR | Eaton | AN19GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-7.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-7.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-8.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-8.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-9.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-9.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-10.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-10.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-11.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-11.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-12.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-12.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-13.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-13.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-14.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-14.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-15.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-15.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-16.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-16.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-17.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-17.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-18.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-18.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-19.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-19.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 200 | 3 | - | 3 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-20.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-20.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 208 | 3 | - | 3 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-21.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-21.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 220-240 | 3 | - | 3 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-22.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-22.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.1 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-23.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-23.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 1.6 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-24.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-24.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS003A0C | 440-480 | 3 | - | 3 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-25.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-25.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-26.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-26.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-27.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-27.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-28.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-28.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-29.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-29.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-30.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-30.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-31.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-31.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-32.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-32.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-33.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-33.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-34.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-34.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-35.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-35.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-36.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-36.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-37.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-37.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-38.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-38.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-39.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-39.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-40.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-40.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-41.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-41.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-42.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-42.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-43.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-43.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-44.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-44.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-45.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-45.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-46.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-46.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-47.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-47.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-48.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-48.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-49.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-49.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-50.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-50.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-51.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-51.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-52.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-52.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-53.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-53.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | CN15GN3*B | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-54.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-54.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-55.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-55.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-56.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-56.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-57.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-57.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-58.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-58.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-59.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-59.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-60.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-60.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-61.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-61.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-62.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-62.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-63.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-63.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-64.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-64.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-65.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-65.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-66.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-66.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-67.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-67.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 2.4 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-68.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-68.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-69.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-69.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-70.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-70.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 2.2 | 0.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-71.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-71.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 3.2 | 0.75 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-72.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-72.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-73.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-73.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 2.1 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-74.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-74.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-75.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-75.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 3.4 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-76.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-76.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-77.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-77.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-78.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-78.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-79.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-79.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-80.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-80.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-81.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-81.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-82.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-82.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-83.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-83.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-84.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-84.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-85.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-85.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-86.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-86.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-87.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-87.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-88.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-88.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-89.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-89.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-90.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-90.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-91.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-91.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-92.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-92.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G005 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-93.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-93.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-94.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-94.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-95.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-95.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-96.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-96.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-97.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-97.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-98.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-98.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-99.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-99.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-100.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-100.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-101.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-101.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-102.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-102.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-103.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-103.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-104.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-104.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-105.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-105.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-106.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-106.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-107.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-107.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-108.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-108.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 200 | 3 | - | 7 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-109.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-109.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 208 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-110.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-110.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-111.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-111.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 220-240 | 3 | - | 7 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-112.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-112.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS007C0C | 440-480 | 3 | - | 7 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-113.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-113.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-114.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-114.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-115.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-115.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-116.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-116.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-117.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-117.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-118.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-118.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-119.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-119.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-120.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-120.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-121.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-121.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-122.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-122.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-123.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-123.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-124.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-124.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-125.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-125.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-126.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-126.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-127.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-127.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-128.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-128.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-129.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-129.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-130.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-130.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-131.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-131.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-132.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-132.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-133.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-133.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-134.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-134.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-135.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-135.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-136.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-136.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-137.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-137.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-138.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-138.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-139.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-139.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-140.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-140.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-141.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-141.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-142.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-142.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-143.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-143.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-144.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-144.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-145.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-145.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-146.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-146.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-147.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-147.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-148.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-148.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-149.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-149.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-150.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-150.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-151.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-151.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-152.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-152.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-153.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-153.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-154.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-154.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-155.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-155.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-156.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-156.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-157.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-157.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-158.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-158.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 4.8 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-159.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-159.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-160.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-160.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-161.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-161.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-162.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-162.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 4.6 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-163.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-163.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-164.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-164.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-165.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-165.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-166.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-166.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 4.2 | 1 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-167.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-167.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-168.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-168.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-169.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-169.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-170.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-170.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 4.8 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-171.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-171.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-172.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-172.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-173.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-173.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-174.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-174.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-175.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-175.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-176.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-176.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-177.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-177.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-178.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-178.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-179.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-179.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-180.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-180.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-181.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-181.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-182.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-182.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-183.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-183.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-184.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-184.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-185.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-185.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-186.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-186.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-187.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-187.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 6.9 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-188.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-188.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-189.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-189.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-190.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-190.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-191.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-191.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 6.6 | 1.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-192.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-192.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-193.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-193.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-194.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-194.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-195.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-195.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 6.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-196.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-196.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-197.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-197.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-198.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-198.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-199.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-199.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-200.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-200.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-201.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-201.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-202.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-202.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-203.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-203.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-204.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-204.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-205.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-205.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-206.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-206.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-207.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-207.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-208.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-208.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-209.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-209.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-210.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-210.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-211.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-211.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-212.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-212.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-213.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-213.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-214.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-214.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-215.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-215.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-216.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-216.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-217.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-217.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-218.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-218.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-219.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-219.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-220.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-220.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-221.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-221.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-222.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-222.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-223.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-223.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-224.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-224.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-225.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-225.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-226.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-226.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-227.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-227.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-228.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-228.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-229.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-229.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-230.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-230.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-231.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-231.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-232.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-232.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-233.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-233.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-234.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-234.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 7.8 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-235.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-235.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-236.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-236.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-237.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-237.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 7.5 | 2 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-238.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-238.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-239.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-239.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-240.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-240.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-241.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-241.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-242.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-242.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 7.6 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-243.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-243.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-244.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-244.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G020 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-245.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-245.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-246.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-246.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-247.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-247.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-248.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-248.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-249.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-249.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-250.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-250.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-251.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-251.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-252.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-252.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-253.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-253.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-254.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-254.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-255.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-255.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-256.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-256.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-257.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-257.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 200 | 3 | - | 15 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-258.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-258.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 208 | 3 | - | 15 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-259.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-259.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 220-240 | 3 | - | 15 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-260.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-260.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS015E0C | 440-480 | 3 | - | 15 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-261.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-261.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-262.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-262.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-263.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-263.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-264.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-264.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-265.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-265.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-266.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-266.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-267.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-267.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-268.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-268.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-269.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-269.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-270.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-270.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-271.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-271.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 200 | 3 | - | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-272.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-272.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-273.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-273.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 208 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-274.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-274.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-275.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-275.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 220-240 | 3 | - | 25 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-276.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-276.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-277.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-277.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-278.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-278.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP025D0C | 440-480 | 3 | - | 25 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-279.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-279.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-280.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-280.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-281.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-281.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-282.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-282.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-283.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-283.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-284.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-284.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-285.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-285.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-286.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-286.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-287.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-287.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-288.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-288.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-289.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-289.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-290.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-290.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-291.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-291.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-292.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-292.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-293.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-293.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-294.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-294.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-295.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-295.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-296.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-296.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-297.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-297.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-298.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-298.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-299.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-299.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-300.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-300.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-301.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-301.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-302.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-302.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-303.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-303.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-304.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-304.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-305.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-305.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-306.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-306.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-307.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-307.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-308.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-308.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-309.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-309.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-310.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-310.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-311.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-311.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-312.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-312.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-313.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-313.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-314.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-314.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-315.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-315.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 11 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-316.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-316.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-317.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-317.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 200 | 3 | - | 30 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-318.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-318.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 10.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-319.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-319.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-320.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-320.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 208 | 3 | - | 30 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-321.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-321.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 9.6 | 3 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-322.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-322.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-323.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-323.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 220-240 | 3 | - | 30 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-324.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-324.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 11 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-325.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-325.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-326.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-326.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS030H1C | 440-480 | 3 | - | 30 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-327.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-327.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-328.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-328.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-329.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-329.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-330.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-330.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-331.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-331.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-332.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-332.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-333.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-333.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-334.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-334.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-335.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-335.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-336.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-336.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-337.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-337.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-338.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-338.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-339.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-339.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-340.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-340.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-341.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-341.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-342.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-342.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-343.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-343.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-344.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-344.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-345.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-345.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-346.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-346.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-347.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-347.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-348.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-348.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-349.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-349.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-350.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-350.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-351.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-351.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-352.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-352.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-353.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-353.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-354.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-354.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-355.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-355.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-356.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-356.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-357.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-357.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-358.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-358.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-359.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-359.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-360.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-360.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-361.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-361.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-362.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-362.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-363.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-363.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-364.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-364.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-365.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-365.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-366.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-366.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-367.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-367.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-368.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-368.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-369.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-369.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-370.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-370.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-371.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-371.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 200 | 3 | - | 50 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-372.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-372.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 16.7 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-373.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-373.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-374.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-374.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 208 | 3 | - | 50 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-375.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-375.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 15.2 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-376.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-376.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-377.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-377.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-378.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-378.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 220-240 | 3 | - | 50 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-379.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-379.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 14 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-380.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-380.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-381.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-381.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-382.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-382.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS050K2C | 440-480 | 3 | - | 50 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-383.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-383.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-384.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-384.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-385.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-385.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-386.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 208 | 3 | - | 70 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-386.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 208 | 3 | - | 70 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-387.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 208 | 3 | - | 70 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-387.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 208 | 3 | - | 70 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-388.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-388.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-389.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-389.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-390.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-390.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-391.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-391.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-392.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-392.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-393.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-393.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | MC | Eaton | AN19GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-394.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-394.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 17.5 | 5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-395.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-395.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-396.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-396.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 200 | 3 | - | 70 | - | 200 | 3 | 65 | 32.2 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 200 | 3 | 5 | 32.2 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-397.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 208 | 3 | - | 70 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-397.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 208 | 3 | - | 70 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-398.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 208 | 3 | - | 70 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-398.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 208 | 3 | - | 70 | - | 208 | 3 | 65 | 30.8 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 208 | 3 | 5 | 30.8 | 10 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-399.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-399.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 22 | 7.5 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-400.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-400.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 28 | 10 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-401.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-401.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 220-240 | 3 | - | 70 | - | 220-240 | 3 | 65 | 42 | 15 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 220-240 | 3 | 5 | 42 | 15 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-402.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-402.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 21 | 15 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-403.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-403.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 27 | 20 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-404.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5E045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA2-D-404.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP070M2C | 440-480 | 3 | - | 70 | - | 440-480 | 3 | 65 | 34 | 25 | 1631 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59GN0*5G045 | 440-480 | 3 | 5 | 34 | 25 | [7 empty] | See Note 1, 2
Conditions of Use:
1. All of the specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches. Additional testing is not required when installed in an enclosure having the same or larger volume.
5. The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor controllers shall be considered in the end - product application
6. Connections between components are made with insulated wire that is sized per the table below:
| Freedom Starter Size | Minimum Wire Size from Breaker to Starter (AWG) |  | Minimum Length (inches)
| 2 (G Frame) | 8 |  | 15
| Note 1: | * notes the one or two digit code for the selection of the magnet coil voltage of the motor controller.
| Note 2: | Overload Relay: …5E… = Standard Feature Set; …5G… = Ground Fault Feature Set

## FdmC440STR Sz 3 Type D MCOLR
Eaton "Type D" Combination Motor Controllers | [18 empty] | Issue Date: 2014-01-21
Freedom Solid State Starters (C440)
Database Identification Number | Listed Combination Motor Controller Information |  | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings
| UL File Number | Volume / Section (Vol#).(Sec#) |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating | Enclosure Volume, cubic inches | Conditions of Use | Other References
FdmC440STR-NEMA3-D-1.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 25.3 | 7.5 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-1.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 25.3 | 7.5 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-2.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 32.2 | 10 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-2.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 32.2 | 10 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-3.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-3.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-4.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-4.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-5.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-5.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-6.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 30.8 | 10 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-6.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 30.8 | 10 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-7.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-7.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-8.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-8.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-9.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-9.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-10.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 28 | 10 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-10.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 28 | 10 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-11.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-11.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-12.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-12.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-13.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-13.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-14.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-14.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-15.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 27 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-15.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 27 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-16.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 34 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-16.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 34 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-17.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-17.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-18.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-18.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-19.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-19.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-20.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 25.3 | 7.5 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-20.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 25.3 | 7.5 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-21.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 32.2 | 10 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-21.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 32.2 | 10 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-22.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-22.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-23.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-23.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-24.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-24.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-25.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 30.8 | 10 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-25.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 30.8 | 10 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-26.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-26.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-27.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-27.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-28.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-28.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-29.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 28 | 10 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-29.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 28 | 10 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-30.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-30.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-31.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-31.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-32.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-32.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-33.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-33.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-34.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 27 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-34.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 27 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-35.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 34 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-35.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 34 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-36.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-36.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-37.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-37.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-38.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-38.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-39.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 25.3 | 7.5 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-39.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 25.3 | 7.5 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-40.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 32.2 | 10 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-40.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 32.2 | 10 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-41.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-41.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-42.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-42.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-43.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-43.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-44.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 30.8 | 10 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-44.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 30.8 | 10 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-45.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-45.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-46.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-46.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-47.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-47.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-48.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 28 | 10 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-48.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 28 | 10 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-49.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-49.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-50.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-50.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-51.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-51.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-52.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-52.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-53.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 27 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-53.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 27 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-54.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 34 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-54.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 34 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-55.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-55.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-56.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-56.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-57.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-57.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-58.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 25.3 | 7.5 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-58.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 25.3 | 7.5 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-59.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 32.2 | 10 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-59.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 32.2 | 10 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-60.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-60.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-61.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-61.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-62.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-62.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 200 | 3 | - | 100 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-63.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 30.8 | 10 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-63.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 30.8 | 10 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-64.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-64.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-65.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-65.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-66.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-66.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 208 | 3 | - | 100 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-67.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 28 | 10 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-67.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 28 | 10 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-68.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-68.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-69.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-69.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-70.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-70.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-71.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-71.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 220-240 | 3 | - | 100 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-72.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 27 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-72.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 27 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-73.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 34 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-73.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 34 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-74.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-74.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-75.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-75.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-76.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-76.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS100R3C | 440-480 | 3 | - | 100 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-77.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-77 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-78.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-78 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-79.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-79 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-80.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-80 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-81.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-81 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-82.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-82 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-83.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-83 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-84.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-84 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-85.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-85 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-86.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-86 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-87.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-87 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-88.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-88 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-89.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-89 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-90.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-90.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-91.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-91.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-92.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-92.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-93.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-93.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-94.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-94.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-95.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-95.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-96.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-96.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-97.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-97.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-98.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-98.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-99.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-99.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-100.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-100.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-101.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-101.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-102.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-102.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-103.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-103.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-104.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-104.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-105.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-105.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-106.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-106.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-107.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-107.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-108.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-108.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-109.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-109.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-110.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-110.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-111.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-111.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-112.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-112.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-113.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-113.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-114.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-114.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-115.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-115.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-116.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-116.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-117.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-117.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-118.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-118.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 200 | 3 | 5 | 78.2 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-119.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-119.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-120.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-120.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-121.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-121.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 208 | 3 | 5 | 74.8 | 25 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-122.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-122.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-123.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-123.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-124.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-124.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-125.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-125.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 220-240 | 3 | 5 | 80 | 30 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-126.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-126.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-127.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-127.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-128.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5E100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA3-D-128.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59KN0*5G100 | 440-480 | 3 | 5 | 65 | 50 | [7 empty] | See Note 1, 2
Conditions of Use:
1. All of the specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches. Additional testing is not required when installed in an enclosure having the same or larger volume.
5. The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor controllers shall be considered in the end - product application
6. Connections between components are made with insulated wire that is sized per the table below:
| Freedom Starter Size | Minimum Wire Size from Breaker to Starter (AWG) | Minimum Length (inches)
| 3 (K Frame) | 4 | 18
| Note 1: | * notes the one or two digit code for the selection of the magnet coil voltage of the motor controller.
| Note 2: | Overload Relay: …5E… = Standard Feature Set; …5G… = Ground Fault Feature Set

## FdmC440STR Sz C4 Type D MCOLR
Eaton "Type D" Combination Motor Controllers | [18 empty] | Issue Date: 2014-01-21
Freedom Solid State Starters (C440)
Database Identification Number | Listed Combination Motor Controller Information |  | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings
| UL File Number | Volume / Section (Vol#).(Sec#) |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating | Enclosure Volume, cubic inches | Conditions of Use | Other References
FdmC440STR-NEMAC4-D-1.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-1.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5G140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-2.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-2.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5G140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-3.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-3.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5G140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-4.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-4.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5G140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-5.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-5.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5G140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-6.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-6.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5G140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-7.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-7.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5G140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-8.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-8.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5G140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-9.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-9.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5G140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-10.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-10.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5G140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-11.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-11.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5G140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-12.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-12.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5G140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-13.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-13.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5G140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-14.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-14.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5G140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-15.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-15.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5G140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-16.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-16.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5G140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-17.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-17.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5G140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-18.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-18.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5G140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-19.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-19.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5G140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-20.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-20.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5G140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-21.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-21.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5G140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-22.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-22.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5G140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-23.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-23.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5G140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-24.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-24.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5G140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-25.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-25.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5G140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-26.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-26.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5G140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-27.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-27.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5G140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-28.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-28.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5G140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-29.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-29.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5G140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-30.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-30.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5G140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-31.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-31.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5G140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-32.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-32.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5G140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-33.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-33.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5G140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-34.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-34.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5G140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-35.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-35.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5G140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-36.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-36.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5G140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-37.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-37.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5G140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-38.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-38.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5G140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-39.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-39.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5G140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-40.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-40.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5G140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-41.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-41.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5G140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-42.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-42.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5G140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-43.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-43.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5G140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-44.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-44.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-45.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-45.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-46.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-46.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-47.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-47.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-48.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-48.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-49.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-49.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-50.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-50.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-51.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-51.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-52.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-52.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-53.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-53.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-54.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-54.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-55.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-55.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-56.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-56.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-57.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-57.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-58.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-58.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-59.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-59.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-60.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-60.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-61.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-61.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-62.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-62.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-63.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-63.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-64.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-64.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-65.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-65.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-66.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-66.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-67.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-67.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-68.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-68.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-69.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-69.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-70.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-70.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-71.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-71.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-72.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-72.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-73.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-73.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-74.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-74.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-75.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-75.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-76.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-76.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-77.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-77.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-78.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-78.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-79.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-79.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-80.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-80.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-81.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-81.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-82.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-82.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-83.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-83.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-84.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-84.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-85.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-85.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-86.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-86.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-87.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-87.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-88.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMAC4-D-88.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59MN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
Conditions of Use:
1. All of the specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches. Additional testing is not required when installed in an enclosure having the same or larger volume.
5. The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor controllers shall be considered in the end - product application
6. Connections between components are made with insulated wire that is sized per the table below:
| Freedom Starter Size | Minimum Wire Size from Breaker to Starter (AWG) |  | Minimum Length (inches)
| 4 (M Frame) | 2 |  | 20
| Note 1: | * notes the one or two digit code for the selection of the magnet coil voltage of the motor controller.
| Note 2: | Overload Relay: …5E… = Standard Feature Set; …5G… = Ground Fault Feature Set

## FdmC440STR Sz 4 Type D MCOLR
Eaton "Type D" Combination Motor Controllers | [18 empty] | Issue Date: 2014-01-21
Freedom Solid State Starters (C440)
Database Identification Number | Listed Combination Motor Controller Information |  | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings
| UL File Number | Volume / Section (Vol#).(Sec#) |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating | Enclosure Volume, cubic inches | Conditions of Use | Other References
FdmC440STR-NEMA4-D-1.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-1.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5G140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-2.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-2.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5G140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-3.03 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-3.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5G140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-4.04 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-4.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5G140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-5.05 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-5.06 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5G140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-6.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-6.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5G140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-7.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-7.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5G140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-8.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-8.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5G140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-9.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-9.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5G140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-10.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-10.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5G140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-11.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-11.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5G140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-12.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-12.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5G140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-13.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-13.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5G140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-14.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-14.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5G140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-15.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-15.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5G140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-16.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-16.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5G140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-17.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-17.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5G140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-18.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-18.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5G140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-19.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-19.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5G140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-20.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-20.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5G140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-21.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-21.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5G140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-22.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-22.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5G140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-23.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-23.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5G140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-24.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-24.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5G140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-25.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-25.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5G140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-26.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-26.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5G140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-27.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-27.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5G140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-28.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-28.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5G140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-29.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-29.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5G140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-30.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-30.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5G140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-31.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-31.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5G140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-32.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-32.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5G140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-33.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-33.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5G140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-34.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-34.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5G140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-35.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-35.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5G140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-36.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-36.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5G140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-37.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-37.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5G140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-38.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-38.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5G140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-39.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-39.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5G140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-40.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-40.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5G140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-41.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-41.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5G140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-42.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-42.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5G140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-43.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-43.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5G140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-44.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-44.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-45.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-45.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-46.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-46.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-47.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-47.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-48.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-48.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-49.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-49.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-50.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-50.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-51.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-51.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-52.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-52.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-53.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-53.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-54.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-54.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-55.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-55.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-56.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-56.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-57.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-57.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-58.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-58.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-59.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-59.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-60.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-60.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-61.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-61.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-62.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-62.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-63.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-63.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-64.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-64.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-65.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-65.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-66.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-66.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | STR | Eaton | AN19NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-67.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-67.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 48.3 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-68.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-68.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 62.1 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-69.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-69.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 78.2 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-70.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-70.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 92 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-71.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-71.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 200 | 3 | - | 150 | - | 200 | 3 | 65 | 120 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 200 | 3 | 10 | 120 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-72.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-72.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 46.2 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-73.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-73.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 59.4 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-74.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-74.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 74.8 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-75.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-75.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 88 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-76.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-76.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 208 | 3 | - | 150 | - | 208 | 3 | 65 | 114 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 208 | 3 | 10 | 114 | 40 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-77.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-77.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 42 | 15 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-78.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-78.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 54 | 20 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-79.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-79.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 68 | 25 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-80.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-80.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 80 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-81.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-81.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 104 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-82.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-82.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 220-240 | 3 | - | 150 | - | 220-240 | 3 | 65 | 130 | 50 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 220-240 | 3 | 10 | 130 | 50 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-83.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-83.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 40 | 30 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-84.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-84.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 52 | 40 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-85.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-85.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 65 | 50 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-86.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-86.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 77 | 60 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-87.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-87.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 96 | 75 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-88.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
FdmC440STR-NEMA4-D-88.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCPS150T4C | 440-480 | 3 | - | 150 | - | 440-480 | 3 | 65 | 124 | 100 | 4811 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59NN0*5E140 | 440-480 | 3 | 10 | 124 | 100 | [7 empty] | See Note 1, 2
Conditions of Use:
1. All of the specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches. Additional testing is not required when installed in an enclosure having the same or larger volume.
5. The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor controllers shall be considered in the end - product application
6. Connections between components are made with insulated wire that is sized per the table below:
| Freedom Starter Size | Minimum Wire Size from Breaker to Starter (AWG) | Minimum Length (inches)
| 4 (N Frame) | 2 | 20
| Note 1: | * notes the one or two digit code for the selection of the magnet coil voltage of the motor controller.
| Note 2: | Overload Relay: …5E… = Standard Feature Set; …5G… = Ground Fault Feature Set

## FdmC440STR Sz 5 Type D MCOLR
Eaton "Type D" Combination Motor Controllers | [18 empty] | Issue Date: 2014-01-21
Freedom Solid State Starters (C440)
Database Identification Number | Listed Combination Motor Controller Information |  | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings
| UL File Number | Volume / Section (Vol#).(Sec#) |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating | Enclosure Volume, cubic inches | Conditions of Use | Other References
FdmC440STR-NEMA5-D-1.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-1.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-2.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-2.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-3.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-3.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-4.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-4.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-5.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-5.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-6.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-6.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-7.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-7.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-8.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-8.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-9.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-9.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-10.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-10.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-11.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-11.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-12.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-12.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-13.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-13.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-14.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-14.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-15.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-15.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-16.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-16.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-17.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-17.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-18.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-18.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-19.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-19.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-20.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-20.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-21.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-21.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-22.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-22.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-23.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-23.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-24.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-24.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-25.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-25.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-26.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-26.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-27.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-27.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-28.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-28.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250A5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-29.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-29.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-30.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-30.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-31.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-31.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-32.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-32.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-33.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-33.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-34.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-34.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-35.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-35.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-36.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-36.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-37.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-37.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-38.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-38.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-39.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-39.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-40.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-40.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-41.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-41.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-42.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-42.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-43.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-43.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-44.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-44.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-45.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-45.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-46.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-46.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-47.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-47.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-48.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-48.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-49.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-49.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-50.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-50.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-51.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-51.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-52.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-52.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-53.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-53.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-54.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-54.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-55.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-55.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-56.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-56.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250C5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-58.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-58.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-59.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-59.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-60.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-60.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-61.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-61.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-62.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-62.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-63.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-63.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-64.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-64.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-65.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-65.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-66.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-66.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-67.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-67.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-68.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-68.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-69.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-69.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-70.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-70.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-71.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-71.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-72.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-72.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-73.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-73.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-74.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-74.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-75.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-75.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-76.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-76.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-77.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-77.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-78.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-78.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-79.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-79.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-80.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-80.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-81.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-81.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-82.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-82.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-83.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-83.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-84.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-84.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-85.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-85.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250D5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-86.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-86.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-87.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-87.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-88.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-88.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-89.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-89.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-90.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-90.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-91.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-91.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-92.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-92.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-93.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-93.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-94.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-94.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-95.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-95.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-96.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-96.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-97.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-97.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-98.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-98.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-99.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-99.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-100.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-100.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-101.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-101.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-102.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-102.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-103.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-103.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-104.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-104.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-105.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-105.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-106.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-106.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-107.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-107.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-108.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-108.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-109.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-109.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-110.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-110.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-111.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-111.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-112.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-112.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-113.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-113.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250F5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-114.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-114.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-115.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-115.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-116.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-116.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-117.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-117.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-118.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-118.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-119.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-119.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-120.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-120.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-121.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-121.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-122.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-122.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-123.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-123.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-124.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-124.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-125.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-125.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-126.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-126.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-127.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-127.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-128.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-128.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-129.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-129.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-130.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-130.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-131.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-131.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-132.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-132.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-133.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-133.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-134.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-134.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-135.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-135.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-136.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-136.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-137.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-137.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-138.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-138.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 65 | 50 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-139.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-139.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-140.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-140.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-141.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-141.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250G5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-142.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-142.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-143.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-143.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-144.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-144.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-145.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-145.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-146.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-146.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-147.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-147.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-148.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-148.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-149.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-149.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-150.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-150.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-151.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-151.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-152.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-152.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-153.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-153.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-154.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-154.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-155.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-155.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 74.8 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-156.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-156.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-157.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-157.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-158.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-158.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 68 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-159.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-159.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-160.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-160.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-161.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-161.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-162.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-162.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-163.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-163.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-164.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-164.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-165.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-165.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 78.2 | 25 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-166.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-166.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-167.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-167.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-168.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-168.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-169.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-169.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-170.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-170.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 92 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-171.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-171.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-172.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-172.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-173.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-173.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-174.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-174.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-175.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-175.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-176.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-176.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-177.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-177.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-178.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-178.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 88 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-179.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-179.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-180.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-180.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-181.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-181.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-182.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-182.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-183.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-183.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 80 | 30 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-184.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-184.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-185.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-185.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-186.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-186.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-187.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-187.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-188.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-188.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-189.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-189.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-190.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-190.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-191.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-191.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250J5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-192.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-192.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-193.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-193.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-194.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-194.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-195.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-195.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 77 | 60 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-196.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-196.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-197.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-197.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250K5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-198.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-198.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-199.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-199.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 200 | 3 | - | 250 | - | 200 | 3 | 65 | 120 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 200 | 3 | 10 | 221 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-200.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-200.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-201.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-201.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 208 | 3 | - | 250 | - | 208 | 3 | 65 | 114 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 208 | 3 | 10 | 211 | 75 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-202.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-202.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-203.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-203.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-204.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-204.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-205.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-205.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-206.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-206.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-207.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-207.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-208.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-208.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 104 | 40 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-209.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-209.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250W5C | 220-240 | 3 | - | 250 | - | 220-240 | 3 | 65 | 130 | 50 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 220-240 | 3 | 10 | 248 | 100 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-210.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-210.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-211.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-211.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | STR | Eaton | AN19SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-212.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-212.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 96 | 75 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-213.01 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5E140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
FdmC440STR-NEMA5-D-213.02 | E176513 | Vol. 1 / Sec. 7 | D | ICB | Eaton | HMCP250L5C | 440-480 | 3 | - | 250 | - | 440-480 | 3 | 65 | 124 | 100 | 16646 | 1, 5, 6
|  |  |  | (REV) STR | Eaton | AN59SN0*5G140 | 440-480 | 3 | 10 | 240 | 200 | [7 empty] | See Note 1, 2, 3
Conditions of Use:
1. All of the specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches. Additional testing is not required when installed in an enclosure having the same or larger volume.
5. The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor controllers shall be considered in the end - product application
6. Connections between components are made with insulated wire that is sized per the table below:
| Freedom Starter Size | Minimum Wire Size from Breaker to Starter (AWG) |  | Minimum Length (inches)
| 5 (S Frame) | 250 MCM |  | 24
| Note 1: | * notes the one or two digit code for the selection of the magnet coil voltage of the motor controller.
| Note 2: | Overload Relay: …5E… = Standard Feature Set; …5G… = Ground Fault Feature Set