## S611 Softstarter Type C
Issue Date: 2016-10-27
Database Identification Number | Listed Combination Motor Controller Information |  | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings
| UL File Number | Volume / Section (Vol#).(Sec#) |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating | Enclosure Volume, cubic inches | Conditions of Use | Other References
RVSS611C0001 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3125 | 200 | 3 | 200 | 125 | 40 | 200 | 3 | 65 | 32.2 | 10 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 200 | 3 | 5 | 52 | 15
RVSS611C0002 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 200 | 3 | 200 | 150 | 50 | 200 | 3 | 65 | 48.3 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 200 | 3 | 5 | 52 | 15
RVSS611C0003 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3100 | 208 | 3 | 200 | 100 | 30 | 208 | 3 | 65 | 30.8 | 10 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 208 | 3 | 5 | 52 | 15
RVSS611C0004 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 208 | 3 | 200 | 150 | 50 | 208 | 3 | 65 | 46.2 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 208 | 3 | 5 | 52 | 15
RVSS611C0005 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3100 | 240 | 3 | 200 | 100 | 30 | 240 | 3 | 65 | 28 | 10 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 240 | 3 | 5 | 52 | 15
RVSS611C0006 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 240 | 3 | 200 | 150 | 50 | 240 | 3 | 65 | 42 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 240 | 3 | 5 | 52 | 15
RVSS611C0007 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3100 | 480 | 3 | 100 | 100 | 75 | 480 | 3 | 65 | 27 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 480 | 3 | 5 | 52 | 40
RVSS611C0008 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3125 | 480 | 3 | 100 | 125 | 100 | 480 | 3 | 65 | 34 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 480 | 3 | 5 | 52 | 40
RVSS611C0009 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 480 | 3 | 100 | 150 | 100 | 480 | 3 | 65 | 40 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 480 | 3 | 5 | 52 | 40
RVSS611C0010 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 480 | 3 | 100 | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 480 | 3 | 5 | 52 | 40
RVSS611C0011 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3100 | 600 | 3 | 35 | 100 | 100 | 600 | 3 | 5 | 27 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 600 | 3 | 5 | 52 | 50
RVSS611C0012 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3125 | 600 | 3 | 35 | 125 | 125 | 600 | 3 | 5 | 32 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 600 | 3 | 5 | 52 | 50
RVSS611C0013 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 600 | 3 | 35 | 150 | 150 | 600 | 3 | 5 | 41 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 600 | 3 | 5 | 52 | 50
RVSS611C0014 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 600 | 3 | 35 | 150 | 150 | 600 | 3 | 5 | 52 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 600 | 3 | 5 | 52 | 50
RVSS611C0015 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 200 | 3 | 200 | 150 | 50 | 200 | 3 | 65 | 48.3 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 200 | 3 | 10 | 65 | 20
RVSS611C0016 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 200 | 3 | 200 | 150 | 50 | 200 | 3 | 65 | 62.1 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 200 | 3 | 10 | 65 | 20
RVSS611C0017 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 208 | 3 | 200 | 150 | 50 | 208 | 3 | 65 | 46.2 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 208 | 3 | 10 | 65 | 20
RVSS611C0018 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 208 | 3 | 200 | 150 | 50 | 208 | 3 | 65 | 59.4 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 208 | 3 | 10 | 65 | 20
RVSS611C0019 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 240 | 3 | 200 | 150 | 50 | 240 | 3 | 65 | 42 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 240 | 3 | 10 | 65 | 20
RVSS611C0020 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 240 | 3 | 200 | 150 | 50 | 240 | 3 | 65 | 54 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 240 | 3 | 10 | 65 | 20
RVSS611C0021 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 480 | 3 | 100 | 150 | 100 | 480 | 3 | 65 | 40 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 480 | 3 | 10 | 65 | 50
RVSS611C0022 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 480 | 3 | 100 | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 480 | 3 | 10 | 65 | 50
RVSS611C0023 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 480 | 3 | 100 | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 480 | 3 | 10 | 65 | 50
RVSS611C0024 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 600 | 3 | 35 | 150 | 150 | 600 | 3 | 10 | 41 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 600 | 3 | 10 | 65 | 60
RVSS611C0025 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 600 | 3 | 35 | 150 | 150 | 600 | 3 | 10 | 52 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 600 | 3 | 10 | 65 | 60
RVSS611C0026 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 600 | 3 | 35 | 150 | 150 | 600 | 3 | 10 | 62 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 600 | 3 | 10 | 65 | 60
RVSS611C0027 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 200 | 3 | 200 | 150 | 50 | 200 | 3 | 65 | 48.3 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 200 | 3 | 10 | 77 | 20
RVSS611C0028 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 200 | 3 | 200 | 150 | 50 | 200 | 3 | 65 | 62.1 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 200 | 3 | 10 | 77 | 20
RVSS611C0029 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 208 | 3 | 200 | 150 | 50 | 208 | 3 | 65 | 46.2 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 208 | 3 | 10 | 77 | 25
RVSS611C0030 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 208 | 3 | 200 | 150 | 50 | 208 | 3 | 65 | 59.4 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 208 | 3 | 10 | 77 | 25
RVSS611C0031 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 208 | 3 | 200 | 150 | 50 | 208 | 3 | 65 | 74.8 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 208 | 3 | 10 | 77 | 25
RVSS611C0032 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 240 | 3 | 200 | 150 | 50 | 240 | 3 | 65 | 42 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 240 | 3 | 10 | 77 | 25
RVSS611C0033 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 240 | 3 | 200 | 150 | 50 | 240 | 3 | 65 | 54 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 240 | 3 | 10 | 77 | 25
RVSS611C0034 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 240 | 3 | 200 | 150 | 50 | 240 | 3 | 65 | 68 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 240 | 3 | 10 | 77 | 25
RVSS611C0035 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 480 | 3 | 100 | 150 | 100 | 480 | 3 | 65 | 40 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 480 | 3 | 10 | 77 | 60
RVSS611C0036 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 480 | 3 | 100 | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 480 | 3 | 10 | 77 | 60
RVSS611C0037 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 480 | 3 | 100 | 150 | 100 | 480 | 3 | 65 | 54 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 480 | 3 | 10 | 77 | 60
RVSS611C0038 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 480 | 3 | 100 | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 480 | 3 | 10 | 77 | 60
RVSS611C0039 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 600 | 3 | 35 | 150 | 150 | 600 | 3 | 10 | 51 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 600 | 3 | 10 | 77 | 75
RVSS611C0040 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 600 | 3 | 35 | 150 | 150 | 600 | 3 | 10 | 52 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 600 | 3 | 10 | 77 | 75
RVSS611C0041 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 600 | 3 | 35 | 150 | 150 | 600 | 3 | 10 | 62 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 600 | 3 | 10 | 77 | 75
RVSS611C0042 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | FDC3150 | 600 | 3 | 35 | 150 | 150 | 600 | 3 | 10 | 77 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 600 | 3 | 10 | 77 | 75
RVSS611C0043 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3175 | 200 | 3 | 100 | 175 | 50 | 200 | 3 | 65 | 48.3 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 200 | 3 | 10 | 99 | 30
RVSS611C0044 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3225 | 200 | 3 | 100 | 225 | 75 | 200 | 3 | 65 | 62.1 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 200 | 3 | 10 | 99 | 30
RVSS611C0045 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 200 | 3 | 100 | 250 | 75 | 200 | 3 | 65 | 78.2 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 200 | 3 | 10 | 99 | 30
RVSS611C0046 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 200 | 3 | 100 | 250 | 75 | 200 | 3 | 65 | 92 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 200 | 3 | 10 | 99 | 30
RVSS611C0047 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3225 | 208 | 3 | 100 | 225 | 75 | 208 | 3 | 65 | 59.4 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 208 | 3 | 10 | 99 | 30
RVSS611C0048 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 208 | 3 | 100 | 250 | 75 | 208 | 3 | 65 | 74.8 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 208 | 3 | 10 | 99 | 30
RVSS611C0049 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 208 | 3 | 100 | 250 | 75 | 208 | 3 | 65 | 88 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 208 | 3 | 10 | 99 | 30
RVSS611C0050 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3200 | 240 | 3 | 100 | 200 | 75 | 240 | 3 | 65 | 54 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 240 | 3 | 10 | 99 | 30
RVSS611C0051 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 240 | 3 | 100 | 250 | 100 | 240 | 3 | 65 | 68 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 240 | 3 | 10 | 99 | 30
RVSS611C0052 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 240 | 3 | 100 | 250 | 100 | 240 | 3 | 65 | 80 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 240 | 3 | 10 | 99 | 30
RVSS611C0053 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3200 | 480 | 3 | 65 | 200 | 150 | 480 | 3 | 65 | 52 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 480 | 3 | 10 | 99 | 75
RVSS611C0054 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 480 | 3 | 65 | 250 | 200 | 480 | 3 | 65 | 65 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 480 | 3 | 10 | 99 | 75
RVSS611C0055 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 480 | 3 | 65 | 250 | 200 | 480 | 3 | 65 | 77 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 480 | 3 | 10 | 99 | 75
RVSS611C0056 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 480 | 3 | 65 | 250 | 200 | 480 | 3 | 65 | 96 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 480 | 3 | 10 | 99 | 75
RVSS611C0057 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3200 | 600 | 3 | 25 | 200 | 200 | 600 | 3 | 10 | 52 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 600 | 3 | 10 | 99 | 100
RVSS611C0058 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3225 | 600 | 3 | 25 | 225 | 200 | 600 | 3 | 10 | 62 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 600 | 3 | 10 | 99 | 100
RVSS611C0059 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 600 | 3 | 25 | 250 | 250 | 600 | 3 | 10 | 77 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 600 | 3 | 10 | 99 | 100
RVSS611C0060 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 600 | 3 | 25 | 250 | 250 | 600 | 3 | 10 | 99 | 100 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 600 | 3 | 10 | 99 | 100
RVSS611C0061 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3175 | 200 | 3 | 200 | 175 | 50 | 200 | 3 | 65 | 48.3 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 200 | 3 | 10 | 99 | 30
RVSS611C0062 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3225 | 200 | 3 | 200 | 225 | 75 | 200 | 3 | 65 | 62.1 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 200 | 3 | 10 | 99 | 30
RVSS611C0063 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 200 | 3 | 200 | 250 | 75 | 200 | 3 | 65 | 78.2 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 200 | 3 | 10 | 99 | 30
RVSS611C0064 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 200 | 3 | 200 | 250 | 75 | 200 | 3 | 65 | 92 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 200 | 3 | 10 | 99 | 30
RVSS611C0065 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3225 | 208 | 3 | 200 | 225 | 75 | 208 | 3 | 65 | 59.4 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 208 | 3 | 10 | 99 | 30
RVSS611C0066 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 208 | 3 | 200 | 250 | 75 | 208 | 3 | 65 | 74.8 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 208 | 3 | 10 | 99 | 30
RVSS611C0067 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 208 | 3 | 200 | 250 | 75 | 208 | 3 | 65 | 88 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 208 | 3 | 10 | 99 | 30
RVSS611C0068 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3200 | 240 | 3 | 200 | 200 | 75 | 240 | 3 | 65 | 54 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 240 | 3 | 10 | 99 | 30
RVSS611C0069 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 240 | 3 | 200 | 250 | 100 | 240 | 3 | 65 | 68 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 240 | 3 | 10 | 99 | 30
RVSS611C0070 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 240 | 3 | 200 | 250 | 100 | 240 | 3 | 65 | 80 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 240 | 3 | 10 | 99 | 30
RVSS611C0071 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3200 | 480 | 3 | 100 | 200 | 150 | 480 | 3 | 65 | 52 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 480 | 3 | 10 | 99 | 75
RVSS611C0072 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 480 | 3 | 100 | 250 | 200 | 480 | 3 | 65 | 65 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 480 | 3 | 10 | 99 | 75
RVSS611C0073 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 480 | 3 | 100 | 250 | 200 | 480 | 3 | 65 | 77 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 480 | 3 | 10 | 99 | 75
RVSS611C0074 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 480 | 3 | 100 | 250 | 200 | 480 | 3 | 65 | 96 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 480 | 3 | 10 | 99 | 75
RVSS611C0075 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3200 | 600 | 3 | 35 | 200 | 200 | 600 | 3 | 10 | 52 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 600 | 3 | 10 | 99 | 100
RVSS611C0076 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3225 | 600 | 3 | 35 | 225 | 200 | 600 | 3 | 10 | 62 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 600 | 3 | 10 | 99 | 100
RVSS611C0077 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 600 | 3 | 35 | 250 | 250 | 600 | 3 | 10 | 77 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 600 | 3 | 10 | 99 | 100
RVSS611C0078 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 600 | 3 | 35 | 250 | 250 | 600 | 3 | 10 | 99 | 100 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 600 | 3 | 10 | 99 | 100
RVSS611C0079 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 200 | 3 | 100 | 250 | 75 | 200 | 3 | 65 | 78.2 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 200 | 3 | 10 | 125 | 40
RVSS611C0080 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 200 | 3 | 100 | 250 | 75 | 200 | 3 | 65 | 92 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 200 | 3 | 10 | 125 | 40
RVSS611C0081 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 200 | 3 | 100 | 250 | 75 | 200 | 3 | 65 | 120 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 200 | 3 | 10 | 125 | 40
RVSS611C0082 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 208 | 3 | 100 | 250 | 75 | 208 | 3 | 65 | 74.8 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 208 | 3 | 10 | 125 | 40
RVSS611C0083 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 208 | 3 | 100 | 250 | 75 | 208 | 3 | 65 | 88 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 208 | 3 | 10 | 125 | 40
RVSS611C0084 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 208 | 3 | 100 | 250 | 75 | 208 | 3 | 65 | 114 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 208 | 3 | 10 | 125 | 40
RVSS611C0085 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 240 | 3 | 100 | 250 | 100 | 240 | 3 | 65 | 68 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 240 | 3 | 10 | 125 | 40
RVSS611C0086 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 240 | 3 | 100 | 250 | 100 | 240 | 3 | 65 | 80 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 240 | 3 | 10 | 125 | 40
RVSS611C0087 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 240 | 3 | 100 | 250 | 100 | 240 | 3 | 65 | 104 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 240 | 3 | 10 | 125 | 40
RVSS611C0088 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 480 | 3 | 65 | 250 | 200 | 480 | 3 | 65 | 65 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 480 | 3 | 10 | 125 | 100
RVSS611C0089 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 480 | 3 | 65 | 250 | 200 | 480 | 3 | 65 | 77 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 480 | 3 | 10 | 125 | 100
RVSS611C0090 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 480 | 3 | 65 | 250 | 200 | 480 | 3 | 65 | 96 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 480 | 3 | 10 | 125 | 100
RVSS611C0091 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 480 | 3 | 65 | 250 | 200 | 480 | 3 | 65 | 124 | 100 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 480 | 3 | 10 | 125 | 100
RVSS611C0092 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 600 | 3 | 25 | 250 | 250 | 600 | 3 | 10 | 77 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 600 | 3 | 10 | 125 | 125
RVSS611C0093 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 600 | 3 | 25 | 250 | 250 | 600 | 3 | 10 | 99 | 100 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 600 | 3 | 10 | 125 | 125
RVSS611C0094 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 600 | 3 | 25 | 250 | 250 | 600 | 3 | 10 | 125 | 125 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 600 | 3 | 10 | 125 | 125
RVSS611C0095 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 200 | 3 | 200 | 250 | 75 | 200 | 3 | 65 | 78.2 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 200 | 3 | 10 | 125 | 40
RVSS611C0096 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 200 | 3 | 200 | 250 | 75 | 200 | 3 | 65 | 92 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 200 | 3 | 10 | 125 | 40
RVSS611C0097 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 200 | 3 | 200 | 250 | 75 | 200 | 3 | 65 | 120 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 200 | 3 | 10 | 125 | 40
RVSS611C0098 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 208 | 3 | 200 | 250 | 75 | 208 | 3 | 65 | 74.8 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 208 | 3 | 10 | 125 | 40
RVSS611C0099 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 208 | 3 | 200 | 250 | 75 | 208 | 3 | 65 | 88 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 208 | 3 | 10 | 125 | 40
RVSS611C0100 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 208 | 3 | 200 | 250 | 75 | 208 | 3 | 65 | 114 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 208 | 3 | 10 | 125 | 40
RVSS611C0101 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 240 | 3 | 200 | 250 | 100 | 240 | 3 | 65 | 68 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 240 | 3 | 10 | 125 | 40
RVSS611C0102 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 240 | 3 | 200 | 250 | 100 | 240 | 3 | 65 | 80 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 240 | 3 | 10 | 125 | 40
RVSS611C0103 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 240 | 3 | 200 | 250 | 100 | 240 | 3 | 65 | 104 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 240 | 3 | 10 | 125 | 40
RVSS611C0104 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 480 | 3 | 100 | 250 | 200 | 480 | 3 | 65 | 65 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 480 | 3 | 10 | 125 | 100
RVSS611C0105 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 480 | 3 | 100 | 250 | 200 | 480 | 3 | 65 | 77 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 480 | 3 | 10 | 125 | 100
RVSS611C0106 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 480 | 3 | 100 | 250 | 200 | 480 | 3 | 65 | 96 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 480 | 3 | 10 | 125 | 100
RVSS611C0107 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 480 | 3 | 100 | 250 | 200 | 480 | 3 | 65 | 124 | 100 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 480 | 3 | 10 | 125 | 100
RVSS611C0108 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 600 | 3 | 35 | 250 | 250 | 600 | 3 | 10 | 77 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 600 | 3 | 10 | 125 | 125
RVSS611C0109 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 600 | 3 | 35 | 250 | 250 | 600 | 3 | 10 | 99 | 100 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 600 | 3 | 10 | 125 | 125
RVSS611C0110 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 600 | 3 | 35 | 250 | 250 | 600 | 3 | 10 | 125 | 125 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 600 | 3 | 10 | 125 | 125
RVSS611C0111 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 200 | 3 | 100 | 250 | 75 | 200 | 3 | 65 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 200 | 3 | 10 | 156 | 50
RVSS611C0112 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 200 | 3 | 100 | 250 | 75 | 200 | 3 | 65 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 200 | 3 | 10 | 156 | 50
RVSS611C0113 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 200 | 3 | 100 | 250 | 75 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 200 | 3 | 10 | 156 | 50
RVSS611C0114 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 200 | 3 | 100 | 250 | 75 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 200 | 3 | 10 | 156 | 50
RVSS611C0115 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 208 | 3 | 100 | 250 | 75 | 208 | 3 | 65 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 208 | 3 | 10 | 156 | 50
RVSS611C0116 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 208 | 3 | 100 | 250 | 75 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 208 | 3 | 10 | 156 | 50
RVSS611C0117 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 208 | 3 | 100 | 250 | 75 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 208 | 3 | 10 | 156 | 50
RVSS611C0118 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 240 | 3 | 100 | 250 | 100 | 240 | 3 | 65 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 240 | 3 | 10 | 156 | 60
RVSS611C0119 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 240 | 3 | 100 | 250 | 100 | 240 | 3 | 65 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 240 | 3 | 10 | 156 | 60
RVSS611C0120 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 240 | 3 | 100 | 250 | 100 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 240 | 3 | 10 | 156 | 60
RVSS611C0121 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 240 | 3 | 100 | 250 | 100 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 240 | 3 | 10 | 156 | 60
RVSS611C0122 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 480 | 3 | 65 | 250 | 200 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 480 | 3 | 10 | 156 | 125
RVSS611C0123 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 480 | 3 | 65 | 250 | 200 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 480 | 3 | 10 | 156 | 125
RVSS611C0124 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 480 | 3 | 65 | 250 | 200 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 480 | 3 | 10 | 156 | 125
RVSS611C0125 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 600 | 3 | 25 | 250 | 250 | 600 | 3 | 10 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 600 | 3 | 10 | 156 | 150
RVSS611C0126 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 600 | 3 | 25 | 250 | 250 | 600 | 3 | 10 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 600 | 3 | 10 | 156 | 150
RVSS611C0127 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 600 | 3 | 25 | 250 | 250 | 600 | 3 | 10 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 600 | 3 | 10 | 156 | 150
RVSS611C0128 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 200 | 3 | 200 | 250 | 75 | 200 | 3 | 65 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 200 | 3 | 10 | 156 | 50
RVSS611C0129 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 200 | 3 | 200 | 250 | 75 | 200 | 3 | 65 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 200 | 3 | 10 | 156 | 50
RVSS611C0130 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 200 | 3 | 200 | 250 | 75 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 200 | 3 | 10 | 156 | 50
RVSS611C0131 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 200 | 3 | 200 | 250 | 75 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 200 | 3 | 10 | 156 | 50
RVSS611C0132 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 208 | 3 | 200 | 250 | 75 | 208 | 3 | 65 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 208 | 3 | 10 | 156 | 50
RVSS611C0133 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 208 | 3 | 200 | 250 | 75 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 208 | 3 | 10 | 156 | 50
RVSS611C0134 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 208 | 3 | 200 | 250 | 75 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 208 | 3 | 10 | 156 | 50
RVSS611C0135 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 240 | 3 | 200 | 250 | 100 | 240 | 3 | 65 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 240 | 3 | 10 | 156 | 60
RVSS611C0136 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 240 | 3 | 200 | 250 | 100 | 240 | 3 | 65 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 240 | 3 | 10 | 156 | 60
RVSS611C0137 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 240 | 3 | 200 | 250 | 100 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 240 | 3 | 10 | 156 | 60
RVSS611C0138 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 240 | 3 | 200 | 250 | 100 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 240 | 3 | 10 | 156 | 60
RVSS611C0139 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 480 | 3 | 100 | 250 | 200 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 480 | 3 | 10 | 156 | 125
RVSS611C0140 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 480 | 3 | 100 | 250 | 200 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 480 | 3 | 10 | 156 | 125
RVSS611C0141 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 480 | 3 | 100 | 250 | 200 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 480 | 3 | 10 | 156 | 125
RVSS611C0142 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 600 | 3 | 35 | 250 | 250 | 600 | 3 | 10 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 600 | 3 | 10 | 156 | 150
RVSS611C0143 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 600 | 3 | 35 | 250 | 250 | 600 | 3 | 10 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 600 | 3 | 10 | 156 | 150
RVSS611C0144 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 600 | 3 | 35 | 250 | 250 | 600 | 3 | 10 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 600 | 3 | 10 | 156 | 150
RVSS611C0145 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 200 | 3 | 100 | 250 | 75 | 200 | 3 | 65 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 200 | 3 | 10 | 180 | 60
RVSS611C0146 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 200 | 3 | 100 | 250 | 75 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 200 | 3 | 10 | 180 | 60
RVSS611C0147 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 200 | 3 | 100 | 250 | 75 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 200 | 3 | 10 | 180 | 60
RVSS611C0148 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 200 | 3 | 100 | 250 | 75 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 200 | 3 | 10 | 180 | 60
RVSS611C0149 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 208 | 3 | 100 | 250 | 75 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 208 | 3 | 10 | 180 | 60
RVSS611C0150 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 208 | 3 | 100 | 250 | 75 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 208 | 3 | 10 | 180 | 60
RVSS611C0151 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 208 | 3 | 100 | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 208 | 3 | 10 | 180 | 60
RVSS611C0152 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 240 | 3 | 100 | 250 | 100 | 240 | 3 | 65 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 240 | 3 | 10 | 180 | 60
RVSS611C0153 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 240 | 3 | 100 | 250 | 100 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 240 | 3 | 10 | 180 | 60
RVSS611C0154 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 240 | 3 | 100 | 250 | 100 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 240 | 3 | 10 | 180 | 60
RVSS611C0155 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 480 | 3 | 65 | 250 | 200 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 480 | 3 | 10 | 180 | 150
RVSS611C0156 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 480 | 3 | 65 | 250 | 200 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 480 | 3 | 10 | 180 | 150
RVSS611C0157 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 480 | 3 | 65 | 250 | 200 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 480 | 3 | 10 | 180 | 150
RVSS611C0158 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 480 | 3 | 65 | 250 | 200 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 480 | 3 | 10 | 180 | 150
RVSS611C0159 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 600 | 3 | 25 | 250 | 250 | 600 | 3 | 10 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 600 | 3 | 10 | 180 | 150
RVSS611C0160 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 600 | 3 | 25 | 250 | 250 | 600 | 3 | 10 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 600 | 3 | 10 | 180 | 150
RVSS611C0161 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HJD3250 | 600 | 3 | 25 | 250 | 250 | 600 | 3 | 10 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 600 | 3 | 10 | 180 | 150
RVSS611C0162 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 200 | 3 | 200 | 250 | 75 | 200 | 3 | 65 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 200 | 3 | 10 | 180 | 60
RVSS611C0163 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 200 | 3 | 200 | 250 | 75 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 200 | 3 | 10 | 180 | 60
RVSS611C0164 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 200 | 3 | 200 | 250 | 75 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 200 | 3 | 10 | 180 | 60
RVSS611C0165 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 200 | 3 | 200 | 250 | 75 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 200 | 3 | 10 | 180 | 60
RVSS611C0166 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 208 | 3 | 200 | 250 | 75 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 208 | 3 | 10 | 180 | 60
RVSS611C0167 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 208 | 3 | 200 | 250 | 75 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 208 | 3 | 10 | 180 | 60
RVSS611C0168 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 208 | 3 | 200 | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 208 | 3 | 10 | 180 | 60
RVSS611C0169 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 240 | 3 | 200 | 250 | 100 | 240 | 3 | 65 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 240 | 3 | 10 | 180 | 60
RVSS611C0170 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 240 | 3 | 200 | 250 | 100 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 240 | 3 | 10 | 180 | 60
RVSS611C0171 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 240 | 3 | 200 | 250 | 100 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 240 | 3 | 10 | 180 | 60
RVSS611C0172 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 480 | 3 | 100 | 250 | 200 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 480 | 3 | 10 | 180 | 150
RVSS611C0173 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 480 | 3 | 100 | 250 | 200 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 480 | 3 | 10 | 180 | 150
RVSS611C0174 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 480 | 3 | 100 | 250 | 200 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 480 | 3 | 10 | 180 | 150
RVSS611C0175 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 480 | 3 | 100 | 250 | 200 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 480 | 3 | 10 | 180 | 150
RVSS611C0176 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 600 | 3 | 35 | 250 | 250 | 600 | 3 | 10 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 600 | 3 | 10 | 180 | 150
RVSS611C0177 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 600 | 3 | 35 | 250 | 250 | 600 | 3 | 10 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 600 | 3 | 10 | 180 | 150
RVSS611C0178 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | JDC3250 | 600 | 3 | 35 | 250 | 250 | 600 | 3 | 10 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 600 | 3 | 10 | 180 | 150
RVSS611C0179 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3350 | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611C0180 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611C0181 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611C0182 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611C0183 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611C0184 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611C0185 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611C0186 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3350 | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611C0187 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611C0188 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611C0189 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3350 | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611C0190 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611C0191 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611C0192 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611C0193 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3350 | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 18 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611C0194 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 18 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611C0195 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611C0196 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611C0197 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3350 | 200 | 3 | 200 | 350 | 100 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611C0198 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 200 | 3 | 200 | 400 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611C0199 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 200 | 3 | 200 | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611C0200 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 200 | 3 | 200 | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611C0201 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 208 | 3 | 200 | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611C0202 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 208 | 3 | 200 | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611C0203 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 208 | 3 | 200 | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611C0204 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3350 | 240 | 3 | 200 | 350 | 125 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611C0205 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 240 | 3 | 200 | 400 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611C0206 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 240 | 3 | 200 | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611C0207 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3350 | 480 | 3 | 100 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611C0208 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 480 | 3 | 100 | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611C0209 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 480 | 3 | 100 | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611C0210 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 480 | 3 | 100 | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611C0211 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3350 | 600 | 3 | 65 | 350 | 350 | 600 | 3 | 18 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611C0212 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 600 | 3 | 65 | 400 | 400 | 600 | 3 | 18 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611C0213 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 600 | 3 | 65 | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611C0214 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 600 | 3 | 65 | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611C0215 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 18 | 177 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611C0216 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611C0217 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611C0218 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 18 | 169 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611C0219 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611C0220 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611C0221 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 18 | 154 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611C0222 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611C0223 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611C0224 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 18 | 156 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611C0225 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 18 | 180 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611C0226 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611C0227 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611C0228 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611C0229 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611C0230 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HKD3400 | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611C0231 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 200 | 3 | 200 | 400 | 125 | 200 | 3 | 18 | 177 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611C0232 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 200 | 3 | 200 | 400 | 125 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611C0233 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 200 | 3 | 200 | 400 | 125 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611C0234 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 208 | 3 | 200 | 400 | 150 | 208 | 3 | 18 | 169 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611C0235 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 208 | 3 | 200 | 400 | 150 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611C0236 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 208 | 3 | 200 | 400 | 150 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611C0237 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 240 | 3 | 200 | 400 | 150 | 240 | 3 | 18 | 154 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611C0238 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 240 | 3 | 200 | 400 | 150 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611C0239 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 240 | 3 | 200 | 400 | 150 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611C0240 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 480 | 3 | 100 | 400 | 300 | 480 | 3 | 18 | 156 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611C0241 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 480 | 3 | 100 | 400 | 300 | 480 | 3 | 18 | 180 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611C0242 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 480 | 3 | 100 | 400 | 300 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611C0243 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 480 | 3 | 100 | 400 | 300 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611C0244 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 600 | 3 | 65 | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611C0245 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 600 | 3 | 65 | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611C0246 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | KDC3400 | 600 | 3 | 65 | 400 | 400 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611C0247 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611C0248 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611C0249 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 18 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611C0250 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611C0251 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611C0252 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 18 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611C0253 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3500 | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611C0254 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611C0255 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 18 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611C0256 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 18 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611C0257 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611C0258 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611C0259 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 18 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611C0260 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3500 | 600 | 3 | 35 | 500 | 500 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611C0261 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611C0262 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611C0263 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 18 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611C0264 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 200 | 3 | 200 | 600 | 200 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611C0265 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 200 | 3 | 200 | 600 | 200 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611C0266 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 200 | 3 | 200 | 600 | 200 | 200 | 3 | 18 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611C0267 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 208 | 3 | 200 | 600 | 200 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611C0268 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 208 | 3 | 200 | 600 | 200 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611C0269 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 208 | 3 | 200 | 600 | 200 | 208 | 3 | 18 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611C0270 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3500 | 240 | 3 | 200 | 500 | 200 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611C0271 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 240 | 3 | 200 | 600 | 200 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611C0272 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 240 | 3 | 200 | 600 | 200 | 240 | 3 | 18 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611C0273 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 240 | 3 | 200 | 600 | 200 | 240 | 3 | 18 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611C0274 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 480 | 3 | 100 | 600 | 500 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611C0275 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 480 | 3 | 100 | 600 | 500 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611C0276 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 480 | 3 | 100 | 600 | 500 | 480 | 3 | 18 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611C0277 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3500 | 600 | 3 | 50 | 500 | 500 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611C0278 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 600 | 3 | 50 | 600 | 500 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611C0279 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 600 | 3 | 50 | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611C0280 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 600 | 3 | 50 | 600 | 500 | 600 | 3 | 18 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611C0281 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 30 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611C0282 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 30 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611C0283 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 30 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611C0284 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 30 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611C0285 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 30 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611C0286 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 30 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611C0287 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 30 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 240 | 3 | 30 | 414 | 150
RVSS611C0288 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 30 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 240 | 3 | 30 | 414 | 150
RVSS611C0289 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 30 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611C0290 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 30 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611C0291 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 30 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611C0292 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 30 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611C0293 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 30 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611C0294 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 30 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611C0295 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | HLD3600 | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 30 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611C0296 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 200 | 3 | 200 | 600 | 200 | 200 | 3 | 30 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611C0297 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 200 | 3 | 200 | 600 | 200 | 200 | 3 | 30 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611C0298 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 200 | 3 | 200 | 600 | 200 | 200 | 3 | 30 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611C0299 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 208 | 3 | 200 | 600 | 200 | 208 | 3 | 30 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611C0300 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 208 | 3 | 200 | 600 | 200 | 208 | 3 | 30 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611C0301 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 208 | 3 | 200 | 600 | 200 | 208 | 3 | 30 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611C0302 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 240 | 3 | 200 | 600 | 200 | 240 | 3 | 30 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 240 | 3 | 30 | 414 | 150
RVSS611C0303 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 240 | 3 | 200 | 600 | 200 | 240 | 3 | 30 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 240 | 3 | 30 | 414 | 150
RVSS611C0304 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 480 | 3 | 100 | 600 | 500 | 480 | 3 | 30 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611C0305 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 480 | 3 | 100 | 600 | 500 | 480 | 3 | 30 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611C0306 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 480 | 3 | 100 | 600 | 500 | 480 | 3 | 30 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611C0307 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 600 | 3 | 50 | 600 | 500 | 600 | 3 | 30 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611C0308 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 600 | 3 | 50 | 600 | 500 | 600 | 3 | 30 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611C0309 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 600 | 3 | 50 | 600 | 500 | 600 | 3 | 30 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611C0310 | E176513 | Vol. 1, Sec. 8 | C | CB | Eaton | LDC3600 | 600 | 3 | 50 | 600 | 500 | 600 | 3 | 30 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
Conditions of Aceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.

## S611 Softstarter Type D
Issue Date: 2016-10-27
Database Identification Number | Listed Combination Motor Controller Information |  | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings
| UL File Number | Volume / Section (Vol#).(Sec#) |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating | Enclosure Volume, cubic inches | Conditions of Use | Other References
RVSS611D0001 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 65 | 32.2 | 10 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 200 | 3 | 5 | 52 | 15
RVSS611D0002 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 65 | 48.3 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 200 | 3 | 5 | 52 | 15
RVSS611D0003 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 65 | 30.8 | 10 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 208 | 3 | 5 | 52 | 15
RVSS611D0004 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 65 | 46.2 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 208 | 3 | 5 | 52 | 15
RVSS611D0005 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 65 | 28 | 10 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 240 | 3 | 5 | 52 | 15
RVSS611D0006 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 65 | 42 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 240 | 3 | 5 | 52 | 15
RVSS611D0007 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 27 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 480 | 3 | 5 | 52 | 40
RVSS611D0008 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 34 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 480 | 3 | 5 | 52 | 40
RVSS611D0009 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 40 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 480 | 3 | 5 | 52 | 40
RVSS611D0010 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 52 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 480 | 3 | 5 | 52 | 40
RVSS611D0011 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 5 | 27 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 600 | 3 | 5 | 52 | 50
RVSS611D0012 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 5 | 32 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 600 | 3 | 5 | 52 | 50
RVSS611D0013 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 5 | 41 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 600 | 3 | 5 | 52 | 50
RVSS611D0014 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 5 | 52 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 600 | 3 | 5 | 52 | 50
RVSS611D0015 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 65 | 32.2 | 10 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 200 | 3 | 5 | 52 | 15
RVSS611D0016 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 65 | 48.3 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 200 | 3 | 5 | 52 | 15
RVSS611D0017 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 65 | 30.8 | 10 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 208 | 3 | 5 | 52 | 15
RVSS611D0018 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 65 | 46.2 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 208 | 3 | 5 | 52 | 15
RVSS611D0019 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 65 | 28 | 10 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 240 | 3 | 5 | 52 | 15
RVSS611D0020 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 65 | 42 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 240 | 3 | 5 | 52 | 15
RVSS611D0021 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 27 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 480 | 3 | 5 | 52 | 40
RVSS611D0022 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 34 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 480 | 3 | 5 | 52 | 40
RVSS611D0023 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 40 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 480 | 3 | 5 | 52 | 40
RVSS611D0024 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 52 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 480 | 3 | 5 | 52 | 40
RVSS611D0025 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 5 | 27 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 600 | 3 | 5 | 52 | 50
RVSS611D0026 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 5 | 32 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 600 | 3 | 5 | 52 | 50
RVSS611D0027 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 5 | 41 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 600 | 3 | 5 | 52 | 50
RVSS611D0028 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 5 | 52 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 600 | 3 | 5 | 52 | 50
RVSS611D0029 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 32.2 | 10 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 200 | 3 | 5 | 52 | 15
RVSS611D0030 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 48.3 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 200 | 3 | 5 | 52 | 15
RVSS611D0031 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 30.8 | 10 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 208 | 3 | 5 | 52 | 15
RVSS611D0032 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 46.2 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 208 | 3 | 5 | 52 | 15
RVSS611D0033 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 28 | 10 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 240 | 3 | 5 | 52 | 15
RVSS611D0034 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 42 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 240 | 3 | 5 | 52 | 15
RVSS611D0035 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 27 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 480 | 3 | 5 | 52 | 40
RVSS611D0036 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 34 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 480 | 3 | 5 | 52 | 40
RVSS611D0037 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 40 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 480 | 3 | 5 | 52 | 40
RVSS611D0038 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 52 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 480 | 3 | 5 | 52 | 40
RVSS611D0039 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 5 | 27 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 600 | 3 | 5 | 52 | 50
RVSS611D0040 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 5 | 32 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 600 | 3 | 5 | 52 | 50
RVSS611D0041 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 5 | 41 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 600 | 3 | 5 | 52 | 50
RVSS611D0042 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 5 | 52 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 600 | 3 | 5 | 52 | 50
RVSS611D0043 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 32.2 | 10 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 200 | 3 | 5 | 52 | 15
RVSS611D0044 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 48.3 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 200 | 3 | 5 | 52 | 15
RVSS611D0045 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 30.8 | 10 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 208 | 3 | 5 | 52 | 15
RVSS611D0046 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 46.2 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 208 | 3 | 5 | 52 | 15
RVSS611D0047 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 28 | 10 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 240 | 3 | 5 | 52 | 15
RVSS611D0048 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 42 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 240 | 3 | 5 | 52 | 15
RVSS611D0049 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 27 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 480 | 3 | 5 | 52 | 40
RVSS611D0050 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 34 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 480 | 3 | 5 | 52 | 40
RVSS611D0051 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 40 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 480 | 3 | 5 | 52 | 40
RVSS611D0052 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 52 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 480 | 3 | 5 | 52 | 40
RVSS611D0053 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 5 | 27 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 600 | 3 | 5 | 52 | 50
RVSS611D0054 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 5 | 32 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 600 | 3 | 5 | 52 | 50
RVSS611D0055 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 5 | 41 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 600 | 3 | 5 | 52 | 50
RVSS611D0056 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 5 | 52 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 600 | 3 | 5 | 52 | 50
RVSS611D0057 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 48.3 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 200 | 3 | 5 | 52 | 15
RVSS611D0058 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 46.2 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 208 | 3 | 5 | 52 | 15
RVSS611D0059 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 42 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 240 | 3 | 5 | 52 | 15
RVSS611D0060 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 40 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 480 | 3 | 5 | 52 | 40
RVSS611D0061 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 480 | 3 | 5 | 52 | 40
RVSS611D0062 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 5 | 41 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 600 | 3 | 5 | 52 | 50
RVSS611D0063 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 5 | 52 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A52N3S | 600 | 3 | 5 | 52 | 50
RVSS611D0064 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 65 | 48.3 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 200 | 3 | 10 | 65 | 20
RVSS611D0065 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 65 | 46.2 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 208 | 3 | 10 | 65 | 20
RVSS611D0066 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 240 | 3 | - | 70 | 20 | 240 | 3 | 65 | 42 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 240 | 3 | 10 | 65 | 20
RVSS611D0067 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 240 | 3 | - | 70 | 20 | 240 | 3 | 65 | 54 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 240 | 3 | 10 | 65 | 20
RVSS611D0068 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 40 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 480 | 3 | 10 | 65 | 50
RVSS611D0069 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 52 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 480 | 3 | 10 | 65 | 50
RVSS611D0070 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 10 | 41 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 600 | 3 | 10 | 65 | 60
RVSS611D0071 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 10 | 52 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 600 | 3 | 10 | 65 | 60
RVSS611D0072 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 65 | 48.3 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 200 | 3 | 10 | 65 | 20
RVSS611D0073 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 65 | 62.1 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 200 | 3 | 10 | 65 | 20
RVSS611D0074 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 65 | 46.2 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 208 | 3 | 10 | 65 | 20
RVSS611D0075 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 65 | 59.4 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 208 | 3 | 10 | 65 | 20
RVSS611D0076 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 20 | 240 | 3 | 65 | 42 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 240 | 3 | 10 | 65 | 20
RVSS611D0077 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 20 | 240 | 3 | 65 | 54 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 240 | 3 | 10 | 65 | 20
RVSS611D0078 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 40 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 480 | 3 | 10 | 65 | 50
RVSS611D0079 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 52 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 480 | 3 | 10 | 65 | 50
RVSS611D0080 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 65 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 480 | 3 | 10 | 65 | 50
RVSS611D0081 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 10 | 41 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 600 | 3 | 10 | 65 | 60
RVSS611D0082 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 10 | 52 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 600 | 3 | 10 | 65 | 60
RVSS611D0083 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 10 | 62 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 600 | 3 | 10 | 65 | 60
RVSS611D0084 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 48.3 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 200 | 3 | 10 | 65 | 20
RVSS611D0085 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 62.1 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 200 | 3 | 10 | 65 | 20
RVSS611D0086 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 46.2 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 208 | 3 | 10 | 65 | 20
RVSS611D0087 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 59.4 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 208 | 3 | 10 | 65 | 20
RVSS611D0088 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 42 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 240 | 3 | 10 | 65 | 20
RVSS611D0089 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 54 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 240 | 3 | 10 | 65 | 20
RVSS611D0090 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 40 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 480 | 3 | 10 | 65 | 50
RVSS611D0091 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 52 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 480 | 3 | 10 | 65 | 50
RVSS611D0092 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 65 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 480 | 3 | 10 | 65 | 50
RVSS611D0093 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 10 | 41 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 600 | 3 | 10 | 65 | 60
RVSS611D0094 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 10 | 52 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 600 | 3 | 10 | 65 | 60
RVSS611D0095 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 10 | 62 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 600 | 3 | 10 | 65 | 60
RVSS611D0096 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 48.3 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 200 | 3 | 10 | 65 | 20
RVSS611D0097 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 62.1 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 200 | 3 | 10 | 65 | 20
RVSS611D0098 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 46.2 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 208 | 3 | 10 | 65 | 20
RVSS611D0099 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 59.4 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 208 | 3 | 10 | 65 | 20
RVSS611D0100 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 42 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 240 | 3 | 10 | 65 | 20
RVSS611D0101 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 54 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 240 | 3 | 10 | 65 | 20
RVSS611D0102 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 40 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 480 | 3 | 10 | 65 | 50
RVSS611D0103 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 52 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 480 | 3 | 10 | 65 | 50
RVSS611D0104 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 65 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 480 | 3 | 10 | 65 | 50
RVSS611D0105 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 10 | 41 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 600 | 3 | 10 | 65 | 60
RVSS611D0106 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 10 | 52 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 600 | 3 | 10 | 65 | 60
RVSS611D0107 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 10 | 62 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 600 | 3 | 10 | 65 | 60
RVSS611D0108 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 48.3 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 200 | 3 | 10 | 65 | 20
RVSS611D0109 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 62.1 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 200 | 3 | 10 | 65 | 20
RVSS611D0110 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 46.2 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 208 | 3 | 10 | 65 | 20
RVSS611D0111 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 59.4 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 208 | 3 | 10 | 65 | 20
RVSS611D0112 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 42 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 240 | 3 | 10 | 65 | 20
RVSS611D0113 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 54 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 240 | 3 | 10 | 65 | 20
RVSS611D0114 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 40 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 480 | 3 | 10 | 65 | 50
RVSS611D0115 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 480 | 3 | 10 | 65 | 50
RVSS611D0116 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 480 | 3 | 10 | 65 | 50
RVSS611D0117 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 41 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 600 | 3 | 10 | 65 | 60
RVSS611D0118 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 52 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 600 | 3 | 10 | 65 | 60
RVSS611D0119 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 62 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 600 | 3 | 10 | 65 | 60
RVSS611D0120 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 62.1 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 200 | 3 | 10 | 65 | 20
RVSS611D0121 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 59.4 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 208 | 3 | 10 | 65 | 20
RVSS611D0122 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 480 | 3 | 10 | 65 | 50
RVSS611D0123 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 62 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A65N3S | 600 | 3 | 10 | 65 | 60
RVSS611D0124 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 65 | 48.3 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 200 | 3 | 10 | 77 | 20
RVSS611D0125 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 65 | 46.2 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 208 | 3 | 10 | 77 | 25
RVSS611D0126 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 65 | 42 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 240 | 3 | 10 | 77 | 25
RVSS611D0127 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 65 | 54 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 240 | 3 | 10 | 77 | 25
RVSS611D0128 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 40 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 480 | 3 | 10 | 77 | 60
RVSS611D0129 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 52 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 480 | 3 | 10 | 77 | 60
RVSS611D0130 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 54 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 480 | 3 | 10 | 77 | 60
RVSS611D0131 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 10 | 51 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 600 | 3 | 10 | 77 | 75
RVSS611D0132 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070J2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 10 | 52 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 600 | 3 | 10 | 77 | 75
RVSS611D0133 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 65 | 48.3 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 200 | 3 | 10 | 77 | 20
RVSS611D0134 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 65 | 62.1 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 200 | 3 | 10 | 77 | 20
RVSS611D0135 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 65 | 46.2 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 208 | 3 | 10 | 77 | 25
RVSS611D0136 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 65 | 59.4 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 208 | 3 | 10 | 77 | 25
RVSS611D0137 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 65 | 42 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 240 | 3 | 10 | 77 | 25
RVSS611D0138 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 65 | 54 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 240 | 3 | 10 | 77 | 25
RVSS611D0139 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 65 | 68 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 240 | 3 | 10 | 77 | 25
RVSS611D0140 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 40 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 480 | 3 | 10 | 77 | 60
RVSS611D0141 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 52 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 480 | 3 | 10 | 77 | 60
RVSS611D0142 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 54 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 480 | 3 | 10 | 77 | 60
RVSS611D0143 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 10 | 51 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 600 | 3 | 10 | 77 | 75
RVSS611D0144 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 10 | 52 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 600 | 3 | 10 | 77 | 75
RVSS611D0145 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 10 | 62 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 600 | 3 | 10 | 77 | 75
RVSS611D0146 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 48.3 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 200 | 3 | 10 | 77 | 20
RVSS611D0147 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 62.1 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 200 | 3 | 10 | 77 | 20
RVSS611D0148 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 46.2 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 208 | 3 | 10 | 77 | 25
RVSS611D0149 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 59.4 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 208 | 3 | 10 | 77 | 25
RVSS611D0150 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 74.8 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 208 | 3 | 10 | 77 | 25
RVSS611D0151 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 42 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 240 | 3 | 10 | 77 | 25
RVSS611D0152 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 54 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 240 | 3 | 10 | 77 | 25
RVSS611D0153 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 68 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 240 | 3 | 10 | 77 | 25
RVSS611D0154 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 40 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 480 | 3 | 10 | 77 | 60
RVSS611D0155 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 52 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 480 | 3 | 10 | 77 | 60
RVSS611D0156 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 54 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 480 | 3 | 10 | 77 | 60
RVSS611D0157 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 77 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 480 | 3 | 10 | 77 | 60
RVSS611D0158 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 10 | 51 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 600 | 3 | 10 | 77 | 75
RVSS611D0159 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 10 | 52 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 600 | 3 | 10 | 77 | 75
RVSS611D0160 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 10 | 62 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 600 | 3 | 10 | 77 | 75
RVSS611D0161 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100L3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 10 | 77 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 600 | 3 | 10 | 77 | 75
RVSS611D0162 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 48.3 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 200 | 3 | 10 | 77 | 20
RVSS611D0163 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 62.1 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 200 | 3 | 10 | 77 | 20
RVSS611D0164 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 46.2 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 208 | 3 | 10 | 77 | 25
RVSS611D0165 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 59.4 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 208 | 3 | 10 | 77 | 25
RVSS611D0166 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 74.8 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 208 | 3 | 10 | 77 | 25
RVSS611D0167 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 42 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 240 | 3 | 10 | 77 | 25
RVSS611D0168 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 54 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 240 | 3 | 10 | 77 | 25
RVSS611D0169 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 68 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 240 | 3 | 10 | 77 | 25
RVSS611D0170 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 40 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 480 | 3 | 10 | 77 | 60
RVSS611D0171 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 52 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 480 | 3 | 10 | 77 | 60
RVSS611D0172 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 54 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 480 | 3 | 10 | 77 | 60
RVSS611D0173 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 77 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 480 | 3 | 10 | 77 | 60
RVSS611D0174 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 10 | 51 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 600 | 3 | 10 | 77 | 75
RVSS611D0175 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 10 | 52 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 600 | 3 | 10 | 77 | 75
RVSS611D0176 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 10 | 62 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 600 | 3 | 10 | 77 | 75
RVSS611D0177 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 10 | 77 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 600 | 3 | 10 | 77 | 75
RVSS611D0178 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 48.3 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 200 | 3 | 10 | 77 | 20
RVSS611D0179 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 62.1 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 200 | 3 | 10 | 77 | 20
RVSS611D0180 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 46.2 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 208 | 3 | 10 | 77 | 25
RVSS611D0181 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 59.4 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 208 | 3 | 10 | 77 | 25
RVSS611D0182 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 74.8 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 208 | 3 | 10 | 77 | 25
RVSS611D0183 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 42 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 240 | 3 | 10 | 77 | 25
RVSS611D0184 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 54 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 240 | 3 | 10 | 77 | 25
RVSS611D0185 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 68 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 240 | 3 | 10 | 77 | 25
RVSS611D0186 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 40 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 480 | 3 | 10 | 77 | 60
RVSS611D0187 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 480 | 3 | 10 | 77 | 60
RVSS611D0188 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 54 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 480 | 3 | 10 | 77 | 60
RVSS611D0189 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 480 | 3 | 10 | 77 | 60
RVSS611D0190 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 51 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 600 | 3 | 10 | 77 | 75
RVSS611D0191 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 52 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 600 | 3 | 10 | 77 | 75
RVSS611D0192 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 62 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 600 | 3 | 10 | 77 | 75
RVSS611D0193 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 77 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 600 | 3 | 10 | 77 | 75
RVSS611D0194 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 62.1 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 200 | 3 | 10 | 77 | 20
RVSS611D0195 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 59.4 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 208 | 3 | 10 | 77 | 25
RVSS611D0196 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 74.8 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 208 | 3 | 10 | 77 | 25
RVSS611D0197 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 68 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 240 | 3 | 10 | 77 | 25
RVSS611D0198 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 480 | 3 | 10 | 77 | 60
RVSS611D0199 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 62 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 600 | 3 | 10 | 77 | 75
RVSS611D0200 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 77 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611A77N3S | 600 | 3 | 10 | 77 | 75
RVSS611D0201 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 48.3 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 200 | 3 | 10 | 99 | 30
RVSS611D0202 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 62.1 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 200 | 3 | 10 | 99 | 30
RVSS611D0203 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 78.2 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 200 | 3 | 10 | 99 | 30
RVSS611D0204 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 92 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 200 | 3 | 10 | 99 | 30
RVSS611D0205 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 59.4 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 208 | 3 | 10 | 99 | 30
RVSS611D0206 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 74.8 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 208 | 3 | 10 | 99 | 30
RVSS611D0207 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 88 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 208 | 3 | 10 | 99 | 30
RVSS611D0208 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 54 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 240 | 3 | 10 | 99 | 30
RVSS611D0209 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 68 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 240 | 3 | 10 | 99 | 30
RVSS611D0210 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 80 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 240 | 3 | 10 | 99 | 30
RVSS611D0211 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 480 | 3 | 10 | 99 | 75
RVSS611D0212 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 480 | 3 | 10 | 99 | 75
RVSS611D0213 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 480 | 3 | 10 | 99 | 75
RVSS611D0214 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 480 | 3 | 10 | 99 | 75
RVSS611D0215 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 52 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 600 | 3 | 10 | 99 | 100
RVSS611D0216 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 62 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 600 | 3 | 10 | 99 | 100
RVSS611D0217 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 77 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 600 | 3 | 10 | 99 | 100
RVSS611D0218 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 99 | 100 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 600 | 3 | 10 | 99 | 100
RVSS611D0219 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 62.1 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 200 | 3 | 10 | 99 | 30
RVSS611D0220 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 78.2 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 200 | 3 | 10 | 99 | 30
RVSS611D0221 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 92 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 200 | 3 | 10 | 99 | 30
RVSS611D0222 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 59.4 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 208 | 3 | 10 | 99 | 30
RVSS611D0223 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 74.8 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 208 | 3 | 10 | 99 | 30
RVSS611D0224 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 88 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 208 | 3 | 10 | 99 | 30
RVSS611D0225 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 68 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 240 | 3 | 10 | 99 | 30
RVSS611D0226 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 80 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 240 | 3 | 10 | 99 | 30
RVSS611D0227 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 480 | 3 | 10 | 99 | 75
RVSS611D0228 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 480 | 3 | 10 | 99 | 75
RVSS611D0229 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 480 | 3 | 10 | 99 | 75
RVSS611D0230 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 62 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 600 | 3 | 10 | 99 | 100
RVSS611D0231 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 77 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 600 | 3 | 10 | 99 | 100
RVSS611D0232 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 99 | 100 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 600 | 3 | 10 | 99 | 100
RVSS611D0233 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 48.3 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 200 | 3 | 10 | 99 | 30
RVSS611D0234 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 62.1 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 200 | 3 | 10 | 99 | 30
RVSS611D0235 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 78.2 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 200 | 3 | 10 | 99 | 30
RVSS611D0236 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 92 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 200 | 3 | 10 | 99 | 30
RVSS611D0237 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 59.4 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 208 | 3 | 10 | 99 | 30
RVSS611D0238 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 74.8 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 208 | 3 | 10 | 99 | 30
RVSS611D0239 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 88 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 208 | 3 | 10 | 99 | 30
RVSS611D0240 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 54 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 240 | 3 | 10 | 99 | 30
RVSS611D0241 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 68 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 240 | 3 | 10 | 99 | 30
RVSS611D0242 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 80 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 240 | 3 | 10 | 99 | 30
RVSS611D0243 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 52 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 480 | 3 | 10 | 99 | 75
RVSS611D0244 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 65 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 480 | 3 | 10 | 99 | 75
RVSS611D0245 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 77 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 480 | 3 | 10 | 99 | 75
RVSS611D0246 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 96 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 480 | 3 | 10 | 99 | 75
RVSS611D0247 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 10 | 52 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 600 | 3 | 10 | 99 | 100
RVSS611D0248 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 10 | 62 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 600 | 3 | 10 | 99 | 100
RVSS611D0249 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 10 | 77 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 600 | 3 | 10 | 99 | 100
RVSS611D0250 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 10 | 99 | 100 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 600 | 3 | 10 | 99 | 100
RVSS611D0251 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 48.3 | 15 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 200 | 3 | 10 | 99 | 30
RVSS611D0252 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 62.1 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 200 | 3 | 10 | 99 | 30
RVSS611D0253 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 78.2 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 200 | 3 | 10 | 99 | 30
RVSS611D0254 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 92 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 200 | 3 | 10 | 99 | 30
RVSS611D0255 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 59.4 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 208 | 3 | 10 | 99 | 30
RVSS611D0256 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 74.8 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 208 | 3 | 10 | 99 | 30
RVSS611D0257 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 88 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 208 | 3 | 10 | 99 | 30
RVSS611D0258 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 54 | 20 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 240 | 3 | 10 | 99 | 30
RVSS611D0259 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 68 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 240 | 3 | 10 | 99 | 30
RVSS611D0260 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 80 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 240 | 3 | 10 | 99 | 30
RVSS611D0261 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 52 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 480 | 3 | 10 | 99 | 75
RVSS611D0262 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 65 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 480 | 3 | 10 | 99 | 75
RVSS611D0263 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 77 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 480 | 3 | 10 | 99 | 75
RVSS611D0264 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 96 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 480 | 3 | 10 | 99 | 75
RVSS611D0265 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 10 | 52 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 600 | 3 | 10 | 99 | 100
RVSS611D0266 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 10 | 62 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 600 | 3 | 10 | 99 | 100
RVSS611D0267 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 10 | 77 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 600 | 3 | 10 | 99 | 100
RVSS611D0268 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 10 | 99 | 100 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B99N3S | 600 | 3 | 10 | 99 | 100
RVSS611D0269 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 78.2 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 200 | 3 | 10 | 125 | 40
RVSS611D0270 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 92 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 200 | 3 | 10 | 125 | 40
RVSS611D0271 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 120 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 200 | 3 | 10 | 125 | 40
RVSS611D0272 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 74.8 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 208 | 3 | 10 | 125 | 40
RVSS611D0273 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 88 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 208 | 3 | 10 | 125 | 40
RVSS611D0274 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 114 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 208 | 3 | 10 | 125 | 40
RVSS611D0275 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 68 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 240 | 3 | 10 | 125 | 40
RVSS611D0276 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 80 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 240 | 3 | 10 | 125 | 40
RVSS611D0277 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 104 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 240 | 3 | 10 | 125 | 40
RVSS611D0278 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 480 | 3 | 10 | 125 | 100
RVSS611D0279 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 480 | 3 | 10 | 125 | 100
RVSS611D0280 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 480 | 3 | 10 | 125 | 100
RVSS611D0281 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 124 | 100 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 480 | 3 | 10 | 125 | 100
RVSS611D0282 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 77 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 600 | 3 | 10 | 125 | 125
RVSS611D0283 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 99 | 100 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 600 | 3 | 10 | 125 | 125
RVSS611D0284 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 125 | 125 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 600 | 3 | 10 | 125 | 125
RVSS611D0285 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 78.2 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 200 | 3 | 10 | 125 | 40
RVSS611D0286 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 92 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 200 | 3 | 10 | 125 | 40
RVSS611D0287 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 120 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 200 | 3 | 10 | 125 | 40
RVSS611D0288 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 74.8 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 208 | 3 | 10 | 125 | 40
RVSS611D0289 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 88 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 208 | 3 | 10 | 125 | 40
RVSS611D0290 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 114 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 208 | 3 | 10 | 125 | 40
RVSS611D0291 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 68 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 240 | 3 | 10 | 125 | 40
RVSS611D0292 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 80 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 240 | 3 | 10 | 125 | 40
RVSS611D0293 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 104 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 240 | 3 | 10 | 125 | 40
RVSS611D0294 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 480 | 3 | 10 | 125 | 100
RVSS611D0295 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 480 | 3 | 10 | 125 | 100
RVSS611D0296 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 480 | 3 | 10 | 125 | 100
RVSS611D0297 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 124 | 100 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 480 | 3 | 10 | 125 | 100
RVSS611D0298 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 77 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 600 | 3 | 10 | 125 | 125
RVSS611D0299 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 99 | 100 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 600 | 3 | 10 | 125 | 125
RVSS611D0300 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 125 | 125 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 600 | 3 | 10 | 125 | 125
RVSS611D0301 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 78.2 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 200 | 3 | 10 | 125 | 40
RVSS611D0302 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 92 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 200 | 3 | 10 | 125 | 40
RVSS611D0303 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 120 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 200 | 3 | 10 | 125 | 40
RVSS611D0304 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 74.8 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 208 | 3 | 10 | 125 | 40
RVSS611D0305 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 88 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 208 | 3 | 10 | 125 | 40
RVSS611D0306 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 114 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 208 | 3 | 10 | 125 | 40
RVSS611D0307 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 68 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 240 | 3 | 10 | 125 | 40
RVSS611D0308 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 80 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 240 | 3 | 10 | 125 | 40
RVSS611D0309 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 104 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 240 | 3 | 10 | 125 | 40
RVSS611D0310 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 65 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 480 | 3 | 10 | 125 | 100
RVSS611D0311 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 77 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 480 | 3 | 10 | 125 | 100
RVSS611D0312 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 96 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 480 | 3 | 10 | 125 | 100
RVSS611D0313 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 124 | 100 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 480 | 3 | 10 | 125 | 100
RVSS611D0314 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 10 | 77 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 600 | 3 | 10 | 125 | 125
RVSS611D0315 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 10 | 99 | 100 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 600 | 3 | 10 | 125 | 125
RVSS611D0316 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 10 | 125 | 125 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 600 | 3 | 10 | 125 | 125
RVSS611D0317 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 78.2 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 200 | 3 | 10 | 125 | 40
RVSS611D0318 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 92 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 200 | 3 | 10 | 125 | 40
RVSS611D0319 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 120 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 200 | 3 | 10 | 125 | 40
RVSS611D0320 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 74.8 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 208 | 3 | 10 | 125 | 40
RVSS611D0321 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 88 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 208 | 3 | 10 | 125 | 40
RVSS611D0322 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 114 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 208 | 3 | 10 | 125 | 40
RVSS611D0323 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 68 | 25 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 240 | 3 | 10 | 125 | 40
RVSS611D0324 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 80 | 30 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 240 | 3 | 10 | 125 | 40
RVSS611D0325 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 104 | 40 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 240 | 3 | 10 | 125 | 40
RVSS611D0326 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 65 | 50 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 480 | 3 | 10 | 125 | 100
RVSS611D0327 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 77 | 60 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 480 | 3 | 10 | 125 | 100
RVSS611D0328 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 96 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 480 | 3 | 10 | 125 | 100
RVSS611D0329 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 124 | 100 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 480 | 3 | 10 | 125 | 100
RVSS611D0330 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 10 | 77 | 75 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 600 | 3 | 10 | 125 | 125
RVSS611D0331 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 10 | 99 | 100 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 600 | 3 | 10 | 125 | 125
RVSS611D0332 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 10 | 125 | 125 | 8752 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611B125N3S | 600 | 3 | 10 | 125 | 125
RVSS611D0333 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 200 | 3 | 10 | 156 | 50
RVSS611D0334 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 200 | 3 | 10 | 156 | 50
RVSS611D0335 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 200 | 3 | 10 | 156 | 50
RVSS611D0336 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 200 | 3 | 10 | 156 | 50
RVSS611D0337 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 208 | 3 | 10 | 156 | 50
RVSS611D0338 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 208 | 3 | 10 | 156 | 50
RVSS611D0339 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 208 | 3 | 10 | 156 | 50
RVSS611D0340 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 240 | 3 | 10 | 156 | 60
RVSS611D0341 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 240 | 3 | 10 | 156 | 60
RVSS611D0342 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 240 | 3 | 10 | 156 | 60
RVSS611D0343 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 480 | 3 | 10 | 156 | 125
RVSS611D0344 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 480 | 3 | 10 | 156 | 125
RVSS611D0345 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 600 | 3 | 10 | 156 | 150
RVSS611D0346 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 600 | 3 | 10 | 156 | 150
RVSS611D0347 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 600 | 3 | 10 | 156 | 150
RVSS611D0348 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 200 | 3 | 10 | 156 | 50
RVSS611D0349 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 200 | 3 | 10 | 156 | 50
RVSS611D0350 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 200 | 3 | 10 | 156 | 50
RVSS611D0351 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 200 | 3 | 10 | 156 | 50
RVSS611D0352 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 208 | 3 | 10 | 156 | 50
RVSS611D0353 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 208 | 3 | 10 | 156 | 50
RVSS611D0354 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 208 | 3 | 10 | 156 | 50
RVSS611D0355 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 240 | 3 | 10 | 156 | 60
RVSS611D0356 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 240 | 3 | 10 | 156 | 60
RVSS611D0357 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 240 | 3 | 10 | 156 | 60
RVSS611D0358 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 480 | 3 | 10 | 156 | 125
RVSS611D0359 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 480 | 3 | 10 | 156 | 125
RVSS611D0360 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 600 | 3 | 10 | 156 | 150
RVSS611D0361 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 600 | 3 | 10 | 156 | 150
RVSS611D0362 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 600 | 3 | 10 | 156 | 150
RVSS611D0363 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 200 | 3 | 10 | 156 | 50
RVSS611D0364 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 200 | 3 | 10 | 156 | 50
RVSS611D0365 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 200 | 3 | 10 | 156 | 50
RVSS611D0366 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 200 | 3 | 10 | 156 | 50
RVSS611D0367 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 208 | 3 | 10 | 156 | 50
RVSS611D0368 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 208 | 3 | 10 | 156 | 50
RVSS611D0369 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 208 | 3 | 10 | 156 | 50
RVSS611D0370 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 65 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 240 | 3 | 10 | 156 | 60
RVSS611D0371 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 65 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 240 | 3 | 10 | 156 | 60
RVSS611D0372 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 240 | 3 | 10 | 156 | 60
RVSS611D0373 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 240 | 3 | 10 | 156 | 60
RVSS611D0374 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 480 | 3 | 10 | 156 | 125
RVSS611D0375 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 480 | 3 | 10 | 156 | 125
RVSS611D0376 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 480 | 3 | 10 | 156 | 125
RVSS611D0377 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 10 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 600 | 3 | 10 | 156 | 150
RVSS611D0378 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 10 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 600 | 3 | 10 | 156 | 150
RVSS611D0379 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 10 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 600 | 3 | 10 | 156 | 150
RVSS611D0380 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 200 | 3 | 10 | 156 | 50
RVSS611D0381 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 200 | 3 | 10 | 156 | 50
RVSS611D0382 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 200 | 3 | 10 | 156 | 50
RVSS611D0383 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 200 | 3 | 10 | 156 | 50
RVSS611D0384 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 208 | 3 | 10 | 156 | 50
RVSS611D0385 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 208 | 3 | 10 | 156 | 50
RVSS611D0386 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 208 | 3 | 10 | 156 | 50
RVSS611D0387 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 65 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 240 | 3 | 10 | 156 | 60
RVSS611D0388 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 65 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 240 | 3 | 10 | 156 | 60
RVSS611D0389 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 240 | 3 | 10 | 156 | 60
RVSS611D0390 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 240 | 3 | 10 | 156 | 60
RVSS611D0391 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 480 | 3 | 10 | 156 | 125
RVSS611D0392 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 480 | 3 | 10 | 156 | 125
RVSS611D0393 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 480 | 3 | 10 | 156 | 125
RVSS611D0394 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 10 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 600 | 3 | 10 | 156 | 150
RVSS611D0395 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 10 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 600 | 3 | 10 | 156 | 150
RVSS611D0396 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 10 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C156N3S | 600 | 3 | 10 | 156 | 150
RVSS611D0397 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 200 | 3 | 10 | 180 | 60
RVSS611D0398 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 200 | 3 | 10 | 180 | 60
RVSS611D0399 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 200 | 3 | 10 | 180 | 60
RVSS611D0400 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 208 | 3 | 10 | 180 | 60
RVSS611D0401 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 208 | 3 | 10 | 180 | 60
RVSS611D0402 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 240 | 3 | 10 | 180 | 60
RVSS611D0403 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 240 | 3 | 10 | 180 | 60
RVSS611D0404 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 480 | 3 | 10 | 180 | 150
RVSS611D0405 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 480 | 3 | 10 | 180 | 150
RVSS611D0406 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 600 | 3 | 10 | 180 | 150
RVSS611D0407 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 600 | 3 | 10 | 180 | 150
RVSS611D0408 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 600 | 3 | 10 | 180 | 150
RVSS611D0409 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 200 | 3 | 10 | 180 | 60
RVSS611D0410 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 200 | 3 | 10 | 180 | 60
RVSS611D0411 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 200 | 3 | 10 | 180 | 60
RVSS611D0412 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 208 | 3 | 10 | 180 | 60
RVSS611D0413 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 208 | 3 | 10 | 180 | 60
RVSS611D0414 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 240 | 3 | 10 | 180 | 60
RVSS611D0415 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 240 | 3 | 10 | 180 | 60
RVSS611D0416 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 480 | 3 | 10 | 180 | 150
RVSS611D0417 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 480 | 3 | 10 | 180 | 150
RVSS611D0418 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 600 | 3 | 10 | 180 | 150
RVSS611D0419 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 600 | 3 | 10 | 180 | 150
RVSS611D0420 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP150U4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 10 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 600 | 3 | 10 | 180 | 150
RVSS611D0421 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 200 | 3 | 10 | 180 | 60
RVSS611D0422 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 200 | 3 | 10 | 180 | 60
RVSS611D0423 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 200 | 3 | 10 | 180 | 60
RVSS611D0424 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 208 | 3 | 10 | 180 | 60
RVSS611D0425 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 208 | 3 | 10 | 180 | 60
RVSS611D0426 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 208 | 3 | 10 | 180 | 60
RVSS611D0427 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 240 | 3 | 10 | 180 | 60
RVSS611D0428 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 240 | 3 | 10 | 180 | 60
RVSS611D0429 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 240 | 3 | 10 | 180 | 60
RVSS611D0430 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 480 | 3 | 10 | 180 | 150
RVSS611D0431 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 480 | 3 | 10 | 180 | 150
RVSS611D0432 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 480 | 3 | 10 | 180 | 150
RVSS611D0433 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 10 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 600 | 3 | 10 | 180 | 150
RVSS611D0434 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 10 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 600 | 3 | 10 | 180 | 150
RVSS611D0435 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 10 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 600 | 3 | 10 | 180 | 150
RVSS611D0436 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 200 | 3 | 10 | 180 | 60
RVSS611D0437 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 200 | 3 | 10 | 180 | 60
RVSS611D0438 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 200 | 3 | 10 | 180 | 60
RVSS611D0439 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 200 | 3 | 10 | 180 | 60
RVSS611D0440 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 208 | 3 | 10 | 180 | 60
RVSS611D0441 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 208 | 3 | 10 | 180 | 60
RVSS611D0442 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 208 | 3 | 10 | 180 | 60
RVSS611D0443 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 240 | 3 | 10 | 180 | 60
RVSS611D0444 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 240 | 3 | 10 | 180 | 60
RVSS611D0445 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 240 | 3 | 10 | 180 | 60
RVSS611D0446 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 480 | 3 | 10 | 180 | 150
RVSS611D0447 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 480 | 3 | 10 | 180 | 150
RVSS611D0448 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 480 | 3 | 10 | 180 | 150
RVSS611D0449 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 480 | 3 | 10 | 180 | 150
RVSS611D0450 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 10 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 600 | 3 | 10 | 180 | 150
RVSS611D0451 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 10 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 600 | 3 | 10 | 180 | 150
RVSS611D0452 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 10 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611C180N3S | 600 | 3 | 10 | 180 | 150
RVSS611D0453 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0454 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0455 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0456 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0457 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0458 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0459 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0460 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0461 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 18 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0462 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 18 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0463 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0464 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0465 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0466 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0467 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0468 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0469 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0470 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0471 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0472 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0473 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0474 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0475 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0476 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 18 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0477 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 18 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0478 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0479 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0481 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0482 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0483 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0484 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0485 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0486 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0487 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0488 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0489 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0490 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0491 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0492 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0493 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0494 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0495 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0496 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0497 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0498 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0499 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0500 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0501 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0502 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0503 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0504 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0505 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0506 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0507 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0508 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0509 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0510 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0511 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0512 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0513 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0514 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0515 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0516 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0517 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0518 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0519 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0520 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0521 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0522 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0523 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0524 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0525 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0526 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0527 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0528 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0529 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0530 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0531 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0532 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0533 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0534 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0535 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0536 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0537 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0538 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0539 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0540 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0541 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0542 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0543 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0544 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0545 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0546 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0547 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0548 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0549 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0550 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0551 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0552 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0553 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0554 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0555 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0556 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0557 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0558 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0559 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0560 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0561 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0562 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0563 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0564 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0565 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0566 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0567 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0568 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0569 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0570 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0571 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0572 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0573 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0574 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0575 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0576 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0577 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0578 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0579 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0580 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0581 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0582 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0583 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0584 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0585 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0586 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0587 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0588 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0589 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0590 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0591 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0592 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0593 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0594 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0595 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0596 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0597 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0598 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0599 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0600 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0601 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0602 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0603 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0604 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0605 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0606 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0607 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0608 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0609 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0610 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0611 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0612 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0613 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0614 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0615 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0616 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0617 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0618 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0619 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0620 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0621 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0622 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0623 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0624 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0625 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0626 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0627 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0628 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0629 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0630 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0631 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0632 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0633 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0634 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0635 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0636 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0637 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0638 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0639 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0640 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0641 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0642 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0643 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0644 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0645 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0646 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0647 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0648 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0649 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 200 | 3 | 18 | 242 | 75
RVSS611D0650 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 208 | 3 | 18 | 242 | 75
RVSS611D0651 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 240 | 3 | 18 | 242 | 75
RVSS611D0652 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0653 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 480 | 3 | 18 | 242 | 200
RVSS611D0654 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0655 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611D242N3S | 600 | 3 | 18 | 242 | 250
RVSS611D0656 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 177 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0657 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0658 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 169 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0659 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0660 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 154 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0661 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0662 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0663 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 156 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0664 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 180 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0665 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0666 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0667 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0668 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 177 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0669 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0670 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0671 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 169 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0672 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0673 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0674 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 154 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0675 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0676 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0677 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 156 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0678 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 180 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0679 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0680 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0681 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0682 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0683 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0684 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 177 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0685 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0686 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0687 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 169 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0688 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0689 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0690 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 154 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0691 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0692 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0693 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 156 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0694 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 180 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0695 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0696 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0697 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0698 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0699 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0700 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 177 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0701 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0702 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0703 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 169 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0704 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0705 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0706 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 154 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0707 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0708 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0709 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 156 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0710 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 180 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0711 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0712 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0713 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0714 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0715 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0716 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 177 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0717 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0718 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0719 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 169 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0720 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0721 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0722 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 154 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0723 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0724 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0725 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 156 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0726 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 180 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0727 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0728 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0729 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0730 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0731 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0732 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 177 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0733 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0734 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0735 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 169 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0736 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0737 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0738 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 154 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0739 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0740 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0741 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 156 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0742 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 180 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0743 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0744 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0745 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0746 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0747 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0748 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 177 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0749 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0750 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0751 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 169 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0752 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0753 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0754 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 154 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0755 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0756 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0757 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 156 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0758 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 180 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0759 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0760 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0761 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0762 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0763 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0764 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 177 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0765 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0766 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0767 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 169 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0768 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0769 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0770 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 154 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0771 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0772 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0773 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 156 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0774 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 180 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0775 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0776 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0777 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0778 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0779 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0780 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 177 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0781 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0782 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0783 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 169 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0784 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0785 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0786 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 154 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0787 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0788 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0789 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 156 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0790 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 180 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0791 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0792 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0793 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0794 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0795 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0796 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 177 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0797 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0798 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0799 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 169 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0800 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0801 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0802 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 154 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0803 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0804 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0805 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 156 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0806 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 180 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0807 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0808 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0809 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0810 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0811 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0812 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 177 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0813 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0814 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0815 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0816 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0817 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0818 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0819 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 180 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0820 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0821 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0822 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0823 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0824 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0825 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 18 | 177 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0826 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0827 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0828 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 18 | 169 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0829 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0830 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0831 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 18 | 154 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0832 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0833 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0834 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 18 | 156 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0835 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 18 | 180 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0836 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0837 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0838 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0839 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0840 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0841 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 18 | 177 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0842 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0843 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0844 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 18 | 169 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0845 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0846 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0847 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 18 | 154 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0848 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0849 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0850 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 18 | 156 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0851 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 18 | 180 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0852 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0853 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0854 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0855 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0856 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0857 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 18 | 177 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0858 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0859 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 200 | 3 | 18 | 302 | 100
RVSS611D0860 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 18 | 169 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0861 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0862 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 208 | 3 | 18 | 302 | 100
RVSS611D0863 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 18 | 154 | 60 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0864 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0865 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 240 | 3 | 18 | 302 | 100
RVSS611D0866 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 18 | 156 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0867 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 18 | 180 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0868 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0869 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 480 | 3 | 18 | 302 | 250
RVSS611D0870 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0871 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0872 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E302N3S | 600 | 3 | 18 | 302 | 300
RVSS611D0873 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D0874 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D0875 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0876 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0877 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D0878 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0879 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0880 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D0881 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D0882 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D0883 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D0884 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0885 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0886 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0887 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D0888 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D0889 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0890 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0891 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0892 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D0893 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D0894 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D0895 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D0896 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D0897 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D0898 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0899 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0900 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0901 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0902 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D0903 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D0904 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D0905 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0906 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0907 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0908 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0909 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D0910 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D0911 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D0912 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D0913 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D0914 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D0915 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0916 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0917 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0918 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0919 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D0920 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D0921 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D0922 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0923 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0924 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0925 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0926 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D0927 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D0928 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D0929 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D0930 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D0931 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D0932 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0933 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0934 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0935 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0936 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D0937 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D0938 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D0939 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0940 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0941 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0942 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0943 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D0944 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D0945 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D0946 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D0947 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D0948 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D0949 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0950 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0951 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0952 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0953 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D0954 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D0955 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D0956 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0957 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0958 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0959 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0960 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D0961 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D0962 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D0963 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D0964 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D0965 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D0966 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0967 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0968 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0969 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0970 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D0971 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D0972 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D0973 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0974 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0975 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0976 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0977 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D0978 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D0979 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D0980 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D0981 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D0982 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D0983 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0984 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0985 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0986 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D0987 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D0988 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D0989 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D0990 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0991 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0992 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0993 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D0994 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D0995 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D0996 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D0997 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D0998 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D0999 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D1000 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D1001 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D1002 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D1003 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D1004 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D1005 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D1006 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D1007 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D1008 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D1009 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D1010 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D1011 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D1012 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D1013 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D1014 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D1015 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D1016 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D1017 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D1018 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D1019 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D1020 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D1021 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D1022 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D1023 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D1024 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D1025 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D1026 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D1027 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D1028 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D1029 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D1030 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 18 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D1031 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D1032 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D1033 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 18 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D1034 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D1035 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D1036 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D1037 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 18 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D1038 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D1039 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D1040 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 18 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D1041 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D1042 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D1043 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D1044 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D1045 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D1046 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D1047 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 18 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D1048 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D1049 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D1050 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 18 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D1051 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 240 | 3 | - | 500 | 200 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D1052 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D1053 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 18 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D1054 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 18 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D1055 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D1056 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D1057 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 18 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D1058 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 500 | 500 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D1059 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D1060 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D1061 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D1062 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D1063 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D1064 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 500 | 200 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D1065 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D1066 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D1067 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 500 | 500 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D1068 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D1069 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 18 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D1070 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 18 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D1071 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 18 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 200 | 3 | 18 | 361 | 125
RVSS611D1072 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 18 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D1073 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 18 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D1074 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 18 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 208 | 3 | 18 | 361 | 125
RVSS611D1075 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 500 | 200 | 240 | 3 | 18 | 192 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D1076 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 18 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D1077 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 18 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D1078 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 18 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 240 | 3 | 18 | 361 | 150
RVSS611D1079 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 18 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D1080 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 18 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D1081 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 18 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 480 | 3 | 18 | 361 | 300
RVSS611D1082 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 500 | 500 | 600 | 3 | 18 | 192 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D1083 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D1084 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D1085 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611E361N3S | 600 | 3 | 18 | 361 | 350
RVSS611D1086 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 30 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611D1087 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 30 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1088 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 30 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 240 | 3 | 30 | 414 | 150
RVSS611D1089 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 30 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611D1090 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 30 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1091 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 30 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611D1092 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 30 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611D1093 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 30 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1094 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 30 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1095 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 30 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 240 | 3 | 30 | 414 | 150
RVSS611D1096 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 30 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 240 | 3 | 30 | 414 | 150
RVSS611D1097 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 30 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611D1098 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 30 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611D1099 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 30 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1100 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 30 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1101 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 30 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611D1102 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 30 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611D1103 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 30 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1104 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 30 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1105 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 30 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1106 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 30 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 240 | 3 | 30 | 414 | 150
RVSS611D1107 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 30 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 240 | 3 | 30 | 414 | 150
RVSS611D1108 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 30 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611D1109 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 30 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611D1110 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 30 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1111 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 30 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1112 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 30 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1113 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 30 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611D1114 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 30 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611D1115 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 30 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1116 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 30 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1117 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 30 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1118 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 30 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 240 | 3 | 30 | 414 | 150
RVSS611D1119 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 30 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 240 | 3 | 30 | 414 | 150
RVSS611D1120 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 30 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611D1121 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 30 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611D1122 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 30 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1123 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 30 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1124 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400K5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 30 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1125 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 30 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611D1126 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 30 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611D1127 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 30 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1128 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 30 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1129 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 30 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1130 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 30 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 240 | 3 | 30 | 414 | 150
RVSS611D1131 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 30 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 240 | 3 | 30 | 414 | 150
RVSS611D1132 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 30 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611D1133 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 30 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611D1134 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 30 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1135 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 30 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1136 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400L5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 30 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1137 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 30 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611D1138 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 30 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611D1139 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 30 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1140 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 30 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1141 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 30 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1142 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 30 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 240 | 3 | 30 | 414 | 150
RVSS611D1143 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 30 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 240 | 3 | 30 | 414 | 150
RVSS611D1144 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 30 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611D1145 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 30 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611D1146 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 30 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1147 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 30 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1148 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400W5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 30 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1149 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 30 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611D1150 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 30 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611D1151 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 30 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1152 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 30 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1153 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 30 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1154 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 30 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 240 | 3 | 30 | 414 | 150
RVSS611D1155 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 30 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 240 | 3 | 30 | 414 | 150
RVSS611D1156 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 30 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611D1157 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 30 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611D1158 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 30 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1159 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 30 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1160 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400N5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 30 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1161 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 30 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611D1162 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 30 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611D1163 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 30 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1164 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 30 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1165 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 30 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1166 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 30 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 240 | 3 | 30 | 414 | 150
RVSS611D1167 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 30 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 240 | 3 | 30 | 414 | 150
RVSS611D1168 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 30 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611D1169 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 30 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611D1170 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 30 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1171 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 30 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1172 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400R5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 30 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1173 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 30 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611D1174 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 30 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611D1175 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 30 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1176 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 30 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1177 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 30 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1178 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 30 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 240 | 3 | 30 | 414 | 150
RVSS611D1179 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 30 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 240 | 3 | 30 | 414 | 150
RVSS611D1180 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 30 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611D1181 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 30 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611D1182 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 30 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1183 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 30 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1184 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400X5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 30 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1185 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 30 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611D1186 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 30 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611D1187 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 30 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1188 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 30 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1189 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 30 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1190 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 30 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 240 | 3 | 30 | 414 | 150
RVSS611D1191 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 30 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 240 | 3 | 30 | 414 | 150
RVSS611D1192 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 30 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611D1193 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 30 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611D1194 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 30 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1195 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 30 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1196 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP400Y5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 30 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1197 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 30 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611D1198 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 30 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611D1199 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 30 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611D1200 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 30 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1201 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 30 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1202 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 30 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1203 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 30 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 240 | 3 | 30 | 414 | 150
RVSS611D1204 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 30 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 240 | 3 | 30 | 414 | 150
RVSS611D1205 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 30 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611D1206 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 30 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611D1207 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 30 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611D1208 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 30 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1209 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 30 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1210 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 30 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1211 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 30 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1212 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 30 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611D1213 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 30 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611D1214 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 30 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 200 | 3 | 30 | 414 | 150
RVSS611D1215 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 30 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1216 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 30 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1217 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 30 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 208 | 3 | 30 | 414 | 150
RVSS611D1218 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 30 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 240 | 3 | 30 | 414 | 150
RVSS611D1219 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 30 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 240 | 3 | 30 | 414 | 150
RVSS611D1220 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 30 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611D1221 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 30 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611D1222 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 30 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 480 | 3 | 30 | 414 | 350
RVSS611D1223 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 30 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1224 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 30 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1225 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 30 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
RVSS611D1226 | E176513 | Vol. 1, Sec. 8 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 30 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S611F414N3S | 600 | 3 | 30 | 414 | 450
Conditions of Aceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.

## S801 Softstarter Type C
Issue Date: 2006-05-18
Revised: 2016-10-27
Database Identification Number | Listed Combination Motor Controller Information |  | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings
| UL File Number | Volume / Section (Vol#).(Sec#) |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating | Enclosure Volume, cubic inches | Conditions of Use | Other References
SSC0001.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3040L | 200 | 3 | 100 | 40 | 10 | 200 | 3 | 100 | 11 | 3 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 200 | 3 | 10 | 37 | 10
SSC0001.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3040L | 200 | 3 | 100 | 40 | 10 | 200 | 3 | 100 | 11 | 3 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0001.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3040L | 200 | 3 | 100 | 40 | 10 | 200 | 3 | 100 | 11 | 3 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 200 | 3 | 10 | 37 | 10
SSC0001.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3040L | 200 | 3 | 100 | 40 | 10 | 200 | 3 | 100 | 11 | 3 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0002.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3070L | 200 | 3 | 100 | 70 | 20 | 200 | 3 | 100 | 17.5 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 200 | 3 | 10 | 37 | 10
SSC0002.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3070L | 200 | 3 | 100 | 70 | 20 | 200 | 3 | 100 | 17.5 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0002.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3070L | 200 | 3 | 100 | 70 | 20 | 200 | 3 | 100 | 17.5 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 200 | 3 | 10 | 37 | 10
SSC0002.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3070L | 200 | 3 | 100 | 70 | 20 | 200 | 3 | 100 | 17.5 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0003.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3100L | 200 | 3 | 100 | 100 | 30 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 200 | 3 | 10 | 37 | 10
SSC0003.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3100L | 200 | 3 | 100 | 100 | 30 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0003.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3100L | 200 | 3 | 100 | 100 | 30 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 200 | 3 | 10 | 37 | 10
SSC0003.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3100L | 200 | 3 | 100 | 100 | 30 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0004.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 200 | 3 | 100 | 125 | 40 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 200 | 3 | 10 | 37 | 10
SSC0004.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 200 | 3 | 100 | 125 | 40 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0004.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 200 | 3 | 100 | 125 | 40 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 200 | 3 | 10 | 37 | 10
SSC0004.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 200 | 3 | 100 | 125 | 40 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0005.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3060L | 208 | 3 | 100 | 60 | 20 | 208 | 3 | 100 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 208 | 3 | 10 | 37 | 10
SSC0005.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3060L | 208 | 3 | 100 | 60 | 20 | 208 | 3 | 100 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0005.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3060L | 208 | 3 | 100 | 60 | 20 | 208 | 3 | 100 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 208 | 3 | 10 | 37 | 10
SSC0005.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3060L | 208 | 3 | 100 | 60 | 20 | 208 | 3 | 100 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0006.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3090L | 208 | 3 | 100 | 90 | 30 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 208 | 3 | 10 | 37 | 10
SSC0006.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3090L | 208 | 3 | 100 | 90 | 30 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0006.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3090L | 208 | 3 | 100 | 90 | 30 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 208 | 3 | 10 | 37 | 10
SSC0006.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3090L | 208 | 3 | 100 | 90 | 30 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0007.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3110L | 208 | 3 | 100 | 110 | 30 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 208 | 3 | 10 | 37 | 10
SSC0007.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3110L | 208 | 3 | 100 | 110 | 30 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0007.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3110L | 208 | 3 | 100 | 110 | 30 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 208 | 3 | 10 | 37 | 10
SSC0007.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3110L | 208 | 3 | 100 | 110 | 30 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0008.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3060L | 240 | 3 | 100 | 60 | 20 | 240 | 3 | 100 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 240 | 3 | 10 | 37 | 10
SSC0008.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3060L | 240 | 3 | 100 | 60 | 20 | 240 | 3 | 100 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0008.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3060L | 240 | 3 | 100 | 60 | 20 | 240 | 3 | 100 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 240 | 3 | 10 | 37 | 10
SSC0008.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3060L | 240 | 3 | 100 | 60 | 20 | 240 | 3 | 100 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0009.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3070L | 240 | 3 | 100 | 70 | 25 | 240 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 240 | 3 | 10 | 37 | 10
SSC0009.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3070L | 240 | 3 | 100 | 70 | 25 | 240 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0009.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3070L | 240 | 3 | 100 | 70 | 25 | 240 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 240 | 3 | 10 | 37 | 10
SSC0009.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3070L | 240 | 3 | 100 | 70 | 25 | 240 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0010.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3110L | 240 | 3 | 100 | 110 | 40 | 240 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 240 | 3 | 10 | 37 | 10
SSC0010.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3110L | 240 | 3 | 100 | 110 | 40 | 240 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0010.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3110L | 240 | 3 | 100 | 110 | 40 | 240 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 240 | 3 | 10 | 37 | 10
SSC0010.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3110L | 240 | 3 | 100 | 110 | 40 | 240 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0011.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3040L | 480 | 3 | 65 | 40 | 30 | 480 | 3 | 65 | 11 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 480 | 3 | 10 | 37 | 25
SSC0011.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3040L | 480 | 3 | 65 | 40 | 30 | 480 | 3 | 65 | 11 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0011.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3040L | 480 | 3 | 65 | 40 | 30 | 480 | 3 | 65 | 11 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 480 | 3 | 10 | 37 | 25
SSC0011.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3040L | 480 | 3 | 65 | 40 | 30 | 480 | 3 | 65 | 11 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0012.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3050L | 480 | 3 | 65 | 50 | 30 | 480 | 3 | 65 | 14 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 480 | 3 | 10 | 37 | 20
SSC0012.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3050L | 480 | 3 | 65 | 50 | 30 | 480 | 3 | 65 | 14 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 480 | 3 | 10 | 37 | 20
SSC0012.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3050L | 480 | 3 | 65 | 50 | 30 | 480 | 3 | 65 | 14 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 480 | 3 | 10 | 37 | 20
SSC0012.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3050L | 480 | 3 | 65 | 50 | 30 | 480 | 3 | 65 | 14 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 480 | 3 | 10 | 37 | 20
SSC0013.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3080L | 480 | 3 | 65 | 80 | 60 | 480 | 3 | 65 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 480 | 3 | 10 | 37 | 20
SSC0013.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3080L | 480 | 3 | 65 | 80 | 60 | 480 | 3 | 65 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 480 | 3 | 10 | 37 | 20
SSC0013.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3080L | 480 | 3 | 65 | 80 | 60 | 480 | 3 | 65 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 480 | 3 | 10 | 37 | 20
SSC0013.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3080L | 480 | 3 | 65 | 80 | 60 | 480 | 3 | 65 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 480 | 3 | 10 | 37 | 20
SSC0014.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3100L | 480 | 3 | 65 | 100 | 75 | 480 | 3 | 65 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 480 | 3 | 10 | 37 | 20
SSC0014.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3100L | 480 | 3 | 65 | 100 | 75 | 480 | 3 | 65 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 480 | 3 | 10 | 37 | 20
SSC0014.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3100L | 480 | 3 | 65 | 100 | 75 | 480 | 3 | 65 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 480 | 3 | 10 | 37 | 20
SSC0014.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3100L | 480 | 3 | 65 | 100 | 75 | 480 | 3 | 65 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 480 | 3 | 10 | 37 | 20
SSC0015.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 480 | 3 | 65 | 125 | 100 | 480 | 3 | 65 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 480 | 3 | 10 | 37 | 20
SSC0015.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 480 | 3 | 65 | 125 | 100 | 480 | 3 | 65 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 480 | 3 | 10 | 37 | 20
SSC0015.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 480 | 3 | 65 | 125 | 100 | 480 | 3 | 65 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 480 | 3 | 10 | 37 | 20
SSC0015.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 480 | 3 | 65 | 125 | 100 | 480 | 3 | 65 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 480 | 3 | 10 | 37 | 20
SSC0016.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3040L | 600 | 3 | 25 | 40 | 30 | 600 | 3 | 25 | 11 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 600 | 3 | 10 | 37 | 30
SSC0016.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3040L | 600 | 3 | 25 | 40 | 30 | 600 | 3 | 25 | 11 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0016.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3040L | 600 | 3 | 25 | 40 | 30 | 600 | 3 | 25 | 11 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 600 | 3 | 10 | 37 | 30
SSC0016.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3040L | 600 | 3 | 25 | 40 | 30 | 600 | 3 | 25 | 11 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0017.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3060L | 600 | 3 | 25 | 60 | 50 | 600 | 3 | 25 | 17 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 600 | 3 | 10 | 37 | 30
SSC0017.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3060L | 600 | 3 | 25 | 60 | 50 | 600 | 3 | 25 | 17 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0017.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3060L | 600 | 3 | 25 | 60 | 50 | 600 | 3 | 25 | 17 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 600 | 3 | 10 | 37 | 30
SSC0017.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3060L | 600 | 3 | 25 | 60 | 50 | 600 | 3 | 25 | 17 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0018.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3080L | 600 | 3 | 25 | 80 | 75 | 600 | 3 | 25 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 600 | 3 | 10 | 37 | 30
SSC0018.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3080L | 600 | 3 | 25 | 80 | 75 | 600 | 3 | 25 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0018.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3080L | 600 | 3 | 25 | 80 | 75 | 600 | 3 | 25 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 600 | 3 | 10 | 37 | 30
SSC0018.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3080L | 600 | 3 | 25 | 80 | 75 | 600 | 3 | 25 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0019.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3100L | 600 | 3 | 25 | 100 | 100 | 600 | 3 | 25 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 600 | 3 | 10 | 37 | 30
SSC0019.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3100L | 600 | 3 | 25 | 100 | 100 | 600 | 3 | 25 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0019.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3100L | 600 | 3 | 25 | 100 | 100 | 600 | 3 | 25 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 600 | 3 | 10 | 37 | 30
SSC0019.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3100L | 600 | 3 | 25 | 100 | 100 | 600 | 3 | 25 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0020.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 600 | 3 | 25 | 125 | 125 | 600 | 3 | 25 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 600 | 3 | 10 | 37 | 30
SSC0020.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 600 | 3 | 25 | 125 | 125 | 600 | 3 | 25 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0020.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 600 | 3 | 25 | 125 | 125 | 600 | 3 | 25 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 600 | 3 | 10 | 37 | 30
SSC0020.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 600 | 3 | 25 | 125 | 125 | 600 | 3 | 25 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0021.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3070* | 200 | 3 | 100 | 70 | 20 | 200 | 3 | 100 | 17.5 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 200 | 3 | 10 | 37 | 10
SSC0021.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3070* | 200 | 3 | 100 | 70 | 20 | 200 | 3 | 100 | 17.5 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0021.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3070* | 200 | 3 | 100 | 70 | 20 | 200 | 3 | 100 | 17.5 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 200 | 3 | 10 | 37 | 10
SSC0021.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3070* | 200 | 3 | 100 | 70 | 20 | 200 | 3 | 100 | 17.5 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0022.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 200 | 3 | 100 | 100 | 30 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 200 | 3 | 10 | 37 | 10
SSC0022.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 200 | 3 | 100 | 100 | 30 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0022.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 200 | 3 | 100 | 100 | 30 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 200 | 3 | 10 | 37 | 10
SSC0022.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 200 | 3 | 100 | 100 | 30 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0023.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 200 | 3 | 100 | 125 | 40 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 200 | 3 | 10 | 37 | 10
SSC0023.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 200 | 3 | 100 | 125 | 40 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0023.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 200 | 3 | 100 | 125 | 40 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 200 | 3 | 10 | 37 | 10
SSC0023.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 200 | 3 | 100 | 125 | 40 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0024.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3090* | 208 | 3 | 100 | 90 | 30 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 208 | 3 | 10 | 37 | 10
SSC0024.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3090* | 208 | 3 | 100 | 90 | 30 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0024.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3090* | 208 | 3 | 100 | 90 | 30 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 208 | 3 | 10 | 37 | 10
SSC0024.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3090* | 208 | 3 | 100 | 90 | 30 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0025.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 208 | 3 | 100 | 100 | 30 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 208 | 3 | 10 | 37 | 10
SSC0025.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 208 | 3 | 100 | 100 | 30 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0025.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 208 | 3 | 100 | 100 | 30 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 208 | 3 | 10 | 37 | 10
SSC0025.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 208 | 3 | 100 | 100 | 30 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0026.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3070* | 240 | 3 | 100 | 70 | 25 | 240 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 240 | 3 | 10 | 37 | 10
SSC0026.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3070* | 240 | 3 | 100 | 70 | 25 | 240 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0026.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3070* | 240 | 3 | 100 | 70 | 25 | 240 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 240 | 3 | 10 | 37 | 10
SSC0026.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3070* | 240 | 3 | 100 | 70 | 25 | 240 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0027.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 240 | 3 | 100 | 100 | 30 | 240 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 240 | 3 | 10 | 37 | 10
SSC0027.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 240 | 3 | 100 | 100 | 30 | 240 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0027.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 240 | 3 | 100 | 100 | 30 | 240 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 240 | 3 | 10 | 37 | 10
SSC0027.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 240 | 3 | 100 | 100 | 30 | 240 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0028.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3070* | 480 | 3 | 65 | 70 | 50 | 480 | 3 | 65 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 480 | 3 | 10 | 37 | 20
SSC0028.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3070* | 480 | 3 | 65 | 70 | 50 | 480 | 3 | 65 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 480 | 3 | 10 | 37 | 20
SSC0028.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3070* | 480 | 3 | 65 | 70 | 50 | 480 | 3 | 65 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 480 | 3 | 10 | 37 | 20
SSC0028.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3070* | 480 | 3 | 65 | 70 | 50 | 480 | 3 | 65 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 480 | 3 | 10 | 37 | 20
SSC0029.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 480 | 3 | 65 | 100 | 75 | 480 | 3 | 65 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 480 | 3 | 10 | 37 | 20
SSC0029.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 480 | 3 | 65 | 100 | 75 | 480 | 3 | 65 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 480 | 3 | 10 | 37 | 20
SSC0029.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 480 | 3 | 65 | 100 | 75 | 480 | 3 | 65 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 480 | 3 | 10 | 37 | 20
SSC0029.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 480 | 3 | 65 | 100 | 75 | 480 | 3 | 65 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 480 | 3 | 10 | 37 | 20
SSC0030.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 480 | 3 | 65 | 125 | 100 | 480 | 3 | 65 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 480 | 3 | 10 | 37 | 20
SSC0030.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 480 | 3 | 65 | 125 | 100 | 480 | 3 | 65 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 480 | 3 | 10 | 37 | 20
SSC0030.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 480 | 3 | 65 | 125 | 100 | 480 | 3 | 65 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 480 | 3 | 10 | 37 | 20
SSC0030.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 480 | 3 | 65 | 125 | 100 | 480 | 3 | 65 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 480 | 3 | 10 | 37 | 20
SSC0031.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3070* | 600 | 3 | 25 | 70 | 60 | 600 | 3 | 25 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 600 | 3 | 10 | 37 | 30
SSC0031.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3070* | 600 | 3 | 25 | 70 | 60 | 600 | 3 | 25 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0031.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3070* | 600 | 3 | 25 | 70 | 60 | 600 | 3 | 25 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 600 | 3 | 10 | 37 | 30
SSC0031.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3070* | 600 | 3 | 25 | 70 | 60 | 600 | 3 | 25 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0032.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 600 | 3 | 25 | 100 | 100 | 600 | 3 | 25 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 600 | 3 | 10 | 37 | 30
SSC0032.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 600 | 3 | 25 | 100 | 100 | 600 | 3 | 25 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0032.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 600 | 3 | 25 | 100 | 100 | 600 | 3 | 25 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 600 | 3 | 10 | 37 | 30
SSC0032.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 600 | 3 | 25 | 100 | 100 | 600 | 3 | 25 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0033.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 600 | 3 | 25 | 125 | 125 | 600 | 3 | 25 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 600 | 3 | 10 | 37 | 30
SSC0033.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 600 | 3 | 25 | 125 | 125 | 600 | 3 | 25 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0033.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 600 | 3 | 25 | 125 | 125 | 600 | 3 | 25 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 600 | 3 | 10 | 37 | 30
SSC0033.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 600 | 3 | 25 | 125 | 125 | 600 | 3 | 25 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0034.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3100L | 200 | 3 | 100 | 100 | 30 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 200 | 3 | 10 | 66 | 20
SSC0034.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3100L | 200 | 3 | 100 | 100 | 30 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0034.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3100L | 200 | 3 | 100 | 100 | 30 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 200 | 3 | 10 | 66 | 20
SSC0034.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3100L | 200 | 3 | 100 | 100 | 30 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0035.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 200 | 3 | 100 | 125 | 40 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 200 | 3 | 10 | 66 | 20
SSC0035.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 200 | 3 | 100 | 125 | 40 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0035.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 200 | 3 | 100 | 125 | 40 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 200 | 3 | 10 | 66 | 20
SSC0035.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 200 | 3 | 100 | 125 | 40 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0036.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 48.3 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 200 | 3 | 10 | 66 | 20
SSC0036.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 48.3 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0036.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 48.3 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 200 | 3 | 10 | 66 | 20
SSC0036.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 48.3 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0037.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 200 | 3 | 10 | 66 | 20
SSC0037.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0037.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 200 | 3 | 10 | 66 | 20
SSC0037.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0038.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3090L | 208 | 3 | 100 | 90 | 30 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 208 | 3 | 10 | 66 | 20
SSC0038.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3090L | 208 | 3 | 100 | 90 | 30 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0038.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3090L | 208 | 3 | 100 | 90 | 30 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 208 | 3 | 10 | 66 | 20
SSC0038.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3090L | 208 | 3 | 100 | 90 | 30 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0039.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3110L | 208 | 3 | 100 | 110 | 30 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 208 | 3 | 10 | 66 | 20
SSC0039.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3110L | 208 | 3 | 100 | 110 | 30 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0039.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3110L | 208 | 3 | 100 | 110 | 30 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 208 | 3 | 10 | 66 | 20
SSC0039.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3110L | 208 | 3 | 100 | 110 | 30 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0040.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 46.2 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 208 | 3 | 10 | 66 | 20
SSC0040.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 46.2 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0040.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 46.2 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 208 | 3 | 10 | 66 | 20
SSC0040.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 46.2 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0041.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 208 | 3 | 10 | 66 | 20
SSC0041.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0041.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 208 | 3 | 10 | 66 | 20
SSC0041.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0042.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3080L | 240 | 3 | 100 | 80 | 30 | 240 | 3 | 100 | 22 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 240 | 3 | 10 | 66 | 20
SSC0042.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3080L | 240 | 3 | 100 | 80 | 30 | 240 | 3 | 100 | 22 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0042.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3080L | 240 | 3 | 100 | 80 | 30 | 240 | 3 | 100 | 22 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 240 | 3 | 10 | 66 | 20
SSC0042.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3080L | 240 | 3 | 100 | 80 | 30 | 240 | 3 | 100 | 22 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0043.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3110L | 240 | 3 | 100 | 110 | 40 | 240 | 3 | 100 | 28 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 240 | 3 | 10 | 66 | 20
SSC0043.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3110L | 240 | 3 | 100 | 110 | 40 | 240 | 3 | 100 | 28 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0043.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3110L | 240 | 3 | 100 | 110 | 40 | 240 | 3 | 100 | 28 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 240 | 3 | 10 | 66 | 20
SSC0043.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3110L | 240 | 3 | 100 | 110 | 40 | 240 | 3 | 100 | 28 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0044.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 42 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 240 | 3 | 10 | 66 | 20
SSC0044.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 42 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0044.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 42 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 240 | 3 | 10 | 66 | 20
SSC0044.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 42 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0045.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 240 | 3 | 10 | 66 | 20
SSC0045.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0045.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 240 | 3 | 10 | 66 | 20
SSC0045.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0046.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3080L | 480 | 3 | 65 | 80 | 60 | 480 | 3 | 65 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0046.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3080L | 480 | 3 | 65 | 80 | 60 | 480 | 3 | 65 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0046.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3080L | 480 | 3 | 65 | 80 | 60 | 480 | 3 | 65 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0046.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3080L | 480 | 3 | 65 | 80 | 60 | 480 | 3 | 65 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0047.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3100L | 480 | 3 | 65 | 100 | 75 | 480 | 3 | 65 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0047.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3100L | 480 | 3 | 65 | 100 | 75 | 480 | 3 | 65 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0047.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3100L | 480 | 3 | 65 | 100 | 75 | 480 | 3 | 65 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0047.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3100L | 480 | 3 | 65 | 100 | 75 | 480 | 3 | 65 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0048.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 480 | 3 | 65 | 125 | 100 | 480 | 3 | 65 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0048.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 480 | 3 | 65 | 125 | 100 | 480 | 3 | 65 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0048.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 480 | 3 | 65 | 125 | 100 | 480 | 3 | 65 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0048.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 480 | 3 | 65 | 125 | 100 | 480 | 3 | 65 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0049.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 40 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0049.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 40 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0049.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 40 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0049.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 40 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0050.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0050.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0050.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0050.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0051.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0051.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0051.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0051.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0052.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3080L | 600 | 3 | 25 | 80 | 75 | 600 | 3 | 25 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 600 | 3 | 10 | 66 | 60
SSC0052.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3080L | 600 | 3 | 25 | 80 | 75 | 600 | 3 | 25 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0052.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3080L | 600 | 3 | 25 | 80 | 75 | 600 | 3 | 25 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 600 | 3 | 10 | 66 | 60
SSC0052.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3080L | 600 | 3 | 25 | 80 | 75 | 600 | 3 | 25 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0053.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3100L | 600 | 3 | 25 | 100 | 100 | 600 | 3 | 25 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 600 | 3 | 10 | 66 | 60
SSC0053.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3100L | 600 | 3 | 25 | 100 | 100 | 600 | 3 | 25 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0053.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3100L | 600 | 3 | 25 | 100 | 100 | 600 | 3 | 25 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 600 | 3 | 10 | 66 | 60
SSC0053.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3100L | 600 | 3 | 25 | 100 | 100 | 600 | 3 | 25 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0054.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 600 | 3 | 25 | 125 | 125 | 600 | 3 | 25 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 600 | 3 | 10 | 66 | 60
SSC0054.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 600 | 3 | 25 | 125 | 125 | 600 | 3 | 25 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0054.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 600 | 3 | 25 | 125 | 125 | 600 | 3 | 25 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 600 | 3 | 10 | 66 | 60
SSC0054.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 600 | 3 | 25 | 125 | 125 | 600 | 3 | 25 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0055.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 41 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 600 | 3 | 10 | 66 | 60
SSC0055.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 41 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0055.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 41 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 600 | 3 | 10 | 66 | 60
SSC0055.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 41 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0056.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 52 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 600 | 3 | 10 | 66 | 60
SSC0056.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 52 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0056.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 52 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 600 | 3 | 10 | 66 | 60
SSC0056.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 52 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0057.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 62 | 60 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 600 | 3 | 10 | 66 | 60
SSC0057.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 62 | 60 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0057.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 62 | 60 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 600 | 3 | 10 | 66 | 60
SSC0057.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 62 | 60 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0058.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 200 | 3 | 100 | 100 | 30 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 200 | 3 | 10 | 66 | 20
SSC0058.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 200 | 3 | 100 | 100 | 30 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0058.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 200 | 3 | 100 | 100 | 30 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 200 | 3 | 10 | 66 | 20
SSC0058.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 200 | 3 | 100 | 100 | 30 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0059.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 200 | 3 | 100 | 125 | 40 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 200 | 3 | 10 | 66 | 20
SSC0059.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 200 | 3 | 100 | 125 | 40 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0059.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 200 | 3 | 100 | 125 | 40 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 200 | 3 | 10 | 66 | 20
SSC0059.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 200 | 3 | 100 | 125 | 40 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0060.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 48.3 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 200 | 3 | 10 | 66 | 20
SSC0060.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 48.3 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0060.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 48.3 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 200 | 3 | 10 | 66 | 20
SSC0060.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 48.3 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0061.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 200 | 3 | 10 | 66 | 20
SSC0061.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0061.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 200 | 3 | 10 | 66 | 20
SSC0061.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0062.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3090* | 208 | 3 | 100 | 90 | 30 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 208 | 3 | 10 | 66 | 20
SSC0062.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3090* | 208 | 3 | 100 | 90 | 30 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0062.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3090* | 208 | 3 | 100 | 90 | 30 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 208 | 3 | 10 | 66 | 20
SSC0062.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3090* | 208 | 3 | 100 | 90 | 30 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0063.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 208 | 3 | 100 | 100 | 30 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 208 | 3 | 10 | 66 | 20
SSC0063.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 208 | 3 | 100 | 100 | 30 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0063.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 208 | 3 | 100 | 100 | 30 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 208 | 3 | 10 | 66 | 20
SSC0063.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 208 | 3 | 100 | 100 | 30 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0064.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 46.2 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 208 | 3 | 10 | 66 | 20
SSC0064.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 46.2 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0064.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 46.2 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 208 | 3 | 10 | 66 | 20
SSC0064.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 46.2 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0065.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 208 | 3 | 10 | 66 | 20
SSC0065.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0065.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 208 | 3 | 10 | 66 | 20
SSC0065.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0066.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3070* | 240 | 3 | 100 | 70 | 20 | 240 | 3 | 100 | 22 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 240 | 3 | 10 | 66 | 20
SSC0066.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3070* | 240 | 3 | 100 | 70 | 20 | 240 | 3 | 100 | 22 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0066.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3070* | 240 | 3 | 100 | 70 | 20 | 240 | 3 | 100 | 22 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 240 | 3 | 10 | 66 | 20
SSC0066.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3070* | 240 | 3 | 100 | 70 | 20 | 240 | 3 | 100 | 22 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0067.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 240 | 3 | 100 | 100 | 30 | 240 | 3 | 100 | 28 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 240 | 3 | 10 | 66 | 20
SSC0067.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 240 | 3 | 100 | 100 | 30 | 240 | 3 | 100 | 28 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0067.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 240 | 3 | 100 | 100 | 30 | 240 | 3 | 100 | 28 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 240 | 3 | 10 | 66 | 20
SSC0067.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 240 | 3 | 100 | 100 | 30 | 240 | 3 | 100 | 28 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0068.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 42 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 240 | 3 | 10 | 66 | 20
SSC0068.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 42 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0068.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 42 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 240 | 3 | 10 | 66 | 20
SSC0068.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 42 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0069.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 240 | 3 | 10 | 66 | 20
SSC0069.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0069.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 240 | 3 | 10 | 66 | 20
SSC0069.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0070.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3070* | 480 | 3 | 65 | 70 | 50 | 480 | 3 | 65 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0070.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3070* | 480 | 3 | 65 | 70 | 50 | 480 | 3 | 65 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0070.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3070* | 480 | 3 | 65 | 70 | 50 | 480 | 3 | 65 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0070.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3070* | 480 | 3 | 65 | 70 | 50 | 480 | 3 | 65 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0071.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 480 | 3 | 65 | 100 | 75 | 480 | 3 | 65 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0071.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 480 | 3 | 65 | 100 | 75 | 480 | 3 | 65 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0071.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 480 | 3 | 65 | 100 | 75 | 480 | 3 | 65 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0071.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 480 | 3 | 65 | 100 | 75 | 480 | 3 | 65 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0072.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 480 | 3 | 65 | 125 | 100 | 480 | 3 | 65 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0072.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 480 | 3 | 65 | 125 | 100 | 480 | 3 | 65 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0072.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 480 | 3 | 65 | 125 | 100 | 480 | 3 | 65 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0072.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 480 | 3 | 65 | 125 | 100 | 480 | 3 | 65 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0073.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 40 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0073.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 40 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0073.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 40 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0073.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 40 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0074.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0074.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0074.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0074.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0075.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0075.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0075.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0075.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0076.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3070* | 600 | 3 | 25 | 70 | 60 | 600 | 3 | 25 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 600 | 3 | 10 | 66 | 60
SSC0076.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3070* | 600 | 3 | 25 | 70 | 60 | 600 | 3 | 25 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0076.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3070* | 600 | 3 | 25 | 70 | 60 | 600 | 3 | 25 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 600 | 3 | 10 | 66 | 60
SSC0076.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3070* | 600 | 3 | 25 | 70 | 60 | 600 | 3 | 25 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0077.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 600 | 3 | 25 | 100 | 100 | 600 | 3 | 25 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 600 | 3 | 10 | 66 | 60
SSC0077.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 600 | 3 | 25 | 100 | 100 | 600 | 3 | 25 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0077.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 600 | 3 | 25 | 100 | 100 | 600 | 3 | 25 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 600 | 3 | 10 | 66 | 60
SSC0077.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3100* | 600 | 3 | 25 | 100 | 100 | 600 | 3 | 25 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0078.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 600 | 3 | 25 | 125 | 125 | 600 | 3 | 25 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 600 | 3 | 10 | 66 | 60
SSC0078.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 600 | 3 | 25 | 125 | 125 | 600 | 3 | 25 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0078.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 600 | 3 | 25 | 125 | 125 | 600 | 3 | 25 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 600 | 3 | 10 | 66 | 60
SSC0078.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 600 | 3 | 25 | 125 | 125 | 600 | 3 | 25 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0079.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 41 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 600 | 3 | 10 | 66 | 60
SSC0079.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 41 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0079.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 41 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 600 | 3 | 10 | 66 | 60
SSC0079.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 41 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0080.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 52 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 600 | 3 | 10 | 66 | 60
SSC0080.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 52 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0080.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 52 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 600 | 3 | 10 | 66 | 60
SSC0080.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 52 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0081.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 62 | 60 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 600 | 3 | 10 | 66 | 60
SSC0081.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 62 | 60 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0081.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 62 | 60 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 600 | 3 | 10 | 66 | 60
SSC0081.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 62 | 60 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0082.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 48.3 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0082.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 48.3 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0082.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 48.3 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0082.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 48.3 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0083.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0083.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0083.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0083.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0084.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0084.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0084.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0084.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0085.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0085.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0085.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0085.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0086.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 46.2 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0086.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 46.2 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0086.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 46.2 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0086.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 46.2 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0087.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0087.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0087.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0087.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0088.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0088.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0088.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0088.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0089.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0089.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0089.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0089.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0090.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 42 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0090.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 42 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0090.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 42 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0090.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 42 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0091.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0091.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0091.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0091.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0092.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0092.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0092.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0092.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0093.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0093.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0093.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0093.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0094.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0094.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0094.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0094.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0095.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 480 | 3 | 65 | 125 | 100 | 480 | 3 | 65 | 34 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 60
SSC0095.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 480 | 3 | 65 | 125 | 100 | 480 | 3 | 65 | 34 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 60
SSC0095.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 480 | 3 | 65 | 125 | 100 | 480 | 3 | 65 | 34 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 60
SSC0095.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 480 | 3 | 65 | 125 | 100 | 480 | 3 | 65 | 34 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 60
SSC0096.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 40 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0096.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 40 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0096.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 40 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0096.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 40 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0097.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0097.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0097.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0097.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0098.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0098.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0098.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0098.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0099.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0099.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0099.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0099.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0100.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0100.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0100.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0100.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0101.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 600 | 3 | 25 | 125 | 125 | 600 | 3 | 25 | 32 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0101.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 600 | 3 | 25 | 125 | 125 | 600 | 3 | 25 | 32 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0101.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 600 | 3 | 25 | 125 | 125 | 600 | 3 | 25 | 32 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0101.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3125L | 600 | 3 | 25 | 125 | 125 | 600 | 3 | 25 | 32 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0102.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 41 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0102.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 41 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0102.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 41 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0102.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 41 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0103.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 52 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0103.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 52 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0103.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 52 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0103.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 52 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0104.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 62 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0104.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 62 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0104.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 62 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0104.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 62 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0105.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 77 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0105.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 77 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0105.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 77 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0105.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 77 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0106.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 99 | 100 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0106.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 99 | 100 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0106.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 99 | 100 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0106.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 99 | 100 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0107.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 48.3 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0107.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 48.3 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0107.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 48.3 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0107.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 48.3 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0108.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0108.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0108.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0108.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0109.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0109.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0109.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0109.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0110.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0110.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0110.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0110.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0111.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 46.2 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0111.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 46.2 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0111.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 46.2 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0111.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 46.2 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0112.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0112.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0112.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0112.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0113.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0113.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0113.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0113.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0114.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0114.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0114.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0114.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0115.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 42 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0115.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 42 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0115.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 42 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0115.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 42 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0116.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0116.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0116.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0116.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0117.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0117.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0117.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0117.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0118.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0118.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0118.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0118.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0119.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0119.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0119.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0119.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0120.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 480 | 3 | 65 | 125 | 100 | 480 | 3 | 65 | 34 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 60
SSC0120.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 480 | 3 | 65 | 125 | 100 | 480 | 3 | 65 | 34 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 60
SSC0120.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 480 | 3 | 65 | 125 | 100 | 480 | 3 | 65 | 34 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 60
SSC0120.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 480 | 3 | 65 | 125 | 100 | 480 | 3 | 65 | 34 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 60
SSC0121.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 40 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0121.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 40 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0121.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 40 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0121.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 40 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0122.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0122.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0122.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0122.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0123.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0123.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0123.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0123.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0124.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0124.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0124.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0124.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0125.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0125.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0125.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0125.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0126.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 600 | 3 | 25 | 125 | 125 | 600 | 3 | 25 | 32 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0126.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 600 | 3 | 25 | 125 | 125 | 600 | 3 | 25 | 32 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0126.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 600 | 3 | 25 | 125 | 125 | 600 | 3 | 25 | 32 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0126.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3125* | 600 | 3 | 25 | 125 | 125 | 600 | 3 | 25 | 32 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0127.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 41 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0127.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 41 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0127.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 41 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0127.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 41 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0128.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 52 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0128.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 52 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0128.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 52 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0128.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 52 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0129.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 62 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0129.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 62 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0129.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 62 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0129.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 62 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0130.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 77 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0130.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 77 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0130.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 77 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0130.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 77 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0131.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 99 | 100 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0131.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 99 | 100 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0131.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 99 | 100 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0131.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 99 | 100 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0132.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3175* | 200 | 3 | 100 | 175 | 50 | 200 | 3 | 50 | 48.3 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0132.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3175* | 200 | 3 | 100 | 175 | 50 | 200 | 3 | 50 | 48.3 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0132.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3175* | 200 | 3 | 100 | 175 | 50 | 200 | 3 | 50 | 48.3 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0132.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3175* | 200 | 3 | 100 | 175 | 50 | 200 | 3 | 50 | 48.3 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0133.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 200 | 3 | 100 | 225 | 75 | 200 | 3 | 50 | 62.1 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0133.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 200 | 3 | 100 | 225 | 75 | 200 | 3 | 50 | 62.1 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0133.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 200 | 3 | 100 | 225 | 75 | 200 | 3 | 50 | 62.1 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0133.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 200 | 3 | 100 | 225 | 75 | 200 | 3 | 50 | 62.1 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0134.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 200 | 3 | 100 | 300 | 100 | 200 | 3 | 50 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 150 | 30
SSC0134.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 200 | 3 | 100 | 300 | 100 | 200 | 3 | 50 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 150 | 30
SSC0134.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 200 | 3 | 100 | 300 | 100 | 200 | 3 | 50 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 150 | 30
SSC0134.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 200 | 3 | 100 | 300 | 100 | 200 | 3 | 50 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 150 | 30
SSC0135.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 50 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0135.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 50 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0135.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 50 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0135.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 50 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0136.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3175* | 208 | 3 | 100 | 175 | 60 | 208 | 3 | 50 | 46.2 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0136.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3175* | 208 | 3 | 100 | 175 | 60 | 208 | 3 | 50 | 46.2 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0136.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3175* | 208 | 3 | 100 | 175 | 60 | 208 | 3 | 50 | 46.2 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0136.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3175* | 208 | 3 | 100 | 175 | 60 | 208 | 3 | 50 | 46.2 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0137.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 208 | 3 | 100 | 225 | 75 | 208 | 3 | 50 | 59.4 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0137.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 208 | 3 | 100 | 225 | 75 | 208 | 3 | 50 | 59.4 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0137.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 208 | 3 | 100 | 225 | 75 | 208 | 3 | 50 | 59.4 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0137.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 208 | 3 | 100 | 225 | 75 | 208 | 3 | 50 | 59.4 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0138.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 208 | 3 | 100 | 250 | 75 | 208 | 3 | 50 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0138.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 208 | 3 | 100 | 250 | 75 | 208 | 3 | 50 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0138.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 208 | 3 | 100 | 250 | 75 | 208 | 3 | 50 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0138.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 208 | 3 | 100 | 250 | 75 | 208 | 3 | 50 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0139.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 208 | 3 | 100 | 350 | 125 | 208 | 3 | 50 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0139.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 208 | 3 | 100 | 350 | 125 | 208 | 3 | 50 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0139.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 208 | 3 | 100 | 350 | 125 | 208 | 3 | 50 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0139.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 208 | 3 | 100 | 350 | 125 | 208 | 3 | 50 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0140.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 50 | 42 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0140.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 50 | 42 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0140.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 50 | 42 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0140.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 50 | 42 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0141.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3200* | 240 | 3 | 100 | 200 | 75 | 240 | 3 | 50 | 54 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 30
SSC0141.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3200* | 240 | 3 | 100 | 200 | 75 | 240 | 3 | 50 | 54 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 30
SSC0141.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3200* | 240 | 3 | 100 | 200 | 75 | 240 | 3 | 50 | 54 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 30
SSC0141.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3200* | 240 | 3 | 100 | 200 | 75 | 240 | 3 | 50 | 54 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 30
SSC0142.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 240 | 3 | 100 | 250 | 100 | 240 | 3 | 50 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0142.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 240 | 3 | 100 | 250 | 100 | 240 | 3 | 50 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0142.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 240 | 3 | 100 | 250 | 100 | 240 | 3 | 50 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0142.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 240 | 3 | 100 | 250 | 100 | 240 | 3 | 50 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0143.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 50 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 150 | 40
SSC0143.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 50 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 150 | 40
SSC0143.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 50 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 150 | 40
SSC0143.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 50 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 150 | 40
SSC0144.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 50 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 150 | 40
SSC0144.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 50 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 150 | 40
SSC0144.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 50 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 150 | 40
SSC0144.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 50 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 150 | 40
SSC0145.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3125* | 480 | 3 | 65 | 125 | 100 | 480 | 3 | 50 | 34 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 60
SSC0145.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3125* | 480 | 3 | 65 | 125 | 100 | 480 | 3 | 50 | 34 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 60
SSC0145.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3125* | 480 | 3 | 65 | 125 | 100 | 480 | 3 | 50 | 34 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 60
SSC0145.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3125* | 480 | 3 | 65 | 125 | 100 | 480 | 3 | 50 | 34 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 60
SSC0146.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 50 | 40 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0146.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 50 | 40 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0146.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 50 | 40 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0146.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 50 | 40 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0147.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3200* | 480 | 3 | 65 | 200 | 150 | 480 | 3 | 50 | 52 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0147.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3200* | 480 | 3 | 65 | 200 | 150 | 480 | 3 | 50 | 52 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0147.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3200* | 480 | 3 | 65 | 200 | 150 | 480 | 3 | 50 | 52 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0147.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3200* | 480 | 3 | 65 | 200 | 150 | 480 | 3 | 50 | 52 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0148.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 480 | 3 | 65 | 250 | 200 | 480 | 3 | 50 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0148.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 480 | 3 | 65 | 250 | 200 | 480 | 3 | 50 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0148.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 480 | 3 | 65 | 250 | 200 | 480 | 3 | 50 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0148.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 480 | 3 | 65 | 250 | 200 | 480 | 3 | 50 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0149.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 480 | 3 | 65 | 300 | 200 | 480 | 3 | 50 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 150 | 75
SSC0149.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 480 | 3 | 65 | 300 | 200 | 480 | 3 | 50 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 150 | 75
SSC0149.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 480 | 3 | 65 | 300 | 200 | 480 | 3 | 50 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 150 | 75
SSC0149.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 480 | 3 | 65 | 300 | 200 | 480 | 3 | 50 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 150 | 75
SSC0150.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 50 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0150.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 50 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0150.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 50 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0150.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 50 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0151.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3125* | 600 | 3 | 35 | 125 | 125 | 600 | 3 | 35 | 32 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0151.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3125* | 600 | 3 | 35 | 125 | 125 | 600 | 3 | 35 | 32 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0151.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3125* | 600 | 3 | 35 | 125 | 125 | 600 | 3 | 35 | 32 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0151.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3125* | 600 | 3 | 35 | 125 | 125 | 600 | 3 | 35 | 32 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0152.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3150* | 600 | 3 | 35 | 150 | 150 | 600 | 3 | 35 | 41 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0152.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3150* | 600 | 3 | 35 | 150 | 150 | 600 | 3 | 35 | 41 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0152.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3150* | 600 | 3 | 35 | 150 | 150 | 600 | 3 | 35 | 41 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0152.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3150* | 600 | 3 | 35 | 150 | 150 | 600 | 3 | 35 | 41 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0153.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3200* | 600 | 3 | 35 | 200 | 200 | 600 | 3 | 35 | 52 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0153.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3200* | 600 | 3 | 35 | 200 | 200 | 600 | 3 | 35 | 52 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0153.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3200* | 600 | 3 | 35 | 200 | 200 | 600 | 3 | 35 | 52 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0153.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3200* | 600 | 3 | 35 | 200 | 200 | 600 | 3 | 35 | 52 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0154.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 600 | 3 | 35 | 225 | 200 | 600 | 3 | 35 | 62 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0154.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 600 | 3 | 35 | 225 | 200 | 600 | 3 | 35 | 62 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0154.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 600 | 3 | 35 | 225 | 200 | 600 | 3 | 35 | 62 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0154.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 600 | 3 | 35 | 225 | 200 | 600 | 3 | 35 | 62 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0155.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 600 | 3 | 35 | 300 | 300 | 600 | 3 | 35 | 77 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 150 | 100
SSC0155.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 600 | 3 | 35 | 300 | 300 | 600 | 3 | 35 | 77 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 150 | 100
SSC0155.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 600 | 3 | 35 | 300 | 300 | 600 | 3 | 35 | 77 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 150 | 100
SSC0155.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 600 | 3 | 35 | 300 | 300 | 600 | 3 | 35 | 77 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 150 | 100
SSC0156.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0156.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0156.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0156.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0157.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 48.3 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0157.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 48.3 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0157.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 48.3 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0157.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 48.3 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0158.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0158.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0158.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0158.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0159.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0159.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0159.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0159.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0160.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0160.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0160.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0160.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0161.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0161.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0161.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0161.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0162.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 46.2 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0162.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 46.2 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0162.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 46.2 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0162.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 46.2 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0163.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0163.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0163.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0163.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0164.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0164.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0164.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0164.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0165.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0165.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0165.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0165.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0166.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0166.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0166.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0166.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0167.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 42 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0167.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 42 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0167.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 42 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0167.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 42 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0168.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0168.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0168.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0168.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0169.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0169.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0169.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0169.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0170.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0170.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0170.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0170.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0171.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0171.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0171.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0171.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0172.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0172.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0172.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0172.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0173.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0173.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0173.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0173.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0174.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0174.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0174.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0174.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0175.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0175.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0175.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0175.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0176.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 52 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0176.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 52 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0176.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 52 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0176.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 52 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0177.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 62 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0177.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 62 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0177.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 62 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0177.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 62 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0178.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 77 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0178.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 77 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0178.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 77 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0178.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 77 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0179.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 99 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0179.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 99 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0179.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 99 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0179.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HFD3150L | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 99 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0180.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 48.3 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0180.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 48.3 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0180.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 48.3 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0180.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 48.3 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0181.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0181.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0181.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0181.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0182.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0182.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0182.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0182.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0183.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0183.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0183.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0183.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0184.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0184.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0184.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0184.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 200 | 3 | 100 | 150 | 50 | 200 | 3 | 100 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0185.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 46.2 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0185.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 46.2 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0185.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 46.2 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0185.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 46.2 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0186.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0186.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0186.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0186.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0187.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0187.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0187.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0187.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0188.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0188.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0188.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0188.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0189.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0189.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0189.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0189.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 208 | 3 | 100 | 150 | 50 | 208 | 3 | 100 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0190.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 42 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0190.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 42 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0190.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 42 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0190.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 42 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0191.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0191.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0191.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0191.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0192.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0192.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0192.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0192.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0193.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0193.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0193.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0193.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0194.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0194.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0194.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0194.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0195.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0195.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0195.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0195.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 52 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0196.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0196.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0196.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0196.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0197.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0197.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0197.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0197.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0198.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0198.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0198.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0198.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 480 | 3 | 65 | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0199.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 52 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0199.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 52 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0199.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 52 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0199.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 52 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0200.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 62 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0200.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 62 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0200.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 62 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0200.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 62 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0201.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 77 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0201.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 77 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0201.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 77 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0201.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 77 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0202.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 99 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0202.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 99 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0202.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 99 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0202.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HJD3150* | 600 | 3 | 25 | 150 | 150 | 600 | 3 | 25 | 99 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0203.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3175* | 200 | 3 | 100 | 175 | 50 | 200 | 3 | 50 | 48.3 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0203.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3175* | 200 | 3 | 100 | 175 | 50 | 200 | 3 | 50 | 48.3 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0203.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3175* | 200 | 3 | 100 | 175 | 50 | 200 | 3 | 50 | 48.3 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0203.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3175* | 200 | 3 | 100 | 175 | 50 | 200 | 3 | 50 | 48.3 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0204.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 200 | 3 | 100 | 225 | 75 | 200 | 3 | 50 | 62.1 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0204.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 200 | 3 | 100 | 225 | 75 | 200 | 3 | 50 | 62.1 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0204.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 200 | 3 | 100 | 225 | 75 | 200 | 3 | 50 | 62.1 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0204.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 200 | 3 | 100 | 225 | 75 | 200 | 3 | 50 | 62.1 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0205.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 200 | 3 | 100 | 300 | 100 | 200 | 3 | 50 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0205.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 200 | 3 | 100 | 300 | 100 | 200 | 3 | 50 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0205.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 200 | 3 | 100 | 300 | 100 | 200 | 3 | 50 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0205.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 200 | 3 | 100 | 300 | 100 | 200 | 3 | 50 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0206.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 50 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0206.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 50 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0206.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 50 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0206.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 50 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0207.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 50 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0207.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 50 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0207.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 50 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0207.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 50 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0208.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3175* | 208 | 3 | 100 | 175 | 60 | 208 | 3 | 50 | 46.2 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0208.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3175* | 208 | 3 | 100 | 175 | 60 | 208 | 3 | 50 | 46.2 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0208.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3175* | 208 | 3 | 100 | 175 | 60 | 208 | 3 | 50 | 46.2 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0208.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3175* | 208 | 3 | 100 | 175 | 60 | 208 | 3 | 50 | 46.2 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0209.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 208 | 3 | 100 | 225 | 75 | 208 | 3 | 50 | 59.4 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0209.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 208 | 3 | 100 | 225 | 75 | 208 | 3 | 50 | 59.4 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0209.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 208 | 3 | 100 | 225 | 75 | 208 | 3 | 50 | 59.4 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0209.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 208 | 3 | 100 | 225 | 75 | 208 | 3 | 50 | 59.4 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0210.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 208 | 3 | 100 | 250 | 75 | 208 | 3 | 50 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0210.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 208 | 3 | 100 | 250 | 75 | 208 | 3 | 50 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0210.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 208 | 3 | 100 | 250 | 75 | 208 | 3 | 50 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0210.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 208 | 3 | 100 | 250 | 75 | 208 | 3 | 50 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0211.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 208 | 3 | 100 | 350 | 125 | 208 | 3 | 50 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0211.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 208 | 3 | 100 | 350 | 125 | 208 | 3 | 50 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0211.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 208 | 3 | 100 | 350 | 125 | 208 | 3 | 50 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0211.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 208 | 3 | 100 | 350 | 125 | 208 | 3 | 50 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0212.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 50 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0212.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 50 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0212.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 50 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0212.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 50 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0213.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 50 | 42 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0213.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 50 | 42 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0213.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 50 | 42 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0213.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3150* | 240 | 3 | 100 | 150 | 50 | 240 | 3 | 50 | 42 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0214.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3200* | 240 | 3 | 100 | 200 | 75 | 240 | 3 | 50 | 54 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 40
SSC0214.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3200* | 240 | 3 | 100 | 200 | 75 | 240 | 3 | 50 | 54 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 40
SSC0214.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3200* | 240 | 3 | 100 | 200 | 75 | 240 | 3 | 50 | 54 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 40
SSC0214.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3200* | 240 | 3 | 100 | 200 | 75 | 240 | 3 | 50 | 54 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 40
SSC0215.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 240 | 3 | 100 | 250 | 100 | 240 | 3 | 50 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0215.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 240 | 3 | 100 | 250 | 100 | 240 | 3 | 50 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0215.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 240 | 3 | 100 | 250 | 100 | 240 | 3 | 50 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0215.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 240 | 3 | 100 | 250 | 100 | 240 | 3 | 50 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0216.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 50 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0216.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 50 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0216.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 50 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0216.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 50 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0217.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 50 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0217.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 50 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0217.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 50 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0217.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 50 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0218.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 50 | 130 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0218.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 50 | 130 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0218.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 50 | 130 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0218.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 50 | 130 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0219.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3200* | 480 | 3 | 65 | 200 | 150 | 480 | 3 | 50 | 52 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0219.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3200* | 480 | 3 | 65 | 200 | 150 | 480 | 3 | 50 | 52 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0219.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3200* | 480 | 3 | 65 | 200 | 150 | 480 | 3 | 50 | 52 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0219.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3200* | 480 | 3 | 65 | 200 | 150 | 480 | 3 | 50 | 52 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0220.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 480 | 3 | 65 | 250 | 200 | 480 | 3 | 50 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0220.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 480 | 3 | 65 | 250 | 200 | 480 | 3 | 50 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0220.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 480 | 3 | 65 | 250 | 200 | 480 | 3 | 50 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0220.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 480 | 3 | 65 | 250 | 200 | 480 | 3 | 50 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0221.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 480 | 3 | 65 | 300 | 200 | 480 | 3 | 50 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0221.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 480 | 3 | 65 | 300 | 200 | 480 | 3 | 50 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0221.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 480 | 3 | 65 | 300 | 200 | 480 | 3 | 50 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0221.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 480 | 3 | 65 | 300 | 200 | 480 | 3 | 50 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0222.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 50 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0222.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 50 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0222.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 50 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0222.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 50 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0223.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 50 | 124 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0223.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 50 | 124 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0223.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 50 | 124 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0223.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 50 | 124 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0224.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3200* | 600 | 3 | 35 | 200 | 200 | 600 | 3 | 35 | 52 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0224.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3200* | 600 | 3 | 35 | 200 | 200 | 600 | 3 | 35 | 52 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0224.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3200* | 600 | 3 | 35 | 200 | 200 | 600 | 3 | 35 | 52 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0224.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3200* | 600 | 3 | 35 | 200 | 200 | 600 | 3 | 35 | 52 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0225.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 600 | 3 | 35 | 225 | 200 | 600 | 3 | 35 | 62 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0225.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 600 | 3 | 35 | 225 | 200 | 600 | 3 | 35 | 62 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0225.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 600 | 3 | 35 | 225 | 200 | 600 | 3 | 35 | 62 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0225.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 600 | 3 | 35 | 225 | 200 | 600 | 3 | 35 | 62 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0226.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 600 | 3 | 35 | 300 | 300 | 600 | 3 | 35 | 77 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0226.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 600 | 3 | 35 | 300 | 300 | 600 | 3 | 35 | 77 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0226.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 600 | 3 | 35 | 300 | 300 | 600 | 3 | 35 | 77 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0226.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 600 | 3 | 35 | 300 | 300 | 600 | 3 | 35 | 77 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0227.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0227.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0227.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0227.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0228.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0228.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0228.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0228.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0229.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 200 | 3 | 100 | 225 | 75 | 200 | 3 | 100 | 62.1 | 20 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 200 | 3 | 18 | 180 | 60
SSC0229.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 200 | 3 | 100 | 225 | 75 | 200 | 3 | 100 | 62.1 | 20 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0229.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 200 | 3 | 100 | 225 | 75 | 200 | 3 | 100 | 62.1 | 20 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 200 | 3 | 18 | 180 | 60
SSC0229.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 200 | 3 | 100 | 225 | 75 | 200 | 3 | 100 | 62.1 | 20 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0230.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 200 | 3 | 100 | 300 | 100 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 200 | 3 | 18 | 180 | 60
SSC0230.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 200 | 3 | 100 | 300 | 100 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0230.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 200 | 3 | 100 | 300 | 100 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 200 | 3 | 18 | 180 | 60
SSC0230.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 200 | 3 | 100 | 300 | 100 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0231.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 200 | 3 | 18 | 180 | 60
SSC0231.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0231.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 200 | 3 | 18 | 180 | 60
SSC0231.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0232.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 200 | 3 | 18 | 180 | 60
SSC0232.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0232.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 200 | 3 | 18 | 180 | 60
SSC0232.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0233.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 200 | 3 | 18 | 180 | 60
SSC0233.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0233.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 200 | 3 | 18 | 180 | 60
SSC0233.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0234.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 200 | 3 | 18 | 180 | 60
SSC0234.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0234.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 200 | 3 | 18 | 180 | 60
SSC0234.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0235.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 208 | 3 | 100 | 225 | 75 | 208 | 3 | 100 | 59.4 | 20 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 208 | 3 | 18 | 180 | 60
SSC0235.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 208 | 3 | 100 | 225 | 75 | 208 | 3 | 100 | 59.4 | 20 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0235.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 208 | 3 | 100 | 225 | 75 | 208 | 3 | 100 | 59.4 | 20 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 208 | 3 | 18 | 180 | 60
SSC0235.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 208 | 3 | 100 | 225 | 75 | 208 | 3 | 100 | 59.4 | 20 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0236.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 208 | 3 | 100 | 250 | 75 | 208 | 3 | 100 | 74.8 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 208 | 3 | 18 | 180 | 60
SSC0236.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 208 | 3 | 100 | 250 | 75 | 208 | 3 | 100 | 74.8 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0236.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 208 | 3 | 100 | 250 | 75 | 208 | 3 | 100 | 74.8 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 208 | 3 | 18 | 180 | 60
SSC0236.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 208 | 3 | 100 | 250 | 75 | 208 | 3 | 100 | 74.8 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0237.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 208 | 3 | 100 | 350 | 125 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 208 | 3 | 18 | 180 | 60
SSC0237.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 208 | 3 | 100 | 350 | 125 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0237.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 208 | 3 | 100 | 350 | 125 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 208 | 3 | 18 | 180 | 60
SSC0237.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 208 | 3 | 100 | 350 | 125 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0238.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 208 | 3 | 18 | 180 | 60
SSC0238.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0238.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 208 | 3 | 18 | 180 | 60
SSC0238.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0239.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 208 | 3 | 18 | 180 | 60
SSC0239.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0239.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 208 | 3 | 18 | 180 | 60
SSC0239.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0240.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 208 | 3 | 18 | 180 | 60
SSC0240.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0240.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 208 | 3 | 18 | 180 | 60
SSC0240.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0241.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 240 | 3 | 100 | 250 | 100 | 240 | 3 | 100 | 68 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 240 | 3 | 18 | 180 | 60
SSC0241.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 240 | 3 | 100 | 250 | 100 | 240 | 3 | 100 | 68 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0241.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 240 | 3 | 100 | 250 | 100 | 240 | 3 | 100 | 68 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 240 | 3 | 18 | 180 | 60
SSC0241.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 240 | 3 | 100 | 250 | 100 | 240 | 3 | 100 | 68 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0242.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 240 | 3 | 18 | 180 | 60
SSC0242.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0242.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 240 | 3 | 18 | 180 | 60
SSC0242.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0243.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 240 | 3 | 18 | 180 | 60
SSC0243.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0243.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 240 | 3 | 18 | 180 | 60
SSC0243.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0244.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 240 | 3 | 18 | 180 | 60
SSC0244.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0244.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 240 | 3 | 18 | 180 | 60
SSC0244.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0245.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 240 | 3 | 18 | 180 | 60
SSC0245.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0245.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 240 | 3 | 18 | 180 | 60
SSC0245.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0246.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 480 | 3 | 65 | 250 | 200 | 480 | 3 | 65 | 65 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 480 | 3 | 18 | 180 | 150
SSC0246.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 480 | 3 | 65 | 250 | 200 | 480 | 3 | 65 | 65 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0246.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 480 | 3 | 65 | 250 | 200 | 480 | 3 | 65 | 65 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 480 | 3 | 18 | 180 | 150
SSC0246.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3250* | 480 | 3 | 65 | 250 | 200 | 480 | 3 | 65 | 65 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0247.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 480 | 3 | 65 | 300 | 250 | 480 | 3 | 65 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 480 | 3 | 18 | 180 | 150
SSC0247.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 480 | 3 | 65 | 300 | 250 | 480 | 3 | 65 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0247.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 480 | 3 | 65 | 300 | 250 | 480 | 3 | 65 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 480 | 3 | 18 | 180 | 150
SSC0247.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 480 | 3 | 65 | 300 | 250 | 480 | 3 | 65 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0248.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 480 | 3 | 18 | 180 | 150
SSC0248.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0248.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 480 | 3 | 18 | 180 | 150
SSC0248.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0249.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 480 | 3 | 18 | 180 | 150
SSC0249.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0249.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 480 | 3 | 18 | 180 | 150
SSC0249.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0250.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 480 | 3 | 18 | 180 | 150
SSC0250.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0250.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 480 | 3 | 18 | 180 | 150
SSC0250.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0251.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 600 | 3 | 35 | 225 | 200 | 600 | 3 | 35 | 62 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 600 | 3 | 18 | 180 | 150
SSC0251.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 600 | 3 | 35 | 225 | 200 | 600 | 3 | 35 | 62 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0251.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 600 | 3 | 35 | 225 | 200 | 600 | 3 | 35 | 62 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 600 | 3 | 18 | 180 | 150
SSC0251.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3225* | 600 | 3 | 35 | 225 | 200 | 600 | 3 | 35 | 62 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0252.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 600 | 3 | 35 | 300 | 300 | 600 | 3 | 35 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 600 | 3 | 18 | 180 | 150
SSC0252.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 600 | 3 | 35 | 300 | 300 | 600 | 3 | 35 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0252.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 600 | 3 | 35 | 300 | 300 | 600 | 3 | 35 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 600 | 3 | 18 | 180 | 150
SSC0252.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 600 | 3 | 35 | 300 | 300 | 600 | 3 | 35 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0253.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 600 | 3 | 18 | 180 | 150
SSC0253.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0253.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 600 | 3 | 18 | 180 | 150
SSC0253.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0254.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 600 | 3 | 18 | 180 | 150
SSC0254.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0254.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 600 | 3 | 18 | 180 | 150
SSC0254.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0255.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 600 | 3 | 18 | 180 | 150
SSC0255.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0255.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 600 | 3 | 18 | 180 | 150
SSC0255.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0256.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 200 | 3 | 100 | 300 | 100 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 200 | 3 | 18 | 180 | 60
SSC0256.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 200 | 3 | 100 | 300 | 100 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0256.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 200 | 3 | 100 | 300 | 100 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 200 | 3 | 18 | 180 | 60
SSC0256.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 200 | 3 | 100 | 300 | 100 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0257.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 200 | 3 | 18 | 180 | 60
SSC0257.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0257.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 200 | 3 | 18 | 180 | 60
SSC0257.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0258.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 200 | 3 | 18 | 180 | 60
SSC0258.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0258.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 200 | 3 | 18 | 180 | 60
SSC0258.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0259.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 200 | 3 | 18 | 180 | 60
SSC0259.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0259.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 200 | 3 | 18 | 180 | 60
SSC0259.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0260.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 200 | 3 | 18 | 180 | 60
SSC0260.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0260.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 200 | 3 | 18 | 180 | 60
SSC0260.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0261.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 208 | 3 | 100 | 350 | 125 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 208 | 3 | 18 | 180 | 60
SSC0261.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 208 | 3 | 100 | 350 | 125 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0261.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 208 | 3 | 100 | 350 | 125 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 208 | 3 | 18 | 180 | 60
SSC0261.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 208 | 3 | 100 | 350 | 125 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0262.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 208 | 3 | 18 | 180 | 60
SSC0262.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0262.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 208 | 3 | 18 | 180 | 60
SSC0262.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0263.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 208 | 3 | 18 | 180 | 60
SSC0263.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0263.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 208 | 3 | 18 | 180 | 60
SSC0263.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0264.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 208 | 3 | 18 | 180 | 60
SSC0264.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0264.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 208 | 3 | 18 | 180 | 60
SSC0264.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0265.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 240 | 3 | 18 | 180 | 60
SSC0265.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0265.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 240 | 3 | 18 | 180 | 60
SSC0265.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0266.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 240 | 3 | 18 | 180 | 60
SSC0266.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0266.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 240 | 3 | 18 | 180 | 60
SSC0266.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0267.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 240 | 3 | 18 | 180 | 60
SSC0267.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0267.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 240 | 3 | 18 | 180 | 60
SSC0267.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0268.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 240 | 3 | 18 | 180 | 60
SSC0268.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0268.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 240 | 3 | 18 | 180 | 60
SSC0268.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0269.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 480 | 3 | 65 | 300 | 250 | 480 | 3 | 65 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 480 | 3 | 18 | 180 | 150
SSC0269.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 480 | 3 | 65 | 300 | 250 | 480 | 3 | 65 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0269.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 480 | 3 | 65 | 300 | 250 | 480 | 3 | 65 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 480 | 3 | 18 | 180 | 150
SSC0269.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 480 | 3 | 65 | 300 | 250 | 480 | 3 | 65 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0270.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 480 | 3 | 18 | 180 | 150
SSC0270.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0270.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 480 | 3 | 18 | 180 | 150
SSC0270.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0271.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 480 | 3 | 18 | 180 | 150
SSC0271.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0271.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 480 | 3 | 18 | 180 | 150
SSC0271.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0272.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 480 | 3 | 18 | 180 | 150
SSC0272.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0272.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 480 | 3 | 18 | 180 | 150
SSC0272.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0273.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 600 | 3 | 35 | 300 | 300 | 600 | 3 | 35 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 600 | 3 | 18 | 180 | 150
SSC0273.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 600 | 3 | 35 | 300 | 300 | 600 | 3 | 35 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0273.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 600 | 3 | 35 | 300 | 300 | 600 | 3 | 35 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 600 | 3 | 18 | 180 | 150
SSC0273.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 600 | 3 | 35 | 300 | 300 | 600 | 3 | 35 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0274.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 600 | 3 | 18 | 180 | 150
SSC0274.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0274.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 600 | 3 | 18 | 180 | 150
SSC0274.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0275.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 600 | 3 | 18 | 180 | 150
SSC0275.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0275.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 600 | 3 | 18 | 180 | 150
SSC0275.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0276.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 600 | 3 | 18 | 180 | 150
SSC0276.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0276.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 600 | 3 | 18 | 180 | 150
SSC0276.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0277.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 200 | 3 | 100 | 450 | 150 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 200 | 3 | 18 | 180 | 60
SSC0277.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 200 | 3 | 100 | 450 | 150 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0277.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 200 | 3 | 100 | 450 | 150 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 200 | 3 | 18 | 180 | 60
SSC0277.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 200 | 3 | 100 | 450 | 150 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0278.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 150 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 200 | 3 | 18 | 180 | 60
SSC0278.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 150 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0278.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 150 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 200 | 3 | 18 | 180 | 60
SSC0278.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 150 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0279.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 208 | 3 | 18 | 180 | 60
SSC0279.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0279.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 208 | 3 | 18 | 180 | 60
SSC0279.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0280.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 240 | 3 | 100 | 450 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 240 | 3 | 18 | 180 | 60
SSC0280.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 240 | 3 | 100 | 450 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0280.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 240 | 3 | 100 | 450 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 240 | 3 | 18 | 180 | 60
SSC0280.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 240 | 3 | 100 | 450 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0281.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 480 | 3 | 18 | 180 | 150
SSC0281.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0281.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 480 | 3 | 18 | 180 | 150
SSC0281.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0282.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 200 | 3 | 100 | 300 | 100 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0282.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 200 | 3 | 100 | 300 | 100 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0282.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 200 | 3 | 100 | 300 | 100 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0282.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 200 | 3 | 100 | 300 | 100 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0283.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0283.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0283.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0283.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0284.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0284.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0284.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0284.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0285.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0285.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0285.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0285.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0286.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0286.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0286.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0286.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0287.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0287.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0287.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0287.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0288.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 208 | 3 | 100 | 350 | 125 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 208 | 3 | 18 | 240 | 75
SSC0288.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 208 | 3 | 100 | 350 | 125 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0288.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 208 | 3 | 100 | 350 | 125 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 208 | 3 | 18 | 240 | 75
SSC0288.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 208 | 3 | 100 | 350 | 125 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0289.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 208 | 3 | 18 | 240 | 75
SSC0289.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0289.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 208 | 3 | 18 | 240 | 75
SSC0289.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0290.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 208 | 3 | 18 | 240 | 75
SSC0290.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0290.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 208 | 3 | 18 | 240 | 75
SSC0290.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0291.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 208 | 3 | 18 | 240 | 75
SSC0291.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0291.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 208 | 3 | 18 | 240 | 75
SSC0291.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0292.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 208 | 3 | 18 | 240 | 75
SSC0292.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0292.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 208 | 3 | 18 | 240 | 75
SSC0292.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0293.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 240 | 3 | 18 | 240 | 75
SSC0293.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0293.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 240 | 3 | 18 | 240 | 75
SSC0293.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0294.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 240 | 3 | 18 | 240 | 75
SSC0294.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0294.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 240 | 3 | 18 | 240 | 75
SSC0294.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0295.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 240 | 3 | 18 | 240 | 75
SSC0295.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0295.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 240 | 3 | 18 | 240 | 75
SSC0295.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0296.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 240 | 3 | 18 | 240 | 75
SSC0296.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0296.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 240 | 3 | 18 | 240 | 75
SSC0296.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0297.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 240 | 3 | 18 | 240 | 75
SSC0297.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0297.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 240 | 3 | 18 | 240 | 75
SSC0297.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0298.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 480 | 3 | 65 | 300 | 200 | 480 | 3 | 65 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0298.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 480 | 3 | 65 | 300 | 200 | 480 | 3 | 65 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0298.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 480 | 3 | 65 | 300 | 200 | 480 | 3 | 65 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0298.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 480 | 3 | 65 | 300 | 200 | 480 | 3 | 65 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0299.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0299.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0299.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0299.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0300.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0300.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0300.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0300.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0301.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0301.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0301.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0301.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0302.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0302.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0302.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0302.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0303.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0303.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0303.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0303.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0304.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 600 | 3 | 35 | 300 | 300 | 600 | 3 | 35 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 600 | 3 | 18 | 240 | 200
SSC0304.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 600 | 3 | 35 | 300 | 300 | 600 | 3 | 35 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0304.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 600 | 3 | 35 | 300 | 300 | 600 | 3 | 35 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 600 | 3 | 18 | 240 | 200
SSC0304.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 600 | 3 | 35 | 300 | 300 | 600 | 3 | 35 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0305.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 600 | 3 | 18 | 240 | 200
SSC0305.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0305.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 600 | 3 | 18 | 240 | 200
SSC0305.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0306.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 600 | 3 | 18 | 240 | 200
SSC0306.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0306.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 600 | 3 | 18 | 240 | 200
SSC0306.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0307.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 600 | 3 | 18 | 240 | 200
SSC0307.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0307.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 600 | 3 | 18 | 240 | 200
SSC0307.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0308.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 600 | 3 | 18 | 240 | 200
SSC0308.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0308.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 600 | 3 | 18 | 240 | 200
SSC0308.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0309.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 200 | 3 | 100 | 300 | 100 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0309.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 200 | 3 | 100 | 300 | 100 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0309.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 200 | 3 | 100 | 300 | 100 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0309.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 200 | 3 | 100 | 300 | 100 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0310.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0310.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0310.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0310.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0311.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0311.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0311.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0311.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0312.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0312.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0312.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0312.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0313.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0313.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0313.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0313.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0314.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0314.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0314.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0314.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0315.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 208 | 3 | 100 | 350 | 125 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 208 | 3 | 18 | 240 | 75
SSC0315.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 208 | 3 | 100 | 350 | 125 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0315.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 208 | 3 | 100 | 350 | 125 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 208 | 3 | 18 | 240 | 75
SSC0315.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 208 | 3 | 100 | 350 | 125 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0316.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 208 | 3 | 18 | 240 | 75
SSC0316.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0316.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 208 | 3 | 18 | 240 | 75
SSC0316.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0317.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 208 | 3 | 18 | 240 | 75
SSC0317.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0317.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 208 | 3 | 18 | 240 | 75
SSC0317.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0318.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 208 | 3 | 18 | 240 | 75
SSC0318.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0318.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 208 | 3 | 18 | 240 | 75
SSC0318.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0319.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 208 | 3 | 18 | 240 | 75
SSC0319.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0319.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 208 | 3 | 18 | 240 | 75
SSC0319.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0320.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 240 | 3 | 18 | 240 | 75
SSC0320.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0320.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 240 | 3 | 18 | 240 | 75
SSC0320.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0321.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 240 | 3 | 18 | 240 | 75
SSC0321.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0321.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 240 | 3 | 18 | 240 | 75
SSC0321.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0322.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 240 | 3 | 18 | 240 | 75
SSC0322.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0322.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 240 | 3 | 18 | 240 | 75
SSC0322.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0323.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 240 | 3 | 18 | 240 | 75
SSC0323.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0323.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 240 | 3 | 18 | 240 | 75
SSC0323.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0324.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 240 | 3 | 18 | 240 | 75
SSC0324.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0324.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 240 | 3 | 18 | 240 | 75
SSC0324.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0325.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 480 | 3 | 65 | 300 | 200 | 480 | 3 | 65 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0325.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 480 | 3 | 65 | 300 | 200 | 480 | 3 | 65 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0325.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 480 | 3 | 65 | 300 | 200 | 480 | 3 | 65 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0325.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 480 | 3 | 65 | 300 | 200 | 480 | 3 | 65 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0326.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0326.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0326.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0326.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0327.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0327.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0327.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0327.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0328.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0328.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0328.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0328.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0329.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0329.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0329.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0329.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0330.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0330.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0330.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0330.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0331.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 600 | 3 | 35 | 300 | 300 | 600 | 3 | 35 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 600 | 3 | 18 | 240 | 200
SSC0331.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 600 | 3 | 35 | 300 | 300 | 600 | 3 | 35 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0331.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 600 | 3 | 35 | 300 | 300 | 600 | 3 | 35 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 600 | 3 | 18 | 240 | 200
SSC0331.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 600 | 3 | 35 | 300 | 300 | 600 | 3 | 35 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0332.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 600 | 3 | 18 | 240 | 200
SSC0332.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0332.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 600 | 3 | 18 | 240 | 200
SSC0332.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0333.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 600 | 3 | 18 | 240 | 200
SSC0333.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0333.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 600 | 3 | 18 | 240 | 200
SSC0333.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0334.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 600 | 3 | 18 | 240 | 200
SSC0334.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0334.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 600 | 3 | 18 | 240 | 200
SSC0334.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0335.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 600 | 3 | 18 | 240 | 200
SSC0335.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0335.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 600 | 3 | 18 | 240 | 200
SSC0335.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0336.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 200 | 3 | 100 | 450 | 150 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0336.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 200 | 3 | 100 | 450 | 150 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0336.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 200 | 3 | 100 | 450 | 150 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0336.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 200 | 3 | 100 | 450 | 150 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0337.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 150 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0337.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 150 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0337.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 150 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0337.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 150 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0338.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0338.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0338.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0338.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0339.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 208 | 3 | 18 | 240 | 75
SSC0339.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0339.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 208 | 3 | 18 | 240 | 75
SSC0339.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0340.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 208 | 3 | 18 | 240 | 75
SSC0340.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0340.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 208 | 3 | 18 | 240 | 75
SSC0340.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0341.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 240 | 3 | 100 | 450 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 240 | 3 | 18 | 240 | 75
SSC0341.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 240 | 3 | 100 | 450 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0341.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 240 | 3 | 100 | 450 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 240 | 3 | 18 | 240 | 75
SSC0341.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 240 | 3 | 100 | 450 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0342.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 240 | 3 | 18 | 240 | 75
SSC0342.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0342.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 240 | 3 | 18 | 240 | 75
SSC0342.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0343.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0343.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0343.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0343.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0344.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0344.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0344.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0344.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0345.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0345.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0345.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0345.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0346.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0346.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0346.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0346.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0347.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0347.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0347.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0347.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0348.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0348.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0348.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0348.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0349.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0349.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0349.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0349.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0350.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0350.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0350.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0350.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0351.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 208 | 3 | 18 | 304 | 100
SSC0351.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0351.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 208 | 3 | 18 | 304 | 100
SSC0351.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0352.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 208 | 3 | 18 | 304 | 100
SSC0352.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0352.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 208 | 3 | 18 | 304 | 100
SSC0352.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0353.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 208 | 3 | 18 | 304 | 100
SSC0353.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0353.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 208 | 3 | 18 | 304 | 100
SSC0353.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0354.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 208 | 3 | 18 | 304 | 100
SSC0354.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0354.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 208 | 3 | 18 | 304 | 100
SSC0354.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0355.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 208 | 3 | 18 | 304 | 100
SSC0355.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0355.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 208 | 3 | 18 | 304 | 100
SSC0355.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0356.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 240 | 3 | 18 | 304 | 100
SSC0356.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0356.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 240 | 3 | 18 | 304 | 100
SSC0356.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0357.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 240 | 3 | 18 | 304 | 100
SSC0357.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0357.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 240 | 3 | 18 | 304 | 100
SSC0357.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0358.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 240 | 3 | 18 | 304 | 100
SSC0358.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0358.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 240 | 3 | 18 | 304 | 100
SSC0358.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0359.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 240 | 3 | 18 | 304 | 100
SSC0359.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0359.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 240 | 3 | 18 | 304 | 100
SSC0359.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0360.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 240 | 3 | 18 | 304 | 100
SSC0360.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0360.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 240 | 3 | 18 | 304 | 100
SSC0360.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0361.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0361.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0361.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0361.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0362.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0362.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0362.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0362.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0363.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0363.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0363.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0363.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0364.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0364.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0364.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0364.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0365.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0365.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0365.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0365.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0366.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0366.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0366.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0366.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0367.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 600 | 3 | 18 | 304 | 300
SSC0367.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0367.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 600 | 3 | 18 | 304 | 300
SSC0367.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0368.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 600 | 3 | 18 | 304 | 300
SSC0368.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0368.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 600 | 3 | 18 | 304 | 300
SSC0368.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0369.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 600 | 3 | 18 | 304 | 300
SSC0369.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0369.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 600 | 3 | 18 | 304 | 300
SSC0369.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0370.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 600 | 3 | 18 | 304 | 300
SSC0370.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0370.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 600 | 3 | 18 | 304 | 300
SSC0370.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0371.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 600 | 3 | 18 | 304 | 300
SSC0371.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0371.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 600 | 3 | 18 | 304 | 300
SSC0371.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0372.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 600 | 3 | 18 | 304 | 300
SSC0372.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0372.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 600 | 3 | 18 | 304 | 300
SSC0372.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HKD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0373.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0373.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0373.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0373.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0374.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0374.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0374.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0374.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0375.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0375.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0375.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0375.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0376.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0376.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0376.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0376.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0377.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0377.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0377.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0377.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 200 | 3 | 100 | 400 | 125 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0378.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 208 | 3 | 18 | 304 | 100
SSC0378.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0378.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 208 | 3 | 18 | 304 | 100
SSC0378.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0379.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 208 | 3 | 18 | 304 | 100
SSC0379.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0379.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 208 | 3 | 18 | 304 | 100
SSC0379.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0380.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 208 | 3 | 18 | 304 | 100
SSC0380.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0380.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 208 | 3 | 18 | 304 | 100
SSC0380.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0381.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 208 | 3 | 18 | 304 | 100
SSC0381.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0381.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 208 | 3 | 18 | 304 | 100
SSC0381.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0382.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 208 | 3 | 18 | 304 | 100
SSC0382.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0382.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 208 | 3 | 18 | 304 | 100
SSC0382.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0383.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 240 | 3 | 18 | 304 | 100
SSC0383.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0383.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 240 | 3 | 18 | 304 | 100
SSC0383.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 240 | 3 | 100 | 300 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0384.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 240 | 3 | 18 | 304 | 100
SSC0384.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0384.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 240 | 3 | 18 | 304 | 100
SSC0384.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0385.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 240 | 3 | 18 | 304 | 100
SSC0385.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0385.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 240 | 3 | 18 | 304 | 100
SSC0385.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0386.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 240 | 3 | 18 | 304 | 100
SSC0386.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0386.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 240 | 3 | 18 | 304 | 100
SSC0386.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0387.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 240 | 3 | 18 | 304 | 100
SSC0387.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0387.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 240 | 3 | 18 | 304 | 100
SSC0387.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 240 | 3 | 100 | 400 | 150 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0388.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0388.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0388.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0388.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0389.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0389.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0389.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0389.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0390.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0390.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0390.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0390.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0391.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0391.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0391.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0391.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0392.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0392.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0392.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0392.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0393.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0393.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0393.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0393.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 480 | 3 | 65 | 400 | 300 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0394.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 600 | 3 | 18 | 304 | 300
SSC0394.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0394.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 600 | 3 | 18 | 304 | 300
SSC0394.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0395.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 600 | 3 | 18 | 304 | 300
SSC0395.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0395.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 600 | 3 | 18 | 304 | 300
SSC0395.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0396.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 600 | 3 | 18 | 304 | 300
SSC0396.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0396.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 600 | 3 | 18 | 304 | 300
SSC0396.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0397.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 600 | 3 | 18 | 304 | 300
SSC0397.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0397.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 600 | 3 | 18 | 304 | 300
SSC0397.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0398.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 600 | 3 | 18 | 304 | 300
SSC0398.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0398.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 600 | 3 | 18 | 304 | 300
SSC0398.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0399.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 600 | 3 | 18 | 304 | 300
SSC0399.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0399.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 600 | 3 | 18 | 304 | 300
SSC0399.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0400.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 200 | 3 | 100 | 450 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0400.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 200 | 3 | 100 | 450 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0400.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 200 | 3 | 100 | 450 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0400.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 200 | 3 | 100 | 450 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0401.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0401.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0401.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0401.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0402.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0402.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0402.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0402.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0403.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 125 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0403.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 125 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0403.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 125 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0403.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 125 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0404.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 208 | 3 | 18 | 304 | 100
SSC0404.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0404.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 208 | 3 | 18 | 304 | 100
SSC0404.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0405.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 208 | 3 | 18 | 304 | 100
SSC0405.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0405.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 208 | 3 | 18 | 304 | 100
SSC0405.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0406.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 150 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 208 | 3 | 18 | 304 | 100
SSC0406.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 150 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0406.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 150 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 208 | 3 | 18 | 304 | 100
SSC0406.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 150 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0407.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 240 | 3 | 100 | 450 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 240 | 3 | 18 | 304 | 100
SSC0407.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 240 | 3 | 100 | 450 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0407.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 240 | 3 | 100 | 450 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 240 | 3 | 18 | 304 | 100
SSC0407.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 240 | 3 | 100 | 450 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0408.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 240 | 3 | 18 | 304 | 100
SSC0408.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0408.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 240 | 3 | 18 | 304 | 100
SSC0408.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0409.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 150 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 240 | 3 | 18 | 304 | 100
SSC0409.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 150 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0409.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 150 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 240 | 3 | 18 | 304 | 100
SSC0409.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 150 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0410.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0410.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0410.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0410.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0411.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0411.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0411.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0411.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0412.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0412.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0412.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0412.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0413.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 300 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0413.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 300 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0413.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 300 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0413.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 300 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0414.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 200 | 3 | 42 | 360 | 125
SSC0414.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0414.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 200 | 3 | 42 | 360 | 125
SSC0414.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0415.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 200 | 3 | 100 | 450 | 150 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 200 | 3 | 42 | 360 | 125
SSC0415.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 200 | 3 | 100 | 450 | 150 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0415.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 200 | 3 | 100 | 450 | 150 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 200 | 3 | 42 | 360 | 125
SSC0415.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 200 | 3 | 100 | 450 | 150 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0416.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 150 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 200 | 3 | 42 | 360 | 125
SSC0416.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 150 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0416.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 150 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 200 | 3 | 42 | 360 | 125
SSC0416.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 150 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0417.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 200 | 3 | 42 | 360 | 125
SSC0417.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0417.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 200 | 3 | 42 | 360 | 125
SSC0417.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0418.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 200 | 3 | 42 | 360 | 125
SSC0418.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0418.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 200 | 3 | 42 | 360 | 125
SSC0418.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0419.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 200 | 3 | 42 | 360 | 125
SSC0419.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0419.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 200 | 3 | 42 | 360 | 125
SSC0419.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0420.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 208 | 3 | 42 | 360 | 125
SSC0420.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0420.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 208 | 3 | 42 | 360 | 125
SSC0420.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0421.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 208 | 3 | 42 | 360 | 125
SSC0421.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0421.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 208 | 3 | 42 | 360 | 125
SSC0421.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0422.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 208 | 3 | 42 | 360 | 125
SSC0422.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0422.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 208 | 3 | 42 | 360 | 125
SSC0422.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0423.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 208 | 3 | 42 | 360 | 125
SSC0423.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0423.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 208 | 3 | 42 | 360 | 125
SSC0423.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0424.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 208 | 3 | 42 | 360 | 125
SSC0424.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0424.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 208 | 3 | 42 | 360 | 125
SSC0424.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0425.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 208 | 3 | 42 | 360 | 125
SSC0425.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0425.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 208 | 3 | 42 | 360 | 125
SSC0425.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0426.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 240 | 3 | 42 | 360 | 150
SSC0426.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0426.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 240 | 3 | 42 | 360 | 150
SSC0426.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0427.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 240 | 3 | 100 | 450 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 240 | 3 | 42 | 360 | 150
SSC0427.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 240 | 3 | 100 | 450 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0427.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 240 | 3 | 100 | 450 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 240 | 3 | 42 | 360 | 150
SSC0427.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 240 | 3 | 100 | 450 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0428.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 240 | 3 | 42 | 360 | 150
SSC0428.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0428.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 240 | 3 | 42 | 360 | 150
SSC0428.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0429.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 240 | 3 | 42 | 360 | 150
SSC0429.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0429.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 240 | 3 | 42 | 360 | 150
SSC0429.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0430.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 240 | 3 | 42 | 360 | 150
SSC0430.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0430.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 240 | 3 | 42 | 360 | 150
SSC0430.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0431.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 240 | 3 | 42 | 360 | 150
SSC0431.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0431.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 240 | 3 | 42 | 360 | 150
SSC0431.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0432.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 480 | 3 | 42 | 360 | 250
SSC0432.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0432.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 480 | 3 | 42 | 360 | 250
SSC0432.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0433.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 480 | 3 | 42 | 360 | 250
SSC0433.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0433.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 480 | 3 | 42 | 360 | 250
SSC0433.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0434.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 480 | 3 | 42 | 360 | 250
SSC0434.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0434.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 480 | 3 | 42 | 360 | 250
SSC0434.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0435.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 480 | 3 | 42 | 360 | 250
SSC0435.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0435.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 480 | 3 | 42 | 360 | 250
SSC0435.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0436.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 480 | 3 | 42 | 360 | 250
SSC0436.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0436.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 480 | 3 | 42 | 360 | 250
SSC0436.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0437.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 600 | 3 | 42 | 360 | 350
SSC0437.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0437.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 600 | 3 | 42 | 360 | 350
SSC0437.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0438.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 600 | 3 | 42 | 360 | 350
SSC0438.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0438.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 600 | 3 | 42 | 360 | 350
SSC0438.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0439.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 600 | 3 | 35 | 500 | 500 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 600 | 3 | 42 | 360 | 350
SSC0439.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 600 | 3 | 35 | 500 | 500 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0439.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 600 | 3 | 35 | 500 | 500 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 600 | 3 | 42 | 360 | 350
SSC0439.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 600 | 3 | 35 | 500 | 500 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0440.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 600 | 3 | 42 | 360 | 350
SSC0440.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0440.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 600 | 3 | 42 | 360 | 350
SSC0440.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0441.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 600 | 3 | 42 | 360 | 350
SSC0441.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0441.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 600 | 3 | 42 | 360 | 350
SSC0441.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0442.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 600 | 3 | 42 | 360 | 350
SSC0442.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0442.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 600 | 3 | 42 | 360 | 350
SSC0442.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0443.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 200 | 3 | 100 | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 200 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S801V36N3S | 200 | 3 | 42 | 360 | 125
SSC0443.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 200 | 3 | 100 | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 200 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S801+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0443.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 200 | 3 | 100 | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 200 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S811V36N3S | 200 | 3 | 42 | 360 | 125
SSC0443.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 200 | 3 | 100 | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 200 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S811+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0444.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 200 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801V36N3S | 200 | 3 | 42 | 360 | 125
SSC0444.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 200 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0444.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 200 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811V36N3S | 200 | 3 | 42 | 360 | 125
SSC0444.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 200 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0445.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 208 | 3 | 100 | 800 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 208 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S801V36N3S | 208 | 3 | 42 | 360 | 125
SSC0445.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 208 | 3 | 100 | 800 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 208 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S801+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0445.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 208 | 3 | 100 | 800 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 208 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S811V36N3S | 208 | 3 | 42 | 360 | 125
SSC0445.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 208 | 3 | 100 | 800 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 208 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S811+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0446.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801V36N3S | 208 | 3 | 42 | 360 | 125
SSC0446.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0446.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811V36N3S | 208 | 3 | 42 | 360 | 125
SSC0446.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0447.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 240 | 3 | 100 | 700 | 250
|  |  |  | RVSS | Eaton | S801V36N3S | 240 | 3 | 42 | 360 | 150
SSC0447.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 240 | 3 | 100 | 700 | 250
|  |  |  | RVSS | Eaton | S801+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0447.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 240 | 3 | 100 | 700 | 250
|  |  |  | RVSS | Eaton | S811V36N3S | 240 | 3 | 42 | 360 | 150
SSC0447.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 240 | 3 | 100 | 700 | 250
|  |  |  | RVSS | Eaton | S811+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0448.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 240 | 3 | 100 | 800 | 300
|  |  |  | RVSS | Eaton | S801V36N3S | 240 | 3 | 42 | 360 | 150
SSC0448.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 240 | 3 | 100 | 800 | 300
|  |  |  | RVSS | Eaton | S801+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0448.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 240 | 3 | 100 | 800 | 300
|  |  |  | RVSS | Eaton | S811V36N3S | 240 | 3 | 42 | 360 | 150
SSC0448.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 240 | 3 | 100 | 800 | 300
|  |  |  | RVSS | Eaton | S811+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0449.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 240 | 3 | 100 | 1000 | 400
|  |  |  | RVSS | Eaton | S801V36N3S | 240 | 3 | 42 | 360 | 150
SSC0449.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 240 | 3 | 100 | 1000 | 400
|  |  |  | RVSS | Eaton | S801+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0449.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 240 | 3 | 100 | 1000 | 400
|  |  |  | RVSS | Eaton | S811V36N3S | 240 | 3 | 42 | 360 | 150
SSC0449.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 240 | 3 | 100 | 1000 | 400
|  |  |  | RVSS | Eaton | S811+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0450.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 480 | 3 | 65 | 700 | 500
|  |  |  | RVSS | Eaton | S801V36N3S | 480 | 3 | 42 | 360 | 250
SSC0450.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 480 | 3 | 65 | 700 | 500
|  |  |  | RVSS | Eaton | S801+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0450.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 480 | 3 | 65 | 700 | 500
|  |  |  | RVSS | Eaton | S811V36N3S | 480 | 3 | 42 | 360 | 250
SSC0450.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 480 | 3 | 65 | 700 | 500
|  |  |  | RVSS | Eaton | S811+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0451.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S801V36N3S | 480 | 3 | 42 | 360 | 250
SSC0451.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S801+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0451.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S811V36N3S | 480 | 3 | 42 | 360 | 250
SSC0451.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S811+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0452.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 600 | 3 | 35 | 700 | 500
|  |  |  | RVSS | Eaton | S801V36N3S | 600 | 3 | 42 | 360 | 250
SSC0452.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 600 | 3 | 35 | 700 | 500
|  |  |  | RVSS | Eaton | S801+V36N3S | 600 | 3 | 42 | 360 | 250
SSC0452.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 600 | 3 | 35 | 700 | 500
|  |  |  | RVSS | Eaton | S811V36N3S | 600 | 3 | 42 | 360 | 250
SSC0452.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 600 | 3 | 35 | 700 | 500
|  |  |  | RVSS | Eaton | S811+V36N3S | 600 | 3 | 42 | 360 | 250
SSC0453.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 600 | 3 | 35 | 800 | 500
|  |  |  | RVSS | Eaton | S801V36N3S | 600 | 3 | 42 | 360 | 250
SSC0453.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 600 | 3 | 35 | 800 | 500
|  |  |  | RVSS | Eaton | S801+V36N3S | 600 | 3 | 42 | 360 | 250
SSC0453.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 600 | 3 | 35 | 800 | 500
|  |  |  | RVSS | Eaton | S811V36N3S | 600 | 3 | 42 | 360 | 250
SSC0453.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 600 | 3 | 35 | 800 | 500
|  |  |  | RVSS | Eaton | S811+V36N3S | 600 | 3 | 42 | 360 | 250
SSC0454.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S801V36N3S | 600 | 3 | 42 | 360 | 250
SSC0454.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S801+V36N3S | 600 | 3 | 42 | 360 | 250
SSC0454.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S811V36N3S | 600 | 3 | 42 | 360 | 250
SSC0454.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S811+V36N3S | 600 | 3 | 42 | 360 | 250
SSC0455.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 200 | 3 | 100 | 450 | 150 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 200 | 3 | 42 | 420 | 150
SSC0455.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 200 | 3 | 100 | 450 | 150 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0455.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 200 | 3 | 100 | 450 | 150 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 200 | 3 | 42 | 420 | 150
SSC0455.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 200 | 3 | 100 | 450 | 150 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0456.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 200 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 200 | 3 | 42 | 420 | 150
SSC0456.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 200 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0456.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 200 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 200 | 3 | 42 | 420 | 150
SSC0456.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 200 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0457.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 200 | 3 | 42 | 420 | 150
SSC0457.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0457.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 200 | 3 | 42 | 420 | 150
SSC0457.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0458.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 200 | 3 | 42 | 420 | 150
SSC0458.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0458.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 200 | 3 | 42 | 420 | 150
SSC0458.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0459.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 200 | 3 | 42 | 420 | 150
SSC0459.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0459.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 200 | 3 | 42 | 420 | 150
SSC0459.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0460.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 200 | 3 | 42 | 420 | 150
SSC0460.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0460.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 200 | 3 | 42 | 420 | 150
SSC0460.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0461.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 208 | 3 | 42 | 420 | 150
SSC0461.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0461.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 208 | 3 | 42 | 420 | 150
SSC0461.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0462.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 208 | 3 | 42 | 420 | 150
SSC0462.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0462.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 208 | 3 | 42 | 420 | 150
SSC0462.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0463.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 208 | 3 | 42 | 420 | 150
SSC0463.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0463.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 208 | 3 | 42 | 420 | 150
SSC0463.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0464.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 208 | 3 | 42 | 420 | 150
SSC0464.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0464.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 208 | 3 | 42 | 420 | 150
SSC0464.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0465.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 208 | 3 | 42 | 420 | 150
SSC0465.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0465.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 208 | 3 | 42 | 420 | 150
SSC0465.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0466.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 208 | 3 | 42 | 420 | 150
SSC0466.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0466.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 208 | 3 | 42 | 420 | 150
SSC0466.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0467.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 240 | 3 | 100 | 450 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 240 | 3 | 42 | 420 | 150
SSC0467.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 240 | 3 | 100 | 450 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0467.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 240 | 3 | 100 | 450 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 240 | 3 | 42 | 420 | 150
SSC0467.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 240 | 3 | 100 | 450 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0468.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 240 | 3 | 42 | 420 | 150
SSC0468.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0468.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 240 | 3 | 42 | 420 | 150
SSC0468.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0469.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 240 | 3 | 42 | 420 | 150
SSC0469.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0469.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 240 | 3 | 42 | 420 | 150
SSC0469.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0470.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 240 | 3 | 42 | 420 | 150
SSC0470.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0470.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 240 | 3 | 42 | 420 | 150
SSC0470.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0471.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 240 | 3 | 42 | 420 | 150
SSC0471.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0471.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 240 | 3 | 42 | 420 | 150
SSC0471.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0472.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 480 | 3 | 42 | 420 | 350
SSC0472.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0472.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 480 | 3 | 42 | 420 | 350
SSC0472.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0473.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 480 | 3 | 42 | 420 | 350
SSC0473.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0473.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 480 | 3 | 42 | 420 | 350
SSC0473.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0474.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 480 | 3 | 42 | 420 | 350
SSC0474.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0474.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 480 | 3 | 42 | 420 | 350
SSC0474.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0475.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 480 | 3 | 42 | 420 | 350
SSC0475.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0475.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 480 | 3 | 42 | 420 | 350
SSC0475.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0476.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 480 | 3 | 42 | 420 | 350
SSC0476.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0476.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 480 | 3 | 42 | 420 | 350
SSC0476.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0477.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 480 | 3 | 42 | 420 | 350
SSC0477.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0477.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 480 | 3 | 42 | 420 | 350
SSC0477.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0478.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 600 | 3 | 42 | 420 | 450
SSC0478.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0478.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 600 | 3 | 42 | 420 | 450
SSC0478.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0479.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 600 | 3 | 35 | 500 | 500 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 600 | 3 | 42 | 420 | 450
SSC0479.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 600 | 3 | 35 | 500 | 500 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0479.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 600 | 3 | 35 | 500 | 500 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 600 | 3 | 42 | 420 | 450
SSC0479.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 600 | 3 | 35 | 500 | 500 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0480.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 600 | 3 | 42 | 420 | 450
SSC0480.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0480.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 600 | 3 | 42 | 420 | 450
SSC0480.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0481.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 600 | 3 | 42 | 420 | 450
SSC0481.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0481.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 600 | 3 | 42 | 420 | 450
SSC0481.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0482.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 600 | 3 | 42 | 420 | 450
SSC0482.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0482.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 600 | 3 | 42 | 420 | 450
SSC0482.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0483.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 600 | 3 | 42 | 420 | 450
SSC0483.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0483.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 600 | 3 | 42 | 420 | 450
SSC0483.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0484.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 600 | 3 | 42 | 420 | 450
SSC0484.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0484.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 600 | 3 | 42 | 420 | 450
SSC0484.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0485.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 200 | 3 | 100 | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 200 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S801V42N3S | 200 | 3 | 42 | 420 | 150
SSC0485.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 200 | 3 | 100 | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 200 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S801+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0485.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 200 | 3 | 100 | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 200 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S811V42N3S | 200 | 3 | 42 | 420 | 150
SSC0485.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 200 | 3 | 100 | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 200 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S811+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0486.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 200 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801V42N3S | 200 | 3 | 42 | 420 | 150
SSC0486.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 200 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0486.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 200 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811V42N3S | 200 | 3 | 42 | 420 | 150
SSC0486.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 200 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0487.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 200 | 3 | 100 | 1200 | 200
|  |  |  | RVSS | Eaton | S801V42N3S | 200 | 3 | 42 | 420 | 150
SSC0487.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 200 | 3 | 100 | 1200 | 200
|  |  |  | RVSS | Eaton | S801+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0487.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 200 | 3 | 100 | 1200 | 200
|  |  |  | RVSS | Eaton | S811V42N3S | 200 | 3 | 42 | 420 | 150
SSC0487.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 200 | 3 | 100 | 1200 | 200
|  |  |  | RVSS | Eaton | S811+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0488.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 208 | 3 | 100 | 800 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 208 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S801V42N3S | 208 | 3 | 42 | 420 | 150
SSC0488.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 208 | 3 | 100 | 800 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 208 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S801+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0488.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 208 | 3 | 100 | 800 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 208 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S811V42N3S | 208 | 3 | 42 | 420 | 150
SSC0488.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 208 | 3 | 100 | 800 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 208 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S811+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0489.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801V42N3S | 208 | 3 | 42 | 420 | 150
SSC0489.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0489.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811V42N3S | 208 | 3 | 42 | 420 | 150
SSC0489.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0490.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801V42N3S | 208 | 3 | 42 | 420 | 150
SSC0490.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0490.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811V42N3S | 208 | 3 | 42 | 420 | 150
SSC0490.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0491.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 240 | 3 | 100 | 700 | 250
|  |  |  | RVSS | Eaton | S801V42N3S | 240 | 3 | 42 | 420 | 150
SSC0491.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 240 | 3 | 100 | 700 | 250
|  |  |  | RVSS | Eaton | S801+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0491.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 240 | 3 | 100 | 700 | 250
|  |  |  | RVSS | Eaton | S811V42N3S | 240 | 3 | 42 | 420 | 150
SSC0491.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 240 | 3 | 100 | 700 | 250
|  |  |  | RVSS | Eaton | S811+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0492.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 240 | 3 | 100 | 800 | 300
|  |  |  | RVSS | Eaton | S801V42N3S | 240 | 3 | 42 | 420 | 150
SSC0492.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 240 | 3 | 100 | 800 | 300
|  |  |  | RVSS | Eaton | S801+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0492.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 240 | 3 | 100 | 800 | 300
|  |  |  | RVSS | Eaton | S811V42N3S | 240 | 3 | 42 | 420 | 150
SSC0492.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 240 | 3 | 100 | 800 | 300
|  |  |  | RVSS | Eaton | S811+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0493.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 240 | 3 | 100 | 1000 | 400
|  |  |  | RVSS | Eaton | S801V42N3S | 240 | 3 | 42 | 420 | 150
SSC0493.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 240 | 3 | 100 | 1000 | 400
|  |  |  | RVSS | Eaton | S801+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0493.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 240 | 3 | 100 | 1000 | 400
|  |  |  | RVSS | Eaton | S811V42N3S | 240 | 3 | 42 | 420 | 150
SSC0493.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 240 | 3 | 100 | 1000 | 400
|  |  |  | RVSS | Eaton | S811+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0494.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 480 | 3 | 65 | 700 | 500
|  |  |  | RVSS | Eaton | S801V42N3S | 480 | 3 | 42 | 420 | 350
SSC0494.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 480 | 3 | 65 | 700 | 500
|  |  |  | RVSS | Eaton | S801+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0494.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 480 | 3 | 65 | 700 | 500
|  |  |  | RVSS | Eaton | S811V42N3S | 480 | 3 | 42 | 420 | 350
SSC0494.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 480 | 3 | 65 | 700 | 500
|  |  |  | RVSS | Eaton | S811+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0495.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S801V42N3S | 480 | 3 | 42 | 420 | 350
SSC0495.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S801+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0495.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S811V42N3S | 480 | 3 | 42 | 420 | 350
SSC0495.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S811+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0496.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S801V42N3S | 480 | 3 | 42 | 420 | 350
SSC0496.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S801+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0496.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S811V42N3S | 480 | 3 | 42 | 420 | 350
SSC0496.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S811+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0497.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V42N3S | 480 | 3 | 42 | 420 | 350
SSC0497.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0497.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V42N3S | 480 | 3 | 42 | 420 | 350
SSC0497.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0498.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 600 | 3 | 35 | 700 | 500
|  |  |  | RVSS | Eaton | S801V42N3S | 600 | 3 | 42 | 420 | 350
SSC0498.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 600 | 3 | 35 | 700 | 500
|  |  |  | RVSS | Eaton | S801+V42N3S | 600 | 3 | 42 | 420 | 350
SSC0498.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 600 | 3 | 35 | 700 | 500
|  |  |  | RVSS | Eaton | S811V42N3S | 600 | 3 | 42 | 420 | 350
SSC0498.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 600 | 3 | 35 | 700 | 500
|  |  |  | RVSS | Eaton | S811+V42N3S | 600 | 3 | 42 | 420 | 350
SSC0499.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 600 | 3 | 35 | 800 | 500
|  |  |  | RVSS | Eaton | S801V42N3S | 600 | 3 | 42 | 420 | 350
SSC0499.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 600 | 3 | 35 | 800 | 500
|  |  |  | RVSS | Eaton | S801+V42N3S | 600 | 3 | 42 | 420 | 350
SSC0499.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 600 | 3 | 35 | 800 | 500
|  |  |  | RVSS | Eaton | S811V42N3S | 600 | 3 | 42 | 420 | 350
SSC0499.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 600 | 3 | 35 | 800 | 500
|  |  |  | RVSS | Eaton | S811+V42N3S | 600 | 3 | 42 | 420 | 350
SSC0500.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S801V42N3S | 600 | 3 | 42 | 420 | 350
SSC0500.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S801+V42N3S | 600 | 3 | 42 | 420 | 350
SSC0500.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S811V42N3S | 600 | 3 | 42 | 420 | 350
SSC0500.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S811+V42N3S | 600 | 3 | 42 | 420 | 350
SSC0501.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S801V42N3S | 600 | 3 | 42 | 420 | 350
SSC0501.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S801+V42N3S | 600 | 3 | 42 | 420 | 350
SSC0501.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S811V42N3S | 600 | 3 | 42 | 420 | 350
SSC0501.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S811+V42N3S | 600 | 3 | 42 | 420 | 350
SSC0502.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V42N3S | 600 | 3 | 42 | 420 | 350
SSC0502.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V42N3S | 600 | 3 | 42 | 420 | 350
SSC0502.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V42N3S | 600 | 3 | 42 | 420 | 350
SSC0502.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V42N3S | 600 | 3 | 42 | 420 | 350
SSC0503.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 150 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 200 | 3 | 42 | 500 | 150
SSC0503.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 150 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0503.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 150 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 200 | 3 | 42 | 500 | 150
SSC0503.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 150 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0504.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 200 | 3 | 42 | 500 | 150
SSC0504.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0504.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 200 | 3 | 42 | 500 | 150
SSC0504.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0505.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 200 | 3 | 42 | 500 | 150
SSC0505.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0505.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 200 | 3 | 42 | 500 | 150
SSC0505.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0506.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 200 | 3 | 42 | 500 | 150
SSC0506.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0506.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 200 | 3 | 42 | 500 | 150
SSC0506.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0507.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 200 | 3 | 42 | 500 | 150
SSC0507.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0507.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 200 | 3 | 42 | 500 | 150
SSC0507.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0508.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 208 | 3 | 42 | 500 | 150
SSC0508.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0508.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 208 | 3 | 42 | 500 | 150
SSC0508.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0509.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 208 | 3 | 42 | 500 | 150
SSC0509.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0509.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 208 | 3 | 42 | 500 | 150
SSC0509.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0510.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 208 | 3 | 42 | 500 | 150
SSC0510.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0510.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 208 | 3 | 42 | 500 | 150
SSC0510.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0511.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 208 | 3 | 42 | 500 | 150
SSC0511.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0511.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 208 | 3 | 42 | 500 | 150
SSC0511.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0512.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 208 | 3 | 42 | 500 | 150
SSC0512.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0512.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 208 | 3 | 42 | 500 | 150
SSC0512.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0513.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 240 | 3 | 42 | 500 | 150
SSC0513.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 240 | 3 | 42 | 500 | 150
SSC0513.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 240 | 3 | 42 | 500 | 150
SSC0513.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 240 | 3 | 42 | 500 | 150
SSC0514.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 240 | 3 | 42 | 500 | 150
SSC0514.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 240 | 3 | 42 | 500 | 150
SSC0514.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 240 | 3 | 42 | 500 | 150
SSC0514.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 240 | 3 | 42 | 500 | 150
SSC0515.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 240 | 3 | 42 | 500 | 150
SSC0515.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 240 | 3 | 42 | 500 | 150
SSC0515.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 240 | 3 | 42 | 500 | 150
SSC0515.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 240 | 3 | 42 | 500 | 150
SSC0516.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 240 | 3 | 42 | 500 | 150
SSC0516.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 240 | 3 | 42 | 500 | 150
SSC0516.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 240 | 3 | 42 | 500 | 150
SSC0516.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 240 | 3 | 42 | 500 | 150
SSC0517.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 240 | 3 | 42 | 500 | 150
SSC0517.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 240 | 3 | 42 | 500 | 150
SSC0517.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 240 | 3 | 42 | 500 | 150
SSC0517.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 240 | 3 | 42 | 500 | 150
SSC0518.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 480 | 3 | 42 | 500 | 400
SSC0518.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0518.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 480 | 3 | 42 | 500 | 400
SSC0518.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0519.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 480 | 3 | 42 | 500 | 400
SSC0519.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0519.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 480 | 3 | 42 | 500 | 400
SSC0519.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0520.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 480 | 3 | 42 | 500 | 400
SSC0520.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0520.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 480 | 3 | 42 | 500 | 400
SSC0520.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0521.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 480 | 3 | 42 | 500 | 400
SSC0521.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0521.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 480 | 3 | 42 | 500 | 400
SSC0521.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0522.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 480 | 3 | 42 | 500 | 400
SSC0522.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0522.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 480 | 3 | 42 | 500 | 400
SSC0522.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0523.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 480 | 3 | 42 | 500 | 400
SSC0523.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0523.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 480 | 3 | 42 | 500 | 400
SSC0523.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0524.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 480 | 3 | 42 | 500 | 400
SSC0524.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0524.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 480 | 3 | 42 | 500 | 400
SSC0524.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0525.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 600 | 3 | 35 | 500 | 500 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 600 | 3 | 42 | 500 | 500
SSC0525.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 600 | 3 | 35 | 500 | 500 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0525.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 600 | 3 | 35 | 500 | 500 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 600 | 3 | 42 | 500 | 500
SSC0525.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 600 | 3 | 35 | 500 | 500 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0526.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 600 | 3 | 42 | 500 | 500
SSC0526.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0526.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 600 | 3 | 42 | 500 | 500
SSC0526.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0527.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 600 | 3 | 42 | 500 | 500
SSC0527.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0527.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 600 | 3 | 42 | 500 | 500
SSC0527.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0528.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 600 | 3 | 42 | 500 | 500
SSC0528.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0528.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 600 | 3 | 42 | 500 | 500
SSC0528.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0529.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 600 | 3 | 42 | 500 | 500
SSC0529.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0529.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 600 | 3 | 42 | 500 | 500
SSC0529.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0530.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 600 | 3 | 42 | 500 | 500
SSC0530.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0530.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 600 | 3 | 42 | 500 | 500
SSC0530.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0531.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 600 | 3 | 42 | 500 | 500
SSC0531.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0531.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 600 | 3 | 42 | 500 | 500
SSC0531.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0532.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 200 | 3 | 100 | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 200 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S801V50N3S | 200 | 3 | 42 | 500 | 150
SSC0532.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 200 | 3 | 100 | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 200 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S801+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0532.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 200 | 3 | 100 | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 200 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S811V50N3S | 200 | 3 | 42 | 500 | 150
SSC0532.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 200 | 3 | 100 | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 200 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S811+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0533.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 200 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801V50N3S | 200 | 3 | 42 | 500 | 150
SSC0533.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 200 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0533.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 200 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811V50N3S | 200 | 3 | 42 | 500 | 150
SSC0533.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 200 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0534.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 200 | 3 | 100 | 1200 | 200
|  |  |  | RVSS | Eaton | S801V50N3S | 200 | 3 | 42 | 500 | 150
SSC0534.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 200 | 3 | 100 | 1200 | 200
|  |  |  | RVSS | Eaton | S801+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0534.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 200 | 3 | 100 | 1200 | 200
|  |  |  | RVSS | Eaton | S811V50N3S | 200 | 3 | 42 | 500 | 150
SSC0534.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 200 | 3 | 100 | 1200 | 200
|  |  |  | RVSS | Eaton | S811+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0535.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 208 | 3 | 100 | 800 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 208 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S801V50N3S | 208 | 3 | 42 | 500 | 150
SSC0535.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 208 | 3 | 100 | 800 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 208 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S801+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0535.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 208 | 3 | 100 | 800 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 208 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S811V50N3S | 208 | 3 | 42 | 500 | 150
SSC0535.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 208 | 3 | 100 | 800 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 208 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S811+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0536.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801V50N3S | 208 | 3 | 42 | 500 | 150
SSC0536.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0536.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811V50N3S | 208 | 3 | 42 | 500 | 150
SSC0536.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0537.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801V50N3S | 208 | 3 | 42 | 500 | 150
SSC0537.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0537.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811V50N3S | 208 | 3 | 42 | 500 | 150
SSC0537.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0538.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 240 | 3 | 100 | 700 | 250
|  |  |  | RVSS | Eaton | S801V50N3S | 240 | 3 | 42 | 500 | 200
SSC0538.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 240 | 3 | 100 | 700 | 250
|  |  |  | RVSS | Eaton | S801+V50N3S | 240 | 3 | 42 | 500 | 200
SSC0538.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 240 | 3 | 100 | 700 | 250
|  |  |  | RVSS | Eaton | S811V50N3S | 240 | 3 | 42 | 500 | 200
SSC0538.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 240 | 3 | 100 | 700 | 250
|  |  |  | RVSS | Eaton | S811+V50N3S | 240 | 3 | 42 | 500 | 200
SSC0539.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 240 | 3 | 100 | 800 | 300
|  |  |  | RVSS | Eaton | S801V50N3S | 240 | 3 | 42 | 500 | 200
SSC0539.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 240 | 3 | 100 | 800 | 300
|  |  |  | RVSS | Eaton | S801+V50N3S | 240 | 3 | 42 | 500 | 200
SSC0539.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 240 | 3 | 100 | 800 | 300
|  |  |  | RVSS | Eaton | S811V50N3S | 240 | 3 | 42 | 500 | 200
SSC0539.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 240 | 3 | 100 | 800 | 300
|  |  |  | RVSS | Eaton | S811+V50N3S | 240 | 3 | 42 | 500 | 200
SSC0540.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 240 | 3 | 100 | 1000 | 500
|  |  |  | RVSS | Eaton | S801V50N3S | 240 | 3 | 42 | 500 | 200
SSC0540.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 240 | 3 | 100 | 1000 | 500
|  |  |  | RVSS | Eaton | S801+V50N3S | 240 | 3 | 42 | 500 | 200
SSC0540.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 240 | 3 | 100 | 1000 | 500
|  |  |  | RVSS | Eaton | S811V50N3S | 240 | 3 | 42 | 500 | 200
SSC0540.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 240 | 3 | 100 | 1000 | 500
|  |  |  | RVSS | Eaton | S811+V50N3S | 240 | 3 | 42 | 500 | 200
SSC0541.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 240 | 3 | 100 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V50N3S | 240 | 3 | 42 | 500 | 200
SSC0541.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 240 | 3 | 100 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V50N3S | 240 | 3 | 42 | 500 | 200
SSC0541.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 240 | 3 | 100 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V50N3S | 240 | 3 | 42 | 500 | 200
SSC0541.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 240 | 3 | 100 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V50N3S | 240 | 3 | 42 | 500 | 200
SSC0542.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 480 | 3 | 65 | 700 | 500
|  |  |  | RVSS | Eaton | S801V50N3S | 480 | 3 | 42 | 500 | 400
SSC0542.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 480 | 3 | 65 | 700 | 500
|  |  |  | RVSS | Eaton | S801+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0542.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 480 | 3 | 65 | 700 | 500
|  |  |  | RVSS | Eaton | S811V50N3S | 480 | 3 | 42 | 500 | 400
SSC0542.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 480 | 3 | 65 | 700 | 500
|  |  |  | RVSS | Eaton | S811+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0543.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S801V50N3S | 480 | 3 | 42 | 500 | 400
SSC0543.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S801+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0543.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S811V50N3S | 480 | 3 | 42 | 500 | 400
SSC0543.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S811+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0544.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S801V50N3S | 480 | 3 | 42 | 500 | 400
SSC0544.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S801+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0544.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S811V50N3S | 480 | 3 | 42 | 500 | 400
SSC0544.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S811+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0545.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V50N3S | 480 | 3 | 42 | 500 | 400
SSC0545.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0545.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V50N3S | 480 | 3 | 42 | 500 | 400
SSC0545.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0546.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V50N3S | 480 | 3 | 42 | 500 | 400
SSC0546.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0546.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V50N3S | 480 | 3 | 42 | 500 | 400
SSC0546.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0547.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 600 | 3 | 35 | 700 | 500
|  |  |  | RVSS | Eaton | S801V50N3S | 600 | 3 | 42 | 500 | 500
SSC0547.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 600 | 3 | 35 | 700 | 500
|  |  |  | RVSS | Eaton | S801+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0547.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 600 | 3 | 35 | 700 | 500
|  |  |  | RVSS | Eaton | S811V50N3S | 600 | 3 | 42 | 500 | 500
SSC0547.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 600 | 3 | 35 | 700 | 500
|  |  |  | RVSS | Eaton | S811+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0548.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 600 | 3 | 35 | 800 | 500
|  |  |  | RVSS | Eaton | S801V50N3S | 600 | 3 | 42 | 500 | 500
SSC0548.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 600 | 3 | 35 | 800 | 500
|  |  |  | RVSS | Eaton | S801+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0548.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 600 | 3 | 35 | 800 | 500
|  |  |  | RVSS | Eaton | S811V50N3S | 600 | 3 | 42 | 500 | 500
SSC0548.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 600 | 3 | 35 | 800 | 500
|  |  |  | RVSS | Eaton | S811+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0549.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S801V50N3S | 600 | 3 | 42 | 500 | 500
SSC0549.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S801+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0549.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S811V50N3S | 600 | 3 | 42 | 500 | 500
SSC0549.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S811+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0550.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S801V50N3S | 600 | 3 | 42 | 500 | 500
SSC0550.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S801+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0550.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S811V50N3S | 600 | 3 | 42 | 500 | 500
SSC0550.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S811+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0551.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V50N3S | 600 | 3 | 42 | 500 | 500
SSC0551.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0551.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V50N3S | 600 | 3 | 42 | 500 | 500
SSC0551.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0552.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V50N3S | 600 | 3 | 42 | 500 | 500
SSC0552.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0552.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V50N3S | 600 | 3 | 42 | 500 | 500
SSC0552.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0553.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 200 | 3 | 100 | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 200 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S801V65N3S | 200 | 3 | 42 | 650 | 200
SSC0553.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 200 | 3 | 100 | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 200 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S801+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0553.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 200 | 3 | 100 | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 200 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S811V65N3S | 200 | 3 | 42 | 650 | 200
SSC0553.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 200 | 3 | 100 | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 200 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S811+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0554.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 200 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801V65N3S | 200 | 3 | 42 | 650 | 200
SSC0554.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 200 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0554.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 200 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811V65N3S | 200 | 3 | 42 | 650 | 200
SSC0554.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 200 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0555.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 200 | 3 | 100 | 1200 | 200
|  |  |  | RVSS | Eaton | S801V65N3S | 200 | 3 | 42 | 650 | 200
SSC0555.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 200 | 3 | 100 | 1200 | 200
|  |  |  | RVSS | Eaton | S801+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0555.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 200 | 3 | 100 | 1200 | 200
|  |  |  | RVSS | Eaton | S811V65N3S | 200 | 3 | 42 | 650 | 200
SSC0555.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 200 | 3 | 100 | 1200 | 200
|  |  |  | RVSS | Eaton | S811+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0556.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 200 | 3 | 100 | 1200 | 200
|  |  |  | RVSS | Eaton | S801V65N3S | 200 | 3 | 42 | 650 | 200
SSC0556.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 200 | 3 | 100 | 1200 | 200
|  |  |  | RVSS | Eaton | S801+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0556.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 200 | 3 | 100 | 1200 | 200
|  |  |  | RVSS | Eaton | S811V65N3S | 200 | 3 | 42 | 650 | 200
SSC0556.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 200 | 3 | 100 | 1200 | 200
|  |  |  | RVSS | Eaton | S811+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0557.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 208 | 3 | 100 | 800 | 200 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 208 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S801V65N3S | 208 | 3 | 42 | 650 | 200
SSC0557.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 208 | 3 | 100 | 800 | 200 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 208 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S801+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0557.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 208 | 3 | 100 | 800 | 200 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 208 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S811V65N3S | 208 | 3 | 42 | 650 | 200
SSC0557.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 208 | 3 | 100 | 800 | 200 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 208 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S811+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0558.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801V65N3S | 208 | 3 | 42 | 650 | 200
SSC0558.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0558.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811V65N3S | 208 | 3 | 42 | 650 | 200
SSC0558.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0559.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801V65N3S | 208 | 3 | 42 | 650 | 200
SSC0559.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0559.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811V65N3S | 208 | 3 | 42 | 650 | 200
SSC0559.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0560.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 208 | 3 | 100 | 1200 | 200
|  |  |  | RVSS | Eaton | S801V65N3S | 208 | 3 | 42 | 650 | 200
SSC0560.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 208 | 3 | 100 | 1200 | 200
|  |  |  | RVSS | Eaton | S801+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0560.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 208 | 3 | 100 | 1200 | 200
|  |  |  | RVSS | Eaton | S811V65N3S | 208 | 3 | 42 | 650 | 200
SSC0560.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 208 | 3 | 100 | 1200 | 200
|  |  |  | RVSS | Eaton | S811+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0561.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 240 | 3 | 100 | 700 | 250
|  |  |  | RVSS | Eaton | S801V65N3S | 240 | 3 | 42 | 650 | 250
SSC0561.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 240 | 3 | 100 | 700 | 250
|  |  |  | RVSS | Eaton | S801+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0561.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 240 | 3 | 100 | 700 | 250
|  |  |  | RVSS | Eaton | S811V65N3S | 240 | 3 | 42 | 650 | 250
SSC0561.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 240 | 3 | 100 | 700 | 250
|  |  |  | RVSS | Eaton | S811+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0562.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 240 | 3 | 100 | 800 | 300
|  |  |  | RVSS | Eaton | S801V65N3S | 240 | 3 | 42 | 650 | 250
SSC0562.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 240 | 3 | 100 | 800 | 300
|  |  |  | RVSS | Eaton | S801+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0562.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 240 | 3 | 100 | 800 | 300
|  |  |  | RVSS | Eaton | S811V65N3S | 240 | 3 | 42 | 650 | 250
SSC0562.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 240 | 3 | 100 | 800 | 300
|  |  |  | RVSS | Eaton | S811+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0563.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 240 | 3 | 100 | 1000 | 400
|  |  |  | RVSS | Eaton | S801V65N3S | 240 | 3 | 42 | 650 | 250
SSC0563.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 240 | 3 | 100 | 1000 | 400
|  |  |  | RVSS | Eaton | S801+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0563.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 240 | 3 | 100 | 1000 | 400
|  |  |  | RVSS | Eaton | S811V65N3S | 240 | 3 | 42 | 650 | 250
SSC0563.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 240 | 3 | 100 | 1000 | 400
|  |  |  | RVSS | Eaton | S811+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0564.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 240 | 3 | 100 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V65N3S | 240 | 3 | 42 | 650 | 250
SSC0564.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 240 | 3 | 100 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0564.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 240 | 3 | 100 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V65N3S | 240 | 3 | 42 | 650 | 250
SSC0564.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 240 | 3 | 100 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0565.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 240 | 3 | 100 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V65N3S | 240 | 3 | 42 | 650 | 250
SSC0565.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 240 | 3 | 100 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0565.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 240 | 3 | 100 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V65N3S | 240 | 3 | 42 | 650 | 250
SSC0565.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 240 | 3 | 100 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0566.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 480 | 3 | 65 | 700 | 500
|  |  |  | RVSS | Eaton | S801V65N3S | 480 | 3 | 42 | 650 | 500
SSC0566.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 480 | 3 | 65 | 700 | 500
|  |  |  | RVSS | Eaton | S801+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0566.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 480 | 3 | 65 | 700 | 500
|  |  |  | RVSS | Eaton | S811V65N3S | 480 | 3 | 42 | 650 | 500
SSC0566.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 480 | 3 | 65 | 700 | 500
|  |  |  | RVSS | Eaton | S811+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0567.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S801V65N3S | 480 | 3 | 42 | 650 | 500
SSC0567.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S801+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0567.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S811V65N3S | 480 | 3 | 42 | 650 | 500
SSC0567.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S811+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0568.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S801V65N3S | 480 | 3 | 42 | 650 | 500
SSC0568.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S801+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0568.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S811V65N3S | 480 | 3 | 42 | 650 | 500
SSC0568.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S811+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0569.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V65N3S | 480 | 3 | 42 | 650 | 500
SSC0569.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0569.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V65N3S | 480 | 3 | 42 | 650 | 500
SSC0569.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0570.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V65N3S | 480 | 3 | 42 | 650 | 500
SSC0570.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0570.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V65N3S | 480 | 3 | 42 | 650 | 500
SSC0570.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0571.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V65N3S | 480 | 3 | 42 | 650 | 500
SSC0571.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0571.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V65N3S | 480 | 3 | 42 | 650 | 500
SSC0571.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0572.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V65N3S | 480 | 3 | 42 | 650 | 500
SSC0572.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0572.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V65N3S | 480 | 3 | 42 | 650 | 500
SSC0572.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0573.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 600 | 3 | 35 | 700 | 500
|  |  |  | RVSS | Eaton | S801V65N3S | 600 | 3 | 42 | 650 | 500
SSC0573.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 600 | 3 | 35 | 700 | 500
|  |  |  | RVSS | Eaton | S801+V65N3S | 600 | 3 | 42 | 650 | 500
SSC0573.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 600 | 3 | 35 | 700 | 500
|  |  |  | RVSS | Eaton | S811V65N3S | 600 | 3 | 42 | 650 | 500
SSC0573.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 600 | 3 | 35 | 700 | 500
|  |  |  | RVSS | Eaton | S811+V65N3S | 600 | 3 | 42 | 650 | 500
SSC0574.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 600 | 3 | 35 | 800 | 500
|  |  |  | RVSS | Eaton | S801V65N3S | 600 | 3 | 42 | 650 | 500
SSC0574.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 600 | 3 | 35 | 800 | 500
|  |  |  | RVSS | Eaton | S801+V65N3S | 600 | 3 | 42 | 650 | 500
SSC0574.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 600 | 3 | 35 | 800 | 500
|  |  |  | RVSS | Eaton | S811V65N3S | 600 | 3 | 42 | 650 | 500
SSC0574.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 600 | 3 | 35 | 800 | 500
|  |  |  | RVSS | Eaton | S811+V65N3S | 600 | 3 | 42 | 650 | 500
SSC0575.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S801V65N3S | 600 | 3 | 42 | 650 | 500
SSC0575.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S801+V65N3S | 600 | 3 | 42 | 650 | 500
SSC0575.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S811V65N3S | 600 | 3 | 42 | 650 | 500
SSC0575.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S811+V65N3S | 600 | 3 | 42 | 650 | 500
SSC0576.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S801V65N3S | 600 | 3 | 42 | 650 | 500
SSC0576.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S801+V65N3S | 600 | 3 | 42 | 650 | 500
SSC0576.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S811V65N3S | 600 | 3 | 42 | 650 | 500
SSC0576.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S811+V65N3S | 600 | 3 | 42 | 650 | 500
SSC0577.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V65N3S | 600 | 3 | 42 | 650 | 500
SSC0577.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V65N3S | 600 | 3 | 42 | 650 | 500
SSC0577.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V65N3S | 600 | 3 | 42 | 650 | 500
SSC0577.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V65N3S | 600 | 3 | 42 | 650 | 500
SSC0578.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V65N3S | 600 | 3 | 42 | 650 | 500
SSC0578.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V65N3S | 600 | 3 | 42 | 650 | 500
SSC0578.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V65N3S | 600 | 3 | 42 | 650 | 500
SSC0578.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V65N3S | 600 | 3 | 42 | 650 | 500
SSC0579.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 200 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 200 | 3 | 125 | 800 | 200
|  |  |  | RVSS | Eaton | S801V65N3S | 200 | 3 | 42 | 650 | 200
SSC0579.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 200 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 200 | 3 | 125 | 800 | 200
|  |  |  | RVSS | Eaton | S801+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0579.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 200 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 200 | 3 | 125 | 800 | 200
|  |  |  | RVSS | Eaton | S811V65N3S | 200 | 3 | 42 | 650 | 200
SSC0579.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 200 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 200 | 3 | 125 | 800 | 200
|  |  |  | RVSS | Eaton | S811+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0580.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 200 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 200 | 3 | 125 | 1000 | 200
|  |  |  | RVSS | Eaton | S801V65N3S | 200 | 3 | 42 | 650 | 200
SSC0580.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 200 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 200 | 3 | 125 | 1000 | 200
|  |  |  | RVSS | Eaton | S801+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0580.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 200 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 200 | 3 | 125 | 1000 | 200
|  |  |  | RVSS | Eaton | S811V65N3S | 200 | 3 | 42 | 650 | 200
SSC0580.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 200 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 200 | 3 | 125 | 1000 | 200
|  |  |  | RVSS | Eaton | S811+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0581.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 200 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 200 | 3 | 125 | 1200 | 200
|  |  |  | RVSS | Eaton | S801V65N3S | 200 | 3 | 42 | 650 | 200
SSC0581.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 200 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 200 | 3 | 125 | 1200 | 200
|  |  |  | RVSS | Eaton | S801+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0581.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 200 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 200 | 3 | 125 | 1200 | 200
|  |  |  | RVSS | Eaton | S811V65N3S | 200 | 3 | 42 | 650 | 200
SSC0581.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 200 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 200 | 3 | 125 | 1200 | 200
|  |  |  | RVSS | Eaton | S811+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0582.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 200 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 200 | 3 | 125 | 1200 | 200
|  |  |  | RVSS | Eaton | S801V65N3S | 200 | 3 | 42 | 650 | 200
SSC0582.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 200 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 200 | 3 | 125 | 1200 | 200
|  |  |  | RVSS | Eaton | S801+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0582.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 200 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 200 | 3 | 125 | 1200 | 200
|  |  |  | RVSS | Eaton | S811V65N3S | 200 | 3 | 42 | 650 | 200
SSC0582.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 200 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 200 | 3 | 125 | 1200 | 200
|  |  |  | RVSS | Eaton | S811+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0583.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 200 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 208 | 3 | 125 | 800 | 200
|  |  |  | RVSS | Eaton | S801V65N3S | 208 | 3 | 42 | 650 | 200
SSC0583.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 200 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 208 | 3 | 125 | 800 | 200
|  |  |  | RVSS | Eaton | S801+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0583.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 200 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 208 | 3 | 125 | 800 | 200
|  |  |  | RVSS | Eaton | S811V65N3S | 208 | 3 | 42 | 650 | 200
SSC0583.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 200 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 208 | 3 | 125 | 800 | 200
|  |  |  | RVSS | Eaton | S811+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0584.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 200 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 200
|  |  |  | RVSS | Eaton | S801V65N3S | 208 | 3 | 42 | 650 | 200
SSC0584.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 200 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 200
|  |  |  | RVSS | Eaton | S801+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0584.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 200 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 200
|  |  |  | RVSS | Eaton | S811V65N3S | 208 | 3 | 42 | 650 | 200
SSC0584.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 200 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 200
|  |  |  | RVSS | Eaton | S811+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0585.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 200 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 200
|  |  |  | RVSS | Eaton | S801V65N3S | 208 | 3 | 42 | 650 | 200
SSC0585.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 200 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 200
|  |  |  | RVSS | Eaton | S801+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0585.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 200 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 200
|  |  |  | RVSS | Eaton | S811V65N3S | 208 | 3 | 42 | 650 | 200
SSC0585.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 200 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 200
|  |  |  | RVSS | Eaton | S811+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0586.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 200 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 208 | 3 | 125 | 1200 | 200
|  |  |  | RVSS | Eaton | S801V65N3S | 208 | 3 | 42 | 650 | 200
SSC0586.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 200 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 208 | 3 | 125 | 1200 | 200
|  |  |  | RVSS | Eaton | S801+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0586.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 200 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 208 | 3 | 125 | 1200 | 200
|  |  |  | RVSS | Eaton | S811V65N3S | 208 | 3 | 42 | 650 | 200
SSC0586.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 200 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 208 | 3 | 125 | 1200 | 200
|  |  |  | RVSS | Eaton | S811+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0587.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 300 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 240 | 3 | 125 | 800 | 300
|  |  |  | RVSS | Eaton | S801V65N3S | 240 | 3 | 42 | 650 | 250
SSC0587.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 300 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 240 | 3 | 125 | 800 | 300
|  |  |  | RVSS | Eaton | S801+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0587.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 300 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 240 | 3 | 125 | 800 | 300
|  |  |  | RVSS | Eaton | S811V65N3S | 240 | 3 | 42 | 650 | 250
SSC0587.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 300 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 240 | 3 | 125 | 800 | 300
|  |  |  | RVSS | Eaton | S811+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0588.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 240 | 3 | 125 | 1000 | 400
|  |  |  | RVSS | Eaton | S801V65N3S | 240 | 3 | 42 | 650 | 250
SSC0588.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 240 | 3 | 125 | 1000 | 400
|  |  |  | RVSS | Eaton | S801+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0588.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 240 | 3 | 125 | 1000 | 400
|  |  |  | RVSS | Eaton | S811V65N3S | 240 | 3 | 42 | 650 | 250
SSC0588.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 240 | 3 | 125 | 1000 | 400
|  |  |  | RVSS | Eaton | S811+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0589.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 240 | 3 | 125 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V65N3S | 240 | 3 | 42 | 650 | 250
SSC0589.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 240 | 3 | 125 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0589.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 240 | 3 | 125 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V65N3S | 240 | 3 | 42 | 650 | 250
SSC0589.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 240 | 3 | 125 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0590.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 240 | 3 | 125 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V65N3S | 240 | 3 | 42 | 650 | 250
SSC0590.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 240 | 3 | 125 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0590.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 240 | 3 | 125 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V65N3S | 240 | 3 | 42 | 650 | 250
SSC0590.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 240 | 3 | 125 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0591.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 65 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S801V65N3S | 480 | 3 | 42 | 650 | 500
SSC0591.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 65 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S801+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0591.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 65 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S811V65N3S | 480 | 3 | 42 | 650 | 500
SSC0591.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 65 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S811+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0592.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 65 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S801V65N3S | 480 | 3 | 42 | 650 | 500
SSC0592.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 65 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S801+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0592.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 65 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S811V65N3S | 480 | 3 | 42 | 650 | 500
SSC0592.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 65 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S811+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0593.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 65 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V65N3S | 480 | 3 | 42 | 650 | 500
SSC0593.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 65 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0593.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 65 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V65N3S | 480 | 3 | 42 | 650 | 500
SSC0593.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 65 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0594.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 65 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V65N3S | 480 | 3 | 42 | 650 | 500
SSC0594.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 65 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0594.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 65 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V65N3S | 480 | 3 | 42 | 650 | 500
SSC0594.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 65 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0595.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 65 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V65N3S | 480 | 3 | 42 | 650 | 500
SSC0595.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 65 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0595.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 65 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V65N3S | 480 | 3 | 42 | 650 | 500
SSC0595.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 65 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0596.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 65 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V65N3S | 480 | 3 | 42 | 650 | 500
SSC0596.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 65 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0596.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 65 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V65N3S | 480 | 3 | 42 | 650 | 500
SSC0596.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 65 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0597.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 600 | 3 | 50 | 800 | 500
|  |  |  | RVSS | Eaton | S801V65N3S | 600 | 3 | 42 | 650 | 500
SSC0597.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 600 | 3 | 50 | 800 | 500
|  |  |  | RVSS | Eaton | S801+V65N3S | 600 | 3 | 42 | 650 | 500
SSC0597.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 600 | 3 | 50 | 800 | 500
|  |  |  | RVSS | Eaton | S811V65N3S | 600 | 3 | 42 | 650 | 500
SSC0597.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 600 | 3 | 50 | 800 | 500
|  |  |  | RVSS | Eaton | S811+V65N3S | 600 | 3 | 42 | 650 | 500
SSC0598.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 500
|  |  |  | RVSS | Eaton | S801V65N3S | 600 | 3 | 42 | 650 | 500
SSC0598.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 500
|  |  |  | RVSS | Eaton | S801+V65N3S | 600 | 3 | 42 | 650 | 500
SSC0598.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 500
|  |  |  | RVSS | Eaton | S811V65N3S | 600 | 3 | 42 | 650 | 500
SSC0598.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 500
|  |  |  | RVSS | Eaton | S811+V65N3S | 600 | 3 | 42 | 650 | 500
SSC0599.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 500
|  |  |  | RVSS | Eaton | S801V65N3S | 600 | 3 | 42 | 650 | 500
SSC0599.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 500
|  |  |  | RVSS | Eaton | S801+V65N3S | 600 | 3 | 42 | 650 | 500
SSC0599.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 500
|  |  |  | RVSS | Eaton | S811V65N3S | 600 | 3 | 42 | 650 | 500
SSC0599.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 500
|  |  |  | RVSS | Eaton | S811+V65N3S | 600 | 3 | 42 | 650 | 500
SSC0600.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V65N3S | 600 | 3 | 42 | 650 | 500
SSC0600.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V65N3S | 600 | 3 | 42 | 650 | 500
SSC0600.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V65N3S | 600 | 3 | 42 | 650 | 500
SSC0600.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V65N3S | 600 | 3 | 42 | 650 | 500
SSC0601.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V65N3S | 600 | 3 | 42 | 650 | 500
SSC0601.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V65N3S | 600 | 3 | 42 | 650 | 500
SSC0601.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V65N3S | 600 | 3 | 42 | 650 | 500
SSC0601.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V65N3S | 600 | 3 | 42 | 650 | 500
SSC0602.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 250 | 200 | 3 | 42 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 200 | 3 | 125 | 800 | 250
|  |  |  | RVSS | Eaton | S801V72N3S | 200 | 3 | 42 | 720 | 250
SSC0602.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 250 | 200 | 3 | 42 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 200 | 3 | 125 | 800 | 250
|  |  |  | RVSS | Eaton | S801+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0602.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 250 | 200 | 3 | 42 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 200 | 3 | 125 | 800 | 250
|  |  |  | RVSS | Eaton | S811V72N3S | 200 | 3 | 42 | 720 | 250
SSC0602.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 250 | 200 | 3 | 42 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 200 | 3 | 125 | 800 | 250
|  |  |  | RVSS | Eaton | S811+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0603.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 250 | 200 | 3 | 42 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 200 | 3 | 125 | 1000 | 250
|  |  |  | RVSS | Eaton | S801V72N3S | 200 | 3 | 42 | 720 | 250
SSC0603.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 250 | 200 | 3 | 42 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 200 | 3 | 125 | 1000 | 250
|  |  |  | RVSS | Eaton | S801+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0603.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 250 | 200 | 3 | 42 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 200 | 3 | 125 | 1000 | 250
|  |  |  | RVSS | Eaton | S811V72N3S | 200 | 3 | 42 | 720 | 250
SSC0603.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 250 | 200 | 3 | 42 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 200 | 3 | 125 | 1000 | 250
|  |  |  | RVSS | Eaton | S811+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0604.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 250 | 200 | 3 | 42 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 200 | 3 | 125 | 1200 | 250
|  |  |  | RVSS | Eaton | S801V72N3S | 200 | 3 | 42 | 720 | 250
SSC0604.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 250 | 200 | 3 | 42 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 200 | 3 | 125 | 1200 | 250
|  |  |  | RVSS | Eaton | S801+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0604.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 250 | 200 | 3 | 42 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 200 | 3 | 125 | 1200 | 250
|  |  |  | RVSS | Eaton | S811V72N3S | 200 | 3 | 42 | 720 | 250
SSC0604.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 250 | 200 | 3 | 42 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 200 | 3 | 125 | 1200 | 250
|  |  |  | RVSS | Eaton | S811+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0605.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 250 | 200 | 3 | 42 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 250
|  |  |  | RVSS | Eaton | S801V72N3S | 200 | 3 | 42 | 720 | 250
SSC0605.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 250 | 200 | 3 | 42 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 250
|  |  |  | RVSS | Eaton | S801+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0605.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 250 | 200 | 3 | 42 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 250
|  |  |  | RVSS | Eaton | S811V72N3S | 200 | 3 | 42 | 720 | 250
SSC0605.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 250 | 200 | 3 | 42 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 250
|  |  |  | RVSS | Eaton | S811+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0606.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 250 | 200 | 3 | 42 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 250
|  |  |  | RVSS | Eaton | S801V72N3S | 200 | 3 | 42 | 720 | 250
SSC0606.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 250 | 200 | 3 | 42 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 250
|  |  |  | RVSS | Eaton | S801+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0606.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 250 | 200 | 3 | 42 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 250
|  |  |  | RVSS | Eaton | S811V72N3S | 200 | 3 | 42 | 720 | 250
SSC0606.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 250 | 200 | 3 | 42 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 250
|  |  |  | RVSS | Eaton | S811+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0607.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 250 | 208 | 3 | 42 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 208 | 3 | 125 | 800 | 250
|  |  |  | RVSS | Eaton | S801V72N3S | 208 | 3 | 42 | 720 | 250
SSC0607.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 250 | 208 | 3 | 42 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 208 | 3 | 125 | 800 | 250
|  |  |  | RVSS | Eaton | S801+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0607.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 250 | 208 | 3 | 42 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 208 | 3 | 125 | 800 | 250
|  |  |  | RVSS | Eaton | S811V72N3S | 208 | 3 | 42 | 720 | 250
SSC0607.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 250 | 208 | 3 | 42 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 208 | 3 | 125 | 800 | 250
|  |  |  | RVSS | Eaton | S811+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0608.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 250 | 208 | 3 | 42 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 250
|  |  |  | RVSS | Eaton | S801V72N3S | 208 | 3 | 42 | 720 | 250
SSC0608.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 250 | 208 | 3 | 42 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 250
|  |  |  | RVSS | Eaton | S801+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0608.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 250 | 208 | 3 | 42 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 250
|  |  |  | RVSS | Eaton | S811V72N3S | 208 | 3 | 42 | 720 | 250
SSC0608.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 250 | 208 | 3 | 42 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 250
|  |  |  | RVSS | Eaton | S811+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0609.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 250 | 208 | 3 | 42 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 250
|  |  |  | RVSS | Eaton | S801V72N3S | 208 | 3 | 42 | 720 | 250
SSC0609.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 250 | 208 | 3 | 42 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 250
|  |  |  | RVSS | Eaton | S801+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0609.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 250 | 208 | 3 | 42 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 250
|  |  |  | RVSS | Eaton | S811V72N3S | 208 | 3 | 42 | 720 | 250
SSC0609.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 250 | 208 | 3 | 42 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 250
|  |  |  | RVSS | Eaton | S811+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0610.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 250 | 208 | 3 | 42 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 208 | 3 | 125 | 1200 | 250
|  |  |  | RVSS | Eaton | S801V72N3S | 208 | 3 | 42 | 720 | 250
SSC0610.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 250 | 208 | 3 | 42 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 208 | 3 | 125 | 1200 | 250
|  |  |  | RVSS | Eaton | S801+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0610.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 250 | 208 | 3 | 42 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 208 | 3 | 125 | 1200 | 250
|  |  |  | RVSS | Eaton | S811V72N3S | 208 | 3 | 42 | 720 | 250
SSC0610.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 250 | 208 | 3 | 42 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 208 | 3 | 125 | 1200 | 250
|  |  |  | RVSS | Eaton | S811+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0611.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 250 | 208 | 3 | 42 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 208 | 3 | 125 | 1600 | 250
|  |  |  | RVSS | Eaton | S801V72N3S | 208 | 3 | 42 | 720 | 250
SSC0611.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 250 | 208 | 3 | 42 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 208 | 3 | 125 | 1600 | 250
|  |  |  | RVSS | Eaton | S801+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0611.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 250 | 208 | 3 | 42 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 208 | 3 | 125 | 1600 | 250
|  |  |  | RVSS | Eaton | S811V72N3S | 208 | 3 | 42 | 720 | 250
SSC0611.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 250 | 208 | 3 | 42 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 208 | 3 | 125 | 1600 | 250
|  |  |  | RVSS | Eaton | S811+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0612.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 240 | 3 | 125 | 800 | 300
|  |  |  | RVSS | Eaton | S801V72N3S | 240 | 3 | 42 | 720 | 250
SSC0612.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 240 | 3 | 125 | 800 | 300
|  |  |  | RVSS | Eaton | S801+V72N3S | 240 | 3 | 42 | 720 | 250
SSC0612.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 240 | 3 | 125 | 800 | 300
|  |  |  | RVSS | Eaton | S811V72N3S | 240 | 3 | 42 | 720 | 250
SSC0612.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 240 | 3 | 125 | 800 | 300
|  |  |  | RVSS | Eaton | S811+V72N3S | 240 | 3 | 42 | 720 | 250
SSC0613.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 240 | 3 | 125 | 1000 | 400
|  |  |  | RVSS | Eaton | S801V72N3S | 240 | 3 | 42 | 720 | 250
SSC0613.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 240 | 3 | 125 | 1000 | 400
|  |  |  | RVSS | Eaton | S801+V72N3S | 240 | 3 | 42 | 720 | 250
SSC0613.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 240 | 3 | 125 | 1000 | 400
|  |  |  | RVSS | Eaton | S811V72N3S | 240 | 3 | 42 | 720 | 250
SSC0613.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 240 | 3 | 125 | 1000 | 400
|  |  |  | RVSS | Eaton | S811+V72N3S | 240 | 3 | 42 | 720 | 250
SSC0614.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 240 | 3 | 125 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V72N3S | 240 | 3 | 42 | 720 | 250
SSC0614.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 240 | 3 | 125 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V72N3S | 240 | 3 | 42 | 720 | 250
SSC0614.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 240 | 3 | 125 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V72N3S | 240 | 3 | 42 | 720 | 250
SSC0614.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 240 | 3 | 125 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V72N3S | 240 | 3 | 42 | 720 | 250
SSC0615.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 240 | 3 | 125 | 1600 | 500
|  |  |  | RVSS | Eaton | S801V72N3S | 240 | 3 | 42 | 720 | 250
SSC0615.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 240 | 3 | 125 | 1600 | 500
|  |  |  | RVSS | Eaton | S801+V72N3S | 240 | 3 | 42 | 720 | 250
SSC0615.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 240 | 3 | 125 | 1600 | 500
|  |  |  | RVSS | Eaton | S811V72N3S | 240 | 3 | 42 | 720 | 250
SSC0615.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 240 | 3 | 125 | 1600 | 500
|  |  |  | RVSS | Eaton | S811+V72N3S | 240 | 3 | 42 | 720 | 250
SSC0616.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 42 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S801V72N3S | 480 | 3 | 42 | 720 | 500
SSC0616.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 42 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S801+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0616.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 42 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S811V72N3S | 480 | 3 | 42 | 720 | 500
SSC0616.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 42 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S811+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0617.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 42 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S801V72N3S | 480 | 3 | 42 | 720 | 500
SSC0617.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 42 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S801+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0617.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 42 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S811V72N3S | 480 | 3 | 42 | 720 | 500
SSC0617.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 42 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S811+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0618.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 42 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S801V72N3S | 480 | 3 | 42 | 720 | 500
SSC0618.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 42 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S801+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0618.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 42 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S811V72N3S | 480 | 3 | 42 | 720 | 500
SSC0618.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 42 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S811+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0619.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 42 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V72N3S | 480 | 3 | 42 | 720 | 500
SSC0619.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 42 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0619.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 42 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V72N3S | 480 | 3 | 42 | 720 | 500
SSC0619.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 42 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0620.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 42 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V72N3S | 480 | 3 | 42 | 720 | 500
SSC0620.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 42 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0620.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 42 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V72N3S | 480 | 3 | 42 | 720 | 500
SSC0620.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 42 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0621.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 42 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 480 | 3 | 65 | 1600 | 500
|  |  |  | RVSS | Eaton | S801V72N3S | 480 | 3 | 42 | 720 | 500
SSC0621.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 42 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 480 | 3 | 65 | 1600 | 500
|  |  |  | RVSS | Eaton | S801+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0621.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 42 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 480 | 3 | 65 | 1600 | 500
|  |  |  | RVSS | Eaton | S811V72N3S | 480 | 3 | 42 | 720 | 500
SSC0621.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 500 | 480 | 3 | 42 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 480 | 3 | 65 | 1600 | 500
|  |  |  | RVSS | Eaton | S811+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0622.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 600 | 3 | 50 | 800 | 500
|  |  |  | RVSS | Eaton | S801V72N3S | 600 | 3 | 42 | 720 | 600
SSC0622.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 600 | 3 | 50 | 800 | 500
|  |  |  | RVSS | Eaton | S801+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0622.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 600 | 3 | 50 | 800 | 500
|  |  |  | RVSS | Eaton | S811V72N3S | 600 | 3 | 42 | 720 | 600
SSC0622.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 600 | 3 | 50 | 800 | 500
|  |  |  | RVSS | Eaton | S811+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0623.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 500
|  |  |  | RVSS | Eaton | S801V72N3S | 600 | 3 | 42 | 720 | 600
SSC0623.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 500
|  |  |  | RVSS | Eaton | S801+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0623.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 500
|  |  |  | RVSS | Eaton | S811V72N3S | 600 | 3 | 42 | 720 | 600
SSC0623.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 500
|  |  |  | RVSS | Eaton | S811+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0624.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 500
|  |  |  | RVSS | Eaton | S801V72N3S | 600 | 3 | 42 | 720 | 600
SSC0624.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 500
|  |  |  | RVSS | Eaton | S801+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0624.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 500
|  |  |  | RVSS | Eaton | S811V72N3S | 600 | 3 | 42 | 720 | 600
SSC0624.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 500
|  |  |  | RVSS | Eaton | S811+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0625.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V72N3S | 600 | 3 | 42 | 720 | 600
SSC0625.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0625.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V72N3S | 600 | 3 | 42 | 720 | 600
SSC0625.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0626.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V72N3S | 600 | 3 | 42 | 720 | 600
SSC0626.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0626.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V72N3S | 600 | 3 | 42 | 720 | 600
SSC0626.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0627.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 600 | 3 | 50 | 1600 | 500
|  |  |  | RVSS | Eaton | S801V72N3S | 600 | 3 | 42 | 720 | 600
SSC0627.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 600 | 3 | 50 | 1600 | 500
|  |  |  | RVSS | Eaton | S801+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0627.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 600 | 3 | 50 | 1600 | 500
|  |  |  | RVSS | Eaton | S811V72N3S | 600 | 3 | 42 | 720 | 600
SSC0627.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 500 | 600 | 3 | 42 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 600 | 3 | 50 | 1600 | 500
|  |  |  | RVSS | Eaton | S811+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0628.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 300 | 200 | 3 | 42 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 200 | 3 | 125 | 800 | 250
|  |  |  | RVSS | Eaton | S801V85N3S | 200 | 3 | 42 | 850 | 300
SSC0628.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 300 | 200 | 3 | 42 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 200 | 3 | 125 | 800 | 250
|  |  |  | RVSS | Eaton | S801+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0628.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 300 | 200 | 3 | 42 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 200 | 3 | 125 | 800 | 250
|  |  |  | RVSS | Eaton | S811V85N3S | 200 | 3 | 42 | 850 | 300
SSC0628.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 300 | 200 | 3 | 42 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 200 | 3 | 125 | 800 | 250
|  |  |  | RVSS | Eaton | S811+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0629.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 300 | 200 | 3 | 42 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 200 | 3 | 125 | 1000 | 300
|  |  |  | RVSS | Eaton | S801V85N3S | 200 | 3 | 42 | 850 | 300
SSC0629.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 300 | 200 | 3 | 42 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 200 | 3 | 125 | 1000 | 300
|  |  |  | RVSS | Eaton | S801+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0629.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 300 | 200 | 3 | 42 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 200 | 3 | 125 | 1000 | 300
|  |  |  | RVSS | Eaton | S811V85N3S | 200 | 3 | 42 | 850 | 300
SSC0629.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 300 | 200 | 3 | 42 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 200 | 3 | 125 | 1000 | 300
|  |  |  | RVSS | Eaton | S811+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0630.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 300 | 200 | 3 | 42 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 200 | 3 | 125 | 1200 | 300
|  |  |  | RVSS | Eaton | S801V85N3S | 200 | 3 | 42 | 850 | 300
SSC0630.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 300 | 200 | 3 | 42 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 200 | 3 | 125 | 1200 | 300
|  |  |  | RVSS | Eaton | S801+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0630.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 300 | 200 | 3 | 42 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 200 | 3 | 125 | 1200 | 300
|  |  |  | RVSS | Eaton | S811V85N3S | 200 | 3 | 42 | 850 | 300
SSC0630.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 300 | 200 | 3 | 42 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 200 | 3 | 125 | 1200 | 300
|  |  |  | RVSS | Eaton | S811+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0631.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 300 | 200 | 3 | 42 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 300
|  |  |  | RVSS | Eaton | S801V85N3S | 200 | 3 | 42 | 850 | 300
SSC0631.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 300 | 200 | 3 | 42 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 300
|  |  |  | RVSS | Eaton | S801+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0631.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 300 | 200 | 3 | 42 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 300
|  |  |  | RVSS | Eaton | S811V85N3S | 200 | 3 | 42 | 850 | 300
SSC0631.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 300 | 200 | 3 | 42 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 300
|  |  |  | RVSS | Eaton | S811+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0632.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 300 | 200 | 3 | 42 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 300
|  |  |  | RVSS | Eaton | S801V85N3S | 200 | 3 | 42 | 850 | 300
SSC0632.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 300 | 200 | 3 | 42 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 300
|  |  |  | RVSS | Eaton | S801+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0632.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 300 | 200 | 3 | 42 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 300
|  |  |  | RVSS | Eaton | S811V85N3S | 200 | 3 | 42 | 850 | 300
SSC0632.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 300 | 200 | 3 | 42 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 300
|  |  |  | RVSS | Eaton | S811+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0633.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 300 | 200 | 3 | 42 | 830 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 300
|  |  |  | RVSS | Eaton | S801V85N3S | 200 | 3 | 42 | 850 | 300
SSC0633.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 300 | 200 | 3 | 42 | 830 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 300
|  |  |  | RVSS | Eaton | S801+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0633.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 300 | 200 | 3 | 42 | 830 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 300
|  |  |  | RVSS | Eaton | S811V85N3S | 200 | 3 | 42 | 850 | 300
SSC0633.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 300 | 200 | 3 | 42 | 830 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 300
|  |  |  | RVSS | Eaton | S811+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0634.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 300 | 208 | 3 | 42 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 208 | 3 | 125 | 800 | 250
|  |  |  | RVSS | Eaton | S801V85N3S | 208 | 3 | 42 | 850 | 300
SSC0634.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 300 | 208 | 3 | 42 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 208 | 3 | 125 | 800 | 250
|  |  |  | RVSS | Eaton | S801+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0634.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 300 | 208 | 3 | 42 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 208 | 3 | 125 | 800 | 250
|  |  |  | RVSS | Eaton | S811V85N3S | 208 | 3 | 42 | 850 | 300
SSC0634.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 300 | 208 | 3 | 42 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 208 | 3 | 125 | 800 | 250
|  |  |  | RVSS | Eaton | S811+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0635.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 300 | 208 | 3 | 42 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 300
|  |  |  | RVSS | Eaton | S801V85N3S | 208 | 3 | 42 | 850 | 300
SSC0635.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 300 | 208 | 3 | 42 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 300
|  |  |  | RVSS | Eaton | S801+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0635.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 300 | 208 | 3 | 42 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 300
|  |  |  | RVSS | Eaton | S811V85N3S | 208 | 3 | 42 | 850 | 300
SSC0635.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 300 | 208 | 3 | 42 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 300
|  |  |  | RVSS | Eaton | S811+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0636.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 300 | 208 | 3 | 42 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 300
|  |  |  | RVSS | Eaton | S801V85N3S | 208 | 3 | 42 | 850 | 300
SSC0636.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 300 | 208 | 3 | 42 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 300
|  |  |  | RVSS | Eaton | S801+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0636.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 300 | 208 | 3 | 42 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 300
|  |  |  | RVSS | Eaton | S811V85N3S | 208 | 3 | 42 | 850 | 300
SSC0636.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 300 | 208 | 3 | 42 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 300
|  |  |  | RVSS | Eaton | S811+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0637.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 300 | 208 | 3 | 42 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 208 | 3 | 125 | 1200 | 300
|  |  |  | RVSS | Eaton | S801V85N3S | 208 | 3 | 42 | 850 | 300
SSC0637.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 300 | 208 | 3 | 42 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 208 | 3 | 125 | 1200 | 300
|  |  |  | RVSS | Eaton | S801+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0637.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 300 | 208 | 3 | 42 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 208 | 3 | 125 | 1200 | 300
|  |  |  | RVSS | Eaton | S811V85N3S | 208 | 3 | 42 | 850 | 300
SSC0637.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 300 | 208 | 3 | 42 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 208 | 3 | 125 | 1200 | 300
|  |  |  | RVSS | Eaton | S811+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0638.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 300 | 208 | 3 | 42 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 208 | 3 | 125 | 1600 | 300
|  |  |  | RVSS | Eaton | S801V85N3S | 208 | 3 | 42 | 850 | 300
SSC0638.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 300 | 208 | 3 | 42 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 208 | 3 | 125 | 1600 | 300
|  |  |  | RVSS | Eaton | S801+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0638.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 300 | 208 | 3 | 42 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 208 | 3 | 125 | 1600 | 300
|  |  |  | RVSS | Eaton | S811V85N3S | 208 | 3 | 42 | 850 | 300
SSC0638.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 300 | 208 | 3 | 42 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 208 | 3 | 125 | 1600 | 300
|  |  |  | RVSS | Eaton | S811+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0639.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 300 | 208 | 3 | 42 | 794 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 208 | 3 | 125 | 1600 | 300
|  |  |  | RVSS | Eaton | S801V85N3S | 208 | 3 | 42 | 850 | 300
SSC0639.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 300 | 208 | 3 | 42 | 794 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 208 | 3 | 125 | 1600 | 300
|  |  |  | RVSS | Eaton | S801+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0639.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 300 | 208 | 3 | 42 | 794 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 208 | 3 | 125 | 1600 | 300
|  |  |  | RVSS | Eaton | S811V85N3S | 208 | 3 | 42 | 850 | 300
SSC0639.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 300 | 208 | 3 | 42 | 794 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 208 | 3 | 125 | 1600 | 300
|  |  |  | RVSS | Eaton | S811+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0640.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 300 | 240 | 3 | 42 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 240 | 3 | 125 | 800 | 300
|  |  |  | RVSS | Eaton | S801V85N3S | 240 | 3 | 42 | 850 | 350
SSC0640.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 300 | 240 | 3 | 42 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 240 | 3 | 125 | 800 | 300
|  |  |  | RVSS | Eaton | S801+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0640.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 300 | 240 | 3 | 42 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 240 | 3 | 125 | 800 | 300
|  |  |  | RVSS | Eaton | S811V85N3S | 240 | 3 | 42 | 850 | 350
SSC0640.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 300 | 240 | 3 | 42 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 240 | 3 | 125 | 800 | 300
|  |  |  | RVSS | Eaton | S811+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0641.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 240 | 3 | 125 | 1000 | 400
|  |  |  | RVSS | Eaton | S801V85N3S | 240 | 3 | 42 | 850 | 350
SSC0641.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 240 | 3 | 125 | 1000 | 400
|  |  |  | RVSS | Eaton | S801+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0641.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 240 | 3 | 125 | 1000 | 400
|  |  |  | RVSS | Eaton | S811V85N3S | 240 | 3 | 42 | 850 | 350
SSC0641.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 240 | 3 | 125 | 1000 | 400
|  |  |  | RVSS | Eaton | S811+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0642.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 240 | 3 | 125 | 1200 | 500
|  |  |  | RVSS | Eaton | S801V85N3S | 240 | 3 | 42 | 850 | 350
SSC0642.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 240 | 3 | 125 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0642.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 240 | 3 | 125 | 1200 | 500
|  |  |  | RVSS | Eaton | S811V85N3S | 240 | 3 | 42 | 850 | 350
SSC0642.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 240 | 3 | 125 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0643.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 240 | 3 | 125 | 1600 | 500
|  |  |  | RVSS | Eaton | S801V85N3S | 240 | 3 | 42 | 850 | 350
SSC0643.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 240 | 3 | 125 | 1600 | 500
|  |  |  | RVSS | Eaton | S801+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0643.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 240 | 3 | 125 | 1600 | 500
|  |  |  | RVSS | Eaton | S811V85N3S | 240 | 3 | 42 | 850 | 350
SSC0643.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 240 | 3 | 125 | 1600 | 500
|  |  |  | RVSS | Eaton | S811+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0644.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 722 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 240 | 3 | 125 | 1600 | 500
|  |  |  | RVSS | Eaton | S801V85N3S | 240 | 3 | 42 | 850 | 350
SSC0644.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 722 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 240 | 3 | 125 | 1600 | 500
|  |  |  | RVSS | Eaton | S801+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0644.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 722 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 240 | 3 | 125 | 1600 | 500
|  |  |  | RVSS | Eaton | S811V85N3S | 240 | 3 | 42 | 850 | 350
SSC0644.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 722 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 240 | 3 | 125 | 1600 | 500
|  |  |  | RVSS | Eaton | S811+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0645.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 828 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 240 | 3 | 125 | 1600 | 500
|  |  |  | RVSS | Eaton | S801V85N3S | 240 | 3 | 42 | 850 | 350
SSC0645.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 828 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 240 | 3 | 125 | 1600 | 500
|  |  |  | RVSS | Eaton | S801+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0645.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 828 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 240 | 3 | 125 | 1600 | 500
|  |  |  | RVSS | Eaton | S811V85N3S | 240 | 3 | 42 | 850 | 350
SSC0645.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 500 | 240 | 3 | 42 | 828 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 240 | 3 | 125 | 1600 | 500
|  |  |  | RVSS | Eaton | S811+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0646.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 600 | 480 | 3 | 42 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 480 | 3 | 65 | 800 | 600
|  |  |  | RVSS | Eaton | S801V85N3S | 480 | 3 | 42 | 850 | 600
SSC0646.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 600 | 480 | 3 | 42 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 480 | 3 | 65 | 800 | 600
|  |  |  | RVSS | Eaton | S801+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0646.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 600 | 480 | 3 | 42 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 480 | 3 | 65 | 800 | 600
|  |  |  | RVSS | Eaton | S811V85N3S | 480 | 3 | 42 | 850 | 600
SSC0646.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 600 | 480 | 3 | 42 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 480 | 3 | 65 | 800 | 600
|  |  |  | RVSS | Eaton | S811+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0647.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 600 | 480 | 3 | 42 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 480 | 3 | 65 | 1000 | 600
|  |  |  | RVSS | Eaton | S801V85N3S | 480 | 3 | 42 | 850 | 600
SSC0647.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 600 | 480 | 3 | 42 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 480 | 3 | 65 | 1000 | 600
|  |  |  | RVSS | Eaton | S801+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0647.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 600 | 480 | 3 | 42 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 480 | 3 | 65 | 1000 | 600
|  |  |  | RVSS | Eaton | S811V85N3S | 480 | 3 | 42 | 850 | 600
SSC0647.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 600 | 480 | 3 | 42 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 480 | 3 | 65 | 1000 | 600
|  |  |  | RVSS | Eaton | S811+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0648.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 600 | 480 | 3 | 42 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 600
|  |  |  | RVSS | Eaton | S801V85N3S | 480 | 3 | 42 | 850 | 600
SSC0648.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 600 | 480 | 3 | 42 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 600
|  |  |  | RVSS | Eaton | S801+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0648.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 600 | 480 | 3 | 42 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 600
|  |  |  | RVSS | Eaton | S811V85N3S | 480 | 3 | 42 | 850 | 600
SSC0648.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 600 | 480 | 3 | 42 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 600
|  |  |  | RVSS | Eaton | S811+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0649.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 600 | 480 | 3 | 42 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 600
|  |  |  | RVSS | Eaton | S801V85N3S | 480 | 3 | 42 | 850 | 600
SSC0649.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 600 | 480 | 3 | 42 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 600
|  |  |  | RVSS | Eaton | S801+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0649.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 600 | 480 | 3 | 42 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 600
|  |  |  | RVSS | Eaton | S811V85N3S | 480 | 3 | 42 | 850 | 600
SSC0649.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 600 | 480 | 3 | 42 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 600
|  |  |  | RVSS | Eaton | S811+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0650.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 600 | 480 | 3 | 42 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 600
|  |  |  | RVSS | Eaton | S801V85N3S | 480 | 3 | 42 | 850 | 600
SSC0650.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 600 | 480 | 3 | 42 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 600
|  |  |  | RVSS | Eaton | S801+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0650.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 600 | 480 | 3 | 42 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 600
|  |  |  | RVSS | Eaton | S811V85N3S | 480 | 3 | 42 | 850 | 600
SSC0650.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 600 | 480 | 3 | 42 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 600
|  |  |  | RVSS | Eaton | S811+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0651.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 600 | 480 | 3 | 42 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 480 | 3 | 65 | 1600 | 600
|  |  |  | RVSS | Eaton | S801V85N3S | 480 | 3 | 42 | 850 | 600
SSC0651.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 600 | 480 | 3 | 42 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 480 | 3 | 65 | 1600 | 600
|  |  |  | RVSS | Eaton | S801+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0651.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 600 | 480 | 3 | 42 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 480 | 3 | 65 | 1600 | 600
|  |  |  | RVSS | Eaton | S811V85N3S | 480 | 3 | 42 | 850 | 600
SSC0651.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 600 | 480 | 3 | 42 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 480 | 3 | 65 | 1600 | 600
|  |  |  | RVSS | Eaton | S811+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0652.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 600 | 480 | 3 | 42 | 701 | 600 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 480 | 3 | 65 | 1600 | 600
|  |  |  | RVSS | Eaton | S801V85N3S | 480 | 3 | 42 | 850 | 600
SSC0652.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 600 | 480 | 3 | 42 | 701 | 600 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 480 | 3 | 65 | 1600 | 600
|  |  |  | RVSS | Eaton | S801+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0652.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 600 | 480 | 3 | 42 | 701 | 600 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 480 | 3 | 65 | 1600 | 600
|  |  |  | RVSS | Eaton | S811V85N3S | 480 | 3 | 42 | 850 | 600
SSC0652.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 600 | 480 | 3 | 42 | 701 | 600 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 480 | 3 | 65 | 1600 | 600
|  |  |  | RVSS | Eaton | S811+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0653.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 700 | 600 | 3 | 42 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 600 | 3 | 50 | 800 | 700
|  |  |  | RVSS | Eaton | S801V85N3S | 600 | 3 | 42 | 850 | 700
SSC0653.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 700 | 600 | 3 | 42 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 600 | 3 | 50 | 800 | 700
|  |  |  | RVSS | Eaton | S801+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0653.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 700 | 600 | 3 | 42 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 600 | 3 | 50 | 800 | 700
|  |  |  | RVSS | Eaton | S811V85N3S | 600 | 3 | 42 | 850 | 700
SSC0653.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 700 | 600 | 3 | 42 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 600 | 3 | 50 | 800 | 700
|  |  |  | RVSS | Eaton | S811+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0654.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 700 | 600 | 3 | 42 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 700
|  |  |  | RVSS | Eaton | S801V85N3S | 600 | 3 | 42 | 850 | 700
SSC0654.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 700 | 600 | 3 | 42 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 700
|  |  |  | RVSS | Eaton | S801+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0654.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 700 | 600 | 3 | 42 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 700
|  |  |  | RVSS | Eaton | S811V85N3S | 600 | 3 | 42 | 850 | 700
SSC0654.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 700 | 600 | 3 | 42 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 700
|  |  |  | RVSS | Eaton | S811+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0655.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 700 | 600 | 3 | 42 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 700
|  |  |  | RVSS | Eaton | S801V85N3S | 600 | 3 | 42 | 850 | 700
SSC0655.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 700 | 600 | 3 | 42 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 700
|  |  |  | RVSS | Eaton | S801+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0655.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 700 | 600 | 3 | 42 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 700
|  |  |  | RVSS | Eaton | S811V85N3S | 600 | 3 | 42 | 850 | 700
SSC0655.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 700 | 600 | 3 | 42 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 700
|  |  |  | RVSS | Eaton | S811+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0656.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 700 | 600 | 3 | 42 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 700
|  |  |  | RVSS | Eaton | S801V85N3S | 600 | 3 | 42 | 850 | 700
SSC0656.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 700 | 600 | 3 | 42 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 700
|  |  |  | RVSS | Eaton | S801+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0656.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 700 | 600 | 3 | 42 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 700
|  |  |  | RVSS | Eaton | S811V85N3S | 600 | 3 | 42 | 850 | 700
SSC0656.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 700 | 600 | 3 | 42 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 700
|  |  |  | RVSS | Eaton | S811+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0657.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 700 | 600 | 3 | 42 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 700
|  |  |  | RVSS | Eaton | S801V85N3S | 600 | 3 | 42 | 850 | 700
SSC0657.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 700 | 600 | 3 | 42 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 700
|  |  |  | RVSS | Eaton | S801+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0657.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 700 | 600 | 3 | 42 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 700
|  |  |  | RVSS | Eaton | S811V85N3S | 600 | 3 | 42 | 850 | 700
SSC0657.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 700 | 600 | 3 | 42 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 700
|  |  |  | RVSS | Eaton | S811+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0658.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 700 | 600 | 3 | 42 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 600 | 3 | 50 | 1600 | 700
|  |  |  | RVSS | Eaton | S801V85N3S | 600 | 3 | 42 | 850 | 700
SSC0658.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 700 | 600 | 3 | 42 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 600 | 3 | 50 | 1600 | 700
|  |  |  | RVSS | Eaton | S801+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0658.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 700 | 600 | 3 | 42 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 600 | 3 | 50 | 1600 | 700
|  |  |  | RVSS | Eaton | S811V85N3S | 600 | 3 | 42 | 850 | 700
SSC0658.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 700 | 600 | 3 | 42 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 600 | 3 | 50 | 1600 | 700
|  |  |  | RVSS | Eaton | S811+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0659.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 700 | 600 | 3 | 42 | 653 | 700 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 600 | 3 | 50 | 1600 | 700
|  |  |  | RVSS | Eaton | S801V85N3S | 600 | 3 | 42 | 850 | 700
SSC0659.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 700 | 600 | 3 | 42 | 653 | 700 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 600 | 3 | 50 | 1600 | 700
|  |  |  | RVSS | Eaton | S801+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0659.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 700 | 600 | 3 | 42 | 653 | 700 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 600 | 3 | 50 | 1600 | 700
|  |  |  | RVSS | Eaton | S811V85N3S | 600 | 3 | 42 | 850 | 700
SSC0659.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 700 | 600 | 3 | 42 | 653 | 700 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 600 | 3 | 50 | 1600 | 700
|  |  |  | RVSS | Eaton | S811+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0660.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 350 | 200 | 3 | 42 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 200 | 3 | 125 | 1000 | 350
|  |  |  | RVSS | Eaton | S801V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0660.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 350 | 200 | 3 | 42 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 200 | 3 | 125 | 1000 | 350
|  |  |  | RVSS | Eaton | S801+V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0660.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 350 | 200 | 3 | 42 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 200 | 3 | 125 | 1000 | 350
|  |  |  | RVSS | Eaton | S811V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0660.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 350 | 200 | 3 | 42 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 200 | 3 | 125 | 1000 | 350
|  |  |  | RVSS | Eaton | S811+V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0661.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 350 | 200 | 3 | 42 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 200 | 3 | 125 | 1200 | 350
|  |  |  | RVSS | Eaton | S801V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0661.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 350 | 200 | 3 | 42 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 200 | 3 | 125 | 1200 | 350
|  |  |  | RVSS | Eaton | S801+V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0661.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 350 | 200 | 3 | 42 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 200 | 3 | 125 | 1200 | 350
|  |  |  | RVSS | Eaton | S811V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0661.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 350 | 200 | 3 | 42 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 200 | 3 | 125 | 1200 | 350
|  |  |  | RVSS | Eaton | S811+V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0662.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 350 | 200 | 3 | 42 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S801V10N3S | 200 | 3 | 42 | 850 | 350
SSC0662.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 350 | 200 | 3 | 42 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S801+V10N3S | 200 | 3 | 42 | 850 | 350
SSC0662.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 350 | 200 | 3 | 42 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S811V10N3S | 200 | 3 | 42 | 850 | 350
SSC0662.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 350 | 200 | 3 | 42 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S811+V10N3S | 200 | 3 | 42 | 850 | 350
SSC0663.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 350 | 200 | 3 | 42 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S801V10N3S | 200 | 3 | 42 | 850 | 350
SSC0663.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 350 | 200 | 3 | 42 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S801+V10N3S | 200 | 3 | 42 | 850 | 350
SSC0663.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 350 | 200 | 3 | 42 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S811V10N3S | 200 | 3 | 42 | 850 | 350
SSC0663.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 350 | 200 | 3 | 42 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S811+V10N3S | 200 | 3 | 42 | 850 | 350
SSC0664.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 350 | 200 | 3 | 42 | 830 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S801V10N3S | 200 | 3 | 42 | 850 | 350
SSC0664.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 350 | 200 | 3 | 42 | 830 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S801+V10N3S | 200 | 3 | 42 | 850 | 350
SSC0664.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 350 | 200 | 3 | 42 | 830 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S811V10N3S | 200 | 3 | 42 | 850 | 350
SSC0664.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 350 | 200 | 3 | 42 | 830 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S811+V10N3S | 200 | 3 | 42 | 850 | 350
SSC0665.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 350 | 200 | 3 | 42 | 952 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S801V10N3S | 200 | 3 | 42 | 850 | 350
SSC0665.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 350 | 200 | 3 | 42 | 952 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S801+V10N3S | 200 | 3 | 42 | 850 | 350
SSC0665.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 350 | 200 | 3 | 42 | 952 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S811V10N3S | 200 | 3 | 42 | 850 | 350
SSC0665.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 200 | 3 | 125 | 1600 | 350 | 200 | 3 | 42 | 952 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 200 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S811+V10N3S | 200 | 3 | 42 | 850 | 350
SSC0666.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 350 | 208 | 3 | 42 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 350
|  |  |  | RVSS | Eaton | S801V10N3S | 208 | 3 | 42 | 850 | 350
SSC0666.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 350 | 208 | 3 | 42 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 350
|  |  |  | RVSS | Eaton | S801+V10N3S | 208 | 3 | 42 | 850 | 350
SSC0666.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 350 | 208 | 3 | 42 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 350
|  |  |  | RVSS | Eaton | S811V10N3S | 208 | 3 | 42 | 850 | 350
SSC0666.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 350 | 208 | 3 | 42 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 350
|  |  |  | RVSS | Eaton | S811+V10N3S | 208 | 3 | 42 | 850 | 350
SSC0667.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 350 | 208 | 3 | 42 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 350
|  |  |  | RVSS | Eaton | S801V10N3S | 208 | 3 | 42 | 850 | 350
SSC0667.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 350 | 208 | 3 | 42 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 350
|  |  |  | RVSS | Eaton | S801+V10N3S | 208 | 3 | 42 | 850 | 350
SSC0667.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 350 | 208 | 3 | 42 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 350
|  |  |  | RVSS | Eaton | S811V10N3S | 208 | 3 | 42 | 850 | 350
SSC0667.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 350 | 208 | 3 | 42 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 208 | 3 | 125 | 1000 | 350
|  |  |  | RVSS | Eaton | S811+V10N3S | 208 | 3 | 42 | 850 | 350
SSC0668.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 350 | 208 | 3 | 42 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 208 | 3 | 125 | 1200 | 350
|  |  |  | RVSS | Eaton | S801V10N3S | 208 | 3 | 42 | 850 | 350
SSC0668.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 350 | 208 | 3 | 42 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 208 | 3 | 125 | 1200 | 350
|  |  |  | RVSS | Eaton | S801+V10N3S | 208 | 3 | 42 | 850 | 350
SSC0668.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 350 | 208 | 3 | 42 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 208 | 3 | 125 | 1200 | 350
|  |  |  | RVSS | Eaton | S811V10N3S | 208 | 3 | 42 | 850 | 350
SSC0668.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 350 | 208 | 3 | 42 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 208 | 3 | 125 | 1200 | 350
|  |  |  | RVSS | Eaton | S811+V10N3S | 208 | 3 | 42 | 850 | 350
SSC0669.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 350 | 208 | 3 | 42 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 208 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S801V10N3S | 208 | 3 | 42 | 850 | 350
SSC0669.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 350 | 208 | 3 | 42 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 208 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S801+V10N3S | 208 | 3 | 42 | 850 | 350
SSC0669.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 350 | 208 | 3 | 42 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 208 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S811V10N3S | 208 | 3 | 42 | 850 | 350
SSC0669.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 350 | 208 | 3 | 42 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 208 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S811+V10N3S | 208 | 3 | 42 | 850 | 350
SSC0670.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 350 | 208 | 3 | 42 | 794 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 208 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S801V10N3S | 208 | 3 | 42 | 850 | 350
SSC0670.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 350 | 208 | 3 | 42 | 794 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 208 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S801+V10N3S | 208 | 3 | 42 | 850 | 350
SSC0670.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 350 | 208 | 3 | 42 | 794 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 208 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S811V10N3S | 208 | 3 | 42 | 850 | 350
SSC0670.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 350 | 208 | 3 | 42 | 794 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 208 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S811+V10N3S | 208 | 3 | 42 | 850 | 350
SSC0671.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 350 | 208 | 3 | 42 | 911 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 208 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S801V10N3S | 208 | 3 | 42 | 850 | 350
SSC0671.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 350 | 208 | 3 | 42 | 911 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 208 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S801+V10N3S | 208 | 3 | 42 | 850 | 350
SSC0671.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 350 | 208 | 3 | 42 | 911 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 208 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S811V10N3S | 208 | 3 | 42 | 850 | 350
SSC0671.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 208 | 3 | 125 | 1600 | 350 | 208 | 3 | 42 | 911 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 208 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S811+V10N3S | 208 | 3 | 42 | 850 | 350
SSC0672.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 350 | 240 | 3 | 42 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 240 | 3 | 125 | 1000 | 350
|  |  |  | RVSS | Eaton | S801V10N3S | 240 | 3 | 42 | 850 | 350
SSC0672.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 350 | 240 | 3 | 42 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 240 | 3 | 125 | 1000 | 350
|  |  |  | RVSS | Eaton | S801+V10N3S | 240 | 3 | 42 | 850 | 350
SSC0672.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 350 | 240 | 3 | 42 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 240 | 3 | 125 | 1000 | 350
|  |  |  | RVSS | Eaton | S811V10N3S | 240 | 3 | 42 | 850 | 350
SSC0672.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 350 | 240 | 3 | 42 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 240 | 3 | 125 | 1000 | 350
|  |  |  | RVSS | Eaton | S811+V10N3S | 240 | 3 | 42 | 850 | 350
SSC0673.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 350 | 240 | 3 | 42 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 240 | 3 | 125 | 1200 | 350
|  |  |  | RVSS | Eaton | S801V10N3S | 240 | 3 | 42 | 850 | 350
SSC0673.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 350 | 240 | 3 | 42 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 240 | 3 | 125 | 1200 | 350
|  |  |  | RVSS | Eaton | S801+V10N3S | 240 | 3 | 42 | 850 | 350
SSC0673.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 350 | 240 | 3 | 42 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 240 | 3 | 125 | 1200 | 350
|  |  |  | RVSS | Eaton | S811V10N3S | 240 | 3 | 42 | 850 | 350
SSC0673.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 350 | 240 | 3 | 42 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 240 | 3 | 125 | 1200 | 350
|  |  |  | RVSS | Eaton | S811+V10N3S | 240 | 3 | 42 | 850 | 350
SSC0674.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 350 | 240 | 3 | 42 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 240 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S801V10N3S | 240 | 3 | 42 | 1000 | 350
SSC0674.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 350 | 240 | 3 | 42 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 240 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S801+V10N3S | 240 | 3 | 42 | 1000 | 350
SSC0674.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 350 | 240 | 3 | 42 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 240 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S811V10N3S | 240 | 3 | 42 | 1000 | 350
SSC0674.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 350 | 240 | 3 | 42 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 240 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S811+V10N3S | 240 | 3 | 42 | 1000 | 350
SSC0675.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 350 | 240 | 3 | 42 | 722 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 240 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S801V10N3S | 240 | 3 | 42 | 1000 | 350
SSC0675.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 350 | 240 | 3 | 42 | 722 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 240 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S801+V10N3S | 240 | 3 | 42 | 1000 | 350
SSC0675.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 350 | 240 | 3 | 42 | 722 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 240 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S811V10N3S | 240 | 3 | 42 | 1000 | 350
SSC0675.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 350 | 240 | 3 | 42 | 722 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 240 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S811+V10N3S | 240 | 3 | 42 | 1000 | 350
SSC0676.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 350 | 240 | 3 | 42 | 828 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 240 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S801V10N3S | 240 | 3 | 42 | 1000 | 350
SSC0676.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 350 | 240 | 3 | 42 | 828 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 240 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S801+V10N3S | 240 | 3 | 42 | 1000 | 350
SSC0676.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 350 | 240 | 3 | 42 | 828 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 240 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S811V10N3S | 240 | 3 | 42 | 1000 | 350
SSC0676.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 240 | 3 | 125 | 1600 | 350 | 240 | 3 | 42 | 828 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 240 | 3 | 125 | 1600 | 350
|  |  |  | RVSS | Eaton | S811+V10N3S | 240 | 3 | 42 | 1000 | 350
SSC0677.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 700 | 480 | 3 | 42 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 480 | 3 | 65 | 1000 | 700
|  |  |  | RVSS | Eaton | S801V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0677.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 700 | 480 | 3 | 42 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 480 | 3 | 65 | 1000 | 700
|  |  |  | RVSS | Eaton | S801+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0677.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 700 | 480 | 3 | 42 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 480 | 3 | 65 | 1000 | 700
|  |  |  | RVSS | Eaton | S811V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0677.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 700 | 480 | 3 | 42 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 480 | 3 | 65 | 1000 | 700
|  |  |  | RVSS | Eaton | S811+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0678.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 700 | 480 | 3 | 42 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 700
|  |  |  | RVSS | Eaton | S801V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0678.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 700 | 480 | 3 | 42 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 700
|  |  |  | RVSS | Eaton | S801+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0678.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 700 | 480 | 3 | 42 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 700
|  |  |  | RVSS | Eaton | S811V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0678.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 700 | 480 | 3 | 42 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 700
|  |  |  | RVSS | Eaton | S811+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0679.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 700 | 480 | 3 | 42 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 700
|  |  |  | RVSS | Eaton | S801V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0679.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 700 | 480 | 3 | 42 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 700
|  |  |  | RVSS | Eaton | S801+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0679.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 700 | 480 | 3 | 42 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 700
|  |  |  | RVSS | Eaton | S811V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0679.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 700 | 480 | 3 | 42 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 700
|  |  |  | RVSS | Eaton | S811+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0680.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 700 | 480 | 3 | 42 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 700
|  |  |  | RVSS | Eaton | S801V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0680.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 700 | 480 | 3 | 42 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 700
|  |  |  | RVSS | Eaton | S801+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0680.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 700 | 480 | 3 | 42 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 700
|  |  |  | RVSS | Eaton | S811V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0680.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 700 | 480 | 3 | 42 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 480 | 3 | 65 | 1200 | 700
|  |  |  | RVSS | Eaton | S811+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0681.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 700 | 480 | 3 | 42 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 480 | 3 | 65 | 1600 | 700
|  |  |  | RVSS | Eaton | S801V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0681.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 700 | 480 | 3 | 42 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 480 | 3 | 65 | 1600 | 700
|  |  |  | RVSS | Eaton | S801+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0681.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 700 | 480 | 3 | 42 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 480 | 3 | 65 | 1600 | 700
|  |  |  | RVSS | Eaton | S811V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0681.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 700 | 480 | 3 | 42 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 480 | 3 | 65 | 1600 | 700
|  |  |  | RVSS | Eaton | S811+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0682.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 700 | 480 | 3 | 42 | 701 | 600 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 480 | 3 | 65 | 1600 | 700
|  |  |  | RVSS | Eaton | S801V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0682.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 700 | 480 | 3 | 42 | 701 | 600 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 480 | 3 | 65 | 1600 | 700
|  |  |  | RVSS | Eaton | S801+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0682.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 700 | 480 | 3 | 42 | 701 | 600 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 480 | 3 | 65 | 1600 | 700
|  |  |  | RVSS | Eaton | S811V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0682.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 700 | 480 | 3 | 42 | 701 | 600 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 480 | 3 | 65 | 1600 | 700
|  |  |  | RVSS | Eaton | S811+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0683.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 700 | 480 | 3 | 42 | 804 | 700 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 480 | 3 | 65 | 1600 | 700
|  |  |  | RVSS | Eaton | S801V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0683.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 700 | 480 | 3 | 42 | 804 | 700 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 480 | 3 | 65 | 1600 | 700
|  |  |  | RVSS | Eaton | S801+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0683.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 700 | 480 | 3 | 42 | 804 | 700 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 480 | 3 | 65 | 1600 | 700
|  |  |  | RVSS | Eaton | S811V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0683.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 480 | 3 | 65 | 1600 | 700 | 480 | 3 | 42 | 804 | 700 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 480 | 3 | 65 | 1600 | 700
|  |  |  | RVSS | Eaton | S811+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0684.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 600 | 3 | 50 | 800 | 800
|  |  |  | RVSS | Eaton | S801V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0684.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 600 | 3 | 50 | 800 | 800
|  |  |  | RVSS | Eaton | S801+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0684.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 600 | 3 | 50 | 800 | 800
|  |  |  | RVSS | Eaton | S811V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0684.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A080 | 600 | 3 | 50 | 800 | 800
|  |  |  | RVSS | Eaton | S811+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0685.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 800
|  |  |  | RVSS | Eaton | S801V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0685.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 800
|  |  |  | RVSS | Eaton | S801+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0685.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 800
|  |  |  | RVSS | Eaton | S811V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0685.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 800
|  |  |  | RVSS | Eaton | S811+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0686.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 800
|  |  |  | RVSS | Eaton | S801V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0686.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 800
|  |  |  | RVSS | Eaton | S801+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0686.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 800
|  |  |  | RVSS | Eaton | S811V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0686.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A100 | 600 | 3 | 50 | 1000 | 800
|  |  |  | RVSS | Eaton | S811+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0687.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 800
|  |  |  | RVSS | Eaton | S801V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0687.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 800
|  |  |  | RVSS | Eaton | S801+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0687.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 800
|  |  |  | RVSS | Eaton | S811V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0687.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 800
|  |  |  | RVSS | Eaton | S811+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0688.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 800
|  |  |  | RVSS | Eaton | S801V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0688.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 800
|  |  |  | RVSS | Eaton | S801+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0688.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 800
|  |  |  | RVSS | Eaton | S811V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0688.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A120 | 600 | 3 | 50 | 1200 | 800
|  |  |  | RVSS | Eaton | S811+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0689.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 600 | 3 | 50 | 1600 | 800
|  |  |  | RVSS | Eaton | S801V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0689.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 600 | 3 | 50 | 1600 | 800
|  |  |  | RVSS | Eaton | S801+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0689.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 600 | 3 | 50 | 1600 | 800
|  |  |  | RVSS | Eaton | S811V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0689.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 600 | 3 | 50 | 1600 | 800
|  |  |  | RVSS | Eaton | S811+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0690.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 653 | 700 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 600 | 3 | 50 | 1600 | 800
|  |  |  | RVSS | Eaton | S801V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0690.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 653 | 700 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 600 | 3 | 50 | 1600 | 800
|  |  |  | RVSS | Eaton | S801+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0690.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 653 | 700 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 600 | 3 | 50 | 1600 | 800
|  |  |  | RVSS | Eaton | S811V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0690.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 653 | 700 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 600 | 3 | 50 | 1600 | 800
|  |  |  | RVSS | Eaton | S811+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0691.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 742 | 800 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 600 | 3 | 50 | 1600 | 800
|  |  |  | RVSS | Eaton | S801V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0691.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 742 | 800 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 600 | 3 | 50 | 1600 | 800
|  |  |  | RVSS | Eaton | S801+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0691.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 742 | 800 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 600 | 3 | 50 | 1600 | 800
|  |  |  | RVSS | Eaton | S811V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0691.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | RD316T*** | 600 | 3 | 50 | 1600 | 800 | 600 | 3 | 42 | 742 | 800 | 50616 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPR16A160 | 600 | 3 | 50 | 1600 | 800
|  |  |  | RVSS | Eaton | S811+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0692.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 200 | 3 | 42 | 360 | 125
SSC0692.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 200 | 3 | 42 | 360 | 125
SSC0692.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 200 | 3 | 42 | 360 | 125
SSC0692.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 200 | 3 | 100 | 350 | 100 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 200 | 3 | 42 | 360 | 125
SSC0693.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 200 | 3 | 100 | 450 | 150 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 200 | 3 | 42 | 360 | 125
SSC0693.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 200 | 3 | 100 | 450 | 150 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 200 | 3 | 42 | 360 | 125
SSC0693.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 200 | 3 | 100 | 450 | 150 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 200 | 3 | 42 | 360 | 125
SSC0693.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 200 | 3 | 100 | 450 | 150 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 200 | 3 | 42 | 360 | 125
SSC0694.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 150 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 200 | 3 | 42 | 360 | 125
SSC0694.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 150 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 200 | 3 | 42 | 360 | 125
SSC0694.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 150 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 200 | 3 | 42 | 360 | 125
SSC0694.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 150 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 200 | 3 | 42 | 360 | 125
SSC0695.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 200 | 3 | 42 | 360 | 125
SSC0695.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 200 | 3 | 42 | 360 | 125
SSC0695.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 200 | 3 | 42 | 360 | 125
SSC0695.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 200 | 3 | 42 | 360 | 125
SSC0696.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 200 | 3 | 42 | 360 | 125
SSC0696.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 200 | 3 | 42 | 360 | 125
SSC0696.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 200 | 3 | 42 | 360 | 125
SSC0696.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 200 | 3 | 42 | 360 | 125
SSC0697.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 200 | 3 | 42 | 360 | 125
SSC0697.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 200 | 3 | 42 | 360 | 125
SSC0697.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 200 | 3 | 42 | 360 | 125
SSC0697.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 200 | 3 | 42 | 360 | 125
SSC0698.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 208 | 3 | 42 | 360 | 125
SSC0698.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 208 | 3 | 42 | 360 | 125
SSC0698.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 208 | 3 | 42 | 360 | 125
SSC0698.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3300* | 208 | 3 | 100 | 300 | 100 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 208 | 3 | 42 | 360 | 125
SSC0699.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 208 | 3 | 42 | 360 | 125
SSC0699.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 208 | 3 | 42 | 360 | 125
SSC0699.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 208 | 3 | 42 | 360 | 125
SSC0699.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 208 | 3 | 42 | 360 | 125
SSC0700.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 208 | 3 | 42 | 360 | 125
SSC0700.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 208 | 3 | 42 | 360 | 125
SSC0700.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 208 | 3 | 42 | 360 | 125
SSC0700.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 208 | 3 | 42 | 360 | 125
SSC0701.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 208 | 3 | 42 | 360 | 125
SSC0701.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 208 | 3 | 42 | 360 | 125
SSC0701.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 208 | 3 | 42 | 360 | 125
SSC0701.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 208 | 3 | 42 | 360 | 125
SSC0702.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 208 | 3 | 42 | 360 | 125
SSC0702.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 208 | 3 | 42 | 360 | 125
SSC0702.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 208 | 3 | 42 | 360 | 125
SSC0702.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 208 | 3 | 42 | 360 | 125
SSC0703.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 208 | 3 | 42 | 360 | 125
SSC0703.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 208 | 3 | 42 | 360 | 125
SSC0703.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 208 | 3 | 42 | 360 | 125
SSC0703.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 208 | 3 | 42 | 360 | 125
SSC0704.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 240 | 3 | 42 | 360 | 150
SSC0704.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 240 | 3 | 42 | 360 | 150
SSC0704.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 240 | 3 | 42 | 360 | 150
SSC0704.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 240 | 3 | 100 | 350 | 125 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 240 | 3 | 42 | 360 | 150
SSC0705.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 240 | 3 | 100 | 450 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 240 | 3 | 42 | 360 | 150
SSC0705.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 240 | 3 | 100 | 450 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 240 | 3 | 42 | 360 | 150
SSC0705.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 240 | 3 | 100 | 450 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 240 | 3 | 42 | 360 | 150
SSC0705.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 240 | 3 | 100 | 450 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 240 | 3 | 42 | 360 | 150
SSC0706.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 240 | 3 | 42 | 360 | 150
SSC0706.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 240 | 3 | 42 | 360 | 150
SSC0706.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 240 | 3 | 42 | 360 | 150
SSC0706.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 240 | 3 | 42 | 360 | 150
SSC0707.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 240 | 3 | 42 | 360 | 150
SSC0707.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 240 | 3 | 42 | 360 | 150
SSC0707.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 240 | 3 | 42 | 360 | 150
SSC0707.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 240 | 3 | 42 | 360 | 150
SSC0708.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 240 | 3 | 42 | 360 | 150
SSC0708.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 240 | 3 | 42 | 360 | 150
SSC0708.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 240 | 3 | 42 | 360 | 150
SSC0708.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 240 | 3 | 42 | 360 | 150
SSC0709.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 240 | 3 | 42 | 360 | 150
SSC0709.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 240 | 3 | 42 | 360 | 150
SSC0709.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 240 | 3 | 42 | 360 | 150
SSC0709.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 240 | 3 | 42 | 360 | 150
SSC0710.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 480 | 3 | 42 | 360 | 250
SSC0710.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 480 | 3 | 42 | 360 | 250
SSC0710.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 480 | 3 | 42 | 360 | 250
SSC0710.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 480 | 3 | 65 | 350 | 250 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 480 | 3 | 42 | 360 | 250
SSC0711.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 480 | 3 | 42 | 360 | 250
SSC0711.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 480 | 3 | 42 | 360 | 250
SSC0711.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 480 | 3 | 42 | 360 | 250
SSC0711.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 480 | 3 | 42 | 360 | 250
SSC0712.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 480 | 3 | 42 | 360 | 250
SSC0712.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 480 | 3 | 42 | 360 | 250
SSC0712.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 480 | 3 | 42 | 360 | 250
SSC0712.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 480 | 3 | 42 | 360 | 250
SSC0713.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 480 | 3 | 42 | 360 | 250
SSC0713.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 480 | 3 | 42 | 360 | 250
SSC0713.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 480 | 3 | 42 | 360 | 250
SSC0713.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 480 | 3 | 42 | 360 | 250
SSC0714.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 480 | 3 | 42 | 360 | 250
SSC0714.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 480 | 3 | 42 | 360 | 250
SSC0714.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 480 | 3 | 42 | 360 | 250
SSC0714.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 480 | 3 | 42 | 360 | 250
SSC0715.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 600 | 3 | 42 | 360 | 350
SSC0715.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 600 | 3 | 42 | 360 | 350
SSC0715.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 600 | 3 | 42 | 360 | 350
SSC0715.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3350* | 600 | 3 | 35 | 350 | 350 | 600 | 3 | 35 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 600 | 3 | 42 | 360 | 350
SSC0716.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 600 | 3 | 42 | 360 | 350
SSC0716.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 600 | 3 | 42 | 360 | 350
SSC0716.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 600 | 3 | 42 | 360 | 350
SSC0716.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 600 | 3 | 42 | 360 | 350
SSC0717.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 600 | 3 | 35 | 500 | 500 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 600 | 3 | 42 | 360 | 350
SSC0717.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 600 | 3 | 35 | 500 | 500 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 600 | 3 | 42 | 360 | 350
SSC0717.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 600 | 3 | 35 | 500 | 500 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 600 | 3 | 42 | 360 | 350
SSC0717.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 600 | 3 | 35 | 500 | 500 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 600 | 3 | 42 | 360 | 350
SSC0718.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 600 | 3 | 42 | 360 | 350
SSC0718.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 600 | 3 | 42 | 360 | 350
SSC0718.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 600 | 3 | 42 | 360 | 350
SSC0718.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 600 | 3 | 42 | 360 | 350
SSC0719.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 600 | 3 | 42 | 360 | 350
SSC0719.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 600 | 3 | 42 | 360 | 350
SSC0719.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 600 | 3 | 42 | 360 | 350
SSC0719.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 600 | 3 | 42 | 360 | 350
SSC0720.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 600 | 3 | 42 | 360 | 350
SSC0720.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 600 | 3 | 42 | 360 | 350
SSC0720.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 600 | 3 | 42 | 360 | 350
SSC0720.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 600 | 3 | 42 | 360 | 350
SSC0721.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 200 | 3 | 100 | 800 | 200 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 200 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S801U36N3S | 200 | 3 | 42 | 360 | 125
SSC0721.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 200 | 3 | 100 | 800 | 200 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 200 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S801+U36N3S | 200 | 3 | 42 | 360 | 125
SSC0721.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 200 | 3 | 100 | 800 | 200 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 200 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S811U36N3S | 200 | 3 | 42 | 360 | 125
SSC0721.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 200 | 3 | 100 | 800 | 200 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 200 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S811+U36N3S | 200 | 3 | 42 | 360 | 125
SSC0722.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 100 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 200 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801U36N3S | 200 | 3 | 42 | 360 | 125
SSC0722.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 100 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 200 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801+U36N3S | 200 | 3 | 42 | 360 | 125
SSC0722.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 100 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 200 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811U36N3S | 200 | 3 | 42 | 360 | 125
SSC0722.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 100 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 200 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811+U36N3S | 200 | 3 | 42 | 360 | 125
SSC0723.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 208 | 3 | 100 | 800 | 200 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 208 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S801U36N3S | 208 | 3 | 42 | 360 | 125
SSC0723.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 208 | 3 | 100 | 800 | 200 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 208 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S801+U36N3S | 208 | 3 | 42 | 360 | 125
SSC0723.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 208 | 3 | 100 | 800 | 200 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 208 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S811U36N3S | 208 | 3 | 42 | 360 | 125
SSC0723.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 208 | 3 | 100 | 800 | 200 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 208 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S811+U36N3S | 208 | 3 | 42 | 360 | 125
SSC0724.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 100 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801U36N3S | 208 | 3 | 42 | 360 | 125
SSC0724.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 100 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801+U36N3S | 208 | 3 | 42 | 360 | 125
SSC0724.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 100 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811U36N3S | 208 | 3 | 42 | 360 | 125
SSC0724.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 100 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811+U36N3S | 208 | 3 | 42 | 360 | 125
SSC0725.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 240 | 3 | 100 | 700 | 250
|  |  |  | RVSS | Eaton | S801U36N3S | 240 | 3 | 42 | 360 | 150
SSC0725.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 240 | 3 | 100 | 700 | 250
|  |  |  | RVSS | Eaton | S801+U36N3S | 240 | 3 | 42 | 360 | 150
SSC0725.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 240 | 3 | 100 | 700 | 250
|  |  |  | RVSS | Eaton | S811U36N3S | 240 | 3 | 42 | 360 | 150
SSC0725.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 240 | 3 | 100 | 700 | 250
|  |  |  | RVSS | Eaton | S811+U36N3S | 240 | 3 | 42 | 360 | 150
SSC0726.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 100 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 240 | 3 | 100 | 800 | 300
|  |  |  | RVSS | Eaton | S801U36N3S | 240 | 3 | 42 | 360 | 150
SSC0726.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 100 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 240 | 3 | 100 | 800 | 300
|  |  |  | RVSS | Eaton | S801+U36N3S | 240 | 3 | 42 | 360 | 150
SSC0726.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 100 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 240 | 3 | 100 | 800 | 300
|  |  |  | RVSS | Eaton | S811U36N3S | 240 | 3 | 42 | 360 | 150
SSC0726.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 100 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 240 | 3 | 100 | 800 | 300
|  |  |  | RVSS | Eaton | S811+U36N3S | 240 | 3 | 42 | 360 | 150
SSC0727.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 100 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 240 | 3 | 100 | 1000 | 400
|  |  |  | RVSS | Eaton | S801U36N3S | 240 | 3 | 42 | 360 | 150
SSC0727.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 100 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 240 | 3 | 100 | 1000 | 400
|  |  |  | RVSS | Eaton | S801+U36N3S | 240 | 3 | 42 | 360 | 150
SSC0727.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 100 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 240 | 3 | 100 | 1000 | 400
|  |  |  | RVSS | Eaton | S811U36N3S | 240 | 3 | 42 | 360 | 150
SSC0727.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 100 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 240 | 3 | 100 | 1000 | 400
|  |  |  | RVSS | Eaton | S811+U36N3S | 240 | 3 | 42 | 360 | 150
SSC0728.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 480 | 3 | 65 | 700 | 500
|  |  |  | RVSS | Eaton | S801U36N3S | 480 | 3 | 42 | 360 | 250
SSC0728.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 480 | 3 | 65 | 700 | 500
|  |  |  | RVSS | Eaton | S801+U36N3S | 480 | 3 | 42 | 360 | 250
SSC0728.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 480 | 3 | 65 | 700 | 500
|  |  |  | RVSS | Eaton | S811U36N3S | 480 | 3 | 42 | 360 | 250
SSC0728.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 480 | 3 | 65 | 700 | 500
|  |  |  | RVSS | Eaton | S811+U36N3S | 480 | 3 | 42 | 360 | 250
SSC0729.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S801U36N3S | 480 | 3 | 42 | 360 | 250
SSC0729.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S801+U36N3S | 480 | 3 | 42 | 360 | 250
SSC0729.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S811U36N3S | 480 | 3 | 42 | 360 | 250
SSC0729.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S811+U36N3S | 480 | 3 | 42 | 360 | 250
SSC0730.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 600 | 3 | 35 | 700 | 500
|  |  |  | RVSS | Eaton | S801U36N3S | 600 | 3 | 42 | 360 | 250
SSC0730.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 600 | 3 | 35 | 700 | 500
|  |  |  | RVSS | Eaton | S801+U36N3S | 600 | 3 | 42 | 360 | 250
SSC0730.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 600 | 3 | 35 | 700 | 500
|  |  |  | RVSS | Eaton | S811U36N3S | 600 | 3 | 42 | 360 | 250
SSC0730.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 600 | 3 | 35 | 700 | 500
|  |  |  | RVSS | Eaton | S811+U36N3S | 600 | 3 | 42 | 360 | 250
SSC0731.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 600 | 3 | 35 | 800 | 500
|  |  |  | RVSS | Eaton | S801U36N3S | 600 | 3 | 42 | 360 | 250
SSC0731.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 600 | 3 | 35 | 800 | 500
|  |  |  | RVSS | Eaton | S801+U36N3S | 600 | 3 | 42 | 360 | 250
SSC0731.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 600 | 3 | 35 | 800 | 500
|  |  |  | RVSS | Eaton | S811U36N3S | 600 | 3 | 42 | 360 | 250
SSC0731.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 600 | 3 | 35 | 800 | 500
|  |  |  | RVSS | Eaton | S811+U36N3S | 600 | 3 | 42 | 360 | 250
SSC0732.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S801U36N3S | 600 | 3 | 42 | 360 | 250
SSC0732.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S801+U36N3S | 600 | 3 | 42 | 360 | 250
SSC0732.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S811U36N3S | 600 | 3 | 42 | 360 | 250
SSC0732.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S811+U36N3S | 600 | 3 | 42 | 360 | 250
SSC0733.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 200 | 3 | 100 | 450 | 150 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 200 | 3 | 42 | 420 | 150
SSC0733.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 200 | 3 | 100 | 450 | 150 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 200 | 3 | 42 | 420 | 150
SSC0733.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 200 | 3 | 100 | 450 | 150 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 200 | 3 | 42 | 420 | 150
SSC0733.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 200 | 3 | 100 | 450 | 150 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 200 | 3 | 42 | 420 | 150
SSC0734.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 200 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 200 | 3 | 42 | 420 | 150
SSC0734.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 200 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 200 | 3 | 42 | 420 | 150
SSC0734.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 200 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 200 | 3 | 42 | 420 | 150
SSC0734.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 200 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 200 | 3 | 42 | 420 | 150
SSC0735.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 200 | 3 | 42 | 420 | 150
SSC0735.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 200 | 3 | 42 | 420 | 150
SSC0735.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 200 | 3 | 42 | 420 | 150
SSC0735.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 200 | 3 | 42 | 420 | 150
SSC0736.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 200 | 3 | 42 | 420 | 150
SSC0736.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 200 | 3 | 42 | 420 | 150
SSC0736.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 200 | 3 | 42 | 420 | 150
SSC0736.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 200 | 3 | 42 | 420 | 150
SSC0737.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 200 | 3 | 42 | 420 | 150
SSC0737.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 200 | 3 | 42 | 420 | 150
SSC0737.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 200 | 3 | 42 | 420 | 150
SSC0737.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 200 | 3 | 42 | 420 | 150
SSC0738.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 200 | 3 | 42 | 420 | 150
SSC0738.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 200 | 3 | 42 | 420 | 150
SSC0738.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 200 | 3 | 42 | 420 | 150
SSC0738.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 200 | 3 | 42 | 420 | 150
SSC0739.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 208 | 3 | 42 | 420 | 150
SSC0739.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 208 | 3 | 42 | 420 | 150
SSC0739.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 208 | 3 | 42 | 420 | 150
SSC0739.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 208 | 3 | 100 | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 208 | 3 | 42 | 420 | 150
SSC0740.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 208 | 3 | 42 | 420 | 150
SSC0740.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 208 | 3 | 42 | 420 | 150
SSC0740.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 208 | 3 | 42 | 420 | 150
SSC0740.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 208 | 3 | 42 | 420 | 150
SSC0741.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 208 | 3 | 42 | 420 | 150
SSC0741.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 208 | 3 | 42 | 420 | 150
SSC0741.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 208 | 3 | 42 | 420 | 150
SSC0741.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 208 | 3 | 42 | 420 | 150
SSC0742.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 208 | 3 | 42 | 420 | 150
SSC0742.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 208 | 3 | 42 | 420 | 150
SSC0742.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 208 | 3 | 42 | 420 | 150
SSC0742.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 208 | 3 | 42 | 420 | 150
SSC0743.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 208 | 3 | 42 | 420 | 150
SSC0743.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 208 | 3 | 42 | 420 | 150
SSC0743.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 208 | 3 | 42 | 420 | 150
SSC0743.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 208 | 3 | 42 | 420 | 150
SSC0744.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 208 | 3 | 42 | 420 | 150
SSC0744.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 208 | 3 | 42 | 420 | 150
SSC0744.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 208 | 3 | 42 | 420 | 150
SSC0744.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 208 | 3 | 42 | 420 | 150
SSC0745.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 240 | 3 | 100 | 450 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 240 | 3 | 42 | 420 | 150
SSC0745.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 240 | 3 | 100 | 450 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 240 | 3 | 42 | 420 | 150
SSC0745.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 240 | 3 | 100 | 450 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 240 | 3 | 42 | 420 | 150
SSC0745.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 240 | 3 | 100 | 450 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 240 | 3 | 42 | 420 | 150
SSC0746.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 240 | 3 | 42 | 420 | 150
SSC0746.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 240 | 3 | 42 | 420 | 150
SSC0746.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 240 | 3 | 42 | 420 | 150
SSC0746.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 240 | 3 | 42 | 420 | 150
SSC0747.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 240 | 3 | 42 | 420 | 150
SSC0747.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 240 | 3 | 42 | 420 | 150
SSC0747.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 240 | 3 | 42 | 420 | 150
SSC0747.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 240 | 3 | 42 | 420 | 150
SSC0748.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 240 | 3 | 42 | 420 | 150
SSC0748.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 240 | 3 | 42 | 420 | 150
SSC0748.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 240 | 3 | 42 | 420 | 150
SSC0748.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 240 | 3 | 42 | 420 | 150
SSC0749.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 240 | 3 | 42 | 420 | 150
SSC0749.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 240 | 3 | 42 | 420 | 150
SSC0749.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 240 | 3 | 42 | 420 | 150
SSC0749.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 240 | 3 | 42 | 420 | 150
SSC0750.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 480 | 3 | 42 | 420 | 350
SSC0750.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 480 | 3 | 42 | 420 | 350
SSC0750.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 480 | 3 | 42 | 420 | 350
SSC0750.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 480 | 3 | 42 | 420 | 350
SSC0751.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 480 | 3 | 42 | 420 | 350
SSC0751.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 480 | 3 | 42 | 420 | 350
SSC0751.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 480 | 3 | 42 | 420 | 350
SSC0751.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 480 | 3 | 42 | 420 | 350
SSC0752.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 480 | 3 | 42 | 420 | 350
SSC0752.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 480 | 3 | 42 | 420 | 350
SSC0752.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 480 | 3 | 42 | 420 | 350
SSC0752.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 480 | 3 | 42 | 420 | 350
SSC0753.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 480 | 3 | 42 | 420 | 350
SSC0753.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 480 | 3 | 42 | 420 | 350
SSC0753.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 480 | 3 | 42 | 420 | 350
SSC0753.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 480 | 3 | 42 | 420 | 350
SSC0754.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 480 | 3 | 42 | 420 | 350
SSC0754.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 480 | 3 | 42 | 420 | 350
SSC0754.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 480 | 3 | 42 | 420 | 350
SSC0754.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 480 | 3 | 42 | 420 | 350
SSC0755.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 480 | 3 | 42 | 420 | 350
SSC0755.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 480 | 3 | 42 | 420 | 350
SSC0755.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 480 | 3 | 42 | 420 | 350
SSC0755.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 480 | 3 | 42 | 420 | 350
SSC0756.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 600 | 3 | 42 | 420 | 450
SSC0756.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 600 | 3 | 42 | 420 | 450
SSC0756.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 600 | 3 | 42 | 420 | 450
SSC0756.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3400* | 600 | 3 | 35 | 400 | 400 | 600 | 3 | 35 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 600 | 3 | 42 | 420 | 450
SSC0757.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 600 | 3 | 35 | 500 | 500 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 600 | 3 | 42 | 420 | 450
SSC0757.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 600 | 3 | 35 | 500 | 500 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 600 | 3 | 42 | 420 | 450
SSC0757.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 600 | 3 | 35 | 500 | 500 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 600 | 3 | 42 | 420 | 450
SSC0757.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 600 | 3 | 35 | 500 | 500 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 600 | 3 | 42 | 420 | 450
SSC0758.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 600 | 3 | 42 | 420 | 450
SSC0758.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 600 | 3 | 42 | 420 | 450
SSC0758.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 600 | 3 | 42 | 420 | 450
SSC0758.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 600 | 3 | 42 | 420 | 450
SSC0759.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 600 | 3 | 42 | 420 | 450
SSC0759.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 600 | 3 | 42 | 420 | 450
SSC0759.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 600 | 3 | 42 | 420 | 450
SSC0759.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 600 | 3 | 42 | 420 | 450
SSC0760.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 600 | 3 | 42 | 420 | 450
SSC0760.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 600 | 3 | 42 | 420 | 450
SSC0760.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 600 | 3 | 42 | 420 | 450
SSC0760.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 600 | 3 | 42 | 420 | 450
SSC0761.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 600 | 3 | 42 | 420 | 450
SSC0761.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 600 | 3 | 42 | 420 | 450
SSC0761.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 600 | 3 | 42 | 420 | 450
SSC0761.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 600 | 3 | 42 | 420 | 450
SSC0762.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 600 | 3 | 42 | 420 | 450
SSC0762.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 600 | 3 | 42 | 420 | 450
SSC0762.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 600 | 3 | 42 | 420 | 450
SSC0762.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 600 | 3 | 42 | 420 | 450
SSC0763.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 200 | 3 | 100 | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 200 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S801U42N3S | 200 | 3 | 42 | 420 | 150
SSC0763.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 200 | 3 | 100 | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 200 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S801+U42N3S | 200 | 3 | 42 | 420 | 150
SSC0763.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 200 | 3 | 100 | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 200 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S811U42N3S | 200 | 3 | 42 | 420 | 150
SSC0763.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 200 | 3 | 100 | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 200 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S811+U42N3S | 200 | 3 | 42 | 420 | 150
SSC0764.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 200 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801U42N3S | 200 | 3 | 42 | 420 | 150
SSC0764.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 200 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801+U42N3S | 200 | 3 | 42 | 420 | 150
SSC0764.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 200 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811U42N3S | 200 | 3 | 42 | 420 | 150
SSC0764.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 200 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811+U42N3S | 200 | 3 | 42 | 420 | 150
SSC0765.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 200 | 3 | 100 | 1200 | 200
|  |  |  | RVSS | Eaton | S801U42N3S | 200 | 3 | 42 | 420 | 150
SSC0765.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 200 | 3 | 100 | 1200 | 200
|  |  |  | RVSS | Eaton | S801+U42N3S | 200 | 3 | 42 | 420 | 150
SSC0765.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 200 | 3 | 100 | 1200 | 200
|  |  |  | RVSS | Eaton | S811U42N3S | 200 | 3 | 42 | 420 | 150
SSC0765.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 200 | 3 | 100 | 1200 | 200
|  |  |  | RVSS | Eaton | S811+U42N3S | 200 | 3 | 42 | 420 | 150
SSC0766.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 208 | 3 | 100 | 800 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 208 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S801U42N3S | 208 | 3 | 42 | 420 | 150
SSC0766.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 208 | 3 | 100 | 800 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 208 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S801+U42N3S | 208 | 3 | 42 | 420 | 150
SSC0766.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 208 | 3 | 100 | 800 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 208 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S811U42N3S | 208 | 3 | 42 | 420 | 150
SSC0766.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 208 | 3 | 100 | 800 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 208 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S811+U42N3S | 208 | 3 | 42 | 420 | 150
SSC0767.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801U42N3S | 208 | 3 | 42 | 420 | 150
SSC0767.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801+U42N3S | 208 | 3 | 42 | 420 | 150
SSC0767.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811U42N3S | 208 | 3 | 42 | 420 | 150
SSC0767.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811+U42N3S | 208 | 3 | 42 | 420 | 150
SSC0768.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801U42N3S | 208 | 3 | 42 | 420 | 150
SSC0768.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801+U42N3S | 208 | 3 | 42 | 420 | 150
SSC0768.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811U42N3S | 208 | 3 | 42 | 420 | 150
SSC0768.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811+U42N3S | 208 | 3 | 42 | 420 | 150
SSC0769.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 240 | 3 | 100 | 700 | 250
|  |  |  | RVSS | Eaton | S801U42N3S | 240 | 3 | 42 | 420 | 150
SSC0769.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 240 | 3 | 100 | 700 | 250
|  |  |  | RVSS | Eaton | S801+U42N3S | 240 | 3 | 42 | 420 | 150
SSC0769.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 240 | 3 | 100 | 700 | 250
|  |  |  | RVSS | Eaton | S811U42N3S | 240 | 3 | 42 | 420 | 150
SSC0769.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 240 | 3 | 100 | 700 | 250
|  |  |  | RVSS | Eaton | S811+U42N3S | 240 | 3 | 42 | 420 | 150
SSC0770.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 240 | 3 | 100 | 800 | 300
|  |  |  | RVSS | Eaton | S801U42N3S | 240 | 3 | 42 | 420 | 150
SSC0770.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 240 | 3 | 100 | 800 | 300
|  |  |  | RVSS | Eaton | S801+U42N3S | 240 | 3 | 42 | 420 | 150
SSC0770.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 240 | 3 | 100 | 800 | 300
|  |  |  | RVSS | Eaton | S811U42N3S | 240 | 3 | 42 | 420 | 150
SSC0770.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 240 | 3 | 100 | 800 | 300
|  |  |  | RVSS | Eaton | S811+U42N3S | 240 | 3 | 42 | 420 | 150
SSC0771.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 240 | 3 | 100 | 1000 | 400
|  |  |  | RVSS | Eaton | S801U42N3S | 240 | 3 | 42 | 420 | 150
SSC0771.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 240 | 3 | 100 | 1000 | 400
|  |  |  | RVSS | Eaton | S801+U42N3S | 240 | 3 | 42 | 420 | 150
SSC0771.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 240 | 3 | 100 | 1000 | 400
|  |  |  | RVSS | Eaton | S811U42N3S | 240 | 3 | 42 | 420 | 150
SSC0771.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 240 | 3 | 100 | 1000 | 400
|  |  |  | RVSS | Eaton | S811+U42N3S | 240 | 3 | 42 | 420 | 150
SSC0772.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 480 | 3 | 65 | 700 | 500
|  |  |  | RVSS | Eaton | S801U42N3S | 480 | 3 | 42 | 420 | 350
SSC0772.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 480 | 3 | 65 | 700 | 500
|  |  |  | RVSS | Eaton | S801+U42N3S | 480 | 3 | 42 | 420 | 350
SSC0772.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 480 | 3 | 65 | 700 | 500
|  |  |  | RVSS | Eaton | S811U42N3S | 480 | 3 | 42 | 420 | 350
SSC0772.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 480 | 3 | 65 | 700 | 500
|  |  |  | RVSS | Eaton | S811+U42N3S | 480 | 3 | 42 | 420 | 350
SSC0773.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S801U42N3S | 480 | 3 | 42 | 420 | 350
SSC0773.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S801+U42N3S | 480 | 3 | 42 | 420 | 350
SSC0773.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S811U42N3S | 480 | 3 | 42 | 420 | 350
SSC0773.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S811+U42N3S | 480 | 3 | 42 | 420 | 350
SSC0774.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S801U42N3S | 480 | 3 | 42 | 420 | 350
SSC0774.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S801+U42N3S | 480 | 3 | 42 | 420 | 350
SSC0774.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S811U42N3S | 480 | 3 | 42 | 420 | 350
SSC0774.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S811+U42N3S | 480 | 3 | 42 | 420 | 350
SSC0775.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801U42N3S | 480 | 3 | 42 | 420 | 350
SSC0775.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+U42N3S | 480 | 3 | 42 | 420 | 350
SSC0775.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811U42N3S | 480 | 3 | 42 | 420 | 350
SSC0775.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+U42N3S | 480 | 3 | 42 | 420 | 350
SSC0776.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 600 | 3 | 35 | 700 | 500
|  |  |  | RVSS | Eaton | S801U42N3S | 600 | 3 | 42 | 420 | 350
SSC0776.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 600 | 3 | 35 | 700 | 500
|  |  |  | RVSS | Eaton | S801+U42N3S | 600 | 3 | 42 | 420 | 350
SSC0776.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 600 | 3 | 35 | 700 | 500
|  |  |  | RVSS | Eaton | S811U42N3S | 600 | 3 | 42 | 420 | 350
SSC0776.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 600 | 3 | 35 | 700 | 500
|  |  |  | RVSS | Eaton | S811+U42N3S | 600 | 3 | 42 | 420 | 350
SSC0777.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 600 | 3 | 35 | 800 | 500
|  |  |  | RVSS | Eaton | S801U42N3S | 600 | 3 | 42 | 420 | 350
SSC0777.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 600 | 3 | 35 | 800 | 500
|  |  |  | RVSS | Eaton | S801+U42N3S | 600 | 3 | 42 | 420 | 350
SSC0777.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 600 | 3 | 35 | 800 | 500
|  |  |  | RVSS | Eaton | S811U42N3S | 600 | 3 | 42 | 420 | 350
SSC0777.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 600 | 3 | 35 | 800 | 500
|  |  |  | RVSS | Eaton | S811+U42N3S | 600 | 3 | 42 | 420 | 350
SSC0778.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S801U42N3S | 600 | 3 | 42 | 420 | 350
SSC0778.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S801+U42N3S | 600 | 3 | 42 | 420 | 350
SSC0778.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S811U42N3S | 600 | 3 | 42 | 420 | 350
SSC0778.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S811+U42N3S | 600 | 3 | 42 | 420 | 350
SSC0779.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S801U42N3S | 600 | 3 | 42 | 420 | 350
SSC0779.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S801+U42N3S | 600 | 3 | 42 | 420 | 350
SSC0779.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S811U42N3S | 600 | 3 | 42 | 420 | 350
SSC0779.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S811+U42N3S | 600 | 3 | 42 | 420 | 350
SSC0780.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S801U42N3S | 600 | 3 | 42 | 420 | 350
SSC0780.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+U42N3S | 600 | 3 | 42 | 420 | 350
SSC0780.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S811U42N3S | 600 | 3 | 42 | 420 | 350
SSC0780.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+U42N3S | 600 | 3 | 42 | 420 | 350
SSC0781.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 150 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 200 | 3 | 42 | 500 | 150
SSC0781.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 150 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 200 | 3 | 42 | 500 | 150
SSC0781.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 150 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 200 | 3 | 42 | 500 | 150
SSC0781.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 200 | 3 | 100 | 500 | 150 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 200 | 3 | 42 | 500 | 150
SSC0782.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 200 | 3 | 42 | 500 | 150
SSC0782.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 200 | 3 | 42 | 500 | 150
SSC0782.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 200 | 3 | 42 | 500 | 150
SSC0782.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 200 | 3 | 42 | 500 | 150
SSC0783.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 200 | 3 | 42 | 500 | 150
SSC0783.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 200 | 3 | 42 | 500 | 150
SSC0783.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 200 | 3 | 42 | 500 | 150
SSC0783.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 200 | 3 | 42 | 500 | 150
SSC0784.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 200 | 3 | 42 | 500 | 150
SSC0784.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 200 | 3 | 42 | 500 | 150
SSC0784.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 200 | 3 | 42 | 500 | 150
SSC0784.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 200 | 3 | 42 | 500 | 150
SSC0785.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 200 | 3 | 42 | 500 | 150
SSC0785.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 200 | 3 | 42 | 500 | 150
SSC0785.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 200 | 3 | 42 | 500 | 150
SSC0785.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 200 | 3 | 100 | 600 | 200 | 200 | 3 | 100 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 200 | 3 | 42 | 500 | 150
SSC0786.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 208 | 3 | 42 | 500 | 150
SSC0786.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 208 | 3 | 42 | 500 | 150
SSC0786.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 208 | 3 | 42 | 500 | 150
SSC0786.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 208 | 3 | 100 | 500 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 208 | 3 | 42 | 500 | 150
SSC0787.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 208 | 3 | 42 | 500 | 150
SSC0787.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 208 | 3 | 42 | 500 | 150
SSC0787.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 208 | 3 | 42 | 500 | 150
SSC0787.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 208 | 3 | 42 | 500 | 150
SSC0788.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 208 | 3 | 42 | 500 | 150
SSC0788.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 208 | 3 | 42 | 500 | 150
SSC0788.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 208 | 3 | 42 | 500 | 150
SSC0788.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 208 | 3 | 42 | 500 | 150
SSC0789.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 208 | 3 | 42 | 500 | 150
SSC0789.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 208 | 3 | 42 | 500 | 150
SSC0789.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 208 | 3 | 42 | 500 | 150
SSC0789.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 208 | 3 | 42 | 500 | 150
SSC0790.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 208 | 3 | 42 | 500 | 150
SSC0790.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 208 | 3 | 42 | 500 | 150
SSC0790.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 208 | 3 | 42 | 500 | 150
SSC0790.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 208 | 3 | 100 | 600 | 200 | 208 | 3 | 100 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 208 | 3 | 42 | 500 | 150
SSC0791.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 240 | 3 | 42 | 500 | 150
SSC0791.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 240 | 3 | 42 | 500 | 150
SSC0791.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 240 | 3 | 42 | 500 | 150
SSC0791.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 240 | 3 | 100 | 500 | 200 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 240 | 3 | 42 | 500 | 150
SSC0792.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 240 | 3 | 42 | 500 | 150
SSC0792.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 240 | 3 | 42 | 500 | 150
SSC0792.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 240 | 3 | 42 | 500 | 150
SSC0792.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 240 | 3 | 42 | 500 | 150
SSC0793.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 240 | 3 | 42 | 500 | 150
SSC0793.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 240 | 3 | 42 | 500 | 150
SSC0793.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 240 | 3 | 42 | 500 | 150
SSC0793.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 240 | 3 | 42 | 500 | 150
SSC0794.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 240 | 3 | 42 | 500 | 150
SSC0794.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 240 | 3 | 42 | 500 | 150
SSC0794.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 240 | 3 | 42 | 500 | 150
SSC0794.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 240 | 3 | 42 | 500 | 150
SSC0795.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 240 | 3 | 42 | 500 | 150
SSC0795.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 240 | 3 | 42 | 500 | 150
SSC0795.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 240 | 3 | 42 | 500 | 150
SSC0795.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 240 | 3 | 100 | 600 | 200 | 240 | 3 | 100 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 240 | 3 | 42 | 500 | 150
SSC0796.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 480 | 3 | 42 | 500 | 400
SSC0796.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 480 | 3 | 42 | 500 | 400
SSC0796.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 480 | 3 | 42 | 500 | 400
SSC0796.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3450* | 480 | 3 | 65 | 450 | 350 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 480 | 3 | 42 | 500 | 400
SSC0797.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 480 | 3 | 42 | 500 | 400
SSC0797.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 480 | 3 | 42 | 500 | 400
SSC0797.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 480 | 3 | 42 | 500 | 400
SSC0797.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 480 | 3 | 65 | 500 | 400 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 480 | 3 | 42 | 500 | 400
SSC0798.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 480 | 3 | 42 | 500 | 400
SSC0798.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 480 | 3 | 42 | 500 | 400
SSC0798.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 480 | 3 | 42 | 500 | 400
SSC0798.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 480 | 3 | 42 | 500 | 400
SSC0799.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 480 | 3 | 42 | 500 | 400
SSC0799.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 480 | 3 | 42 | 500 | 400
SSC0799.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 480 | 3 | 42 | 500 | 400
SSC0799.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 480 | 3 | 42 | 500 | 400
SSC0800.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 480 | 3 | 42 | 500 | 400
SSC0800.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 480 | 3 | 42 | 500 | 400
SSC0800.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 480 | 3 | 42 | 500 | 400
SSC0800.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 480 | 3 | 42 | 500 | 400
SSC0801.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 480 | 3 | 42 | 500 | 400
SSC0801.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 480 | 3 | 42 | 500 | 400
SSC0801.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 480 | 3 | 42 | 500 | 400
SSC0801.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 480 | 3 | 42 | 500 | 400
SSC0802.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 480 | 3 | 42 | 500 | 400
SSC0802.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 480 | 3 | 42 | 500 | 400
SSC0802.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 480 | 3 | 42 | 500 | 400
SSC0802.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 480 | 3 | 65 | 600 | 500 | 480 | 3 | 65 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 480 | 3 | 42 | 500 | 400
SSC0803.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 600 | 3 | 35 | 500 | 500 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 600 | 3 | 42 | 500 | 500
SSC0803.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 600 | 3 | 35 | 500 | 500 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 600 | 3 | 42 | 500 | 500
SSC0803.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 600 | 3 | 35 | 500 | 500 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 600 | 3 | 42 | 500 | 500
SSC0803.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3500* | 600 | 3 | 35 | 500 | 500 | 600 | 3 | 35 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 600 | 3 | 42 | 500 | 500
SSC0804.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 600 | 3 | 42 | 500 | 500
SSC0804.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 600 | 3 | 42 | 500 | 500
SSC0804.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 600 | 3 | 42 | 500 | 500
SSC0804.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 600 | 3 | 42 | 500 | 500
SSC0805.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 600 | 3 | 42 | 500 | 500
SSC0805.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 600 | 3 | 42 | 500 | 500
SSC0805.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 600 | 3 | 42 | 500 | 500
SSC0805.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 600 | 3 | 42 | 500 | 500
SSC0806.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 600 | 3 | 42 | 500 | 500
SSC0806.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 600 | 3 | 42 | 500 | 500
SSC0806.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 600 | 3 | 42 | 500 | 500
SSC0806.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 600 | 3 | 42 | 500 | 500
SSC0807.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 600 | 3 | 42 | 500 | 500
SSC0807.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 600 | 3 | 42 | 500 | 500
SSC0807.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 600 | 3 | 42 | 500 | 500
SSC0807.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 600 | 3 | 42 | 500 | 500
SSC0808.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 600 | 3 | 42 | 500 | 500
SSC0808.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 600 | 3 | 42 | 500 | 500
SSC0808.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 600 | 3 | 42 | 500 | 500
SSC0808.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 600 | 3 | 42 | 500 | 500
SSC0809.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 600 | 3 | 42 | 500 | 500
SSC0809.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 600 | 3 | 42 | 500 | 500
SSC0809.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 600 | 3 | 42 | 500 | 500
SSC0809.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HLD3600* | 600 | 3 | 35 | 600 | 500 | 600 | 3 | 35 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 600 | 3 | 42 | 500 | 500
SSC0810.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 200 | 3 | 100 | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 200 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S801U50N3S | 200 | 3 | 42 | 500 | 150
SSC0810.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 200 | 3 | 100 | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 200 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S801+U50N3S | 200 | 3 | 42 | 500 | 150
SSC0810.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 200 | 3 | 100 | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 200 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S811U50N3S | 200 | 3 | 42 | 500 | 150
SSC0810.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 200 | 3 | 100 | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 200 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S811+U50N3S | 200 | 3 | 42 | 500 | 150
SSC0811.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 200 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801U50N3S | 200 | 3 | 42 | 500 | 150
SSC0811.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 200 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801+U50N3S | 200 | 3 | 42 | 500 | 150
SSC0811.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 200 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811U50N3S | 200 | 3 | 42 | 500 | 150
SSC0811.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 200 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811+U50N3S | 200 | 3 | 42 | 500 | 150
SSC0812.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 200 | 3 | 100 | 1200 | 200
|  |  |  | RVSS | Eaton | S801U50N3S | 200 | 3 | 42 | 500 | 150
SSC0812.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 200 | 3 | 100 | 1200 | 200
|  |  |  | RVSS | Eaton | S801+U50N3S | 200 | 3 | 42 | 500 | 150
SSC0812.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 200 | 3 | 100 | 1200 | 200
|  |  |  | RVSS | Eaton | S811U50N3S | 200 | 3 | 42 | 500 | 150
SSC0812.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 200 | 3 | 100 | 1200 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 200 | 3 | 100 | 1200 | 200
|  |  |  | RVSS | Eaton | S811+U50N3S | 200 | 3 | 42 | 500 | 150
SSC0813.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 208 | 3 | 100 | 800 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 208 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S801U50N3S | 208 | 3 | 42 | 500 | 150
SSC0813.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 208 | 3 | 100 | 800 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 208 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S801+U50N3S | 208 | 3 | 42 | 500 | 150
SSC0813.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 208 | 3 | 100 | 800 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 208 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S811U50N3S | 208 | 3 | 42 | 500 | 150
SSC0813.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 208 | 3 | 100 | 800 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 208 | 3 | 100 | 800 | 200
|  |  |  | RVSS | Eaton | S811+U50N3S | 208 | 3 | 42 | 500 | 150
SSC0814.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801U50N3S | 208 | 3 | 42 | 500 | 150
SSC0814.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801+U50N3S | 208 | 3 | 42 | 500 | 150
SSC0814.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811U50N3S | 208 | 3 | 42 | 500 | 150
SSC0814.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811+U50N3S | 208 | 3 | 42 | 500 | 150
SSC0815.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801U50N3S | 208 | 3 | 42 | 500 | 150
SSC0815.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S801+U50N3S | 208 | 3 | 42 | 500 | 150
SSC0815.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811U50N3S | 208 | 3 | 42 | 500 | 150
SSC0815.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 208 | 3 | 100 | 1200 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 208 | 3 | 100 | 1000 | 200
|  |  |  | RVSS | Eaton | S811+U50N3S | 208 | 3 | 42 | 500 | 150
SSC0816.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 240 | 3 | 100 | 700 | 250
|  |  |  | RVSS | Eaton | S801U50N3S | 240 | 3 | 42 | 500 | 200
SSC0816.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 240 | 3 | 100 | 700 | 250
|  |  |  | RVSS | Eaton | S801+U50N3S | 240 | 3 | 42 | 500 | 200
SSC0816.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 240 | 3 | 100 | 700 | 250
|  |  |  | RVSS | Eaton | S811U50N3S | 240 | 3 | 42 | 500 | 200
SSC0816.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 240 | 3 | 100 | 700 | 250
|  |  |  | RVSS | Eaton | S811+U50N3S | 240 | 3 | 42 | 500 | 200
SSC0817.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 240 | 3 | 100 | 800 | 300
|  |  |  | RVSS | Eaton | S801U50N3S | 240 | 3 | 42 | 500 | 200
SSC0817.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 240 | 3 | 100 | 800 | 300
|  |  |  | RVSS | Eaton | S801+U50N3S | 240 | 3 | 42 | 500 | 200
SSC0817.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 240 | 3 | 100 | 800 | 300
|  |  |  | RVSS | Eaton | S811U50N3S | 240 | 3 | 42 | 500 | 200
SSC0817.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 240 | 3 | 100 | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 240 | 3 | 100 | 800 | 300
|  |  |  | RVSS | Eaton | S811+U50N3S | 240 | 3 | 42 | 500 | 200
SSC0818.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 240 | 3 | 100 | 1000 | 500
|  |  |  | RVSS | Eaton | S801U50N3S | 240 | 3 | 42 | 500 | 200
SSC0818.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 240 | 3 | 100 | 1000 | 500
|  |  |  | RVSS | Eaton | S801+U50N3S | 240 | 3 | 42 | 500 | 200
SSC0818.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 240 | 3 | 100 | 1000 | 500
|  |  |  | RVSS | Eaton | S811U50N3S | 240 | 3 | 42 | 500 | 200
SSC0818.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 240 | 3 | 100 | 1000 | 500
|  |  |  | RVSS | Eaton | S811+U50N3S | 240 | 3 | 42 | 500 | 200
SSC0819.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 240 | 3 | 100 | 1200 | 500
|  |  |  | RVSS | Eaton | S801U50N3S | 240 | 3 | 42 | 500 | 200
SSC0819.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 240 | 3 | 100 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+U50N3S | 240 | 3 | 42 | 500 | 200
SSC0819.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 240 | 3 | 100 | 1200 | 500
|  |  |  | RVSS | Eaton | S811U50N3S | 240 | 3 | 42 | 500 | 200
SSC0819.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 240 | 3 | 100 | 1200 | 500 | 240 | 3 | 65 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 240 | 3 | 100 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+U50N3S | 240 | 3 | 42 | 500 | 200
SSC0820.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 480 | 3 | 65 | 700 | 500
|  |  |  | RVSS | Eaton | S801U50N3S | 480 | 3 | 42 | 500 | 400
SSC0820.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 480 | 3 | 65 | 700 | 500
|  |  |  | RVSS | Eaton | S801+U50N3S | 480 | 3 | 42 | 500 | 400
SSC0820.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 480 | 3 | 65 | 700 | 500
|  |  |  | RVSS | Eaton | S811U50N3S | 480 | 3 | 42 | 500 | 400
SSC0820.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 480 | 3 | 65 | 700 | 500
|  |  |  | RVSS | Eaton | S811+U50N3S | 480 | 3 | 42 | 500 | 400
SSC0821.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S801U50N3S | 480 | 3 | 42 | 500 | 400
SSC0821.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S801+U50N3S | 480 | 3 | 42 | 500 | 400
SSC0821.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S811U50N3S | 480 | 3 | 42 | 500 | 400
SSC0821.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 480 | 3 | 65 | 800 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 480 | 3 | 65 | 800 | 500
|  |  |  | RVSS | Eaton | S811+U50N3S | 480 | 3 | 42 | 500 | 400
SSC0822.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S801U50N3S | 480 | 3 | 42 | 500 | 400
SSC0822.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S801+U50N3S | 480 | 3 | 42 | 500 | 400
SSC0822.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S811U50N3S | 480 | 3 | 42 | 500 | 400
SSC0822.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 480 | 3 | 65 | 1000 | 500
|  |  |  | RVSS | Eaton | S811+U50N3S | 480 | 3 | 42 | 500 | 400
SSC0823.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801U50N3S | 480 | 3 | 42 | 500 | 400
SSC0823.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+U50N3S | 480 | 3 | 42 | 500 | 400
SSC0823.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811U50N3S | 480 | 3 | 42 | 500 | 400
SSC0823.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+U50N3S | 480 | 3 | 42 | 500 | 400
SSC0824.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801U50N3S | 480 | 3 | 42 | 500 | 400
SSC0824.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+U50N3S | 480 | 3 | 42 | 500 | 400
SSC0824.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811U50N3S | 480 | 3 | 42 | 500 | 400
SSC0824.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 480 | 3 | 65 | 1200 | 500 | 480 | 3 | 65 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 480 | 3 | 65 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+U50N3S | 480 | 3 | 42 | 500 | 400
SSC0825.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 600 | 3 | 35 | 700 | 500
|  |  |  | RVSS | Eaton | S801U50N3S | 600 | 3 | 42 | 500 | 500
SSC0825.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 600 | 3 | 35 | 700 | 500
|  |  |  | RVSS | Eaton | S801+U50N3S | 600 | 3 | 42 | 500 | 500
SSC0825.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 600 | 3 | 35 | 700 | 500
|  |  |  | RVSS | Eaton | S811U50N3S | 600 | 3 | 42 | 500 | 500
SSC0825.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A700 | 600 | 3 | 35 | 700 | 500
|  |  |  | RVSS | Eaton | S811+U50N3S | 600 | 3 | 42 | 500 | 500
SSC0826.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 600 | 3 | 35 | 800 | 500
|  |  |  | RVSS | Eaton | S801U50N3S | 600 | 3 | 42 | 500 | 500
SSC0826.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 600 | 3 | 35 | 800 | 500
|  |  |  | RVSS | Eaton | S801+U50N3S | 600 | 3 | 42 | 500 | 500
SSC0826.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 600 | 3 | 35 | 800 | 500
|  |  |  | RVSS | Eaton | S811U50N3S | 600 | 3 | 42 | 500 | 500
SSC0826.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND3800T*** | 600 | 3 | 35 | 800 | 500 | 600 | 3 | 35 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN80A800 | 600 | 3 | 35 | 800 | 500
|  |  |  | RVSS | Eaton | S811+U50N3S | 600 | 3 | 42 | 500 | 500
SSC0827.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S801U50N3S | 600 | 3 | 42 | 500 | 500
SSC0827.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S801+U50N3S | 600 | 3 | 42 | 500 | 500
SSC0827.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S811U50N3S | 600 | 3 | 42 | 500 | 500
SSC0827.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S811+U50N3S | 600 | 3 | 42 | 500 | 500
SSC0828.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S801U50N3S | 600 | 3 | 42 | 500 | 500
SSC0828.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S801+U50N3S | 600 | 3 | 42 | 500 | 500
SSC0828.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S811U50N3S | 600 | 3 | 42 | 500 | 500
SSC0828.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A100 | 600 | 3 | 35 | 1000 | 500
|  |  |  | RVSS | Eaton | S811+U50N3S | 600 | 3 | 42 | 500 | 500
SSC0829.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S801U50N3S | 600 | 3 | 42 | 500 | 500
SSC0829.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+U50N3S | 600 | 3 | 42 | 500 | 500
SSC0829.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S811U50N3S | 600 | 3 | 42 | 500 | 500
SSC0829.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+U50N3S | 600 | 3 | 42 | 500 | 500
SSC0830.01 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S801U50N3S | 600 | 3 | 42 | 500 | 500
SSC0830.02 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S801+U50N3S | 600 | 3 | 42 | 500 | 500
SSC0830.03 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S811U50N3S | 600 | 3 | 42 | 500 | 500
SSC0830.04 | E176513 | Vol. 1, Sec. 4 | C | CB | Eaton | HND312T*** | 600 | 3 | 35 | 1200 | 500 | 600 | 3 | 35 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | TU | Eaton | ORPN12A120 | 600 | 3 | 35 | 1200 | 500
|  |  |  | RVSS | Eaton | S811+U50N3S | 600 | 3 | 42 | 500 | 500
Conditions of Aceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.

## S801 Softstarter Type D
Issue Date: 2006-05-18
Revised: 2016-10-27
Database Identification Number | Listed Combination Motor Controller Information |  | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings
| UL File Number | Volume / Section (Vol#).(Sec#) |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating | Enclosure Volume, cubic inches | Conditions of Use | Other References
SSC0001.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP015E0* | 200 | 3 | - | 15 | 3 | 200 | 3 | 50 | 11 | 3 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 200 | 3 | 10 | 37 | 10
SSC0001.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP015E0* | 200 | 3 | - | 15 | 3 | 200 | 3 | 50 | 11 | 3 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0001.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP015E0* | 200 | 3 | - | 15 | 3 | 200 | 3 | 50 | 11 | 3 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 200 | 3 | 10 | 37 | 10
SSC0001.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP015E0* | 200 | 3 | - | 15 | 3 | 200 | 3 | 50 | 11 | 3 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0002.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 200 | 3 | - | 30 | 7.5 | 200 | 3 | 50 | 11 | 3 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 200 | 3 | 10 | 37 | 10
SSC0002.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 200 | 3 | - | 30 | 7.5 | 200 | 3 | 50 | 11 | 3 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0002.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 200 | 3 | - | 30 | 7.5 | 200 | 3 | 50 | 11 | 3 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 200 | 3 | 10 | 37 | 10
SSC0002.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 200 | 3 | - | 30 | 7.5 | 200 | 3 | 50 | 11 | 3 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0003.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 200 | 3 | - | 30 | 7.5 | 200 | 3 | 50 | 17.5 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 200 | 3 | 10 | 37 | 10
SSC0003.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 200 | 3 | - | 30 | 7.5 | 200 | 3 | 50 | 17.5 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0003.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 200 | 3 | - | 30 | 7.5 | 200 | 3 | 50 | 17.5 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 200 | 3 | 10 | 37 | 10
SSC0003.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 200 | 3 | - | 30 | 7.5 | 200 | 3 | 50 | 17.5 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0004.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 50 | 17.5 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 200 | 3 | 10 | 37 | 10
SSC0004.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 50 | 17.5 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0004.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 50 | 17.5 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 200 | 3 | 10 | 37 | 10
SSC0004.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 50 | 17.5 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0005.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 50 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 200 | 3 | 10 | 37 | 10
SSC0005.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 50 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0005.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 50 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 200 | 3 | 10 | 37 | 10
SSC0005.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 50 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0006.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 50 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 200 | 3 | 10 | 37 | 10
SSC0006.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 50 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0006.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 50 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 200 | 3 | 10 | 37 | 10
SSC0006.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 50 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0007.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 50 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 200 | 3 | 10 | 37 | 10
SSC0007.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 50 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0007.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 50 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 200 | 3 | 10 | 37 | 10
SSC0007.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 50 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0008.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 50 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 200 | 3 | 10 | 37 | 10
SSC0008.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 50 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0008.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 50 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 200 | 3 | 10 | 37 | 10
SSC0008.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 50 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0009.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 208 | 3 | - | 30 | 7.5 | 208 | 3 | 50 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 208 | 3 | 10 | 37 | 10
SSC0009.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 208 | 3 | - | 30 | 7.5 | 208 | 3 | 50 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0009.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 208 | 3 | - | 30 | 7.5 | 208 | 3 | 50 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 208 | 3 | 10 | 37 | 10
SSC0009.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 208 | 3 | - | 30 | 7.5 | 208 | 3 | 50 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0010.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 208 | 3 | - | 50 | 15 | 208 | 3 | 50 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 208 | 3 | 10 | 37 | 10
SSC0010.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 208 | 3 | - | 50 | 15 | 208 | 3 | 50 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0010.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 208 | 3 | - | 50 | 15 | 208 | 3 | 50 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 208 | 3 | 10 | 37 | 10
SSC0010.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 208 | 3 | - | 50 | 15 | 208 | 3 | 50 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0011.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 208 | 3 | - | 50 | 15 | 208 | 3 | 50 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 208 | 3 | 10 | 37 | 10
SSC0011.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 208 | 3 | - | 50 | 15 | 208 | 3 | 50 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0011.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 208 | 3 | - | 50 | 15 | 208 | 3 | 50 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 208 | 3 | 10 | 37 | 10
SSC0011.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 208 | 3 | - | 50 | 15 | 208 | 3 | 50 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0012.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 50 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 208 | 3 | 10 | 37 | 10
SSC0012.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 50 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0012.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 50 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 208 | 3 | 10 | 37 | 10
SSC0012.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 50 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0013.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 208 | 3 | - | 50 | 15 | 208 | 3 | 50 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 208 | 3 | 10 | 37 | 10
SSC0013.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 208 | 3 | - | 50 | 15 | 208 | 3 | 50 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0013.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 208 | 3 | - | 50 | 15 | 208 | 3 | 50 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 208 | 3 | 10 | 37 | 10
SSC0013.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 208 | 3 | - | 50 | 15 | 208 | 3 | 50 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0014.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 50 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 208 | 3 | 10 | 37 | 10
SSC0014.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 50 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0014.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 50 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 208 | 3 | 10 | 37 | 10
SSC0014.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 50 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0015.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 240 | 3 | - | 30 | 10 | 240 | 3 | 50 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 240 | 3 | 10 | 37 | 10
SSC0015.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 240 | 3 | - | 30 | 10 | 240 | 3 | 50 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0015.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 240 | 3 | - | 30 | 10 | 240 | 3 | 50 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 240 | 3 | 10 | 37 | 10
SSC0015.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 240 | 3 | - | 30 | 10 | 240 | 3 | 50 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0016.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 240 | 3 | - | 50 | 15 | 240 | 3 | 50 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 240 | 3 | 10 | 37 | 10
SSC0016.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 240 | 3 | - | 50 | 15 | 240 | 3 | 50 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0016.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 240 | 3 | - | 50 | 15 | 240 | 3 | 50 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 240 | 3 | 10 | 37 | 10
SSC0016.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 240 | 3 | - | 50 | 15 | 240 | 3 | 50 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0017.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 240 | 3 | - | 50 | 15 | 240 | 3 | 50 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 240 | 3 | 10 | 37 | 10
SSC0017.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 240 | 3 | - | 50 | 15 | 240 | 3 | 50 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0017.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 240 | 3 | - | 50 | 15 | 240 | 3 | 50 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 240 | 3 | 10 | 37 | 10
SSC0017.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 240 | 3 | - | 50 | 15 | 240 | 3 | 50 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0018.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 50 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 240 | 3 | 10 | 37 | 10
SSC0018.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 50 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0018.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 50 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 240 | 3 | 10 | 37 | 10
SSC0018.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 50 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0019.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 240 | 3 | - | 50 | 15 | 240 | 3 | 50 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 240 | 3 | 10 | 37 | 10
SSC0019.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 240 | 3 | - | 50 | 15 | 240 | 3 | 50 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0019.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 240 | 3 | - | 50 | 15 | 240 | 3 | 50 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 240 | 3 | 10 | 37 | 10
SSC0019.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 240 | 3 | - | 50 | 15 | 240 | 3 | 50 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0020.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 50 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 240 | 3 | 10 | 37 | 10
SSC0020.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 50 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0020.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 50 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 240 | 3 | 10 | 37 | 10
SSC0020.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 50 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0021.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP015E0* | 480 | 3 | - | 15 | 10 | 480 | 3 | 50 | 11 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 480 | 3 | 10 | 37 | 25
SSC0021.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP015E0* | 480 | 3 | - | 15 | 10 | 480 | 3 | 50 | 11 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0021.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP015E0* | 480 | 3 | - | 15 | 10 | 480 | 3 | 50 | 11 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 480 | 3 | 10 | 37 | 25
SSC0021.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP015E0* | 480 | 3 | - | 15 | 10 | 480 | 3 | 50 | 11 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0022.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 480 | 3 | - | 30 | 20 | 480 | 3 | 50 | 11 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 480 | 3 | 10 | 37 | 25
SSC0022.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 480 | 3 | - | 30 | 20 | 480 | 3 | 50 | 11 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0022.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 480 | 3 | - | 30 | 20 | 480 | 3 | 50 | 11 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 480 | 3 | 10 | 37 | 25
SSC0022.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 480 | 3 | - | 30 | 20 | 480 | 3 | 50 | 11 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0023.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 480 | 3 | - | 30 | 20 | 480 | 3 | 50 | 14 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 480 | 3 | 10 | 37 | 25
SSC0023.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 480 | 3 | - | 30 | 20 | 480 | 3 | 50 | 14 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0023.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 480 | 3 | - | 30 | 20 | 480 | 3 | 50 | 14 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 480 | 3 | 10 | 37 | 25
SSC0023.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 480 | 3 | - | 30 | 20 | 480 | 3 | 50 | 14 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0024.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 50 | 14 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 480 | 3 | 10 | 37 | 25
SSC0024.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 50 | 14 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0024.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 50 | 14 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 480 | 3 | 10 | 37 | 25
SSC0024.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 50 | 14 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0025.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 480 | 3 | - | 30 | 20 | 480 | 3 | 50 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 480 | 3 | 10 | 37 | 25
SSC0025.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 480 | 3 | - | 30 | 20 | 480 | 3 | 50 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0025.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 480 | 3 | - | 30 | 20 | 480 | 3 | 50 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 480 | 3 | 10 | 37 | 25
SSC0025.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 480 | 3 | - | 30 | 20 | 480 | 3 | 50 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0026.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 50 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 480 | 3 | 10 | 37 | 25
SSC0026.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 50 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0026.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 50 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 480 | 3 | 10 | 37 | 25
SSC0026.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 50 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0027.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 50 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 480 | 3 | 10 | 37 | 25
SSC0027.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 50 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0027.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 50 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 480 | 3 | 10 | 37 | 25
SSC0027.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 50 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0028.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 50 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 480 | 3 | 10 | 37 | 25
SSC0028.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 50 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0028.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 50 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 480 | 3 | 10 | 37 | 25
SSC0028.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 50 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0029.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 50 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 480 | 3 | 10 | 37 | 25
SSC0029.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 50 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0029.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 50 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 480 | 3 | 10 | 37 | 25
SSC0029.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 50 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0030.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 50 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 480 | 3 | 10 | 37 | 25
SSC0030.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 50 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0030.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 50 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 480 | 3 | 10 | 37 | 25
SSC0030.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 50 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0031.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP015E0* | 600 | 3 | - | 15 | 10 | 600 | 3 | 50 | 11 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 600 | 3 | 10 | 37 | 30
SSC0031.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP015E0* | 600 | 3 | - | 15 | 10 | 600 | 3 | 50 | 11 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0031.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP015E0* | 600 | 3 | - | 15 | 10 | 600 | 3 | 50 | 11 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 600 | 3 | 10 | 37 | 30
SSC0031.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP015E0* | 600 | 3 | - | 15 | 10 | 600 | 3 | 50 | 11 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0032.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 600 | 3 | - | 30 | 25 | 600 | 3 | 50 | 11 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 600 | 3 | 10 | 37 | 30
SSC0032.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 600 | 3 | - | 30 | 25 | 600 | 3 | 50 | 11 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0032.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 600 | 3 | - | 30 | 25 | 600 | 3 | 50 | 11 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 600 | 3 | 10 | 37 | 30
SSC0032.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 600 | 3 | - | 30 | 25 | 600 | 3 | 50 | 11 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0033.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 600 | 3 | - | 30 | 25 | 600 | 3 | 50 | 17 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 600 | 3 | 10 | 37 | 30
SSC0033.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 600 | 3 | - | 30 | 25 | 600 | 3 | 50 | 17 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0033.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 600 | 3 | - | 30 | 25 | 600 | 3 | 50 | 17 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 600 | 3 | 10 | 37 | 30
SSC0033.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 600 | 3 | - | 30 | 25 | 600 | 3 | 50 | 17 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0034.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 600 | 3 | - | 50 | 40 | 600 | 3 | 50 | 17 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 600 | 3 | 10 | 37 | 30
SSC0034.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 600 | 3 | - | 50 | 40 | 600 | 3 | 50 | 17 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0034.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 600 | 3 | - | 50 | 40 | 600 | 3 | 50 | 17 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 600 | 3 | 10 | 37 | 30
SSC0034.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 600 | 3 | - | 50 | 40 | 600 | 3 | 50 | 17 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0035.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 600 | 3 | - | 30 | 25 | 600 | 3 | 50 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 600 | 3 | 10 | 37 | 30
SSC0035.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 600 | 3 | - | 30 | 25 | 600 | 3 | 50 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0035.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 600 | 3 | - | 30 | 25 | 600 | 3 | 50 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 600 | 3 | 10 | 37 | 30
SSC0035.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP030H1* | 600 | 3 | - | 30 | 25 | 600 | 3 | 50 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0036.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 600 | 3 | - | 50 | 40 | 600 | 3 | 50 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 600 | 3 | 10 | 37 | 30
SSC0036.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 600 | 3 | - | 50 | 40 | 600 | 3 | 50 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0036.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 600 | 3 | - | 50 | 40 | 600 | 3 | 50 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 600 | 3 | 10 | 37 | 30
SSC0036.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 600 | 3 | - | 50 | 40 | 600 | 3 | 50 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0037.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 600 | 3 | - | 50 | 40 | 600 | 3 | 50 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 600 | 3 | 10 | 37 | 30
SSC0037.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 600 | 3 | - | 50 | 40 | 600 | 3 | 50 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0037.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 600 | 3 | - | 50 | 40 | 600 | 3 | 50 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 600 | 3 | 10 | 37 | 30
SSC0037.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 600 | 3 | - | 50 | 40 | 600 | 3 | 50 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0038.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 600 | 3 | 10 | 37 | 30
SSC0038.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0038.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 600 | 3 | 10 | 37 | 30
SSC0038.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0039.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 600 | 3 | - | 50 | 40 | 600 | 3 | 50 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 600 | 3 | 10 | 37 | 30
SSC0039.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 600 | 3 | - | 50 | 40 | 600 | 3 | 50 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0039.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 600 | 3 | - | 50 | 40 | 600 | 3 | 50 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 600 | 3 | 10 | 37 | 30
SSC0039.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 600 | 3 | - | 50 | 40 | 600 | 3 | 50 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0040.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 600 | 3 | 10 | 37 | 30
SSC0040.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0040.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 600 | 3 | 10 | 37 | 30
SSC0040.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 600 | 3 | 10 | 37 | 30
SSC0041.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS015E0* | 200 | 3 | - | 15 | 3 | 200 | 3 | 100 | 11 | 3 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 200 | 3 | 10 | 37 | 10
SSC0041.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS015E0* | 200 | 3 | - | 15 | 3 | 200 | 3 | 100 | 11 | 3 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0041.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS015E0* | 200 | 3 | - | 15 | 3 | 200 | 3 | 100 | 11 | 3 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 200 | 3 | 10 | 37 | 10
SSC0041.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS015E0* | 200 | 3 | - | 15 | 3 | 200 | 3 | 100 | 11 | 3 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0042.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS030H1* | 200 | 3 | - | 30 | 7.5 | 200 | 3 | 100 | 11 | 3 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 200 | 3 | 10 | 37 | 10
SSC0042.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS030H1* | 200 | 3 | - | 30 | 7.5 | 200 | 3 | 100 | 11 | 3 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0042.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS030H1* | 200 | 3 | - | 30 | 7.5 | 200 | 3 | 100 | 11 | 3 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 200 | 3 | 10 | 37 | 10
SSC0042.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS030H1* | 200 | 3 | - | 30 | 7.5 | 200 | 3 | 100 | 11 | 3 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0043.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS030H1* | 200 | 3 | - | 30 | 7.5 | 200 | 3 | 100 | 17.5 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 200 | 3 | 10 | 37 | 10
SSC0043.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS030H1* | 200 | 3 | - | 30 | 7.5 | 200 | 3 | 100 | 17.5 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0043.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS030H1* | 200 | 3 | - | 30 | 7.5 | 200 | 3 | 100 | 17.5 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 200 | 3 | 10 | 37 | 10
SSC0043.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS030H1* | 200 | 3 | - | 30 | 7.5 | 200 | 3 | 100 | 17.5 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0044.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 100 | 17.5 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 200 | 3 | 10 | 37 | 10
SSC0044.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 100 | 17.5 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0044.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 100 | 17.5 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 200 | 3 | 10 | 37 | 10
SSC0044.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 100 | 17.5 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0045.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 200 | 3 | 10 | 37 | 10
SSC0045.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0045.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 200 | 3 | 10 | 37 | 10
SSC0045.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0046.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 200 | 3 | 10 | 37 | 10
SSC0046.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0046.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 200 | 3 | 10 | 37 | 10
SSC0046.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0047.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 200 | 3 | 10 | 37 | 10
SSC0047.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0047.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 200 | 3 | 10 | 37 | 10
SSC0047.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0048.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 200 | 3 | 10 | 37 | 10
SSC0048.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0048.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 200 | 3 | 10 | 37 | 10
SSC0048.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 200 | 3 | 10 | 37 | 10
SSC0049.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS030H1* | 208 | 3 | - | 30 | 7.5 | 208 | 3 | 100 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 208 | 3 | 10 | 37 | 10
SSC0049.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS030H1* | 208 | 3 | - | 30 | 7.5 | 208 | 3 | 100 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0049.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS030H1* | 208 | 3 | - | 30 | 7.5 | 208 | 3 | 100 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 208 | 3 | 10 | 37 | 10
SSC0049.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS030H1* | 208 | 3 | - | 30 | 7.5 | 208 | 3 | 100 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0050.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 208 | 3 | - | 50 | 15 | 208 | 3 | 100 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 208 | 3 | 10 | 37 | 10
SSC0050.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 208 | 3 | - | 50 | 15 | 208 | 3 | 100 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0050.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 208 | 3 | - | 50 | 15 | 208 | 3 | 100 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 208 | 3 | 10 | 37 | 10
SSC0050.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 208 | 3 | - | 50 | 15 | 208 | 3 | 100 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0051.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 208 | 3 | - | 50 | 15 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 208 | 3 | 10 | 37 | 10
SSC0051.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 208 | 3 | - | 50 | 15 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0051.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 208 | 3 | - | 50 | 15 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 208 | 3 | 10 | 37 | 10
SSC0051.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 208 | 3 | - | 50 | 15 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0052.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 208 | 3 | 10 | 37 | 10
SSC0052.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0052.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 208 | 3 | 10 | 37 | 10
SSC0052.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0053.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 208 | 3 | - | 50 | 15 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 208 | 3 | 10 | 37 | 10
SSC0053.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 208 | 3 | - | 50 | 15 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0053.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 208 | 3 | - | 50 | 15 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 208 | 3 | 10 | 37 | 10
SSC0053.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 208 | 3 | - | 50 | 15 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0054.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 208 | 3 | 10 | 37 | 10
SSC0054.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0054.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 208 | 3 | 10 | 37 | 10
SSC0054.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 208 | 3 | 10 | 37 | 10
SSC0055.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS030H1* | 240 | 3 | - | 30 | 10 | 240 | 3 | 100 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 240 | 3 | 10 | 37 | 10
SSC0055.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS030H1* | 240 | 3 | - | 30 | 10 | 240 | 3 | 100 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0055.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS030H1* | 240 | 3 | - | 30 | 10 | 240 | 3 | 100 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 240 | 3 | 10 | 37 | 10
SSC0055.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS030H1* | 240 | 3 | - | 30 | 10 | 240 | 3 | 100 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0056.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 240 | 3 | - | 50 | 15 | 240 | 3 | 100 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 240 | 3 | 10 | 37 | 10
SSC0056.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 240 | 3 | - | 50 | 15 | 240 | 3 | 100 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0056.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 240 | 3 | - | 50 | 15 | 240 | 3 | 100 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 240 | 3 | 10 | 37 | 10
SSC0056.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 240 | 3 | - | 50 | 15 | 240 | 3 | 100 | 16.7 | 5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0057.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 240 | 3 | - | 50 | 15 | 240 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 240 | 3 | 10 | 37 | 10
SSC0057.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 240 | 3 | - | 50 | 15 | 240 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0057.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 240 | 3 | - | 50 | 15 | 240 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 240 | 3 | 10 | 37 | 10
SSC0057.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 240 | 3 | - | 50 | 15 | 240 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0058.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 240 | 3 | 10 | 37 | 10
SSC0058.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0058.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 240 | 3 | 10 | 37 | 10
SSC0058.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0059.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 240 | 3 | - | 50 | 15 | 240 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 240 | 3 | 10 | 37 | 10
SSC0059.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 240 | 3 | - | 50 | 15 | 240 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0059.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 240 | 3 | - | 50 | 15 | 240 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 240 | 3 | 10 | 37 | 10
SSC0059.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 240 | 3 | - | 50 | 15 | 240 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0060.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 240 | 3 | 10 | 37 | 10
SSC0060.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0060.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 240 | 3 | 10 | 37 | 10
SSC0060.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 240 | 3 | 10 | 37 | 10
SSC0061.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS015E0* | 480 | 3 | - | 15 | 10 | 480 | 3 | 100 | 11 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 480 | 3 | 10 | 37 | 25
SSC0061.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS015E0* | 480 | 3 | - | 15 | 10 | 480 | 3 | 100 | 11 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0061.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS015E0* | 480 | 3 | - | 15 | 10 | 480 | 3 | 100 | 11 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 480 | 3 | 10 | 37 | 25
SSC0061.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS015E0* | 480 | 3 | - | 15 | 10 | 480 | 3 | 100 | 11 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0062.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS030H1* | 480 | 3 | - | 30 | 20 | 480 | 3 | 100 | 11 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 480 | 3 | 10 | 37 | 25
SSC0062.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS030H1* | 480 | 3 | - | 30 | 20 | 480 | 3 | 100 | 11 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0062.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS030H1* | 480 | 3 | - | 30 | 20 | 480 | 3 | 100 | 11 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 480 | 3 | 10 | 37 | 25
SSC0062.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS030H1* | 480 | 3 | - | 30 | 20 | 480 | 3 | 100 | 11 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0063.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS030H1* | 480 | 3 | - | 30 | 20 | 480 | 3 | 100 | 14 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 480 | 3 | 10 | 37 | 25
SSC0063.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS030H1* | 480 | 3 | - | 30 | 20 | 480 | 3 | 100 | 14 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0063.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS030H1* | 480 | 3 | - | 30 | 20 | 480 | 3 | 100 | 14 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 480 | 3 | 10 | 37 | 25
SSC0063.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS030H1* | 480 | 3 | - | 30 | 20 | 480 | 3 | 100 | 14 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0064.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 100 | 14 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 480 | 3 | 10 | 37 | 25
SSC0064.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 100 | 14 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0064.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 100 | 14 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 480 | 3 | 10 | 37 | 25
SSC0064.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 100 | 14 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0065.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS030H1* | 480 | 3 | - | 30 | 20 | 480 | 3 | 100 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 480 | 3 | 10 | 37 | 25
SSC0065.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS030H1* | 480 | 3 | - | 30 | 20 | 480 | 3 | 100 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0065.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS030H1* | 480 | 3 | - | 30 | 20 | 480 | 3 | 100 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 480 | 3 | 10 | 37 | 25
SSC0065.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS030H1* | 480 | 3 | - | 30 | 20 | 480 | 3 | 100 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0066.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 100 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 480 | 3 | 10 | 37 | 25
SSC0066.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 100 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0066.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 100 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 480 | 3 | 10 | 37 | 25
SSC0066.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 100 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0067.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 100 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 480 | 3 | 10 | 37 | 25
SSC0067.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 100 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0067.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 100 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 480 | 3 | 10 | 37 | 25
SSC0067.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 100 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0068.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 480 | 3 | 10 | 37 | 25
SSC0068.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0068.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 480 | 3 | 10 | 37 | 25
SSC0068.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0069.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 480 | 3 | 10 | 37 | 25
SSC0069.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0069.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 480 | 3 | 10 | 37 | 25
SSC0069.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0070.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N37N3S | 480 | 3 | 10 | 37 | 25
SSC0070.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0070.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N37N3S | 480 | 3 | 10 | 37 | 25
SSC0070.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N37N3S | 480 | 3 | 10 | 37 | 25
SSC0071.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 50 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 200 | 3 | 10 | 66 | 20
SSC0071.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 50 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0071.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 50 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 200 | 3 | 10 | 66 | 20
SSC0071.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 50 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0072.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 50 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 200 | 3 | 10 | 66 | 20
SSC0072.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 50 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0072.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 50 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 200 | 3 | 10 | 66 | 20
SSC0072.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 50 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0073.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 50 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 200 | 3 | 10 | 66 | 20
SSC0073.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 50 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0073.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 50 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 200 | 3 | 10 | 66 | 20
SSC0073.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 50 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0074.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 50 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 200 | 3 | 10 | 66 | 20
SSC0074.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 50 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0074.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 50 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 200 | 3 | 10 | 66 | 20
SSC0074.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 50 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0075.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 50 | 48.3 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 200 | 3 | 10 | 66 | 20
SSC0075.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 50 | 48.3 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0075.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 50 | 48.3 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 200 | 3 | 10 | 66 | 20
SSC0075.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 50 | 48.3 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0076.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 50 | 48.3 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 200 | 3 | 10 | 66 | 20
SSC0076.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 50 | 48.3 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0076.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 50 | 48.3 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 200 | 3 | 10 | 66 | 20
SSC0076.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 50 | 48.3 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0077.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 50 | 62.1 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 200 | 3 | 10 | 66 | 20
SSC0077.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 50 | 62.1 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0077.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 50 | 62.1 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 200 | 3 | 10 | 66 | 20
SSC0077.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 50 | 62.1 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0078.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 50 | 62.1 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 200 | 3 | 10 | 66 | 20
SSC0078.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 50 | 62.1 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0078.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 50 | 62.1 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 200 | 3 | 10 | 66 | 20
SSC0078.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 50 | 62.1 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0079.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 50 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 208 | 3 | 10 | 66 | 20
SSC0079.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 50 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0079.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 50 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 208 | 3 | 10 | 66 | 20
SSC0079.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 50 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0080.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 50 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 208 | 3 | 10 | 66 | 20
SSC0080.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 50 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0080.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 50 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 208 | 3 | 10 | 66 | 20
SSC0080.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 50 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0081.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 50 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 208 | 3 | 10 | 66 | 20
SSC0081.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 50 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0081.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 50 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 208 | 3 | 10 | 66 | 20
SSC0081.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 50 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0082.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 50 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 208 | 3 | 10 | 66 | 20
SSC0082.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 50 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0082.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 50 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 208 | 3 | 10 | 66 | 20
SSC0082.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 50 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0083.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 50 | 46.2 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 208 | 3 | 10 | 66 | 20
SSC0083.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 50 | 46.2 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0083.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 50 | 46.2 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 208 | 3 | 10 | 66 | 20
SSC0083.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 50 | 46.2 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0084.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 50 | 46.2 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 208 | 3 | 10 | 66 | 20
SSC0084.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 50 | 46.2 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0084.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 50 | 46.2 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 208 | 3 | 10 | 66 | 20
SSC0084.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 50 | 46.2 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0085.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 50 | 59.4 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 208 | 3 | 10 | 66 | 20
SSC0085.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 50 | 59.4 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0085.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 50 | 59.4 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 208 | 3 | 10 | 66 | 20
SSC0085.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 50 | 59.4 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0086.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 50 | 59.4 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 208 | 3 | 10 | 66 | 20
SSC0086.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 50 | 59.4 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0086.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 50 | 59.4 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 208 | 3 | 10 | 66 | 20
SSC0086.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 50 | 59.4 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0087.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 50 | 22 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 240 | 3 | 10 | 66 | 20
SSC0087.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 50 | 22 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0087.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 50 | 22 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 240 | 3 | 10 | 66 | 20
SSC0087.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 50 | 22 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0088.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 50 | 22 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 240 | 3 | 10 | 66 | 20
SSC0088.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 50 | 22 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0088.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 50 | 22 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 240 | 3 | 10 | 66 | 20
SSC0088.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 50 | 22 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0089.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 50 | 28 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 240 | 3 | 10 | 66 | 20
SSC0089.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 50 | 28 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0089.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 50 | 28 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 240 | 3 | 10 | 66 | 20
SSC0089.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 50 | 28 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0090.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 50 | 28 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 240 | 3 | 10 | 66 | 20
SSC0090.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 50 | 28 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0090.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 50 | 28 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 240 | 3 | 10 | 66 | 20
SSC0090.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 50 | 28 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0091.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 50 | 42 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 240 | 3 | 10 | 66 | 20
SSC0091.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 50 | 42 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0091.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 50 | 42 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 240 | 3 | 10 | 66 | 20
SSC0091.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 50 | 42 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0092.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 50 | 42 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 240 | 3 | 10 | 66 | 20
SSC0092.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 50 | 42 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0092.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 50 | 42 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 240 | 3 | 10 | 66 | 20
SSC0092.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 50 | 42 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0093.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 50 | 54 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 240 | 3 | 10 | 66 | 20
SSC0093.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 50 | 54 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0093.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 50 | 54 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 240 | 3 | 10 | 66 | 20
SSC0093.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 50 | 54 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0094.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 50 | 54 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 240 | 3 | 10 | 66 | 20
SSC0094.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 50 | 54 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0094.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 50 | 54 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 240 | 3 | 10 | 66 | 20
SSC0094.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 50 | 54 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0095.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 50 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0095.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 50 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0095.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 50 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0095.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 50 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0096.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 50 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0096.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 50 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0096.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 50 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0096.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 50 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0097.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 50 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0097.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 50 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0097.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 50 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0097.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 50 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0098.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 50 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0098.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 50 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0098.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 50 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0098.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 50 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0099.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 50 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0099.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 50 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0099.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 50 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0099.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 50 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0100.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 50 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0100.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 50 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0100.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 50 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0100.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 50 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0101.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 50 | 40 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0101.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 50 | 40 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0101.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 50 | 40 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0101.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 50 | 40 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0102.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 50 | 40 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0102.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 50 | 40 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0102.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 50 | 40 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0102.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 50 | 40 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0103.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 50 | 52 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0103.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 50 | 52 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0103.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 50 | 52 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0103.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 50 | 52 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0104.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 50 | 52 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0104.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 50 | 52 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0104.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 50 | 52 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0104.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 50 | 52 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0105.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 50 | 65 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0105.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 50 | 65 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0105.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 50 | 65 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0105.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 50 | 65 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0106.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 50 | 65 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0106.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 50 | 65 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0106.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 50 | 65 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0106.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 50 | 65 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0107.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 600 | 3 | 10 | 66 | 60
SSC0107.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0107.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 600 | 3 | 10 | 66 | 60
SSC0107.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0108.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 600 | 3 | 10 | 66 | 60
SSC0108.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0108.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 600 | 3 | 10 | 66 | 60
SSC0108.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 22 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0109.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 600 | 3 | 10 | 66 | 60
SSC0109.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0109.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 600 | 3 | 10 | 66 | 60
SSC0109.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0110.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 600 | 3 | 10 | 66 | 60
SSC0110.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0110.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 600 | 3 | 10 | 66 | 60
SSC0110.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 27 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0111.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 600 | 3 | 10 | 66 | 60
SSC0111.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0111.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 600 | 3 | 10 | 66 | 60
SSC0111.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0112.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 600 | 3 | 10 | 66 | 60
SSC0112.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0112.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 600 | 3 | 10 | 66 | 60
SSC0112.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 32 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0113.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 41 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 600 | 3 | 10 | 66 | 60
SSC0113.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 41 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0113.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 41 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 600 | 3 | 10 | 66 | 60
SSC0113.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 41 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0114.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 41 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 600 | 3 | 10 | 66 | 60
SSC0114.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 41 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0114.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 41 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 600 | 3 | 10 | 66 | 60
SSC0114.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 41 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0115.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 52 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 600 | 3 | 10 | 66 | 60
SSC0115.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 52 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0115.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 52 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 600 | 3 | 10 | 66 | 60
SSC0115.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 52 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0116.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 52 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 600 | 3 | 10 | 66 | 60
SSC0116.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 52 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0116.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 52 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 600 | 3 | 10 | 66 | 60
SSC0116.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 52 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0117.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 62 | 60 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 600 | 3 | 10 | 66 | 60
SSC0117.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 62 | 60 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0117.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 62 | 60 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 600 | 3 | 10 | 66 | 60
SSC0117.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 62 | 60 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0118.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 62 | 60 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 600 | 3 | 10 | 66 | 60
SSC0118.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 62 | 60 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0118.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 62 | 60 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 600 | 3 | 10 | 66 | 60
SSC0118.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 62 | 60 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 600 | 3 | 10 | 66 | 60
SSC0119.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 200 | 3 | 10 | 66 | 20
SSC0119.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0119.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 200 | 3 | 10 | 66 | 20
SSC0119.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0120.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 200 | 3 | 10 | 66 | 20
SSC0120.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0120.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 200 | 3 | 10 | 66 | 20
SSC0120.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 25.3 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0121.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 200 | 3 | 10 | 66 | 20
SSC0121.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0121.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 200 | 3 | 10 | 66 | 20
SSC0121.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0122.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 200 | 3 | 10 | 66 | 20
SSC0122.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0122.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 200 | 3 | 10 | 66 | 20
SSC0122.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 32.2 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0123.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 48.3 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 200 | 3 | 10 | 66 | 20
SSC0123.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 48.3 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0123.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 48.3 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 200 | 3 | 10 | 66 | 20
SSC0123.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 48.3 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0124.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 48.3 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 200 | 3 | 10 | 66 | 20
SSC0124.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 48.3 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0124.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 48.3 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 200 | 3 | 10 | 66 | 20
SSC0124.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 48.3 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0125.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 62.1 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 200 | 3 | 10 | 66 | 20
SSC0125.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 62.1 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0125.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 62.1 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 200 | 3 | 10 | 66 | 20
SSC0125.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 62.1 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0126.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 200 | 3 | 10 | 66 | 20
SSC0126.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0126.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 200 | 3 | 10 | 66 | 20
SSC0126.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 200 | 3 | 10 | 66 | 20
SSC0127.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 208 | 3 | 10 | 66 | 20
SSC0127.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0127.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 208 | 3 | 10 | 66 | 20
SSC0127.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0128.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 208 | 3 | 10 | 66 | 20
SSC0128.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0128.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 208 | 3 | 10 | 66 | 20
SSC0128.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 24.2 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0129.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 208 | 3 | 10 | 66 | 20
SSC0129.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0129.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 208 | 3 | 10 | 66 | 20
SSC0129.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0130.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 208 | 3 | 10 | 66 | 20
SSC0130.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0130.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 208 | 3 | 10 | 66 | 20
SSC0130.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 30.8 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0131.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 100 | 46.2 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 208 | 3 | 10 | 66 | 20
SSC0131.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 100 | 46.2 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0131.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 100 | 46.2 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 208 | 3 | 10 | 66 | 20
SSC0131.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 100 | 46.2 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0132.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 46.2 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 208 | 3 | 10 | 66 | 20
SSC0132.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 46.2 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0132.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 46.2 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 208 | 3 | 10 | 66 | 20
SSC0132.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 46.2 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0133.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 59.4 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 208 | 3 | 10 | 66 | 20
SSC0133.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 59.4 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0133.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 59.4 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 208 | 3 | 10 | 66 | 20
SSC0133.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 59.4 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0134.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 208 | 3 | 10 | 66 | 20
SSC0134.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0134.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 208 | 3 | 10 | 66 | 20
SSC0134.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 208 | 3 | 10 | 66 | 20
SSC0135.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 100 | 22 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 240 | 3 | 10 | 66 | 20
SSC0135.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 100 | 22 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0135.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 100 | 22 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 240 | 3 | 10 | 66 | 20
SSC0135.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 100 | 22 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0136.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 22 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 240 | 3 | 10 | 66 | 20
SSC0136.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 22 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0136.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 22 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 240 | 3 | 10 | 66 | 20
SSC0136.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 22 | 7.5 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0137.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 100 | 28 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 240 | 3 | 10 | 66 | 20
SSC0137.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 100 | 28 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0137.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 100 | 28 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 240 | 3 | 10 | 66 | 20
SSC0137.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 100 | 28 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0138.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 28 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 240 | 3 | 10 | 66 | 20
SSC0138.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 28 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0138.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 28 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 240 | 3 | 10 | 66 | 20
SSC0138.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 28 | 10 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0139.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 100 | 42 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 240 | 3 | 10 | 66 | 20
SSC0139.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 100 | 42 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0139.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 100 | 42 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 240 | 3 | 10 | 66 | 20
SSC0139.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 100 | 42 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0140.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 42 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 240 | 3 | 10 | 66 | 20
SSC0140.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 42 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0140.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 42 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 240 | 3 | 10 | 66 | 20
SSC0140.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 42 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0141.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 54 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 240 | 3 | 10 | 66 | 20
SSC0141.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 54 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0141.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 54 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 240 | 3 | 10 | 66 | 20
SSC0141.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 54 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0142.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 240 | 3 | 10 | 66 | 20
SSC0142.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0142.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 240 | 3 | 10 | 66 | 20
SSC0142.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 240 | 3 | 10 | 66 | 20
SSC0143.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0143.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0143.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0143.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0144.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0144.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0144.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0144.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 21 | 15 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0145.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0145.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0145.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0145.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0146.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0146.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0146.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0146.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 27 | 20 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0147.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0147.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0147.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0147.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0148.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0148.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0148.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0148.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 34 | 25 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0149.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 40 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0149.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 40 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0149.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 40 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0149.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 40 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0150.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 40 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0150.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 40 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0150.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 40 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0150.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 40 | 30 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0151.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 52 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0151.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 52 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0151.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 52 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0151.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 52 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0152.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 52 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0152.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 52 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0152.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 52 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0152.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 52 | 40 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0153.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 65 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0153.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 65 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0153.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 65 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0153.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 65 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0154.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 65 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801N66N3S | 480 | 3 | 10 | 66 | 50
SSC0154.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 65 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0154.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 65 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811N66N3S | 480 | 3 | 10 | 66 | 50
SSC0154.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 65 | 50 | 2355 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+N66N3S | 480 | 3 | 10 | 66 | 50
SSC0155.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 65 | 32.2 | 10 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0155.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 65 | 32.2 | 10 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0155.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 65 | 32.2 | 10 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0155.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 65 | 32.2 | 10 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0156.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 65 | 32.2 | 10 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0156.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 65 | 32.2 | 10 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0156.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 65 | 32.2 | 10 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0156.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 65 | 32.2 | 10 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0157.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 65 | 48.3 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0157.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 65 | 48.3 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0157.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 65 | 48.3 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0157.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 65 | 48.3 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0158.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 48.3 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0158.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 48.3 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0158.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 48.3 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0158.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 48.3 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0159.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 62.1 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0159.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 62.1 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0159.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 62.1 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0159.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 62.1 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0160.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 62.1 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0160.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 62.1 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0160.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 62.1 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0160.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 62.1 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0161.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0161.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0161.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0161.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0162.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0162.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0162.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0162.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0163.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0163.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0163.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0163.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0164.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0164.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0164.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0164.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0165.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 65 | 46.2 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0165.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 65 | 46.2 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0165.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 65 | 46.2 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0165.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 65 | 46.2 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0166.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 46.2 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0166.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 46.2 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0166.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 46.2 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0166.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 46.2 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0167.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 59.4 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0167.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 59.4 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0167.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 59.4 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0167.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 59.4 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0168.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 59.4 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0168.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 59.4 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0168.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 59.4 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0168.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 59.4 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0169.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0169.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0169.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0169.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0170.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0170.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0170.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0170.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0171.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0171.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0171.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0171.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0172.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0172.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0172.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0172.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0173.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 65 | 42 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0173.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 65 | 42 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0173.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 65 | 42 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0173.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 65 | 42 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0174.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 42 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0174.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 42 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0174.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 42 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0174.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 42 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0175.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 54 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0175.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 54 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0175.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 54 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0175.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 54 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0176.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 54 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0176.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 54 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0176.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 54 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0176.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 54 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0177.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0177.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0177.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0177.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0178.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0178.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0178.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0178.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0179.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0179.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0179.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0179.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0180.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0180.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0180.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0180.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0181.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0181.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0181.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0181.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0182.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0182.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0182.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0182.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0183.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 65 | 34 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0183.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 65 | 34 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0183.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 65 | 34 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0183.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 65 | 34 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0184.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 34 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0184.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 34 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0184.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 34 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0184.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 34 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0185.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 40 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0185.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 40 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0185.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 40 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0185.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 40 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0186.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 40 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0186.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 40 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0186.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 40 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0186.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 40 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0187.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 52 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0187.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 52 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0187.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 52 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0187.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 52 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0188.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 52 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0188.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 52 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0188.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 52 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0188.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 52 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0189.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0189.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0189.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0189.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0190.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0190.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0190.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0190.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0191.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0191.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0191.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0191.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0192.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0192.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0192.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0192.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0193.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0193.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0193.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0193.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0194.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0194.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0194.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0194.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0195.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 600 | 3 | - | 50 | 40 | 600 | 3 | 50 | 32 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0195.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 600 | 3 | - | 50 | 40 | 600 | 3 | 50 | 32 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0195.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 600 | 3 | - | 50 | 40 | 600 | 3 | 50 | 32 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0195.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP050K2* | 600 | 3 | - | 50 | 40 | 600 | 3 | 50 | 32 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0196.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 32 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0196.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 32 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0196.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 32 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0196.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 32 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0197.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 41 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0197.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 41 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0197.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 41 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0197.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 41 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0198.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 41 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0198.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 41 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0198.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 41 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0198.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 41 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0199.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 52 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0199.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 52 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0199.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 52 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0199.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 52 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0200.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 52 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0200.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 52 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0200.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 52 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0200.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 52 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0201.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 62 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0201.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 62 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0201.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 62 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0201.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 62 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0202.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 62 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0202.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 62 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0202.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 62 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0202.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 62 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0203.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 77 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0203.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 77 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0203.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 77 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0203.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 77 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0204.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 77 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0204.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 77 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0204.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 77 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0204.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 77 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0205.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 99 | 100 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0205.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 99 | 100 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0205.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 99 | 100 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0205.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 99 | 100 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0206.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 99 | 100 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0206.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 99 | 100 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0206.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 99 | 100 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0206.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 99 | 100 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0207.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 100 | 32.2 | 10 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0207.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 100 | 32.2 | 10 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0207.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 100 | 32.2 | 10 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0207.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 200 | 3 | - | 50 | 15 | 200 | 3 | 100 | 32.2 | 10 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0208.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 32.2 | 10 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0208.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 32.2 | 10 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0208.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 32.2 | 10 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0208.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 32.2 | 10 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0209.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 48.3 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0209.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 48.3 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0209.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 48.3 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0209.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 48.3 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0210.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 48.3 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0210.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 48.3 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0210.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 48.3 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0210.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 48.3 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0211.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 62.1 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0211.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 62.1 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0211.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 62.1 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0211.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 62.1 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0212.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0212.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0212.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0212.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0213.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0213.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0213.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0213.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0214.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0214.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0214.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0214.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0215.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0215.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0215.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0215.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0216.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0216.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0216.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0216.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0217.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 100 | 46.2 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0217.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 100 | 46.2 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0217.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 100 | 46.2 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0217.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 100 | 46.2 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0218.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 46.2 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0218.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 46.2 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0218.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 46.2 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0218.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 46.2 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0219.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 59.4 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0219.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 59.4 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0219.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 59.4 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0219.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 59.4 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0220.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0220.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0220.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0220.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0221.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0221.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0221.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0221.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0222.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0222.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0222.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0222.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0223.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0223.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0223.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0223.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0224.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0224.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0224.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0224.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0225.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 100 | 42 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0225.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 100 | 42 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0225.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 100 | 42 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0225.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 100 | 42 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0226.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 42 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0226.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 42 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0226.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 42 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0226.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 42 | 15 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0227.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 54 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0227.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 54 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0227.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 54 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0227.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 54 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0228.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0228.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0228.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0228.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0229.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0229.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0229.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0229.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0230.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0230.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0230.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0230.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0231.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0231.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0231.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0231.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0232.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0232.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0232.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0232.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0233.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0233.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0233.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0233.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0234.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0234.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0234.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0234.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0235.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 100 | 34 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0235.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 100 | 34 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0235.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 100 | 34 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0235.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS050K2* | 480 | 3 | - | 50 | 30 | 480 | 3 | 100 | 34 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0236.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 34 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0236.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 34 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0236.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 34 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0236.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 34 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0237.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 40 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0237.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 40 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0237.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 40 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0237.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 40 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0238.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 40 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0238.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 40 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0238.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 40 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0238.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 40 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0239.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 52 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0239.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 52 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0239.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 52 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0239.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 52 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0240.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 52 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0240.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 52 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0240.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 52 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0240.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 52 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0241.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0241.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0241.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0241.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0242.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0242.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0242.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0242.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0243.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0243.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0243.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0243.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0244.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0244.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0244.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0244.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0245.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0245.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0245.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0245.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0246.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0246.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0246.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0246.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0247.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0247.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0247.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0247.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0248.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0248.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0248.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0248.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 78.2 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0249.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0249.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0249.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0249.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0250.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 200 | 3 | 10 | 105 | 30
SSC0250.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0250.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 200 | 3 | 10 | 105 | 30
SSC0250.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 92 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 200 | 3 | 10 | 105 | 30
SSC0251.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0251.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0251.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0251.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0252.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0252.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0252.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0252.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 74.8 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0253.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0253.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0253.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0253.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0254.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 208 | 3 | 10 | 105 | 30
SSC0254.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0254.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 208 | 3 | 10 | 105 | 30
SSC0254.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 88 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 208 | 3 | 10 | 105 | 30
SSC0255.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 50 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0255.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 50 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0255.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 50 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0255.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 50 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0256.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 50 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0256.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 50 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0256.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 50 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0256.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 50 | 68 | 25 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0257.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 50 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0257.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 50 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0257.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 50 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0257.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 50 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0258.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 50 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0258.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 50 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0258.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 50 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0258.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 50 | 80 | 30 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0259.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 150 | 240 | 3 | 50 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0259.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 150 | 240 | 3 | 50 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0259.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 150 | 240 | 3 | 50 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0259.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 150 | 240 | 3 | 50 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0260.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 50 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 240 | 3 | 10 | 105 | 40
SSC0260.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 50 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0260.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 50 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 240 | 3 | 10 | 105 | 40
SSC0260.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 50 | 104 | 40 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 240 | 3 | 10 | 105 | 40
SSC0261.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0261.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0261.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0261.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0262.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0262.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0262.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0262.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 65 | 50 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0263.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0263.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0263.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0263.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0264.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0264.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0264.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0264.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 77 | 60 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0265.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0265.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0265.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0265.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0266.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 480 | 3 | 10 | 105 | 75
SSC0266.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0266.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 480 | 3 | 10 | 105 | 75
SSC0266.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 96 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 480 | 3 | 10 | 105 | 75
SSC0267.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0267.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0267.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0267.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0268.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0268.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0268.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0268.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0269.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0269.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0269.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0269.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0270.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R10N3S | 600 | 3 | 10 | 105 | 100
SSC0270.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0270.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R10N3S | 600 | 3 | 10 | 105 | 100
SSC0270.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 3835 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R10N3S | 600 | 3 | 10 | 105 | 100
SSC0271.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 65 | 48.3 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0271.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 65 | 48.3 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0271.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 65 | 48.3 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0271.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 65 | 48.3 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0272.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 48.3 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0272.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 48.3 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0272.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 48.3 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0272.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 48.3 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0273.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 62.1 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0273.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 62.1 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0273.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 62.1 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0273.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 62.1 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0274.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 62.1 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0274.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 62.1 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0274.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 62.1 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0274.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 62.1 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0275.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0275.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0275.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0275.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 65 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0276.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0276.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0276.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0276.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0277.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0277.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0277.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0277.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0278.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0278.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0278.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0278.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0279.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0279.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0279.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0279.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0280.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0280.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0280.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0280.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 65 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0281.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 65 | 46.2 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0281.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 65 | 46.2 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0281.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 65 | 46.2 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0281.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 65 | 46.2 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0282.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 46.2 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0282.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 46.2 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0282.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 46.2 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0282.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 46.2 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0283.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 59.4 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0283.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 59.4 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0283.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 59.4 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0283.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 59.4 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0284.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 59.4 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0284.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 59.4 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0284.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 59.4 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0284.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 59.4 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0285.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0285.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0285.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0285.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 65 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0286.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0286.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0286.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0286.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0287.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0287.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0287.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0287.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0288.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0288.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0288.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0288.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0289.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0289.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0289.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0289.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0290.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0290.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0290.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0290.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 65 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0291.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 65 | 42 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0291.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 65 | 42 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0291.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 65 | 42 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0291.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 65 | 42 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0292.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 42 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0292.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 42 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0292.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 42 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0292.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 42 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0293.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 54 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0293.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 54 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0293.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 54 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0293.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 54 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0294.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 54 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0294.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 54 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0294.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 54 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0294.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 54 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0295.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0295.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0295.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0295.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0296.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0296.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0296.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0296.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0297.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0297.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0297.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0297.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 65 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0298.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0298.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0298.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0298.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0299.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0299.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0299.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0299.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0300.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0300.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0300.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0300.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0301.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 130 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0301.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 130 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0301.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 130 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0301.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 130 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0302.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 130 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0302.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 130 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0302.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 130 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0302.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 65 | 130 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0303.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 52 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0303.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 52 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0303.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 52 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0303.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 65 | 52 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0304.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 52 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0304.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 52 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0304.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 52 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0304.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 52 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0305.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0305.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0305.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0305.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0306.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0306.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0306.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0306.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0307.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0307.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0307.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0307.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 65 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0308.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0308.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0308.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0308.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0309.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0309.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0309.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0309.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0310.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0310.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0310.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0310.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0311.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 124 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0311.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 124 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0311.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 124 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0311.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 124 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0312.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 124 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0312.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 124 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0312.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 124 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0312.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 65 | 124 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0313.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 52 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0313.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 52 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0313.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 52 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0313.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP070M2* | 600 | 3 | - | 70 | 60 | 600 | 3 | 50 | 52 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0314.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 52 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0314.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 52 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0314.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 52 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0314.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 52 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0315.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 62 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0315.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 62 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0315.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 62 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0315.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 62 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0316.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 62 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0316.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 62 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0316.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 62 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0316.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 62 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0317.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 77 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0317.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 77 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0317.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 77 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0317.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP100R3* | 600 | 3 | - | 100 | 100 | 600 | 3 | 50 | 77 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0318.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 77 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0318.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 77 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0318.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 77 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0318.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 77 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0319.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 99 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0319.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 99 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0319.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 99 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0319.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 99 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0320.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 99 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0320.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 99 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0320.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 99 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0320.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 99 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0321.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 125 | 125 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0321.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 125 | 125 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0321.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 125 | 125 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0321.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150T4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 125 | 125 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0322.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 125 | 125 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0322.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 125 | 125 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0322.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 125 | 125 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0322.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP150U4* | 600 | 3 | - | 150 | 150 | 600 | 3 | 50 | 125 | 125 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0323.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 48.3 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0323.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 48.3 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0323.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 48.3 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0323.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 200 | 3 | - | 70 | 20 | 200 | 3 | 100 | 48.3 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0324.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 48.3 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0324.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 48.3 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0324.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 48.3 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0324.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 48.3 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0325.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 62.1 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0325.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 62.1 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0325.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 62.1 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0325.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 62.1 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0326.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0326.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0326.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0326.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 62.1 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0327.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0327.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0327.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0327.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 200 | 3 | - | 100 | 30 | 200 | 3 | 100 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0328.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0328.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0328.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0328.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0329.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0329.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0329.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0329.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0330.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0330.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0330.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0330.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0331.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0331.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0331.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0331.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0332.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0332.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0332.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0332.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 200 | 3 | - | 150 | 50 | 200 | 3 | 100 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0333.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 100 | 46.2 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0333.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 100 | 46.2 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0333.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 100 | 46.2 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0333.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 208 | 3 | - | 70 | 20 | 208 | 3 | 100 | 46.2 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0334.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 46.2 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0334.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 46.2 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0334.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 46.2 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0334.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 46.2 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0335.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 59.4 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0335.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 59.4 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0335.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 59.4 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0335.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 59.4 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0336.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0336.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0336.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0336.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 59.4 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0337.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0337.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0337.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0337.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 208 | 3 | - | 100 | 30 | 208 | 3 | 100 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0338.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0338.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0338.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0338.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0339.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0339.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0339.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0339.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0340.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0340.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0340.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0340.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0341.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0341.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0341.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0341.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0342.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0342.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0342.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0342.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 208 | 3 | - | 150 | 50 | 208 | 3 | 100 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0343.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 100 | 42 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0343.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 100 | 42 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0343.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 100 | 42 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0343.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 240 | 3 | - | 70 | 25 | 240 | 3 | 100 | 42 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0344.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 42 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0344.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 42 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0344.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 42 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0344.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 42 | 15 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0345.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 54 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0345.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 54 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0345.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 54 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0345.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 54 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0346.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0346.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0346.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0346.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 54 | 20 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0347.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0347.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0347.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0347.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0348.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0348.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0348.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0348.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0349.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0349.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0349.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0349.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 240 | 3 | - | 100 | 30 | 240 | 3 | 100 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0350.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0350.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0350.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0350.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0351.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0351.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0351.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0351.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0352.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0352.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0352.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0352.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0353.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 130 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0353.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 130 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0353.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 130 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0353.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 130 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0354.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 130 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0354.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 130 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0354.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 130 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0354.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 240 | 3 | - | 150 | 50 | 240 | 3 | 100 | 130 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0355.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 52 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0355.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 52 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0355.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 52 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0355.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS070M2* | 480 | 3 | - | 70 | 50 | 480 | 3 | 100 | 52 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0356.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 52 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0356.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 52 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0356.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 52 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0356.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 52 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0357.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0357.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0357.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0357.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0358.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0358.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0358.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0358.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0359.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0359.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0359.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0359.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS100R3* | 480 | 3 | - | 100 | 75 | 480 | 3 | 100 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0360.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0360.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0360.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0360.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0361.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0361.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0361.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0361.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0362.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0362.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0362.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0362.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0363.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 124 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0363.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 124 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0363.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 124 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0363.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150T4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 124 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0364.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 124 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0364.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 124 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0364.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 124 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0364.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCPS150U4* | 480 | 3 | - | 150 | 100 | 480 | 3 | 100 | 124 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0365.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0365.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0365.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0365.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0366.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0366.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0366.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0366.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 78.2 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0367.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0367.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0367.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0367.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0368.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0368.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0368.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0368.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 92 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0369.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0369.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0369.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0369.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 50 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0370.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 50 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 200 | 3 | 10 | 135 | 40
SSC0370.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 50 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0370.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 50 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 200 | 3 | 10 | 135 | 40
SSC0370.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 50 | 120 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 200 | 3 | 10 | 135 | 40
SSC0371.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0371.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0371.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0371.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0372.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0372.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0372.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0372.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 74.8 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0373.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0373.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0373.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0373.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0374.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0374.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0374.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0374.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 88 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0375.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0375.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0375.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0375.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 50 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0376.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 50 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 208 | 3 | 10 | 135 | 40
SSC0376.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 50 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0376.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 50 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 208 | 3 | 10 | 135 | 40
SSC0376.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 50 | 114 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 208 | 3 | 10 | 135 | 40
SSC0377.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 50 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0377.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 50 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0377.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 50 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0377.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 50 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0378.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 50 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0378.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 50 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0378.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 50 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0378.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 50 | 68 | 25 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0379.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 50 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0379.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 50 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0379.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 50 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0379.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 50 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0380.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 50 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0380.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 50 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0380.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 50 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0380.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 50 | 80 | 30 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0381.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 50 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0381.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 50 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0381.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 50 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0381.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 50 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0382.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 50 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0382.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 50 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0382.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 50 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0382.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 50 | 104 | 40 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0383.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 50 | 130 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0383.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 50 | 130 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0383.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 50 | 130 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0383.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 75 | 240 | 3 | 50 | 130 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0384.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 50 | 130 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 240 | 3 | 10 | 135 | 50
SSC0384.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 50 | 130 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0384.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 50 | 130 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 240 | 3 | 10 | 135 | 50
SSC0384.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 50 | 130 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 240 | 3 | 10 | 135 | 50
SSC0385.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0385.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0385.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0385.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0386.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0386.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0386.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0386.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 65 | 50 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0387.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0387.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0387.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0387.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0388.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0388.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0388.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0388.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 77 | 60 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0389.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0389.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0389.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0389.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0390.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0390.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0390.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0390.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 96 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0391.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 124 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0391.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 124 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0391.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 124 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0391.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 124 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0392.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 124 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 480 | 3 | 10 | 135 | 100
SSC0392.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 124 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0392.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 124 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 480 | 3 | 10 | 135 | 100
SSC0392.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 124 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 480 | 3 | 10 | 135 | 100
SSC0393.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0393.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0393.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0393.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0394.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0394.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0394.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0394.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0395.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0395.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0395.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0395.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0396.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0396.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0396.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0396.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0397.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 125 | 125 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0397.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 125 | 125 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0397.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 125 | 125 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0397.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 125 | 125 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0398.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 125 | 125 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801R13N3S | 600 | 3 | 10 | 135 | 125
SSC0398.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 125 | 125 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0398.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 125 | 125 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811R13N3S | 600 | 3 | 10 | 135 | 125
SSC0398.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 125 | 125 | 5077 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+R13N3S | 600 | 3 | 10 | 135 | 125
SSC0399.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 200 | 3 | 18 | 180 | 60
SSC0399.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0399.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 200 | 3 | 18 | 180 | 60
SSC0399.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0400.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 200 | 3 | 18 | 180 | 60
SSC0400.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0400.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 200 | 3 | 18 | 180 | 60
SSC0400.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0401.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 200 | 3 | 18 | 180 | 60
SSC0401.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0401.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 200 | 3 | 18 | 180 | 60
SSC0401.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0402.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 200 | 3 | 18 | 180 | 60
SSC0402.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0402.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 200 | 3 | 18 | 180 | 60
SSC0402.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0403.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 200 | 3 | 18 | 180 | 60
SSC0403.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0403.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 200 | 3 | 18 | 180 | 60
SSC0403.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0404.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 200 | 3 | 18 | 180 | 60
SSC0404.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0404.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 200 | 3 | 18 | 180 | 60
SSC0404.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0405.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 200 | 3 | 18 | 180 | 60
SSC0405.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0405.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 200 | 3 | 18 | 180 | 60
SSC0405.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0406.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 200 | 3 | 18 | 180 | 60
SSC0406.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0406.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 200 | 3 | 18 | 180 | 60
SSC0406.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0407.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 200 | 3 | 18 | 180 | 60
SSC0407.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0407.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 200 | 3 | 18 | 180 | 60
SSC0407.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0408.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 200 | 3 | 18 | 180 | 60
SSC0408.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0408.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 200 | 3 | 18 | 180 | 60
SSC0408.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0409.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 74.8 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 208 | 3 | 18 | 180 | 60
SSC0409.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 74.8 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0409.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 74.8 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 208 | 3 | 18 | 180 | 60
SSC0409.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 74.8 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0410.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 74.8 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 208 | 3 | 18 | 180 | 60
SSC0410.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 74.8 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0410.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 74.8 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 208 | 3 | 18 | 180 | 60
SSC0410.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 74.8 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0411.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 208 | 3 | 18 | 180 | 60
SSC0411.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0411.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 208 | 3 | 18 | 180 | 60
SSC0411.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0412.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 208 | 3 | 18 | 180 | 60
SSC0412.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0412.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 208 | 3 | 18 | 180 | 60
SSC0412.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0413.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 208 | 3 | 18 | 180 | 60
SSC0413.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0413.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 208 | 3 | 18 | 180 | 60
SSC0413.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0414.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 208 | 3 | 18 | 180 | 60
SSC0414.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0414.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 208 | 3 | 18 | 180 | 60
SSC0414.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0415.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 208 | 3 | 18 | 180 | 60
SSC0415.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0415.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 208 | 3 | 18 | 180 | 60
SSC0415.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0416.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 208 | 3 | 18 | 180 | 60
SSC0416.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0416.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 208 | 3 | 18 | 180 | 60
SSC0416.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0417.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 208 | 3 | 18 | 180 | 60
SSC0417.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0417.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 208 | 3 | 18 | 180 | 60
SSC0417.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0418.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 208 | 3 | 18 | 180 | 60
SSC0418.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0418.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 208 | 3 | 18 | 180 | 60
SSC0418.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0419.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 68 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 240 | 3 | 18 | 180 | 60
SSC0419.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 68 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0419.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 68 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 240 | 3 | 18 | 180 | 60
SSC0419.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 68 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0420.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 68 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 240 | 3 | 18 | 180 | 60
SSC0420.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 68 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0420.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 68 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 240 | 3 | 18 | 180 | 60
SSC0420.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 68 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0421.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 240 | 3 | 18 | 180 | 60
SSC0421.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0421.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 240 | 3 | 18 | 180 | 60
SSC0421.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0422.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 240 | 3 | 18 | 180 | 60
SSC0422.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0422.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 240 | 3 | 18 | 180 | 60
SSC0422.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0423.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 240 | 3 | 18 | 180 | 60
SSC0423.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0423.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 240 | 3 | 18 | 180 | 60
SSC0423.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0424.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 240 | 3 | 18 | 180 | 60
SSC0424.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0424.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 240 | 3 | 18 | 180 | 60
SSC0424.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0425.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 240 | 3 | 18 | 180 | 60
SSC0425.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0425.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 240 | 3 | 18 | 180 | 60
SSC0425.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0426.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 240 | 3 | 18 | 180 | 60
SSC0426.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0426.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 240 | 3 | 18 | 180 | 60
SSC0426.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0427.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 240 | 3 | 18 | 180 | 60
SSC0427.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0427.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 240 | 3 | 18 | 180 | 60
SSC0427.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0428.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 240 | 3 | 18 | 180 | 60
SSC0428.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0428.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 240 | 3 | 18 | 180 | 60
SSC0428.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0429.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 65 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 480 | 3 | 18 | 180 | 150
SSC0429.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 65 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0429.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 65 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 480 | 3 | 18 | 180 | 150
SSC0429.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 65 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0430.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 65 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 480 | 3 | 18 | 180 | 150
SSC0430.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 65 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0430.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 65 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 480 | 3 | 18 | 180 | 150
SSC0430.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 65 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0431.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 480 | 3 | 18 | 180 | 150
SSC0431.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0431.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 480 | 3 | 18 | 180 | 150
SSC0431.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0432.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 480 | 3 | 18 | 180 | 150
SSC0432.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0432.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 480 | 3 | 18 | 180 | 150
SSC0432.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0433.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 480 | 3 | 18 | 180 | 150
SSC0433.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0433.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 480 | 3 | 18 | 180 | 150
SSC0433.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0434.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 480 | 3 | 18 | 180 | 150
SSC0434.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0434.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 480 | 3 | 18 | 180 | 150
SSC0434.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0435.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 480 | 3 | 18 | 180 | 150
SSC0435.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0435.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 480 | 3 | 18 | 180 | 150
SSC0435.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0436.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 480 | 3 | 18 | 180 | 150
SSC0436.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0436.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 480 | 3 | 18 | 180 | 150
SSC0436.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0437.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 480 | 3 | 18 | 180 | 150
SSC0437.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0437.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 480 | 3 | 18 | 180 | 150
SSC0437.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0438.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 480 | 3 | 18 | 180 | 150
SSC0438.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0438.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 480 | 3 | 18 | 180 | 150
SSC0438.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0439.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 480 | 3 | 18 | 180 | 150
SSC0439.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0439.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 480 | 3 | 18 | 180 | 150
SSC0439.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0440.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 480 | 3 | 18 | 180 | 150
SSC0440.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0440.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 480 | 3 | 18 | 180 | 150
SSC0440.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0441.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 600 | 3 | 18 | 180 | 150
SSC0441.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0441.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 600 | 3 | 18 | 180 | 150
SSC0441.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0442.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 600 | 3 | 18 | 180 | 150
SSC0442.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0442.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 600 | 3 | 18 | 180 | 150
SSC0442.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0443.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 600 | 3 | 18 | 180 | 150
SSC0443.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0443.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 600 | 3 | 18 | 180 | 150
SSC0443.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0444.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 600 | 3 | 18 | 180 | 150
SSC0444.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0444.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 600 | 3 | 18 | 180 | 150
SSC0444.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0445.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 600 | 3 | 18 | 180 | 150
SSC0445.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0445.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 600 | 3 | 18 | 180 | 150
SSC0445.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0446.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 600 | 3 | 18 | 180 | 150
SSC0446.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0446.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 600 | 3 | 18 | 180 | 150
SSC0446.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0447.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 600 | 3 | 18 | 180 | 150
SSC0447.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0447.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 600 | 3 | 18 | 180 | 150
SSC0447.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0448.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 600 | 3 | 18 | 180 | 150
SSC0448.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0448.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 600 | 3 | 18 | 180 | 150
SSC0448.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 600 | 3 | 18 | 180 | 150
SSC0449.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 200 | 3 | 18 | 180 | 60
SSC0449.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0449.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 200 | 3 | 18 | 180 | 60
SSC0449.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0450.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 200 | 3 | 18 | 180 | 60
SSC0450.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0450.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 200 | 3 | 18 | 180 | 60
SSC0450.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 200 | 3 | 18 | 180 | 60
SSC0451.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 208 | 3 | 18 | 180 | 60
SSC0451.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0451.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 208 | 3 | 18 | 180 | 60
SSC0451.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 208 | 3 | 18 | 180 | 60
SSC0452.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 240 | 3 | 18 | 180 | 60
SSC0452.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0452.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 240 | 3 | 18 | 180 | 60
SSC0452.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 240 | 3 | 18 | 180 | 60
SSC0453.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 480 | 3 | 18 | 180 | 150
SSC0453.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0453.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 480 | 3 | 18 | 180 | 150
SSC0453.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0454.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T18N3S | 480 | 3 | 18 | 180 | 150
SSC0454.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0454.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T18N3S | 480 | 3 | 18 | 180 | 150
SSC0454.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T18N3S | 480 | 3 | 18 | 180 | 150
SSC0455.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0455.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0455.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0455.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0456.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0456.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0456.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0456.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 78.2 | 25 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0457.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0457.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0457.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0457.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0458.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0458.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0458.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0458.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 92 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0459.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0459.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0459.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0459.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0460.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0460.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0460.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0460.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0461.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0461.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0461.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0461.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0462.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0462.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0462.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0462.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0463.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0463.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0463.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0463.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0464.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0464.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0464.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0464.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0465.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0465.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0465.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0465.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0466.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0466.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0466.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0466.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0467.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 208 | 3 | 18 | 240 | 75
SSC0467.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0467.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 208 | 3 | 18 | 240 | 75
SSC0467.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0468.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 208 | 3 | 18 | 240 | 75
SSC0468.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0468.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 208 | 3 | 18 | 240 | 75
SSC0468.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 88 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0469.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 208 | 3 | 18 | 240 | 75
SSC0469.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0469.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 208 | 3 | 18 | 240 | 75
SSC0469.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0470.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 208 | 3 | 18 | 240 | 75
SSC0470.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0470.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 208 | 3 | 18 | 240 | 75
SSC0470.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0471.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 208 | 3 | 18 | 240 | 75
SSC0471.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0471.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 208 | 3 | 18 | 240 | 75
SSC0471.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0472.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 208 | 3 | 18 | 240 | 75
SSC0472.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0472.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 208 | 3 | 18 | 240 | 75
SSC0472.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0473.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 208 | 3 | 18 | 240 | 75
SSC0473.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0473.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 208 | 3 | 18 | 240 | 75
SSC0473.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0474.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 208 | 3 | 18 | 240 | 75
SSC0474.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0474.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 208 | 3 | 18 | 240 | 75
SSC0474.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0475.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 208 | 3 | 18 | 240 | 75
SSC0475.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0475.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 208 | 3 | 18 | 240 | 75
SSC0475.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0476.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 208 | 3 | 18 | 240 | 75
SSC0476.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0476.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 208 | 3 | 18 | 240 | 75
SSC0476.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0477.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 240 | 3 | 18 | 240 | 75
SSC0477.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0477.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 240 | 3 | 18 | 240 | 75
SSC0477.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0478.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 240 | 3 | 18 | 240 | 75
SSC0478.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0478.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 240 | 3 | 18 | 240 | 75
SSC0478.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 80 | 30 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0479.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 240 | 3 | 18 | 240 | 75
SSC0479.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0479.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 240 | 3 | 18 | 240 | 75
SSC0479.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0480.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 240 | 3 | 18 | 240 | 75
SSC0480.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0480.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 240 | 3 | 18 | 240 | 75
SSC0480.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0481.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 240 | 3 | 18 | 240 | 75
SSC0481.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0481.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 240 | 3 | 18 | 240 | 75
SSC0481.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0482.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 240 | 3 | 18 | 240 | 75
SSC0482.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0482.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 240 | 3 | 18 | 240 | 75
SSC0482.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0483.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 240 | 3 | 18 | 240 | 75
SSC0483.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0483.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 240 | 3 | 18 | 240 | 75
SSC0483.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0484.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 240 | 3 | 18 | 240 | 75
SSC0484.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0484.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 240 | 3 | 18 | 240 | 75
SSC0484.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0485.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 240 | 3 | 18 | 240 | 75
SSC0485.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0485.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 240 | 3 | 18 | 240 | 75
SSC0485.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0486.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 240 | 3 | 18 | 240 | 75
SSC0486.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0486.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 240 | 3 | 18 | 240 | 75
SSC0486.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0487.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0487.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0487.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0487.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0488.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0488.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0488.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0488.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 77 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0489.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0489.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0489.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0489.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0490.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0490.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0490.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0490.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0491.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0491.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0491.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0491.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0492.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0492.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0492.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0492.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0493.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0493.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0493.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0493.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0494.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0494.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0494.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0494.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0495.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0495.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0495.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0495.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0496.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0496.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0496.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0496.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0497.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0497.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0497.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0497.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0498.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400K5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0498.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400K5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0498.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400K5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0498.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400K5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0499.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 600 | 3 | 18 | 240 | 200
SSC0499.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0499.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 600 | 3 | 18 | 240 | 200
SSC0499.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0500.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 600 | 3 | 18 | 240 | 200
SSC0500.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0500.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 600 | 3 | 18 | 240 | 200
SSC0500.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 77 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0501.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 600 | 3 | 18 | 240 | 200
SSC0501.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0501.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 600 | 3 | 18 | 240 | 200
SSC0501.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0502.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 600 | 3 | 18 | 240 | 200
SSC0502.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0502.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 600 | 3 | 18 | 240 | 200
SSC0502.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0503.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 600 | 3 | 18 | 240 | 200
SSC0503.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0503.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 600 | 3 | 18 | 240 | 200
SSC0503.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0504.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 600 | 3 | 18 | 240 | 200
SSC0504.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0504.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 600 | 3 | 18 | 240 | 200
SSC0504.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0505.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 600 | 3 | 18 | 240 | 200
SSC0505.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0505.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 600 | 3 | 18 | 240 | 200
SSC0505.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0506.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 600 | 3 | 18 | 240 | 200
SSC0506.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0506.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 600 | 3 | 18 | 240 | 200
SSC0506.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0507.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 600 | 3 | 18 | 240 | 200
SSC0507.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0507.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 600 | 3 | 18 | 240 | 200
SSC0507.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0508.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 600 | 3 | 18 | 240 | 200
SSC0508.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0508.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 600 | 3 | 18 | 240 | 200
SSC0508.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 600 | 3 | 18 | 240 | 200
SSC0509.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0509.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0509.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0509.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0510.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0510.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0510.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0510.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0511.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0511.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0511.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0511.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0512.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 200 | 3 | 18 | 240 | 75
SSC0512.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0512.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 200 | 3 | 18 | 240 | 75
SSC0512.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 200 | 3 | 18 | 240 | 75
SSC0513.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 208 | 3 | 18 | 240 | 75
SSC0513.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0513.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 208 | 3 | 18 | 240 | 75
SSC0513.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0514.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 208 | 3 | 18 | 240 | 75
SSC0514.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0514.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 208 | 3 | 18 | 240 | 75
SSC0514.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0515.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 208 | 3 | 18 | 240 | 75
SSC0515.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0515.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 208 | 3 | 18 | 240 | 75
SSC0515.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 208 | 3 | 18 | 240 | 75
SSC0516.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 240 | 3 | 18 | 240 | 75
SSC0516.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0516.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 240 | 3 | 18 | 240 | 75
SSC0516.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0517.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 240 | 3 | 18 | 240 | 75
SSC0517.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0517.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 240 | 3 | 18 | 240 | 75
SSC0517.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 240 | 3 | 18 | 240 | 75
SSC0518.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0518.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0518.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0518.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0519.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0519.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0519.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0519.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0520.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0520.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0520.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0520.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0521.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T24N3S | 480 | 3 | 18 | 240 | 200
SSC0521.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0521.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T24N3S | 480 | 3 | 18 | 240 | 200
SSC0521.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T24N3S | 480 | 3 | 18 | 240 | 200
SSC0522.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0522.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0522.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0522.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0523.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0523.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0523.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0523.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0524.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0524.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0524.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0524.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0525.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0525.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0525.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0525.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0526.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0526.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0526.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0526.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0527.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0527.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0527.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0527.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0528.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0528.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0528.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0528.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0529.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0529.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0529.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0529.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0530.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0530.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0530.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0530.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0531.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400L5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0531.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400L5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0531.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400L5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0531.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400L5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 100 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0532.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 208 | 3 | 18 | 304 | 100
SSC0532.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0532.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 208 | 3 | 18 | 304 | 100
SSC0532.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0533.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 208 | 3 | 18 | 304 | 100
SSC0533.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0533.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 208 | 3 | 18 | 304 | 100
SSC0533.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0534.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 208 | 3 | 18 | 304 | 100
SSC0534.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0534.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 208 | 3 | 18 | 304 | 100
SSC0534.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0535.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 208 | 3 | 18 | 304 | 100
SSC0535.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0535.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 208 | 3 | 18 | 304 | 100
SSC0535.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0536.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 208 | 3 | 18 | 304 | 100
SSC0536.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0536.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 208 | 3 | 18 | 304 | 100
SSC0536.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0537.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 208 | 3 | 18 | 304 | 100
SSC0537.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0537.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 208 | 3 | 18 | 304 | 100
SSC0537.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0538.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 208 | 3 | 18 | 304 | 100
SSC0538.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0538.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 208 | 3 | 18 | 304 | 100
SSC0538.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0539.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 208 | 3 | 18 | 304 | 100
SSC0539.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0539.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 208 | 3 | 18 | 304 | 100
SSC0539.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0540.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 208 | 3 | 18 | 304 | 100
SSC0540.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0540.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 208 | 3 | 18 | 304 | 100
SSC0540.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0541.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400L5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 208 | 3 | 18 | 304 | 100
SSC0541.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400L5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0541.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400L5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 208 | 3 | 18 | 304 | 100
SSC0541.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400L5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 100 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0542.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 240 | 3 | 18 | 304 | 100
SSC0542.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0542.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 240 | 3 | 18 | 304 | 100
SSC0542.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0543.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 240 | 3 | 18 | 304 | 100
SSC0543.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0543.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 240 | 3 | 18 | 304 | 100
SSC0543.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 104 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0544.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 240 | 3 | 18 | 304 | 100
SSC0544.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0544.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 240 | 3 | 18 | 304 | 100
SSC0544.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0545.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 240 | 3 | 18 | 304 | 100
SSC0545.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0545.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 240 | 3 | 18 | 304 | 100
SSC0545.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0546.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 240 | 3 | 18 | 304 | 100
SSC0546.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0546.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 240 | 3 | 18 | 304 | 100
SSC0546.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0547.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 240 | 3 | 18 | 304 | 100
SSC0547.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0547.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 240 | 3 | 18 | 304 | 100
SSC0547.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0548.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 240 | 3 | 18 | 304 | 100
SSC0548.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0548.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 240 | 3 | 18 | 304 | 100
SSC0548.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0549.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 240 | 3 | 18 | 304 | 100
SSC0549.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0549.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 240 | 3 | 18 | 304 | 100
SSC0549.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0550.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 240 | 3 | 18 | 304 | 100
SSC0550.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0550.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 240 | 3 | 18 | 304 | 100
SSC0550.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0551.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400K5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 240 | 3 | 18 | 304 | 100
SSC0551.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400K5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0551.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400K5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 240 | 3 | 18 | 304 | 100
SSC0551.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400K5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 100 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0552.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0552.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0552.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0552.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0553.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0553.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0553.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0553.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 96 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0554.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0554.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0554.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0554.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0555.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0555.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0555.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0555.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0556.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0556.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0556.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0556.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 100 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0557.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0557.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0557.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0557.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0558.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0558.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0558.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0558.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0559.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0559.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0559.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0559.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0560.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0560.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0560.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0560.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0561.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400K5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0561.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400K5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0561.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400K5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0561.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400K5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0562.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0562.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0562.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0562.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0563.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400W5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0563.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400W5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0563.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400W5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0563.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400W5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 100 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0564.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 600 | 3 | 18 | 304 | 300
SSC0564.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0564.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 600 | 3 | 18 | 304 | 300
SSC0564.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250A5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0565.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 600 | 3 | 18 | 304 | 300
SSC0565.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0565.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 600 | 3 | 18 | 304 | 300
SSC0565.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 99 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0566.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 600 | 3 | 18 | 304 | 300
SSC0566.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0566.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 600 | 3 | 18 | 304 | 300
SSC0566.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0567.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 600 | 3 | 18 | 304 | 300
SSC0567.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0567.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 600 | 3 | 18 | 304 | 300
SSC0567.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0568.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 600 | 3 | 18 | 304 | 300
SSC0568.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0568.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 600 | 3 | 18 | 304 | 300
SSC0568.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0569.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 600 | 3 | 18 | 304 | 300
SSC0569.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0569.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 600 | 3 | 18 | 304 | 300
SSC0569.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0570.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 600 | 3 | 18 | 304 | 300
SSC0570.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0570.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 600 | 3 | 18 | 304 | 300
SSC0570.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0571.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 600 | 3 | 18 | 304 | 300
SSC0571.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0571.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 600 | 3 | 18 | 304 | 300
SSC0571.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0572.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 600 | 3 | 18 | 304 | 300
SSC0572.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0572.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 600 | 3 | 18 | 304 | 300
SSC0572.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0573.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400K5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 600 | 3 | 18 | 304 | 300
SSC0573.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400K5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0573.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400K5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 600 | 3 | 18 | 304 | 300
SSC0573.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400K5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0574.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 600 | 3 | 18 | 304 | 300
SSC0574.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0574.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 600 | 3 | 18 | 304 | 300
SSC0574.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0575.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400W5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 600 | 3 | 18 | 304 | 300
SSC0575.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400W5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0575.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400W5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 600 | 3 | 18 | 304 | 300
SSC0575.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400W5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 600 | 3 | 18 | 304 | 300
SSC0576.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0576.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0576.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0576.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0577.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0577.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0577.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0577.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0578.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0578.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0578.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0578.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0579.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0579.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0579.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0579.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0580.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0580.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0580.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0580.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0581.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 200 | 3 | 18 | 304 | 100
SSC0581.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0581.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 200 | 3 | 18 | 304 | 100
SSC0581.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 200 | 3 | 18 | 304 | 100
SSC0582.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 208 | 3 | 18 | 304 | 100
SSC0582.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0582.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 208 | 3 | 18 | 304 | 100
SSC0582.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0583.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 208 | 3 | 18 | 304 | 100
SSC0583.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0583.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 208 | 3 | 18 | 304 | 100
SSC0583.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0584.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 208 | 3 | 18 | 304 | 100
SSC0584.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0584.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 208 | 3 | 18 | 304 | 100
SSC0584.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0585.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 208 | 3 | 18 | 304 | 100
SSC0585.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0585.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 208 | 3 | 18 | 304 | 100
SSC0585.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0586.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 208 | 3 | 18 | 304 | 100
SSC0586.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0586.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 208 | 3 | 18 | 304 | 100
SSC0586.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 208 | 3 | 18 | 304 | 100
SSC0587.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 240 | 3 | 18 | 304 | 100
SSC0587.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0587.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 240 | 3 | 18 | 304 | 100
SSC0587.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0588.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 240 | 3 | 18 | 304 | 100
SSC0588.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0588.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 240 | 3 | 18 | 304 | 100
SSC0588.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0589.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 240 | 3 | 18 | 304 | 100
SSC0589.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0589.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 240 | 3 | 18 | 304 | 100
SSC0589.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0590.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 240 | 3 | 18 | 304 | 100
SSC0590.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0590.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 240 | 3 | 18 | 304 | 100
SSC0590.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 240 | 3 | 18 | 304 | 100
SSC0591.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0591.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0591.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0591.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0592.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0592.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0592.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0592.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0593.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0593.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0593.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0593.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0594.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0594.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0594.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0594.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0595.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0595.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0595.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0595.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0596.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801T30N3S | 480 | 3 | 18 | 304 | 250
SSC0596.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0596.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811T30N3S | 480 | 3 | 18 | 304 | 250
SSC0596.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+T30N3S | 480 | 3 | 18 | 304 | 250
SSC0597.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 200 | 3 | 42 | 360 | 125
SSC0597.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0597.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 200 | 3 | 42 | 360 | 125
SSC0597.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0598.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 200 | 3 | 42 | 360 | 125
SSC0598.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0598.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 200 | 3 | 42 | 360 | 125
SSC0598.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0599.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 200 | 3 | 42 | 360 | 125
SSC0599.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0599.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 200 | 3 | 42 | 360 | 125
SSC0599.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0600.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 200 | 3 | 42 | 360 | 125
SSC0600.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0600.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 200 | 3 | 42 | 360 | 125
SSC0600.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0601.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 200 | 3 | 42 | 360 | 125
SSC0601.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0601.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 200 | 3 | 42 | 360 | 125
SSC0601.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0602.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 200 | 3 | 42 | 360 | 125
SSC0602.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0602.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 200 | 3 | 42 | 360 | 125
SSC0602.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0603.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 200 | 3 | 42 | 360 | 125
SSC0603.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0603.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 200 | 3 | 42 | 360 | 125
SSC0603.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0604.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 200 | 3 | 42 | 360 | 125
SSC0604.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0604.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 200 | 3 | 42 | 360 | 125
SSC0604.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0605.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 200 | 3 | 42 | 360 | 125
SSC0605.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0605.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 200 | 3 | 42 | 360 | 125
SSC0605.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0606.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 200 | 3 | 42 | 360 | 125
SSC0606.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0606.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 200 | 3 | 42 | 360 | 125
SSC0606.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0607.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 200 | 3 | 42 | 360 | 125
SSC0607.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0607.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 200 | 3 | 42 | 360 | 125
SSC0607.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0608.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 200 | 3 | 42 | 360 | 125
SSC0608.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0608.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 200 | 3 | 42 | 360 | 125
SSC0608.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 200 | 3 | 42 | 360 | 125
SSC0609.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 208 | 3 | 42 | 360 | 125
SSC0609.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0609.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 208 | 3 | 42 | 360 | 125
SSC0609.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0610.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 208 | 3 | 42 | 360 | 125
SSC0610.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0610.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 208 | 3 | 42 | 360 | 125
SSC0610.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0611.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 208 | 3 | 42 | 360 | 125
SSC0611.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0611.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 208 | 3 | 42 | 360 | 125
SSC0611.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0612.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 208 | 3 | 42 | 360 | 125
SSC0612.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0612.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 208 | 3 | 42 | 360 | 125
SSC0612.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0613.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 208 | 3 | 42 | 360 | 125
SSC0613.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0613.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 208 | 3 | 42 | 360 | 125
SSC0613.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0614.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 208 | 3 | 42 | 360 | 125
SSC0614.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0614.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 208 | 3 | 42 | 360 | 125
SSC0614.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0615.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 208 | 3 | 42 | 360 | 125
SSC0615.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0615.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 208 | 3 | 42 | 360 | 125
SSC0615.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0616.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 208 | 3 | 42 | 360 | 125
SSC0616.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0616.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 208 | 3 | 42 | 360 | 125
SSC0616.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0617.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 208 | 3 | 42 | 360 | 125
SSC0617.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0617.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 208 | 3 | 42 | 360 | 125
SSC0617.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0618.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 208 | 3 | 42 | 360 | 125
SSC0618.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0618.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 208 | 3 | 42 | 360 | 125
SSC0618.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0619.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 208 | 3 | 42 | 360 | 125
SSC0619.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0619.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 208 | 3 | 42 | 360 | 125
SSC0619.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0620.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 208 | 3 | 42 | 360 | 125
SSC0620.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0620.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 208 | 3 | 42 | 360 | 125
SSC0620.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 208 | 3 | 42 | 360 | 125
SSC0621.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 240 | 3 | 42 | 360 | 150
SSC0621.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0621.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 240 | 3 | 42 | 360 | 150
SSC0621.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0622.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 240 | 3 | 42 | 360 | 150
SSC0622.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0622.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 240 | 3 | 42 | 360 | 150
SSC0622.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0623.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 240 | 3 | 42 | 360 | 150
SSC0623.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0623.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 240 | 3 | 42 | 360 | 150
SSC0623.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0624.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 240 | 3 | 42 | 360 | 150
SSC0624.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0624.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 240 | 3 | 42 | 360 | 150
SSC0624.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0625.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 240 | 3 | 42 | 360 | 150
SSC0625.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0625.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 240 | 3 | 42 | 360 | 150
SSC0625.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0626.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 240 | 3 | 42 | 360 | 150
SSC0626.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0626.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 240 | 3 | 42 | 360 | 150
SSC0626.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0627.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 240 | 3 | 42 | 360 | 150
SSC0627.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0627.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 240 | 3 | 42 | 360 | 150
SSC0627.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0628.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 240 | 3 | 42 | 360 | 150
SSC0628.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0628.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 240 | 3 | 42 | 360 | 150
SSC0628.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0629.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 240 | 3 | 42 | 360 | 150
SSC0629.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0629.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 240 | 3 | 42 | 360 | 150
SSC0629.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0630.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 240 | 3 | 42 | 360 | 150
SSC0630.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0630.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 240 | 3 | 42 | 360 | 150
SSC0630.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0631.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 240 | 3 | 42 | 360 | 150
SSC0631.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0631.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 240 | 3 | 42 | 360 | 150
SSC0631.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0632.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 240 | 3 | 42 | 360 | 150
SSC0632.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0632.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 240 | 3 | 42 | 360 | 150
SSC0632.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 240 | 3 | 42 | 360 | 150
SSC0633.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 480 | 3 | 42 | 360 | 250
SSC0633.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0633.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 480 | 3 | 42 | 360 | 250
SSC0633.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0634.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 480 | 3 | 42 | 360 | 250
SSC0634.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0634.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 480 | 3 | 42 | 360 | 250
SSC0634.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0635.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 480 | 3 | 42 | 360 | 250
SSC0635.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0635.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 480 | 3 | 42 | 360 | 250
SSC0635.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0636.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 480 | 3 | 42 | 360 | 250
SSC0636.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0636.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 480 | 3 | 42 | 360 | 250
SSC0636.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0637.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 480 | 3 | 42 | 360 | 250
SSC0637.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0637.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 480 | 3 | 42 | 360 | 250
SSC0637.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0638.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 480 | 3 | 42 | 360 | 250
SSC0638.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0638.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 480 | 3 | 42 | 360 | 250
SSC0638.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0639.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 480 | 3 | 42 | 360 | 250
SSC0639.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0639.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 480 | 3 | 42 | 360 | 250
SSC0639.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0640.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 480 | 3 | 42 | 360 | 250
SSC0640.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0640.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 480 | 3 | 42 | 360 | 250
SSC0640.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0641.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 480 | 3 | 42 | 360 | 250
SSC0641.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0641.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 480 | 3 | 42 | 360 | 250
SSC0641.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0642.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 480 | 3 | 42 | 360 | 250
SSC0642.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0642.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 480 | 3 | 42 | 360 | 250
SSC0642.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 480 | 3 | 42 | 360 | 250
SSC0643.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 600 | 3 | 42 | 360 | 350
SSC0643.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0643.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 600 | 3 | 42 | 360 | 350
SSC0643.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0644.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 600 | 3 | 42 | 360 | 350
SSC0644.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0644.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 600 | 3 | 42 | 360 | 350
SSC0644.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0645.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 600 | 3 | 42 | 360 | 350
SSC0645.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0645.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 600 | 3 | 42 | 360 | 350
SSC0645.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0646.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 600 | 3 | 42 | 360 | 350
SSC0646.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0646.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 600 | 3 | 42 | 360 | 350
SSC0646.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0647.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 600 | 3 | 42 | 360 | 350
SSC0647.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0647.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 600 | 3 | 42 | 360 | 350
SSC0647.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0648.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 600 | 3 | 42 | 360 | 350
SSC0648.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0648.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 600 | 3 | 42 | 360 | 350
SSC0648.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0649.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 600 | 3 | 42 | 360 | 350
SSC0649.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0649.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 600 | 3 | 42 | 360 | 350
SSC0649.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0650.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 600 | 3 | 42 | 360 | 350
SSC0650.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0650.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 600 | 3 | 42 | 360 | 350
SSC0650.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0651.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 600 | 3 | 42 | 360 | 350
SSC0651.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0651.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 600 | 3 | 42 | 360 | 350
SSC0651.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0652.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 600 | 3 | 42 | 360 | 350
SSC0652.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0652.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 600 | 3 | 42 | 360 | 350
SSC0652.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0653.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 600 | 3 | 42 | 360 | 350
SSC0653.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0653.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 600 | 3 | 42 | 360 | 350
SSC0653.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0654.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V36N3S | 600 | 3 | 42 | 360 | 350
SSC0654.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0654.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V36N3S | 600 | 3 | 42 | 360 | 350
SSC0654.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V36N3S | 600 | 3 | 42 | 360 | 350
SSC0655.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 200 | 3 | 42 | 420 | 150
SSC0655.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0655.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 200 | 3 | 42 | 420 | 150
SSC0655.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0656.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 200 | 3 | 42 | 420 | 150
SSC0656.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0656.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 200 | 3 | 42 | 420 | 150
SSC0656.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0657.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 200 | 3 | 42 | 420 | 150
SSC0657.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0657.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 200 | 3 | 42 | 420 | 150
SSC0657.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0658.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 200 | 3 | 42 | 420 | 150
SSC0658.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0658.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 200 | 3 | 42 | 420 | 150
SSC0658.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0659.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 200 | 3 | 42 | 420 | 150
SSC0659.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0659.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 200 | 3 | 42 | 420 | 150
SSC0659.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0660.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 200 | 3 | 42 | 420 | 150
SSC0660.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0660.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 200 | 3 | 42 | 420 | 150
SSC0660.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0661.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 200 | 3 | 42 | 420 | 150
SSC0661.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0661.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 200 | 3 | 42 | 420 | 150
SSC0661.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0662.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 200 | 3 | 42 | 420 | 150
SSC0662.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0662.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 200 | 3 | 42 | 420 | 150
SSC0662.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0663.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 200 | 3 | 42 | 420 | 150
SSC0663.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0663.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 200 | 3 | 42 | 420 | 150
SSC0663.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0664.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 200 | 3 | 42 | 420 | 150
SSC0664.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0664.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 200 | 3 | 42 | 420 | 150
SSC0664.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0665.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 200 | 3 | 42 | 420 | 150
SSC0665.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0665.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 200 | 3 | 42 | 420 | 150
SSC0665.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0666.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 200 | 3 | 42 | 420 | 150
SSC0666.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0666.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 200 | 3 | 42 | 420 | 150
SSC0666.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 200 | 3 | 42 | 420 | 150
SSC0667.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 208 | 3 | 42 | 420 | 150
SSC0667.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0667.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 208 | 3 | 42 | 420 | 150
SSC0667.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0668.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 208 | 3 | 42 | 420 | 150
SSC0668.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0668.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 208 | 3 | 42 | 420 | 150
SSC0668.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0669.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 208 | 3 | 42 | 420 | 150
SSC0669.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0669.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 208 | 3 | 42 | 420 | 150
SSC0669.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0670.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 208 | 3 | 42 | 420 | 150
SSC0670.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0670.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 208 | 3 | 42 | 420 | 150
SSC0670.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0671.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 208 | 3 | 42 | 420 | 150
SSC0671.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0671.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 208 | 3 | 42 | 420 | 150
SSC0671.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0672.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 208 | 3 | 42 | 420 | 150
SSC0672.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0672.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 208 | 3 | 42 | 420 | 150
SSC0672.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0673.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 208 | 3 | 42 | 420 | 150
SSC0673.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0673.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 208 | 3 | 42 | 420 | 150
SSC0673.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0674.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 208 | 3 | 42 | 420 | 150
SSC0674.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0674.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 208 | 3 | 42 | 420 | 150
SSC0674.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0675.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 208 | 3 | 42 | 420 | 150
SSC0675.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0675.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 208 | 3 | 42 | 420 | 150
SSC0675.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0676.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 208 | 3 | 42 | 420 | 150
SSC0676.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0676.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 208 | 3 | 42 | 420 | 150
SSC0676.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0677.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 208 | 3 | 42 | 420 | 150
SSC0677.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0677.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 208 | 3 | 42 | 420 | 150
SSC0677.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0678.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 208 | 3 | 42 | 420 | 150
SSC0678.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0678.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 208 | 3 | 42 | 420 | 150
SSC0678.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 208 | 3 | 42 | 420 | 150
SSC0679.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 240 | 3 | 42 | 420 | 150
SSC0679.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0679.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 240 | 3 | 42 | 420 | 150
SSC0679.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0680.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 240 | 3 | 42 | 420 | 150
SSC0680.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0680.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 240 | 3 | 42 | 420 | 150
SSC0680.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0681.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 240 | 3 | 42 | 420 | 150
SSC0681.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0681.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 240 | 3 | 42 | 420 | 150
SSC0681.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0682.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 240 | 3 | 42 | 420 | 150
SSC0682.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0682.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 240 | 3 | 42 | 420 | 150
SSC0682.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0683.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 240 | 3 | 42 | 420 | 150
SSC0683.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0683.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 240 | 3 | 42 | 420 | 150
SSC0683.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0684.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 240 | 3 | 42 | 420 | 150
SSC0684.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0684.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 240 | 3 | 42 | 420 | 150
SSC0684.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0685.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 240 | 3 | 42 | 420 | 150
SSC0685.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0685.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 240 | 3 | 42 | 420 | 150
SSC0685.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0686.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 240 | 3 | 42 | 420 | 150
SSC0686.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0686.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 240 | 3 | 42 | 420 | 150
SSC0686.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0687.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 240 | 3 | 42 | 420 | 150
SSC0687.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0687.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 240 | 3 | 42 | 420 | 150
SSC0687.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0688.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 240 | 3 | 42 | 420 | 150
SSC0688.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0688.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 240 | 3 | 42 | 420 | 150
SSC0688.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 240 | 3 | 42 | 420 | 150
SSC0689.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 480 | 3 | 42 | 420 | 350
SSC0689.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0689.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 480 | 3 | 42 | 420 | 350
SSC0689.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0690.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 480 | 3 | 42 | 420 | 350
SSC0690.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0690.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 480 | 3 | 42 | 420 | 350
SSC0690.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0691.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 480 | 3 | 42 | 420 | 350
SSC0691.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0691.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 480 | 3 | 42 | 420 | 350
SSC0691.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0692.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 480 | 3 | 42 | 420 | 350
SSC0692.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0692.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 480 | 3 | 42 | 420 | 350
SSC0692.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0693.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 480 | 3 | 42 | 420 | 350
SSC0693.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0693.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 480 | 3 | 42 | 420 | 350
SSC0693.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0694.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 480 | 3 | 42 | 420 | 350
SSC0694.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0694.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 480 | 3 | 42 | 420 | 350
SSC0694.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0695.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 480 | 3 | 42 | 420 | 350
SSC0695.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0695.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 480 | 3 | 42 | 420 | 350
SSC0695.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0696.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 480 | 3 | 42 | 420 | 350
SSC0696.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0696.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 480 | 3 | 42 | 420 | 350
SSC0696.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0697.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 302 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 480 | 3 | 42 | 420 | 350
SSC0697.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 302 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0697.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 302 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 480 | 3 | 42 | 420 | 350
SSC0697.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 302 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0698.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 302 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 480 | 3 | 42 | 420 | 350
SSC0698.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 302 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0698.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 302 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 480 | 3 | 42 | 420 | 350
SSC0698.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 302 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0699.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 480 | 3 | 42 | 420 | 350
SSC0699.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0699.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 480 | 3 | 42 | 420 | 350
SSC0699.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0700.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 480 | 3 | 42 | 420 | 350
SSC0700.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0700.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 480 | 3 | 42 | 420 | 350
SSC0700.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 480 | 3 | 42 | 420 | 350
SSC0701.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 600 | 3 | 42 | 420 | 450
SSC0701.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0701.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 600 | 3 | 42 | 420 | 450
SSC0701.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0702.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 600 | 3 | 42 | 420 | 450
SSC0702.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0702.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 600 | 3 | 42 | 420 | 450
SSC0702.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0703.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 600 | 3 | 42 | 420 | 450
SSC0703.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0703.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 600 | 3 | 42 | 420 | 450
SSC0703.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0704.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 600 | 3 | 42 | 420 | 450
SSC0704.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0704.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 600 | 3 | 42 | 420 | 450
SSC0704.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0705.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 600 | 3 | 42 | 420 | 450
SSC0705.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0705.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 600 | 3 | 42 | 420 | 450
SSC0705.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0706.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 600 | 3 | 42 | 420 | 450
SSC0706.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0706.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 600 | 3 | 42 | 420 | 450
SSC0706.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0707.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 600 | 3 | 42 | 420 | 450
SSC0707.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0707.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 600 | 3 | 42 | 420 | 450
SSC0707.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0708.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 600 | 3 | 42 | 420 | 450
SSC0708.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0708.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 600 | 3 | 42 | 420 | 450
SSC0708.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0709.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 600 | 3 | 42 | 420 | 450
SSC0709.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0709.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 600 | 3 | 42 | 420 | 450
SSC0709.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0710.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 600 | 3 | 42 | 420 | 450
SSC0710.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0710.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 600 | 3 | 42 | 420 | 450
SSC0710.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0711.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 600 | 3 | 42 | 420 | 450
SSC0711.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0711.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 600 | 3 | 42 | 420 | 450
SSC0711.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0712.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 600 | 3 | 42 | 420 | 450
SSC0712.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0712.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 600 | 3 | 42 | 420 | 450
SSC0712.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0713.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 600 | 3 | 42 | 420 | 450
SSC0713.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0713.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 600 | 3 | 42 | 420 | 450
SSC0713.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0714.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V42N3S | 600 | 3 | 42 | 420 | 450
SSC0714.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0714.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V42N3S | 600 | 3 | 42 | 420 | 450
SSC0714.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V42N3S | 600 | 3 | 42 | 420 | 450
SSC0715.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 200 | 3 | 42 | 500 | 150
SSC0715.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0715.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 200 | 3 | 42 | 500 | 150
SSC0715.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0716.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 200 | 3 | 42 | 500 | 150
SSC0716.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0716.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 200 | 3 | 42 | 500 | 150
SSC0716.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0717.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 200 | 3 | 42 | 500 | 150
SSC0717.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0717.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 200 | 3 | 42 | 500 | 150
SSC0717.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0718.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 200 | 3 | 42 | 500 | 150
SSC0718.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0718.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 200 | 3 | 42 | 500 | 150
SSC0718.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0719.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 200 | 3 | 42 | 500 | 150
SSC0719.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0719.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 200 | 3 | 42 | 500 | 150
SSC0719.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0720.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 200 | 3 | 42 | 500 | 150
SSC0720.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0720.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 200 | 3 | 42 | 500 | 150
SSC0720.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0721.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 200 | 3 | 42 | 500 | 150
SSC0721.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0721.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 200 | 3 | 42 | 500 | 150
SSC0721.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0722.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 200 | 3 | 42 | 500 | 150
SSC0722.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0722.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 200 | 3 | 42 | 500 | 150
SSC0722.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0723.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 200 | 3 | 42 | 500 | 150
SSC0723.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0723.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 200 | 3 | 42 | 500 | 150
SSC0723.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0724.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 200 | 3 | 42 | 500 | 150
SSC0724.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0724.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 200 | 3 | 42 | 500 | 150
SSC0724.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 200 | 3 | 42 | 500 | 150
SSC0725.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 208 | 3 | 42 | 500 | 150
SSC0725.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0725.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 208 | 3 | 42 | 500 | 150
SSC0725.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0726.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 208 | 3 | 42 | 500 | 150
SSC0726.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0726.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 208 | 3 | 42 | 500 | 150
SSC0726.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0727.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 208 | 3 | 42 | 500 | 150
SSC0727.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0727.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 208 | 3 | 42 | 500 | 150
SSC0727.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0728.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 208 | 3 | 42 | 500 | 150
SSC0728.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0728.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 208 | 3 | 42 | 500 | 150
SSC0728.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0729.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 208 | 3 | 42 | 500 | 150
SSC0729.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0729.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 208 | 3 | 42 | 500 | 150
SSC0729.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0730.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 208 | 3 | 42 | 500 | 150
SSC0730.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0730.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 208 | 3 | 42 | 500 | 150
SSC0730.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0731.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 208 | 3 | 42 | 500 | 150
SSC0731.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0731.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 208 | 3 | 42 | 500 | 150
SSC0731.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0732.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 208 | 3 | 42 | 500 | 150
SSC0732.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0732.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 208 | 3 | 42 | 500 | 150
SSC0732.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0733.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 208 | 3 | 42 | 500 | 150
SSC0733.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0733.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 208 | 3 | 42 | 500 | 150
SSC0733.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0734.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 208 | 3 | 42 | 500 | 150
SSC0734.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0734.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 208 | 3 | 42 | 500 | 150
SSC0734.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 208 | 3 | 42 | 500 | 150
SSC0735.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 240 | 3 | 42 | 500 | 200
SSC0735.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 240 | 3 | 42 | 500 | 200
SSC0735.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 240 | 3 | 42 | 500 | 200
SSC0735.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 240 | 3 | 42 | 500 | 200
SSC0736.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 240 | 3 | 42 | 500 | 200
SSC0736.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 240 | 3 | 42 | 500 | 200
SSC0736.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 240 | 3 | 42 | 500 | 200
SSC0736.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 240 | 3 | 42 | 500 | 200
SSC0737.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 240 | 3 | 42 | 500 | 200
SSC0737.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 240 | 3 | 42 | 500 | 200
SSC0737.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 240 | 3 | 42 | 500 | 200
SSC0737.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 240 | 3 | 42 | 500 | 200
SSC0738.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 240 | 3 | 42 | 500 | 200
SSC0738.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 240 | 3 | 42 | 500 | 200
SSC0738.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 240 | 3 | 42 | 500 | 200
SSC0738.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 240 | 3 | 42 | 500 | 200
SSC0739.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 240 | 3 | 42 | 500 | 200
SSC0739.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 240 | 3 | 42 | 500 | 200
SSC0739.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 240 | 3 | 42 | 500 | 200
SSC0739.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 240 | 3 | 42 | 500 | 200
SSC0740.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 240 | 3 | 42 | 500 | 200
SSC0740.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 240 | 3 | 42 | 500 | 200
SSC0740.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 240 | 3 | 42 | 500 | 200
SSC0740.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 240 | 3 | 42 | 500 | 200
SSC0741.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 240 | 3 | 42 | 500 | 200
SSC0741.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 240 | 3 | 42 | 500 | 200
SSC0741.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 240 | 3 | 42 | 500 | 200
SSC0741.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 240 | 3 | 42 | 500 | 200
SSC0742.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 240 | 3 | 42 | 500 | 200
SSC0742.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 240 | 3 | 42 | 500 | 200
SSC0742.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 240 | 3 | 42 | 500 | 200
SSC0742.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 240 | 3 | 42 | 500 | 200
SSC0743.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 200 | 240 | 3 | 65 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 240 | 3 | 42 | 500 | 200
SSC0743.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 200 | 240 | 3 | 65 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 240 | 3 | 42 | 500 | 200
SSC0743.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 200 | 240 | 3 | 65 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 240 | 3 | 42 | 500 | 200
SSC0743.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 200 | 240 | 3 | 65 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 240 | 3 | 42 | 500 | 200
SSC0744.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 200 | 240 | 3 | 65 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 240 | 3 | 42 | 500 | 200
SSC0744.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 200 | 240 | 3 | 65 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 240 | 3 | 42 | 500 | 200
SSC0744.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 200 | 240 | 3 | 65 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 240 | 3 | 42 | 500 | 200
SSC0744.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 200 | 240 | 3 | 65 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 240 | 3 | 42 | 500 | 200
SSC0745.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 480 | 3 | 42 | 500 | 400
SSC0745.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0745.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 480 | 3 | 42 | 500 | 400
SSC0745.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 50 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0746.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 480 | 3 | 42 | 500 | 400
SSC0746.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0746.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 480 | 3 | 42 | 500 | 400
SSC0746.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0747.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 480 | 3 | 42 | 500 | 400
SSC0747.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0747.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 480 | 3 | 42 | 500 | 400
SSC0747.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0748.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 480 | 3 | 42 | 500 | 400
SSC0748.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0748.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 480 | 3 | 42 | 500 | 400
SSC0748.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0749.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 480 | 3 | 42 | 500 | 400
SSC0749.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0749.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 480 | 3 | 42 | 500 | 400
SSC0749.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0750.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 480 | 3 | 42 | 500 | 400
SSC0750.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0750.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 480 | 3 | 42 | 500 | 400
SSC0750.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0751.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 480 | 3 | 42 | 500 | 400
SSC0751.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0751.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 480 | 3 | 42 | 500 | 400
SSC0751.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0752.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 480 | 3 | 42 | 500 | 400
SSC0752.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0752.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 480 | 3 | 42 | 500 | 400
SSC0752.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0753.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 480 | 3 | 42 | 500 | 400
SSC0753.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0753.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 480 | 3 | 42 | 500 | 400
SSC0753.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0754.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 480 | 3 | 42 | 500 | 400
SSC0754.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0754.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 480 | 3 | 42 | 500 | 400
SSC0754.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0755.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 480 | 3 | 42 | 500 | 400
SSC0755.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0755.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 480 | 3 | 42 | 500 | 400
SSC0755.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0756.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 480 | 3 | 42 | 500 | 400
SSC0756.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0756.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 480 | 3 | 42 | 500 | 400
SSC0756.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0757.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 480 | 3 | 42 | 500 | 400
SSC0757.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0757.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 480 | 3 | 42 | 500 | 400
SSC0757.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0758.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 500 | 480 | 3 | 50 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 480 | 3 | 42 | 500 | 400
SSC0758.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 500 | 480 | 3 | 50 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0758.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 500 | 480 | 3 | 50 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 480 | 3 | 42 | 500 | 400
SSC0758.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 500 | 480 | 3 | 50 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 480 | 3 | 42 | 500 | 400
SSC0759.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 600 | 3 | 42 | 500 | 500
SSC0759.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0759.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 600 | 3 | 42 | 500 | 500
SSC0759.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0760.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 600 | 3 | 42 | 500 | 500
SSC0760.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0760.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 600 | 3 | 42 | 500 | 500
SSC0760.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0761.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 600 | 3 | 42 | 500 | 500
SSC0761.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0761.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 600 | 3 | 42 | 500 | 500
SSC0761.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0762.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 600 | 3 | 42 | 500 | 500
SSC0762.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0762.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 600 | 3 | 42 | 500 | 500
SSC0762.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0763.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 600 | 3 | 42 | 500 | 500
SSC0763.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0763.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 600 | 3 | 42 | 500 | 500
SSC0763.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0764.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 600 | 3 | 42 | 500 | 500
SSC0764.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0764.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 600 | 3 | 42 | 500 | 500
SSC0764.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0765.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 600 | 3 | 42 | 500 | 500
SSC0765.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0765.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 600 | 3 | 42 | 500 | 500
SSC0765.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0766.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 600 | 3 | 42 | 500 | 500
SSC0766.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0766.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 600 | 3 | 42 | 500 | 500
SSC0766.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0767.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 600 | 3 | 42 | 500 | 500
SSC0767.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0767.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 600 | 3 | 42 | 500 | 500
SSC0767.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0768.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 600 | 3 | 42 | 500 | 500
SSC0768.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0768.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 600 | 3 | 42 | 500 | 500
SSC0768.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0769.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 600 | 3 | 42 | 500 | 500
SSC0769.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0769.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 600 | 3 | 42 | 500 | 500
SSC0769.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0770.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 600 | 3 | 42 | 500 | 500
SSC0770.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0770.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 600 | 3 | 42 | 500 | 500
SSC0770.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0771.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 600 | 3 | 42 | 500 | 500
SSC0771.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0771.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 600 | 3 | 42 | 500 | 500
SSC0771.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0772.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V50N3S | 600 | 3 | 42 | 500 | 500
SSC0772.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0772.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V50N3S | 600 | 3 | 42 | 500 | 500
SSC0772.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 50 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V50N3S | 600 | 3 | 42 | 500 | 500
SSC0773.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 200 | 3 | 42 | 650 | 200
SSC0773.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0773.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 200 | 3 | 42 | 650 | 200
SSC0773.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0774.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 200 | 3 | 42 | 650 | 200
SSC0774.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0774.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 200 | 3 | 42 | 650 | 200
SSC0774.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0775.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 200 | 3 | 42 | 650 | 200
SSC0775.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0775.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 200 | 3 | 42 | 650 | 200
SSC0775.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0776.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 200 | 3 | 42 | 650 | 200
SSC0776.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0776.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 200 | 3 | 42 | 650 | 200
SSC0776.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0777.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 200 | 3 | 42 | 650 | 200
SSC0777.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0777.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 200 | 3 | 42 | 650 | 200
SSC0777.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0778.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 200 | 3 | 42 | 650 | 200
SSC0778.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0778.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 200 | 3 | 42 | 650 | 200
SSC0778.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0779.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 200 | 3 | 42 | 650 | 200
SSC0779.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0779.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 200 | 3 | 42 | 650 | 200
SSC0779.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0780.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 200 | 3 | 42 | 650 | 200
SSC0780.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0780.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 200 | 3 | 42 | 650 | 200
SSC0780.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0781.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 200 | 3 | 42 | 650 | 200
SSC0781.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0781.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 200 | 3 | 42 | 650 | 200
SSC0781.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 200 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0782.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 200 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 200 | 3 | 42 | 650 | 200
SSC0782.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 200 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0782.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 200 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 200 | 3 | 42 | 650 | 200
SSC0782.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 200 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 200 | 3 | 42 | 650 | 200
SSC0783.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 208 | 3 | 42 | 650 | 200
SSC0783.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0783.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 208 | 3 | 42 | 650 | 200
SSC0783.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0784.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 208 | 3 | 42 | 650 | 200
SSC0784.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0784.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 208 | 3 | 42 | 650 | 200
SSC0784.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0785.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 208 | 3 | 42 | 650 | 200
SSC0785.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0785.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 208 | 3 | 42 | 650 | 200
SSC0785.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0786.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 208 | 3 | 42 | 650 | 200
SSC0786.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0786.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 208 | 3 | 42 | 650 | 200
SSC0786.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0787.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 208 | 3 | 42 | 650 | 200
SSC0787.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0787.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 208 | 3 | 42 | 650 | 200
SSC0787.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0788.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 208 | 3 | 42 | 650 | 200
SSC0788.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0788.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 208 | 3 | 42 | 650 | 200
SSC0788.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0789.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 208 | 3 | 42 | 650 | 200
SSC0789.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0789.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 208 | 3 | 42 | 650 | 200
SSC0789.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0790.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 208 | 3 | 42 | 650 | 200
SSC0790.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0790.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 208 | 3 | 42 | 650 | 200
SSC0790.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0791.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 208 | 3 | 42 | 650 | 200
SSC0791.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0791.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 208 | 3 | 42 | 650 | 200
SSC0791.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 200 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0792.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 200 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 208 | 3 | 42 | 650 | 200
SSC0792.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 200 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0792.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 200 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 208 | 3 | 42 | 650 | 200
SSC0792.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 200 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 208 | 3 | 42 | 650 | 200
SSC0793.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 240 | 3 | 42 | 650 | 250
SSC0793.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0793.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 240 | 3 | 42 | 650 | 250
SSC0793.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0794.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 240 | 3 | 42 | 650 | 250
SSC0794.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0794.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 240 | 3 | 42 | 650 | 250
SSC0794.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0795.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 240 | 3 | 42 | 650 | 250
SSC0795.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0795.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 240 | 3 | 42 | 650 | 250
SSC0795.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0796.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 240 | 3 | 42 | 650 | 250
SSC0796.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0796.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 240 | 3 | 42 | 650 | 250
SSC0796.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0797.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 240 | 3 | 42 | 650 | 250
SSC0797.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0797.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 240 | 3 | 42 | 650 | 250
SSC0797.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0798.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 240 | 3 | 42 | 650 | 250
SSC0798.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0798.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 240 | 3 | 42 | 650 | 250
SSC0798.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0799.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 240 | 3 | 42 | 650 | 250
SSC0799.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0799.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 240 | 3 | 42 | 650 | 250
SSC0799.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0800.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 300 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 240 | 3 | 42 | 650 | 250
SSC0800.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 300 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0800.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 300 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 240 | 3 | 42 | 650 | 250
SSC0800.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 300 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0801.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 240 | 3 | 42 | 650 | 250
SSC0801.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0801.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 240 | 3 | 42 | 650 | 250
SSC0801.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0802.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 300 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 240 | 3 | 42 | 650 | 250
SSC0802.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 300 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0802.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 300 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 240 | 3 | 42 | 650 | 250
SSC0802.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 300 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 240 | 3 | 42 | 650 | 250
SSC0803.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 480 | 3 | 42 | 650 | 500
SSC0803.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0803.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 480 | 3 | 42 | 650 | 500
SSC0803.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 50 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0804.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 480 | 3 | 42 | 650 | 500
SSC0804.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0804.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 480 | 3 | 42 | 650 | 500
SSC0804.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 240 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0805.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 480 | 3 | 42 | 650 | 500
SSC0805.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0805.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 480 | 3 | 42 | 650 | 500
SSC0805.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0806.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 480 | 3 | 42 | 650 | 500
SSC0806.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0806.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 480 | 3 | 42 | 650 | 500
SSC0806.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0807.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 480 | 3 | 42 | 650 | 500
SSC0807.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0807.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 480 | 3 | 42 | 650 | 500
SSC0807.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0808.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 480 | 3 | 42 | 650 | 500
SSC0808.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0808.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 480 | 3 | 42 | 650 | 500
SSC0808.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0809.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 480 | 3 | 42 | 650 | 500
SSC0809.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0809.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 480 | 3 | 42 | 650 | 500
SSC0809.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0810.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 480 | 3 | 42 | 650 | 500
SSC0810.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0810.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 480 | 3 | 42 | 650 | 500
SSC0810.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0811.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 480 | 3 | 42 | 650 | 500
SSC0811.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0811.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 480 | 3 | 42 | 650 | 500
SSC0811.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0812.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 500 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 480 | 3 | 42 | 650 | 500
SSC0812.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 500 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0812.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 500 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 480 | 3 | 42 | 650 | 500
SSC0812.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 500 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0813.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 480 | 3 | 42 | 650 | 500
SSC0813.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0813.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 480 | 3 | 42 | 650 | 500
SSC0813.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0814.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 500 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 480 | 3 | 42 | 650 | 500
SSC0814.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 500 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0814.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 500 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 480 | 3 | 42 | 650 | 500
SSC0814.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 500 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0815.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 480 | 3 | 42 | 650 | 500
SSC0815.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0815.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 480 | 3 | 42 | 650 | 500
SSC0815.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0816.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 500 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 480 | 3 | 42 | 650 | 500
SSC0816.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 500 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0816.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 500 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 480 | 3 | 42 | 650 | 500
SSC0816.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 500 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 480 | 3 | 42 | 650 | 500
SSC0817.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 25 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 600 | 3 | 42 | 650 | 600
SSC0817.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 25 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 600 | 3 | 42 | 650 | 600
SSC0817.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 25 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 600 | 3 | 42 | 650 | 600
SSC0817.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 25 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 600 | 3 | 42 | 650 | 600
SSC0818.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 600 | 3 | 42 | 650 | 600
SSC0818.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 600 | 3 | 42 | 650 | 600
SSC0818.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 600 | 3 | 42 | 650 | 600
SSC0818.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 242 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 600 | 3 | 42 | 650 | 600
SSC0819.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 600 | 3 | 42 | 650 | 600
SSC0819.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 600 | 3 | 42 | 650 | 600
SSC0819.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 600 | 3 | 42 | 650 | 600
SSC0819.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 600 | 3 | 42 | 650 | 600
SSC0820.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 600 | 3 | 42 | 650 | 600
SSC0820.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 600 | 3 | 42 | 650 | 600
SSC0820.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 600 | 3 | 42 | 650 | 600
SSC0820.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 600 | 3 | 42 | 650 | 600
SSC0821.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 600 | 3 | 42 | 650 | 600
SSC0821.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 600 | 3 | 42 | 650 | 600
SSC0821.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 600 | 3 | 42 | 650 | 600
SSC0821.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 600 | 3 | 42 | 650 | 600
SSC0822.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 600 | 3 | 42 | 650 | 600
SSC0822.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 600 | 3 | 42 | 650 | 600
SSC0822.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 600 | 3 | 42 | 650 | 600
SSC0822.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 600 | 3 | 42 | 650 | 600
SSC0823.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 600 | 3 | 42 | 650 | 600
SSC0823.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 600 | 3 | 42 | 650 | 600
SSC0823.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 600 | 3 | 42 | 650 | 600
SSC0823.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 600 | 3 | 42 | 650 | 600
SSC0824.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 600 | 3 | 42 | 650 | 600
SSC0824.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 600 | 3 | 42 | 650 | 600
SSC0824.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 600 | 3 | 42 | 650 | 600
SSC0824.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 600 | 3 | 42 | 650 | 600
SSC0825.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 600 | 3 | 42 | 650 | 600
SSC0825.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 600 | 3 | 42 | 650 | 600
SSC0825.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 600 | 3 | 42 | 650 | 600
SSC0825.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 600 | 3 | 42 | 650 | 600
SSC0826.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 600 | 3 | 42 | 650 | 600
SSC0826.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 600 | 3 | 42 | 650 | 600
SSC0826.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 600 | 3 | 42 | 650 | 600
SSC0826.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 600 | 3 | 42 | 650 | 600
SSC0827.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 600 | 3 | 42 | 650 | 600
SSC0827.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 600 | 3 | 42 | 650 | 600
SSC0827.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 600 | 3 | 42 | 650 | 600
SSC0827.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 600 | 3 | 42 | 650 | 600
SSC0828.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 600 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 600 | 3 | 42 | 650 | 600
SSC0828.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 600 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 600 | 3 | 42 | 650 | 600
SSC0828.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 600 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 600 | 3 | 42 | 650 | 600
SSC0828.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 600 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 600 | 3 | 42 | 650 | 600
SSC0829.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 600 | 3 | 42 | 650 | 600
SSC0829.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 600 | 3 | 42 | 650 | 600
SSC0829.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 600 | 3 | 42 | 650 | 600
SSC0829.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 600 | 3 | 42 | 650 | 600
SSC0830.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 600 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V65N3S | 600 | 3 | 42 | 650 | 600
SSC0830.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 600 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V65N3S | 600 | 3 | 42 | 650 | 600
SSC0830.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 600 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V65N3S | 600 | 3 | 42 | 650 | 600
SSC0830.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 600 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V65N3S | 600 | 3 | 42 | 650 | 600
SSC0831.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 200 | 3 | 42 | 720 | 250
SSC0831.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0831.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 200 | 3 | 42 | 720 | 250
SSC0831.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0832.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 200 | 3 | 42 | 720 | 250
SSC0832.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0832.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 200 | 3 | 42 | 720 | 250
SSC0832.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0833.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 200 | 3 | 42 | 720 | 250
SSC0833.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0833.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 200 | 3 | 42 | 720 | 250
SSC0833.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0834.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 200 | 3 | 42 | 720 | 250
SSC0834.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0834.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 200 | 3 | 42 | 720 | 250
SSC0834.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0835.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 200 | 3 | 42 | 720 | 250
SSC0835.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0835.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 200 | 3 | 42 | 720 | 250
SSC0835.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0836.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 200 | 3 | 42 | 720 | 250
SSC0836.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0836.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 200 | 3 | 42 | 720 | 250
SSC0836.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0837.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 200 | 3 | 42 | 720 | 250
SSC0837.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0837.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 200 | 3 | 42 | 720 | 250
SSC0837.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0838.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 250 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 200 | 3 | 42 | 720 | 250
SSC0838.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 250 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0838.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 250 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 200 | 3 | 42 | 720 | 250
SSC0838.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 250 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0839.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 200 | 3 | 42 | 720 | 250
SSC0839.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0839.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 200 | 3 | 42 | 720 | 250
SSC0839.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0840.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 250 | 200 | 3 | 65 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 200 | 3 | 42 | 720 | 250
SSC0840.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 250 | 200 | 3 | 65 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0840.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 250 | 200 | 3 | 65 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 200 | 3 | 42 | 720 | 250
SSC0840.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 250 | 200 | 3 | 65 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 200 | 3 | 42 | 720 | 250
SSC0841.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 208 | 3 | 42 | 720 | 250
SSC0841.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0841.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 208 | 3 | 42 | 720 | 250
SSC0841.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0842.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 208 | 3 | 42 | 720 | 250
SSC0842.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0842.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 208 | 3 | 42 | 720 | 250
SSC0842.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0843.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 208 | 3 | 42 | 720 | 250
SSC0843.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0843.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 208 | 3 | 42 | 720 | 250
SSC0843.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0844.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 250 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 208 | 3 | 42 | 720 | 250
SSC0844.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 250 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0844.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 250 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 208 | 3 | 42 | 720 | 250
SSC0844.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 250 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0845.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 208 | 3 | 42 | 720 | 250
SSC0845.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0845.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 208 | 3 | 42 | 720 | 250
SSC0845.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0846.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 250 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 208 | 3 | 42 | 720 | 250
SSC0846.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 250 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0846.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 250 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 208 | 3 | 42 | 720 | 250
SSC0846.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 250 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0847.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 250 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 208 | 3 | 42 | 720 | 250
SSC0847.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 250 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0847.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 250 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 208 | 3 | 42 | 720 | 250
SSC0847.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 250 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0848.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 250 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 208 | 3 | 42 | 720 | 250
SSC0848.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 250 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0848.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 250 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 208 | 3 | 42 | 720 | 250
SSC0848.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 250 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0849.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 250 | 208 | 3 | 65 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 208 | 3 | 42 | 720 | 250
SSC0849.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 250 | 208 | 3 | 65 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0849.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 250 | 208 | 3 | 65 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 208 | 3 | 42 | 720 | 250
SSC0849.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 250 | 208 | 3 | 65 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0850.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 250 | 208 | 3 | 65 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 208 | 3 | 42 | 720 | 250
SSC0850.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 250 | 208 | 3 | 65 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0850.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 250 | 208 | 3 | 65 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 208 | 3 | 42 | 720 | 250
SSC0850.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 250 | 208 | 3 | 65 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 208 | 3 | 42 | 720 | 250
SSC0851.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 240 | 3 | 42 | 720 | 250
SSC0851.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 240 | 3 | 42 | 720 | 250
SSC0851.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 240 | 3 | 42 | 720 | 250
SSC0851.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 240 | 3 | 42 | 720 | 250
SSC0852.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 250 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 240 | 3 | 42 | 720 | 250
SSC0852.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 250 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 240 | 3 | 42 | 720 | 250
SSC0852.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 250 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 240 | 3 | 42 | 720 | 250
SSC0852.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 250 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 240 | 3 | 42 | 720 | 250
SSC0853.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 240 | 3 | 42 | 720 | 250
SSC0853.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 240 | 3 | 42 | 720 | 250
SSC0853.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 240 | 3 | 42 | 720 | 250
SSC0853.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 240 | 3 | 42 | 720 | 250
SSC0854.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 250 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 240 | 3 | 42 | 720 | 250
SSC0854.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 250 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 240 | 3 | 42 | 720 | 250
SSC0854.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 250 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 240 | 3 | 42 | 720 | 250
SSC0854.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 250 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 240 | 3 | 42 | 720 | 250
SSC0855.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 250 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 240 | 3 | 42 | 720 | 250
SSC0855.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 250 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 240 | 3 | 42 | 720 | 250
SSC0855.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 250 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 240 | 3 | 42 | 720 | 250
SSC0855.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 250 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 240 | 3 | 42 | 720 | 250
SSC0856.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 250 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 240 | 3 | 42 | 720 | 250
SSC0856.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 250 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 240 | 3 | 42 | 720 | 250
SSC0856.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 250 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 240 | 3 | 42 | 720 | 250
SSC0856.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 250 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 240 | 3 | 42 | 720 | 250
SSC0857.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 250 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 240 | 3 | 42 | 720 | 250
SSC0857.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 250 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 240 | 3 | 42 | 720 | 250
SSC0857.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 250 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 240 | 3 | 42 | 720 | 250
SSC0857.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 250 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 240 | 3 | 42 | 720 | 250
SSC0858.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 250 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 240 | 3 | 42 | 720 | 250
SSC0858.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 250 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 240 | 3 | 42 | 720 | 250
SSC0858.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 250 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 240 | 3 | 42 | 720 | 250
SSC0858.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 250 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 240 | 3 | 42 | 720 | 250
SSC0859.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 480 | 3 | 42 | 720 | 500
SSC0859.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0859.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 480 | 3 | 42 | 720 | 500
SSC0859.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0860.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 480 | 3 | 42 | 720 | 500
SSC0860.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0860.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 480 | 3 | 42 | 720 | 500
SSC0860.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0861.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 480 | 3 | 42 | 720 | 500
SSC0861.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0861.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 480 | 3 | 42 | 720 | 500
SSC0861.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0862.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 480 | 3 | 42 | 720 | 500
SSC0862.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0862.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 480 | 3 | 42 | 720 | 500
SSC0862.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0863.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 480 | 3 | 42 | 720 | 500
SSC0863.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0863.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 480 | 3 | 42 | 720 | 500
SSC0863.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0864.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 480 | 3 | 42 | 720 | 500
SSC0864.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0864.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 480 | 3 | 42 | 720 | 500
SSC0864.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0865.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 480 | 3 | 42 | 720 | 500
SSC0865.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0865.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 480 | 3 | 42 | 720 | 500
SSC0865.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0866.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 500 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 480 | 3 | 42 | 720 | 500
SSC0866.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 500 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0866.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 500 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 480 | 3 | 42 | 720 | 500
SSC0866.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 500 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0867.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 480 | 3 | 42 | 720 | 500
SSC0867.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0867.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 480 | 3 | 42 | 720 | 500
SSC0867.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0868.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 500 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 480 | 3 | 42 | 720 | 500
SSC0868.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 500 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0868.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 500 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 480 | 3 | 42 | 720 | 500
SSC0868.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 500 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0869.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 480 | 3 | 42 | 720 | 500
SSC0869.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0869.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 480 | 3 | 42 | 720 | 500
SSC0869.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 500 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0870.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 500 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 480 | 3 | 42 | 720 | 500
SSC0870.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 500 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0870.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 500 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 480 | 3 | 42 | 720 | 500
SSC0870.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 500 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 480 | 3 | 42 | 720 | 500
SSC0871.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 600 | 3 | 42 | 720 | 600
SSC0871.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0871.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 600 | 3 | 42 | 720 | 600
SSC0871.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0872.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 600 | 3 | 42 | 720 | 600
SSC0872.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0872.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 600 | 3 | 42 | 720 | 600
SSC0872.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0873.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 600 | 3 | 42 | 720 | 600
SSC0873.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0873.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 600 | 3 | 42 | 720 | 600
SSC0873.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0874.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 600 | 3 | 42 | 720 | 600
SSC0874.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0874.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 600 | 3 | 42 | 720 | 600
SSC0874.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0875.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 600 | 3 | 42 | 720 | 600
SSC0875.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0875.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 600 | 3 | 42 | 720 | 600
SSC0875.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0876.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 600 | 3 | 42 | 720 | 600
SSC0876.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0876.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 600 | 3 | 42 | 720 | 600
SSC0876.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0877.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 600 | 3 | 42 | 720 | 600
SSC0877.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0877.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 600 | 3 | 42 | 720 | 600
SSC0877.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0878.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 600 | 3 | 42 | 720 | 600
SSC0878.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0878.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 600 | 3 | 42 | 720 | 600
SSC0878.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0879.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 600 | 3 | 42 | 720 | 600
SSC0879.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0879.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 600 | 3 | 42 | 720 | 600
SSC0879.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0880.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 600 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 600 | 3 | 42 | 720 | 600
SSC0880.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 600 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0880.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 600 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 600 | 3 | 42 | 720 | 600
SSC0880.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 600 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0881.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 600 | 3 | 42 | 720 | 600
SSC0881.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0881.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 600 | 3 | 42 | 720 | 600
SSC0881.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 600 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0882.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 600 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V72N3S | 600 | 3 | 42 | 720 | 600
SSC0882.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 600 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0882.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 600 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V72N3S | 600 | 3 | 42 | 720 | 600
SSC0882.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 600 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V72N3S | 600 | 3 | 42 | 720 | 600
SSC0883.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 200 | 3 | 42 | 850 | 300
SSC0883.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0883.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 200 | 3 | 42 | 850 | 300
SSC0883.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0884.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 200 | 3 | 42 | 850 | 300
SSC0884.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0884.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 200 | 3 | 42 | 850 | 300
SSC0884.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 285 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0885.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 200 | 3 | 42 | 850 | 300
SSC0885.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0885.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 200 | 3 | 42 | 850 | 300
SSC0885.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0886.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 200 | 3 | 42 | 850 | 300
SSC0886.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0886.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 200 | 3 | 42 | 850 | 300
SSC0886.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0887.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 200 | 3 | 42 | 850 | 300
SSC0887.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0887.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 200 | 3 | 42 | 850 | 300
SSC0887.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0888.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 200 | 3 | 42 | 850 | 300
SSC0888.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0888.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 200 | 3 | 42 | 850 | 300
SSC0888.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0889.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 200 | 3 | 42 | 850 | 300
SSC0889.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0889.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 200 | 3 | 42 | 850 | 300
SSC0889.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0890.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 300 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 200 | 3 | 42 | 850 | 300
SSC0890.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 300 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0890.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 300 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 200 | 3 | 42 | 850 | 300
SSC0890.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 300 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0891.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 200 | 3 | 42 | 850 | 300
SSC0891.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0891.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 200 | 3 | 42 | 850 | 300
SSC0891.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0892.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 300 | 200 | 3 | 65 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 200 | 3 | 42 | 850 | 300
SSC0892.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 300 | 200 | 3 | 65 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0892.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 300 | 200 | 3 | 65 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 200 | 3 | 42 | 850 | 300
SSC0892.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 300 | 200 | 3 | 65 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0893.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 300 | 200 | 3 | 65 | 830 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 200 | 3 | 42 | 850 | 300
SSC0893.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 300 | 200 | 3 | 65 | 830 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0893.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 300 | 200 | 3 | 65 | 830 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 200 | 3 | 42 | 850 | 300
SSC0893.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 300 | 200 | 3 | 65 | 830 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 200 | 3 | 42 | 850 | 300
SSC0894.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 208 | 3 | 42 | 850 | 300
SSC0894.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0894.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 208 | 3 | 42 | 850 | 300
SSC0894.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0895.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 208 | 3 | 42 | 850 | 300
SSC0895.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0895.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 208 | 3 | 42 | 850 | 300
SSC0895.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0896.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 208 | 3 | 42 | 850 | 300
SSC0896.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0896.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 208 | 3 | 42 | 850 | 300
SSC0896.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0897.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 208 | 3 | 42 | 850 | 300
SSC0897.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0897.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 208 | 3 | 42 | 850 | 300
SSC0897.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0898.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 208 | 3 | 42 | 850 | 300
SSC0898.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0898.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 208 | 3 | 42 | 850 | 300
SSC0898.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0899.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 208 | 3 | 42 | 850 | 300
SSC0899.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0899.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 208 | 3 | 42 | 850 | 300
SSC0899.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0900.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 208 | 3 | 42 | 850 | 300
SSC0900.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0900.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 208 | 3 | 42 | 850 | 300
SSC0900.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0901.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 300 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 208 | 3 | 42 | 850 | 300
SSC0901.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 300 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0901.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 300 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 208 | 3 | 42 | 850 | 300
SSC0901.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 300 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0902.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 208 | 3 | 42 | 850 | 300
SSC0902.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0902.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 208 | 3 | 42 | 850 | 300
SSC0902.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0903.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 300 | 208 | 3 | 65 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 208 | 3 | 42 | 850 | 300
SSC0903.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 300 | 208 | 3 | 65 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0903.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 300 | 208 | 3 | 65 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 208 | 3 | 42 | 850 | 300
SSC0903.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 300 | 208 | 3 | 65 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0904.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 300 | 208 | 3 | 65 | 794 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 208 | 3 | 42 | 850 | 300
SSC0904.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 300 | 208 | 3 | 65 | 794 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0904.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 300 | 208 | 3 | 65 | 794 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 208 | 3 | 42 | 850 | 300
SSC0904.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 300 | 208 | 3 | 65 | 794 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 208 | 3 | 42 | 850 | 300
SSC0905.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 240 | 3 | 42 | 850 | 350
SSC0905.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0905.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 240 | 3 | 42 | 850 | 350
SSC0905.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0906.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 240 | 3 | 42 | 850 | 350
SSC0906.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0906.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 240 | 3 | 42 | 850 | 350
SSC0906.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 312 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0907.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 240 | 3 | 42 | 850 | 350
SSC0907.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0907.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 240 | 3 | 42 | 850 | 350
SSC0907.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0908.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 240 | 3 | 42 | 850 | 350
SSC0908.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0908.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 240 | 3 | 42 | 850 | 350
SSC0908.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0909.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 240 | 3 | 42 | 850 | 350
SSC0909.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0909.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 240 | 3 | 42 | 850 | 350
SSC0909.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0910.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 240 | 3 | 42 | 850 | 350
SSC0910.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0910.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 240 | 3 | 42 | 850 | 350
SSC0910.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0911.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 240 | 3 | 42 | 850 | 350
SSC0911.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0911.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 240 | 3 | 42 | 850 | 350
SSC0911.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0912.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 240 | 3 | 42 | 850 | 350
SSC0912.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0912.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 240 | 3 | 42 | 850 | 350
SSC0912.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0913.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 722 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 240 | 3 | 42 | 850 | 350
SSC0913.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 722 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0913.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 722 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 240 | 3 | 42 | 850 | 350
SSC0913.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 722 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0914.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 722 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 240 | 3 | 42 | 850 | 350
SSC0914.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 722 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0914.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 722 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 240 | 3 | 42 | 850 | 350
SSC0914.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 722 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0915.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 828 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 240 | 3 | 42 | 850 | 350
SSC0915.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 828 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0915.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 828 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 240 | 3 | 42 | 850 | 350
SSC0915.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 828 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 240 | 3 | 42 | 850 | 350
SSC0916.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 480 | 3 | 42 | 850 | 600
SSC0916.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0916.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 480 | 3 | 42 | 850 | 600
SSC0916.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0917.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 480 | 3 | 42 | 850 | 600
SSC0917.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0917.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 480 | 3 | 42 | 850 | 600
SSC0917.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 302 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0918.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 480 | 3 | 42 | 850 | 600
SSC0918.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0918.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 480 | 3 | 42 | 850 | 600
SSC0918.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0919.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 480 | 3 | 42 | 850 | 600
SSC0919.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0919.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 480 | 3 | 42 | 850 | 600
SSC0919.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0920.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 480 | 3 | 42 | 850 | 600
SSC0920.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0920.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 480 | 3 | 42 | 850 | 600
SSC0920.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0921.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 480 | 3 | 42 | 850 | 600
SSC0921.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0921.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 480 | 3 | 42 | 850 | 600
SSC0921.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0922.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 480 | 3 | 42 | 850 | 600
SSC0922.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0922.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 480 | 3 | 42 | 850 | 600
SSC0922.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0923.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 600 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 480 | 3 | 42 | 850 | 600
SSC0923.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 600 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0923.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 600 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 480 | 3 | 42 | 850 | 600
SSC0923.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 600 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0924.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 480 | 3 | 42 | 850 | 600
SSC0924.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0924.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 480 | 3 | 42 | 850 | 600
SSC0924.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0925.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 600 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 480 | 3 | 42 | 850 | 600
SSC0925.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 600 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0925.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 600 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 480 | 3 | 42 | 850 | 600
SSC0925.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 600 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0926.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 480 | 3 | 42 | 850 | 600
SSC0926.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0926.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 480 | 3 | 42 | 850 | 600
SSC0926.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0927.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 600 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 480 | 3 | 42 | 850 | 600
SSC0927.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 600 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0927.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 600 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 480 | 3 | 42 | 850 | 600
SSC0927.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 600 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0928.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 701 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 480 | 3 | 42 | 850 | 600
SSC0928.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 701 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0928.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 701 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 480 | 3 | 42 | 850 | 600
SSC0928.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 701 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0929.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 600 | 480 | 3 | 50 | 701 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 480 | 3 | 42 | 850 | 600
SSC0929.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 600 | 480 | 3 | 50 | 701 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0929.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 600 | 480 | 3 | 50 | 701 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 480 | 3 | 42 | 850 | 600
SSC0929.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 600 | 480 | 3 | 50 | 701 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 480 | 3 | 42 | 850 | 600
SSC0930.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 600 | 600 | 3 | 25 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 600 | 3 | 42 | 850 | 700
SSC0930.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 600 | 600 | 3 | 25 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0930.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 600 | 600 | 3 | 25 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 600 | 3 | 42 | 850 | 700
SSC0930.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 600 | 600 | 3 | 25 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0931.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 700 | 600 | 3 | 25 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 600 | 3 | 42 | 850 | 700
SSC0931.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 700 | 600 | 3 | 25 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0931.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 700 | 600 | 3 | 25 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 600 | 3 | 42 | 850 | 700
SSC0931.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 700 | 600 | 3 | 25 | 289 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0932.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 600 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 600 | 3 | 42 | 850 | 700
SSC0932.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 600 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0932.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 600 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 600 | 3 | 42 | 850 | 700
SSC0932.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 600 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0933.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 700 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 600 | 3 | 42 | 850 | 700
SSC0933.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 700 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0933.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 700 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 600 | 3 | 42 | 850 | 700
SSC0933.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 700 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0934.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 600 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 600 | 3 | 42 | 850 | 700
SSC0934.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 600 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0934.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 600 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 600 | 3 | 42 | 850 | 700
SSC0934.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 600 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0935.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 700 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 600 | 3 | 42 | 850 | 700
SSC0935.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 700 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0935.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 700 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 600 | 3 | 42 | 850 | 700
SSC0935.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 700 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0936.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 600 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 600 | 3 | 42 | 850 | 700
SSC0936.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 600 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0936.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 600 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 600 | 3 | 42 | 850 | 700
SSC0936.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 600 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0937.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 700 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 600 | 3 | 42 | 850 | 700
SSC0937.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 700 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0937.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 700 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 600 | 3 | 42 | 850 | 700
SSC0937.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 700 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0938.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 700 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 600 | 3 | 42 | 850 | 700
SSC0938.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 700 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0938.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 700 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 600 | 3 | 42 | 850 | 700
SSC0938.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 700 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0939.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 700 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 600 | 3 | 42 | 850 | 700
SSC0939.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 700 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0939.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 700 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 600 | 3 | 42 | 850 | 700
SSC0939.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 700 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0940.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 700 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 600 | 3 | 42 | 850 | 700
SSC0940.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 700 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0940.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 700 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 600 | 3 | 42 | 850 | 700
SSC0940.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 700 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0941.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 700 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 600 | 3 | 42 | 850 | 700
SSC0941.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 700 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0941.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 700 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 600 | 3 | 42 | 850 | 700
SSC0941.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 700 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0942.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 700 | 600 | 3 | 25 | 653 | 700 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 600 | 3 | 42 | 850 | 700
SSC0942.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 700 | 600 | 3 | 25 | 653 | 700 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0942.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 700 | 600 | 3 | 25 | 653 | 700 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 600 | 3 | 42 | 850 | 700
SSC0942.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 700 | 600 | 3 | 25 | 653 | 700 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0943.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 700 | 600 | 3 | 25 | 653 | 700 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V85N3S | 600 | 3 | 42 | 850 | 700
SSC0943.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 700 | 600 | 3 | 25 | 653 | 700 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0943.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 700 | 600 | 3 | 25 | 653 | 700 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V85N3S | 600 | 3 | 42 | 850 | 700
SSC0943.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 700 | 600 | 3 | 25 | 653 | 700 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V85N3S | 600 | 3 | 42 | 850 | 700
SSC0944.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0944.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0944.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0944.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0945.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0945.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0945.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0945.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 359 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0946.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0946.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0946.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0946.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0947.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0947.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0947.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0947.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 414 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0948.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0948.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0948.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0948.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0949.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 350 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0949.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 350 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0949.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 350 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0949.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 350 | 200 | 3 | 65 | 552 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0950.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0950.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0950.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0950.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 200 | 3 | - | 800 | 250 | 200 | 3 | 65 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0951.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 350 | 200 | 3 | 65 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0951.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 350 | 200 | 3 | 65 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0951.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 350 | 200 | 3 | 65 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0951.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 350 | 200 | 3 | 65 | 695 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0952.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 350 | 200 | 3 | 65 | 830 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0952.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 350 | 200 | 3 | 65 | 830 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0952.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 350 | 200 | 3 | 65 | 830 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0952.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 350 | 200 | 3 | 65 | 830 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0953.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 350 | 200 | 3 | 65 | 952 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0953.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 350 | 200 | 3 | 65 | 952 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0953.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 350 | 200 | 3 | 65 | 952 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0953.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 200 | 3 | - | 1200 | 350 | 200 | 3 | 65 | 952 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 200 | 3 | 42 | 1000 | 350
SSC0954.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0954.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0954.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0954.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0955.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0955.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0955.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0955.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 343 | 125 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0956.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0956.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0956.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0956.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0957.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0957.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0957.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0957.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 396 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0958.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0958.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0958.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0958.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0959.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 350 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0959.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 350 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0959.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 350 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0959.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 350 | 208 | 3 | 65 | 528 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0960.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0960.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0960.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0960.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 208 | 3 | - | 800 | 300 | 208 | 3 | 65 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0961.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 350 | 208 | 3 | 65 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0961.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 350 | 208 | 3 | 65 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0961.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 350 | 208 | 3 | 65 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0961.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 350 | 208 | 3 | 65 | 665 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0962.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 350 | 208 | 3 | 65 | 794 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0962.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 350 | 208 | 3 | 65 | 794 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0962.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 350 | 208 | 3 | 65 | 794 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0962.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 350 | 208 | 3 | 65 | 794 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0963.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 350 | 208 | 3 | 65 | 911 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0963.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 350 | 208 | 3 | 65 | 911 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0963.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 350 | 208 | 3 | 65 | 911 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0963.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 208 | 3 | - | 1200 | 350 | 208 | 3 | 65 | 911 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 208 | 3 | 42 | 1000 | 350
SSC0964.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0964.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0964.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0964.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0965.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0965.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0965.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0965.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 360 | 150 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0966.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0966.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0966.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0966.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0967.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0967.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0967.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0967.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 480 | 200 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0968.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0968.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0968.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0968.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0969.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0969.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0969.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0969.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 604 | 250 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0970.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 722 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0970.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 722 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0970.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 722 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0970.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 240 | 3 | - | 800 | 300 | 240 | 3 | 65 | 722 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0971.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 722 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0971.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 722 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0971.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 722 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0971.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 722 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0972.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 828 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0972.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 828 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0972.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 828 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0972.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 828 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0973.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 954 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0973.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 954 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0973.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 954 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0973.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 240 | 3 | - | 1200 | 500 | 240 | 3 | 65 | 954 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 240 | 3 | 42 | 1000 | 400
SSC0974.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0974.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0974.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0974.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0975.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0975.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0975.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0975.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 361 | 300 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0976.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0976.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0976.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0976.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0977.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0977.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0977.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0977.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 414 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0978.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0978.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0978.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0978.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0979.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 700 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0979.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 700 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0979.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 700 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0979.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 700 | 480 | 3 | 50 | 477 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0980.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0980.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0980.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0980.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0981.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 700 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0981.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 700 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0981.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 700 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0981.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 700 | 480 | 3 | 50 | 515 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0982.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0982.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0982.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0982.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0983.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 700 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0983.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 700 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0983.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 700 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0983.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 700 | 480 | 3 | 50 | 590 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0984.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 701 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0984.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 701 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0984.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 701 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0984.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 480 | 3 | - | 800 | 600 | 480 | 3 | 50 | 701 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0985.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 700 | 480 | 3 | 50 | 701 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0985.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 700 | 480 | 3 | 50 | 701 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0985.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 700 | 480 | 3 | 50 | 701 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0985.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 700 | 480 | 3 | 50 | 701 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0986.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 700 | 480 | 3 | 50 | 804 | 700 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0986.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 700 | 480 | 3 | 50 | 804 | 700 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0986.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 700 | 480 | 3 | 50 | 804 | 700 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0986.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 480 | 3 | - | 1200 | 700 | 480 | 3 | 50 | 804 | 700 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 480 | 3 | 42 | 1000 | 700
SSC0987.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 600 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0987.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 600 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0987.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 600 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0987.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 600 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0988.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 800 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0988.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 800 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0988.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 800 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0988.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 800 | 600 | 3 | 25 | 336 | 350 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0989.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 600 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0989.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 600 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0989.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 600 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0989.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 600 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0990.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 800 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0990.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 800 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0990.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 800 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0990.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 800 | 600 | 3 | 25 | 382 | 400 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0991.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 600 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0991.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 600 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0991.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 600 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0991.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 600 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0992.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 800 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0992.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 800 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0992.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 800 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0992.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 800 | 600 | 3 | 25 | 412 | 450 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0993.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 800 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0993.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 800 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0993.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 800 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0993.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 800 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0994.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 800 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0994.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 800 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0994.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 800 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0994.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 800 | 600 | 3 | 25 | 472 | 500 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0995.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 800 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0995.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 800 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0995.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 800 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0995.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 800 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0996.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 800 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0996.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 800 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0996.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 800 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0996.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 800 | 600 | 3 | 25 | 561 | 600 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0997.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 800 | 600 | 3 | 25 | 653 | 700 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0997.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 800 | 600 | 3 | 25 | 653 | 700 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0997.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 800 | 600 | 3 | 25 | 653 | 700 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0997.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 800 | 600 | 3 | 25 | 653 | 700 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0998.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 800 | 600 | 3 | 25 | 653 | 700 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0998.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 800 | 600 | 3 | 25 | 653 | 700 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0998.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 800 | 600 | 3 | 25 | 653 | 700 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0998.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 800 | 600 | 3 | 25 | 653 | 700 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0999.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 800 | 600 | 3 | 25 | 742 | 800 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0999.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 800 | 600 | 3 | 25 | 742 | 800 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0999.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 800 | 600 | 3 | 25 | 742 | 800 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 600 | 3 | 42 | 1000 | 800
SSC0999.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 800 | 600 | 3 | 25 | 742 | 800 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC01000.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 800 | 600 | 3 | 25 | 742 | 800 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801V10N3S | 600 | 3 | 42 | 1000 | 800
SSC01000.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 800 | 600 | 3 | 25 | 742 | 800 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC01000.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 800 | 600 | 3 | 25 | 742 | 800 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811V10N3S | 600 | 3 | 42 | 1000 | 800
SSC01000.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP12Y8W | 600 | 3 | - | 1200 | 800 | 600 | 3 | 25 | 742 | 800 | 50616 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+V10N3S | 600 | 3 | 42 | 1000 | 800
SSC01001.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 200 | 3 | 42 | 360 | 125
SSC01001.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 200 | 3 | 42 | 360 | 125
SSC01001.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 200 | 3 | 42 | 360 | 125
SSC01001.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 200 | 3 | 42 | 360 | 125
SSC01002.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 200 | 3 | 42 | 360 | 125
SSC01002.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 200 | 3 | 42 | 360 | 125
SSC01002.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 200 | 3 | 42 | 360 | 125
SSC01002.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 120 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 200 | 3 | 42 | 360 | 125
SSC01003.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 200 | 3 | 42 | 360 | 125
SSC01003.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 200 | 3 | 42 | 360 | 125
SSC01003.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 200 | 3 | 42 | 360 | 125
SSC01003.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 200 | 3 | 42 | 360 | 125
SSC01004.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 200 | 3 | 42 | 360 | 125
SSC01004.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 200 | 3 | 42 | 360 | 125
SSC01004.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 200 | 3 | 42 | 360 | 125
SSC01004.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 200 | 3 | 42 | 360 | 125
SSC01005.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 200 | 3 | 42 | 360 | 125
SSC01005.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 200 | 3 | 42 | 360 | 125
SSC01005.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 200 | 3 | 42 | 360 | 125
SSC01005.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 200 | 3 | 42 | 360 | 125
SSC01006.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 200 | 3 | 42 | 360 | 125
SSC01006.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 200 | 3 | 42 | 360 | 125
SSC01006.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 200 | 3 | 42 | 360 | 125
SSC01006.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 200 | 3 | 42 | 360 | 125
SSC01007.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 200 | 3 | 42 | 360 | 125
SSC01007.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 200 | 3 | 42 | 360 | 125
SSC01007.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 200 | 3 | 42 | 360 | 125
SSC01007.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 200 | 3 | 42 | 360 | 125
SSC01008.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 200 | 3 | 42 | 360 | 125
SSC01008.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 200 | 3 | 42 | 360 | 125
SSC01008.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 200 | 3 | 42 | 360 | 125
SSC01008.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 200 | 3 | 42 | 360 | 125
SSC01009.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 200 | 3 | 42 | 360 | 125
SSC01009.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 200 | 3 | 42 | 360 | 125
SSC01009.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 200 | 3 | 42 | 360 | 125
SSC01009.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 200 | 3 | 42 | 360 | 125
SSC01010.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 200 | 3 | 42 | 360 | 125
SSC01010.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 200 | 3 | 42 | 360 | 125
SSC01010.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 200 | 3 | 42 | 360 | 125
SSC01010.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 200 | 3 | 42 | 360 | 125
SSC01011.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 200 | 3 | 42 | 360 | 125
SSC01011.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 200 | 3 | 42 | 360 | 125
SSC01011.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 200 | 3 | 42 | 360 | 125
SSC01011.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 200 | 3 | 42 | 360 | 125
SSC01012.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 200 | 3 | 42 | 360 | 125
SSC01012.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 200 | 3 | 42 | 360 | 125
SSC01012.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 200 | 3 | 42 | 360 | 125
SSC01012.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 200 | 3 | 42 | 360 | 125
SSC01013.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 208 | 3 | 42 | 360 | 125
SSC01013.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 208 | 3 | 42 | 360 | 125
SSC01013.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 208 | 3 | 42 | 360 | 125
SSC01013.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 208 | 3 | 42 | 360 | 125
SSC01014.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 208 | 3 | 42 | 360 | 125
SSC01014.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 208 | 3 | 42 | 360 | 125
SSC01014.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 208 | 3 | 42 | 360 | 125
SSC01014.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 114 | 40 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 208 | 3 | 42 | 360 | 125
SSC01015.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 208 | 3 | 42 | 360 | 125
SSC01015.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 208 | 3 | 42 | 360 | 125
SSC01015.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 208 | 3 | 42 | 360 | 125
SSC01015.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 208 | 3 | 42 | 360 | 125
SSC01016.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 208 | 3 | 42 | 360 | 125
SSC01016.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 208 | 3 | 42 | 360 | 125
SSC01016.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 208 | 3 | 42 | 360 | 125
SSC01016.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 208 | 3 | 42 | 360 | 125
SSC01017.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 208 | 3 | 42 | 360 | 125
SSC01017.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 208 | 3 | 42 | 360 | 125
SSC01017.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 208 | 3 | 42 | 360 | 125
SSC01017.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 208 | 3 | 42 | 360 | 125
SSC01018.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 208 | 3 | 42 | 360 | 125
SSC01018.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 208 | 3 | 42 | 360 | 125
SSC01018.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 208 | 3 | 42 | 360 | 125
SSC01018.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 208 | 3 | 42 | 360 | 125
SSC01019.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 208 | 3 | 42 | 360 | 125
SSC01019.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 208 | 3 | 42 | 360 | 125
SSC01019.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 208 | 3 | 42 | 360 | 125
SSC01019.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 208 | 3 | 42 | 360 | 125
SSC01020.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 208 | 3 | 42 | 360 | 125
SSC01020.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 208 | 3 | 42 | 360 | 125
SSC01020.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 208 | 3 | 42 | 360 | 125
SSC01020.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 208 | 3 | 42 | 360 | 125
SSC01021.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 208 | 3 | 42 | 360 | 125
SSC01021.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 208 | 3 | 42 | 360 | 125
SSC01021.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 208 | 3 | 42 | 360 | 125
SSC01021.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 208 | 3 | 42 | 360 | 125
SSC01022.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 208 | 3 | 42 | 360 | 125
SSC01022.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 208 | 3 | 42 | 360 | 125
SSC01022.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 208 | 3 | 42 | 360 | 125
SSC01022.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 208 | 3 | 42 | 360 | 125
SSC01023.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 208 | 3 | 42 | 360 | 125
SSC01023.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 208 | 3 | 42 | 360 | 125
SSC01023.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 208 | 3 | 42 | 360 | 125
SSC01023.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 208 | 3 | 42 | 360 | 125
SSC01024.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 208 | 3 | 42 | 360 | 125
SSC01024.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 208 | 3 | 42 | 360 | 125
SSC01024.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 208 | 3 | 42 | 360 | 125
SSC01024.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 208 | 3 | 42 | 360 | 125
SSC01025.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 240 | 3 | 42 | 360 | 150
SSC01025.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 240 | 3 | 42 | 360 | 150
SSC01025.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 240 | 3 | 42 | 360 | 150
SSC01025.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 240 | 3 | 42 | 360 | 150
SSC01026.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 240 | 3 | 42 | 360 | 150
SSC01026.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 240 | 3 | 42 | 360 | 150
SSC01026.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 240 | 3 | 42 | 360 | 150
SSC01026.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 130 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 240 | 3 | 42 | 360 | 150
SSC01027.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 240 | 3 | 42 | 360 | 150
SSC01027.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 240 | 3 | 42 | 360 | 150
SSC01027.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 240 | 3 | 42 | 360 | 150
SSC01027.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 240 | 3 | 42 | 360 | 150
SSC01028.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 240 | 3 | 42 | 360 | 150
SSC01028.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 240 | 3 | 42 | 360 | 150
SSC01028.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 240 | 3 | 42 | 360 | 150
SSC01028.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 240 | 3 | 42 | 360 | 150
SSC01029.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 240 | 3 | 42 | 360 | 150
SSC01029.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 240 | 3 | 42 | 360 | 150
SSC01029.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 240 | 3 | 42 | 360 | 150
SSC01029.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 240 | 3 | 42 | 360 | 150
SSC01030.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 240 | 3 | 42 | 360 | 150
SSC01030.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 240 | 3 | 42 | 360 | 150
SSC01030.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 240 | 3 | 42 | 360 | 150
SSC01030.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 240 | 3 | 42 | 360 | 150
SSC01031.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 240 | 3 | 42 | 360 | 150
SSC01031.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 240 | 3 | 42 | 360 | 150
SSC01031.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 240 | 3 | 42 | 360 | 150
SSC01031.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 240 | 3 | 42 | 360 | 150
SSC01032.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 240 | 3 | 42 | 360 | 150
SSC01032.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 240 | 3 | 42 | 360 | 150
SSC01032.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 240 | 3 | 42 | 360 | 150
SSC01032.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 240 | 3 | 42 | 360 | 150
SSC01033.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 240 | 3 | 42 | 360 | 150
SSC01033.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 240 | 3 | 42 | 360 | 150
SSC01033.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 240 | 3 | 42 | 360 | 150
SSC01033.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 240 | 3 | 42 | 360 | 150
SSC01034.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 240 | 3 | 42 | 360 | 150
SSC01034.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 240 | 3 | 42 | 360 | 150
SSC01034.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 240 | 3 | 42 | 360 | 150
SSC01034.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 240 | 3 | 42 | 360 | 150
SSC01035.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 240 | 3 | 42 | 360 | 150
SSC01035.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 240 | 3 | 42 | 360 | 150
SSC01035.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 240 | 3 | 42 | 360 | 150
SSC01035.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 240 | 3 | 42 | 360 | 150
SSC01036.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 240 | 3 | 42 | 360 | 150
SSC01036.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 240 | 3 | 42 | 360 | 150
SSC01036.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 240 | 3 | 42 | 360 | 150
SSC01036.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 240 | 3 | 42 | 360 | 150
SSC01037.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 480 | 3 | 42 | 360 | 250
SSC01037.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 480 | 3 | 42 | 360 | 250
SSC01037.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 480 | 3 | 42 | 360 | 250
SSC01037.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 480 | 3 | 42 | 360 | 250
SSC01038.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 480 | 3 | 42 | 360 | 250
SSC01038.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 480 | 3 | 42 | 360 | 250
SSC01038.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 480 | 3 | 42 | 360 | 250
SSC01038.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 124 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 480 | 3 | 42 | 360 | 250
SSC01039.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 480 | 3 | 42 | 360 | 250
SSC01039.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 480 | 3 | 42 | 360 | 250
SSC01039.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 480 | 3 | 42 | 360 | 250
SSC01039.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 480 | 3 | 42 | 360 | 250
SSC01040.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 480 | 3 | 42 | 360 | 250
SSC01040.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 480 | 3 | 42 | 360 | 250
SSC01040.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 480 | 3 | 42 | 360 | 250
SSC01040.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 480 | 3 | 42 | 360 | 250
SSC01041.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 480 | 3 | 42 | 360 | 250
SSC01041.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 480 | 3 | 42 | 360 | 250
SSC01041.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 480 | 3 | 42 | 360 | 250
SSC01041.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 480 | 3 | 42 | 360 | 250
SSC01042.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 480 | 3 | 42 | 360 | 250
SSC01042.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 480 | 3 | 42 | 360 | 250
SSC01042.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 480 | 3 | 42 | 360 | 250
SSC01042.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 480 | 3 | 42 | 360 | 250
SSC01043.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 480 | 3 | 42 | 360 | 250
SSC01043.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 480 | 3 | 42 | 360 | 250
SSC01043.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 480 | 3 | 42 | 360 | 250
SSC01043.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 480 | 3 | 42 | 360 | 250
SSC01044.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 480 | 3 | 42 | 360 | 250
SSC01044.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 480 | 3 | 42 | 360 | 250
SSC01044.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 480 | 3 | 42 | 360 | 250
SSC01044.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 480 | 3 | 42 | 360 | 250
SSC01045.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 480 | 3 | 42 | 360 | 250
SSC01045.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 480 | 3 | 42 | 360 | 250
SSC01045.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 480 | 3 | 42 | 360 | 250
SSC01045.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 480 | 3 | 42 | 360 | 250
SSC01046.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 480 | 3 | 42 | 360 | 250
SSC01046.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 480 | 3 | 42 | 360 | 250
SSC01046.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 480 | 3 | 42 | 360 | 250
SSC01046.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 480 | 3 | 42 | 360 | 250
SSC01047.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 18 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 600 | 3 | 42 | 360 | 350
SSC01047.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 18 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 600 | 3 | 42 | 360 | 350
SSC01047.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 18 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 600 | 3 | 42 | 360 | 350
SSC01047.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 18 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 600 | 3 | 42 | 360 | 350
SSC01048.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 600 | 3 | 42 | 360 | 350
SSC01048.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 600 | 3 | 42 | 360 | 350
SSC01048.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 600 | 3 | 42 | 360 | 350
SSC01048.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 125 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 600 | 3 | 42 | 360 | 350
SSC01049.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 18 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 600 | 3 | 42 | 360 | 350
SSC01049.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 18 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 600 | 3 | 42 | 360 | 350
SSC01049.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 18 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 600 | 3 | 42 | 360 | 350
SSC01049.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 18 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 600 | 3 | 42 | 360 | 350
SSC01050.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 600 | 3 | 42 | 360 | 350
SSC01050.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 600 | 3 | 42 | 360 | 350
SSC01050.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 600 | 3 | 42 | 360 | 350
SSC01050.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 600 | 3 | 42 | 360 | 350
SSC01051.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 600 | 3 | 42 | 360 | 350
SSC01051.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 600 | 3 | 42 | 360 | 350
SSC01051.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 600 | 3 | 42 | 360 | 350
SSC01051.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 600 | 3 | 42 | 360 | 350
SSC01052.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 600 | 3 | 42 | 360 | 350
SSC01052.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 600 | 3 | 42 | 360 | 350
SSC01052.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 600 | 3 | 42 | 360 | 350
SSC01052.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 600 | 3 | 42 | 360 | 350
SSC01053.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 600 | 3 | 42 | 360 | 350
SSC01053.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 600 | 3 | 42 | 360 | 350
SSC01053.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 600 | 3 | 42 | 360 | 350
SSC01053.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 600 | 3 | 42 | 360 | 350
SSC01054.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 600 | 3 | 42 | 360 | 350
SSC01054.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 600 | 3 | 42 | 360 | 350
SSC01054.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 600 | 3 | 42 | 360 | 350
SSC01054.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 600 | 3 | 42 | 360 | 350
SSC01055.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 600 | 3 | 42 | 360 | 350
SSC01055.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 600 | 3 | 42 | 360 | 350
SSC01055.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 600 | 3 | 42 | 360 | 350
SSC01055.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 600 | 3 | 42 | 360 | 350
SSC01056.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 600 | 3 | 42 | 360 | 350
SSC01056.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 600 | 3 | 42 | 360 | 350
SSC01056.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 600 | 3 | 42 | 360 | 350
SSC01056.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 600 | 3 | 42 | 360 | 350
SSC01057.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 600 | 3 | 42 | 360 | 350
SSC01057.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 600 | 3 | 42 | 360 | 350
SSC01057.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 600 | 3 | 42 | 360 | 350
SSC01057.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 600 | 3 | 42 | 360 | 350
SSC01058.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U36N3S | 600 | 3 | 42 | 360 | 350
SSC01058.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U36N3S | 600 | 3 | 42 | 360 | 350
SSC01058.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U36N3S | 600 | 3 | 42 | 360 | 350
SSC01058.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U36N3S | 600 | 3 | 42 | 360 | 350
SSC01059.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 200 | 3 | 42 | 420 | 150
SSC01059.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 200 | 3 | 42 | 420 | 150
SSC01059.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 200 | 3 | 42 | 420 | 150
SSC01059.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 200 | 3 | - | 250 | 75 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 200 | 3 | 42 | 420 | 150
SSC01060.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 200 | 3 | 42 | 420 | 150
SSC01060.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 200 | 3 | 42 | 420 | 150
SSC01060.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 200 | 3 | 42 | 420 | 150
SSC01060.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 150 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 200 | 3 | 42 | 420 | 150
SSC01061.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 200 | 3 | 42 | 420 | 150
SSC01061.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 200 | 3 | 42 | 420 | 150
SSC01061.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 200 | 3 | 42 | 420 | 150
SSC01061.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 200 | 3 | 42 | 420 | 150
SSC01062.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 200 | 3 | 42 | 420 | 150
SSC01062.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 200 | 3 | 42 | 420 | 150
SSC01062.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 200 | 3 | 42 | 420 | 150
SSC01062.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 200 | 3 | 42 | 420 | 150
SSC01063.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 200 | 3 | 42 | 420 | 150
SSC01063.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 200 | 3 | 42 | 420 | 150
SSC01063.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 200 | 3 | 42 | 420 | 150
SSC01063.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 200 | 3 | 42 | 420 | 150
SSC01064.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 200 | 3 | 42 | 420 | 150
SSC01064.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 200 | 3 | 42 | 420 | 150
SSC01064.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 200 | 3 | 42 | 420 | 150
SSC01064.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 200 | 3 | 42 | 420 | 150
SSC01065.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 200 | 3 | 42 | 420 | 150
SSC01065.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 200 | 3 | 42 | 420 | 150
SSC01065.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 200 | 3 | 42 | 420 | 150
SSC01065.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 200 | 3 | 42 | 420 | 150
SSC01066.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 200 | 3 | 42 | 420 | 150
SSC01066.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 200 | 3 | 42 | 420 | 150
SSC01066.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 200 | 3 | 42 | 420 | 150
SSC01066.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 200 | 3 | 42 | 420 | 150
SSC01067.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 200 | 3 | 42 | 420 | 150
SSC01067.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 200 | 3 | 42 | 420 | 150
SSC01067.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 200 | 3 | 42 | 420 | 150
SSC01067.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 200 | 3 | 42 | 420 | 150
SSC01068.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 200 | 3 | 42 | 420 | 150
SSC01068.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 200 | 3 | 42 | 420 | 150
SSC01068.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 200 | 3 | 42 | 420 | 150
SSC01068.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 200 | 3 | 42 | 420 | 150
SSC01069.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 200 | 3 | 42 | 420 | 150
SSC01069.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 200 | 3 | 42 | 420 | 150
SSC01069.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 200 | 3 | 42 | 420 | 150
SSC01069.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 200 | 3 | 42 | 420 | 150
SSC01070.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 200 | 3 | 42 | 420 | 150
SSC01070.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 200 | 3 | 42 | 420 | 150
SSC01070.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 200 | 3 | 42 | 420 | 150
SSC01070.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 200 | 3 | 42 | 420 | 150
SSC01071.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 208 | 3 | 42 | 420 | 150
SSC01071.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 208 | 3 | 42 | 420 | 150
SSC01071.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 208 | 3 | 42 | 420 | 150
SSC01071.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 208 | 3 | 42 | 420 | 150
SSC01072.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 208 | 3 | 42 | 420 | 150
SSC01072.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 208 | 3 | 42 | 420 | 150
SSC01072.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 208 | 3 | 42 | 420 | 150
SSC01072.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 143 | 50 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 208 | 3 | 42 | 420 | 150
SSC01073.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 208 | 3 | 42 | 420 | 150
SSC01073.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 208 | 3 | 42 | 420 | 150
SSC01073.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 208 | 3 | 42 | 420 | 150
SSC01073.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 208 | 3 | 42 | 420 | 150
SSC01074.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 208 | 3 | 42 | 420 | 150
SSC01074.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 208 | 3 | 42 | 420 | 150
SSC01074.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 208 | 3 | 42 | 420 | 150
SSC01074.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 208 | 3 | 42 | 420 | 150
SSC01075.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 208 | 3 | 42 | 420 | 150
SSC01075.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 208 | 3 | 42 | 420 | 150
SSC01075.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 208 | 3 | 42 | 420 | 150
SSC01075.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 208 | 3 | 42 | 420 | 150
SSC01076.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 208 | 3 | 42 | 420 | 150
SSC01076.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 208 | 3 | 42 | 420 | 150
SSC01076.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 208 | 3 | 42 | 420 | 150
SSC01076.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 208 | 3 | 42 | 420 | 150
SSC01077.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 208 | 3 | 42 | 420 | 150
SSC01077.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 208 | 3 | 42 | 420 | 150
SSC01077.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 208 | 3 | 42 | 420 | 150
SSC01077.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 208 | 3 | 42 | 420 | 150
SSC01078.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 208 | 3 | 42 | 420 | 150
SSC01078.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 208 | 3 | 42 | 420 | 150
SSC01078.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 208 | 3 | 42 | 420 | 150
SSC01078.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 208 | 3 | 42 | 420 | 150
SSC01079.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 208 | 3 | 42 | 420 | 150
SSC01079.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 208 | 3 | 42 | 420 | 150
SSC01079.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 208 | 3 | 42 | 420 | 150
SSC01079.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 208 | 3 | 42 | 420 | 150
SSC01080.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 208 | 3 | 42 | 420 | 150
SSC01080.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 208 | 3 | 42 | 420 | 150
SSC01080.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 208 | 3 | 42 | 420 | 150
SSC01080.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 208 | 3 | 42 | 420 | 150
SSC01081.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 208 | 3 | 42 | 420 | 150
SSC01081.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 208 | 3 | 42 | 420 | 150
SSC01081.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 208 | 3 | 42 | 420 | 150
SSC01081.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 208 | 3 | 42 | 420 | 150
SSC01082.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 208 | 3 | 42 | 420 | 150
SSC01082.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 208 | 3 | 42 | 420 | 150
SSC01082.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 208 | 3 | 42 | 420 | 150
SSC01082.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 208 | 3 | 42 | 420 | 150
SSC01083.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 240 | 3 | 42 | 420 | 150
SSC01083.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 240 | 3 | 42 | 420 | 150
SSC01083.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 240 | 3 | 42 | 420 | 150
SSC01083.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 240 | 3 | - | 250 | 100 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 240 | 3 | 42 | 420 | 150
SSC01084.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 240 | 3 | 42 | 420 | 150
SSC01084.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 240 | 3 | 42 | 420 | 150
SSC01084.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 240 | 3 | 42 | 420 | 150
SSC01084.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 154 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 240 | 3 | 42 | 420 | 150
SSC01085.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 240 | 3 | 42 | 420 | 150
SSC01085.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 240 | 3 | 42 | 420 | 150
SSC01085.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 240 | 3 | 42 | 420 | 150
SSC01085.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 240 | 3 | 42 | 420 | 150
SSC01086.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 240 | 3 | 42 | 420 | 150
SSC01086.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 240 | 3 | 42 | 420 | 150
SSC01086.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 240 | 3 | 42 | 420 | 150
SSC01086.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 240 | 3 | 42 | 420 | 150
SSC01087.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 240 | 3 | 42 | 420 | 150
SSC01087.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 240 | 3 | 42 | 420 | 150
SSC01087.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 240 | 3 | 42 | 420 | 150
SSC01087.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 240 | 3 | 42 | 420 | 150
SSC01088.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 240 | 3 | 42 | 420 | 150
SSC01088.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 240 | 3 | 42 | 420 | 150
SSC01088.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 240 | 3 | 42 | 420 | 150
SSC01088.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 240 | 3 | 42 | 420 | 150
SSC01089.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 240 | 3 | 42 | 420 | 150
SSC01089.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 240 | 3 | 42 | 420 | 150
SSC01089.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 240 | 3 | 42 | 420 | 150
SSC01089.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 240 | 3 | 42 | 420 | 150
SSC01090.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 240 | 3 | 42 | 420 | 150
SSC01090.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 240 | 3 | 42 | 420 | 150
SSC01090.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 240 | 3 | 42 | 420 | 150
SSC01090.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 240 | 3 | 42 | 420 | 150
SSC01091.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 240 | 3 | 42 | 420 | 150
SSC01091.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 240 | 3 | 42 | 420 | 150
SSC01091.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 240 | 3 | 42 | 420 | 150
SSC01091.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 240 | 3 | 42 | 420 | 150
SSC01092.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 240 | 3 | 42 | 420 | 150
SSC01092.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 240 | 3 | 42 | 420 | 150
SSC01092.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 240 | 3 | 42 | 420 | 150
SSC01092.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 240 | 3 | 42 | 420 | 150
SSC01093.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 480 | 3 | 42 | 420 | 350
SSC01093.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 480 | 3 | 42 | 420 | 350
SSC01093.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 480 | 3 | 42 | 420 | 350
SSC01093.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 480 | 3 | 42 | 420 | 350
SSC01094.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 480 | 3 | 42 | 420 | 350
SSC01094.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 480 | 3 | 42 | 420 | 350
SSC01094.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 480 | 3 | 42 | 420 | 350
SSC01094.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 480 | 3 | 42 | 420 | 350
SSC01095.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 480 | 3 | 42 | 420 | 350
SSC01095.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 480 | 3 | 42 | 420 | 350
SSC01095.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 480 | 3 | 42 | 420 | 350
SSC01095.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 480 | 3 | 42 | 420 | 350
SSC01096.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 480 | 3 | 42 | 420 | 350
SSC01096.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 480 | 3 | 42 | 420 | 350
SSC01096.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 480 | 3 | 42 | 420 | 350
SSC01096.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 480 | 3 | 42 | 420 | 350
SSC01097.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 480 | 3 | 42 | 420 | 350
SSC01097.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 480 | 3 | 42 | 420 | 350
SSC01097.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 480 | 3 | 42 | 420 | 350
SSC01097.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 480 | 3 | 42 | 420 | 350
SSC01098.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 480 | 3 | 42 | 420 | 350
SSC01098.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 480 | 3 | 42 | 420 | 350
SSC01098.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 480 | 3 | 42 | 420 | 350
SSC01098.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 480 | 3 | 42 | 420 | 350
SSC01099.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 480 | 3 | 42 | 420 | 350
SSC01099.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 480 | 3 | 42 | 420 | 350
SSC01099.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 480 | 3 | 42 | 420 | 350
SSC01099.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 480 | 3 | 42 | 420 | 350
SSC01100.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 480 | 3 | 42 | 420 | 350
SSC01100.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 480 | 3 | 42 | 420 | 350
SSC01100.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 480 | 3 | 42 | 420 | 350
SSC01100.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 480 | 3 | 42 | 420 | 350
SSC01101.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 480 | 3 | 42 | 420 | 350
SSC01101.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 480 | 3 | 42 | 420 | 350
SSC01101.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 480 | 3 | 42 | 420 | 350
SSC01101.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 480 | 3 | 42 | 420 | 350
SSC01102.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 480 | 3 | 42 | 420 | 350
SSC01102.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 480 | 3 | 42 | 420 | 350
SSC01102.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 480 | 3 | 42 | 420 | 350
SSC01102.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 480 | 3 | 42 | 420 | 350
SSC01103.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 480 | 3 | 42 | 420 | 350
SSC01103.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 480 | 3 | 42 | 420 | 350
SSC01103.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 480 | 3 | 42 | 420 | 350
SSC01103.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 480 | 3 | 42 | 420 | 350
SSC01104.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 480 | 3 | 42 | 420 | 350
SSC01104.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 480 | 3 | 42 | 420 | 350
SSC01104.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 480 | 3 | 42 | 420 | 350
SSC01104.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 480 | 3 | 42 | 420 | 350
SSC01105.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 65 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 600 | 3 | 42 | 420 | 450
SSC01105.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 65 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 600 | 3 | 42 | 420 | 450
SSC01105.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 65 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 600 | 3 | 42 | 420 | 450
SSC01105.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 600 | 3 | - | 250 | 250 | 600 | 3 | 65 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 600 | 3 | 42 | 420 | 450
SSC01106.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 600 | 3 | 42 | 420 | 450
SSC01106.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 600 | 3 | 42 | 420 | 450
SSC01106.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 600 | 3 | 42 | 420 | 450
SSC01106.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 144 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 600 | 3 | 42 | 420 | 450
SSC01107.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 600 | 3 | 42 | 420 | 450
SSC01107.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 600 | 3 | 42 | 420 | 450
SSC01107.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 600 | 3 | 42 | 420 | 450
SSC01107.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 600 | 3 | 42 | 420 | 450
SSC01108.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 600 | 3 | 42 | 420 | 450
SSC01108.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 600 | 3 | 42 | 420 | 450
SSC01108.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 600 | 3 | 42 | 420 | 450
SSC01108.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 600 | 3 | 42 | 420 | 450
SSC01109.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 600 | 3 | 42 | 420 | 450
SSC01109.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 600 | 3 | 42 | 420 | 450
SSC01109.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 600 | 3 | 42 | 420 | 450
SSC01109.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 600 | 3 | 42 | 420 | 450
SSC01110.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 600 | 3 | 42 | 420 | 450
SSC01110.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 600 | 3 | 42 | 420 | 450
SSC01110.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 600 | 3 | 42 | 420 | 450
SSC01110.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 600 | 3 | 42 | 420 | 450
SSC01111.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 600 | 3 | 42 | 420 | 450
SSC01111.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 600 | 3 | 42 | 420 | 450
SSC01111.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 600 | 3 | 42 | 420 | 450
SSC01111.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 600 | 3 | 42 | 420 | 450
SSC01112.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 600 | 3 | 42 | 420 | 450
SSC01112.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 600 | 3 | 42 | 420 | 450
SSC01112.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 600 | 3 | 42 | 420 | 450
SSC01112.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 600 | 3 | 42 | 420 | 450
SSC01113.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 600 | 3 | 42 | 420 | 450
SSC01113.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 600 | 3 | 42 | 420 | 450
SSC01113.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 600 | 3 | 42 | 420 | 450
SSC01113.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 600 | 3 | 42 | 420 | 450
SSC01114.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 600 | 3 | 42 | 420 | 450
SSC01114.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 600 | 3 | 42 | 420 | 450
SSC01114.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 600 | 3 | 42 | 420 | 450
SSC01114.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 600 | 3 | 42 | 420 | 450
SSC01115.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 600 | 3 | 42 | 420 | 450
SSC01115.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 600 | 3 | 42 | 420 | 450
SSC01115.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 600 | 3 | 42 | 420 | 450
SSC01115.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 600 | 3 | 42 | 420 | 450
SSC01116.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 600 | 3 | 42 | 420 | 450
SSC01116.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 600 | 3 | 42 | 420 | 450
SSC01116.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 600 | 3 | 42 | 420 | 450
SSC01116.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 600 | 3 | 42 | 420 | 450
SSC01117.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 600 | 3 | 42 | 420 | 450
SSC01117.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 600 | 3 | 42 | 420 | 450
SSC01117.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 600 | 3 | 42 | 420 | 450
SSC01117.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 600 | 3 | 42 | 420 | 450
SSC01118.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U42N3S | 600 | 3 | 42 | 420 | 450
SSC01118.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U42N3S | 600 | 3 | 42 | 420 | 450
SSC01118.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U42N3S | 600 | 3 | 42 | 420 | 450
SSC01118.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U42N3S | 600 | 3 | 42 | 420 | 450
SSC01119.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 200 | 3 | 42 | 500 | 150
SSC01119.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 200 | 3 | 42 | 500 | 150
SSC01119.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 200 | 3 | 42 | 500 | 150
SSC01119.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 200 | 3 | 42 | 500 | 150
SSC01120.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 200 | 3 | 42 | 500 | 150
SSC01120.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 200 | 3 | 42 | 500 | 150
SSC01120.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 200 | 3 | 42 | 500 | 150
SSC01120.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 177 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 200 | 3 | 42 | 500 | 150
SSC01121.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 200 | 3 | 42 | 500 | 150
SSC01121.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 200 | 3 | 42 | 500 | 150
SSC01121.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 200 | 3 | 42 | 500 | 150
SSC01121.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 200 | 3 | - | 400 | 125 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 200 | 3 | 42 | 500 | 150
SSC01122.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 200 | 3 | 42 | 500 | 150
SSC01122.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 200 | 3 | 42 | 500 | 150
SSC01122.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 200 | 3 | 42 | 500 | 150
SSC01122.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 221 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 200 | 3 | 42 | 500 | 150
SSC01123.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 200 | 3 | 42 | 500 | 150
SSC01123.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 200 | 3 | 42 | 500 | 150
SSC01123.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 200 | 3 | 42 | 500 | 150
SSC01123.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 200 | 3 | 42 | 500 | 150
SSC01124.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 200 | 3 | 42 | 500 | 150
SSC01124.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 200 | 3 | 42 | 500 | 150
SSC01124.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 200 | 3 | 42 | 500 | 150
SSC01124.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 285 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 200 | 3 | 42 | 500 | 150
SSC01125.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 200 | 3 | 42 | 500 | 150
SSC01125.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 200 | 3 | 42 | 500 | 150
SSC01125.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 200 | 3 | 42 | 500 | 150
SSC01125.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 200 | 3 | 42 | 500 | 150
SSC01126.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 200 | 3 | 42 | 500 | 150
SSC01126.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 200 | 3 | 42 | 500 | 150
SSC01126.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 200 | 3 | 42 | 500 | 150
SSC01126.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 359 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 200 | 3 | 42 | 500 | 150
SSC01127.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 200 | 3 | 42 | 500 | 150
SSC01127.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 200 | 3 | 42 | 500 | 150
SSC01127.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 200 | 3 | 42 | 500 | 150
SSC01127.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 200 | 3 | 42 | 500 | 150
SSC01128.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 200 | 3 | 42 | 500 | 150
SSC01128.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 200 | 3 | 42 | 500 | 150
SSC01128.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 200 | 3 | 42 | 500 | 150
SSC01128.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 200 | 3 | - | 600 | 200 | 200 | 3 | 65 | 414 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 200 | 3 | 42 | 500 | 150
SSC01129.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 208 | 3 | 42 | 500 | 150
SSC01129.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 208 | 3 | 42 | 500 | 150
SSC01129.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 208 | 3 | 42 | 500 | 150
SSC01129.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 208 | 3 | - | 250 | 75 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 208 | 3 | 42 | 500 | 150
SSC01130.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 208 | 3 | 42 | 500 | 150
SSC01130.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 208 | 3 | 42 | 500 | 150
SSC01130.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 208 | 3 | 42 | 500 | 150
SSC01130.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 169 | 60 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 208 | 3 | 42 | 500 | 150
SSC01131.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 208 | 3 | 42 | 500 | 150
SSC01131.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 208 | 3 | 42 | 500 | 150
SSC01131.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 208 | 3 | 42 | 500 | 150
SSC01131.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 208 | 3 | - | 400 | 150 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 208 | 3 | 42 | 500 | 150
SSC01132.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 208 | 3 | 42 | 500 | 150
SSC01132.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 208 | 3 | 42 | 500 | 150
SSC01132.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 208 | 3 | 42 | 500 | 150
SSC01132.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 211 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 208 | 3 | 42 | 500 | 150
SSC01133.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 208 | 3 | 42 | 500 | 150
SSC01133.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 208 | 3 | 42 | 500 | 150
SSC01133.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 208 | 3 | 42 | 500 | 150
SSC01133.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 208 | 3 | 42 | 500 | 150
SSC01134.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 208 | 3 | 42 | 500 | 150
SSC01134.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 208 | 3 | 42 | 500 | 150
SSC01134.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 208 | 3 | 42 | 500 | 150
SSC01134.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 273 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 208 | 3 | 42 | 500 | 150
SSC01135.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 208 | 3 | 42 | 500 | 150
SSC01135.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 208 | 3 | 42 | 500 | 150
SSC01135.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 208 | 3 | 42 | 500 | 150
SSC01135.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 208 | 3 | 42 | 500 | 150
SSC01136.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 208 | 3 | 42 | 500 | 150
SSC01136.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 208 | 3 | 42 | 500 | 150
SSC01136.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 208 | 3 | 42 | 500 | 150
SSC01136.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 343 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 208 | 3 | 42 | 500 | 150
SSC01137.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 208 | 3 | 42 | 500 | 150
SSC01137.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 208 | 3 | 42 | 500 | 150
SSC01137.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 208 | 3 | 42 | 500 | 150
SSC01137.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 208 | 3 | 42 | 500 | 150
SSC01138.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 208 | 3 | 42 | 500 | 150
SSC01138.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 208 | 3 | 42 | 500 | 150
SSC01138.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 208 | 3 | 42 | 500 | 150
SSC01138.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 208 | 3 | - | 600 | 200 | 208 | 3 | 65 | 396 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 208 | 3 | 42 | 500 | 150
SSC01139.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 240 | 3 | 42 | 500 | 200
SSC01139.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 240 | 3 | 42 | 500 | 200
SSC01139.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 240 | 3 | 42 | 500 | 200
SSC01139.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 240 | 3 | 42 | 500 | 200
SSC01140.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 240 | 3 | 42 | 500 | 200
SSC01140.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 240 | 3 | 42 | 500 | 200
SSC01140.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 240 | 3 | 42 | 500 | 200
SSC01140.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 192 | 75 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 240 | 3 | 42 | 500 | 200
SSC01141.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 240 | 3 | 42 | 500 | 200
SSC01141.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 240 | 3 | 42 | 500 | 200
SSC01141.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 240 | 3 | 42 | 500 | 200
SSC01141.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 240 | 3 | - | 400 | 150 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 240 | 3 | 42 | 500 | 200
SSC01142.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 240 | 3 | 42 | 500 | 200
SSC01142.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 240 | 3 | 42 | 500 | 200
SSC01142.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 240 | 3 | 42 | 500 | 200
SSC01142.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 248 | 100 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 240 | 3 | 42 | 500 | 200
SSC01143.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 240 | 3 | 42 | 500 | 200
SSC01143.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 240 | 3 | 42 | 500 | 200
SSC01143.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 240 | 3 | 42 | 500 | 200
SSC01143.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 240 | 3 | 42 | 500 | 200
SSC01144.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 240 | 3 | 42 | 500 | 200
SSC01144.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 240 | 3 | 42 | 500 | 200
SSC01144.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 240 | 3 | 42 | 500 | 200
SSC01144.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 312 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 240 | 3 | 42 | 500 | 200
SSC01145.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 240 | 3 | 42 | 500 | 200
SSC01145.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 240 | 3 | 42 | 500 | 200
SSC01145.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 240 | 3 | 42 | 500 | 200
SSC01145.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 240 | 3 | 42 | 500 | 200
SSC01146.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 240 | 3 | 42 | 500 | 200
SSC01146.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 240 | 3 | 42 | 500 | 200
SSC01146.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 240 | 3 | 42 | 500 | 200
SSC01146.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 360 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 240 | 3 | 42 | 500 | 200
SSC01147.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 240 | 3 | 42 | 500 | 200
SSC01147.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 240 | 3 | 42 | 500 | 200
SSC01147.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 240 | 3 | 42 | 500 | 200
SSC01147.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 240 | 3 | 42 | 500 | 200
SSC01148.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 240 | 3 | 42 | 500 | 200
SSC01148.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 240 | 3 | 42 | 500 | 200
SSC01148.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 240 | 3 | 42 | 500 | 200
SSC01148.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 240 | 3 | - | 600 | 200 | 240 | 3 | 65 | 480 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 240 | 3 | 42 | 500 | 200
SSC01149.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 480 | 3 | 42 | 500 | 400
SSC01149.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 480 | 3 | 42 | 500 | 400
SSC01149.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 480 | 3 | 42 | 500 | 400
SSC01149.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP250C5* | 480 | 3 | - | 250 | 200 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 480 | 3 | 42 | 500 | 400
SSC01150.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 480 | 3 | 42 | 500 | 400
SSC01150.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 480 | 3 | 42 | 500 | 400
SSC01150.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 480 | 3 | 42 | 500 | 400
SSC01150.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400F5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 156 | 125 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 480 | 3 | 42 | 500 | 400
SSC01151.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 480 | 3 | 42 | 500 | 400
SSC01151.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 480 | 3 | 42 | 500 | 400
SSC01151.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 480 | 3 | 42 | 500 | 400
SSC01151.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 480 | 3 | 42 | 500 | 400
SSC01152.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 480 | 3 | 42 | 500 | 400
SSC01152.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 480 | 3 | 42 | 500 | 400
SSC01152.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 480 | 3 | 42 | 500 | 400
SSC01152.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 180 | 150 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 480 | 3 | 42 | 500 | 400
SSC01153.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 480 | 3 | 42 | 500 | 400
SSC01153.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 480 | 3 | 42 | 500 | 400
SSC01153.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 480 | 3 | 42 | 500 | 400
SSC01153.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 480 | 3 | - | 400 | 300 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 480 | 3 | 42 | 500 | 400
SSC01154.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 480 | 3 | 42 | 500 | 400
SSC01154.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 480 | 3 | 42 | 500 | 400
SSC01154.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 480 | 3 | 42 | 500 | 400
SSC01154.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 240 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 480 | 3 | 42 | 500 | 400
SSC01155.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 480 | 3 | 42 | 500 | 400
SSC01155.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 480 | 3 | 42 | 500 | 400
SSC01155.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 480 | 3 | 42 | 500 | 400
SSC01155.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 480 | 3 | 42 | 500 | 400
SSC01156.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 480 | 3 | 42 | 500 | 400
SSC01156.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 480 | 3 | 42 | 500 | 400
SSC01156.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 480 | 3 | 42 | 500 | 400
SSC01156.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 302 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 480 | 3 | 42 | 500 | 400
SSC01157.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 480 | 3 | 42 | 500 | 400
SSC01157.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 480 | 3 | 42 | 500 | 400
SSC01157.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 480 | 3 | 42 | 500 | 400
SSC01157.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 480 | 3 | 42 | 500 | 400
SSC01158.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 480 | 3 | 42 | 500 | 400
SSC01158.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 480 | 3 | 42 | 500 | 400
SSC01158.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 480 | 3 | 42 | 500 | 400
SSC01158.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 361 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 480 | 3 | 42 | 500 | 400
SSC01159.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 480 | 3 | 42 | 500 | 400
SSC01159.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 480 | 3 | 42 | 500 | 400
SSC01159.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 480 | 3 | 42 | 500 | 400
SSC01159.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 480 | 3 | 42 | 500 | 400
SSC01160.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 480 | 3 | 42 | 500 | 400
SSC01160.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 480 | 3 | 42 | 500 | 400
SSC01160.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 480 | 3 | 42 | 500 | 400
SSC01160.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 414 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 480 | 3 | 42 | 500 | 400
SSC01161.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 480 | 3 | 42 | 500 | 400
SSC01161.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 480 | 3 | 42 | 500 | 400
SSC01161.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 480 | 3 | 42 | 500 | 400
SSC01161.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 480 | 3 | 42 | 500 | 400
SSC01162.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 480 | 3 | 42 | 500 | 400
SSC01162.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 480 | 3 | 42 | 500 | 400
SSC01162.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 480 | 3 | 42 | 500 | 400
SSC01162.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 480 | 3 | - | 600 | 500 | 480 | 3 | 65 | 477 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 480 | 3 | 42 | 500 | 400
SSC01163.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 600 | 3 | 42 | 500 | 500
SSC01163.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 600 | 3 | 42 | 500 | 500
SSC01163.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 600 | 3 | 42 | 500 | 500
SSC01163.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400D5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 600 | 3 | 42 | 500 | 500
SSC01164.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 600 | 3 | 42 | 500 | 500
SSC01164.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 600 | 3 | 42 | 500 | 500
SSC01164.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 600 | 3 | 42 | 500 | 500
SSC01164.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400J5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 192 | 200 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 600 | 3 | 42 | 500 | 500
SSC01165.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 600 | 3 | 42 | 500 | 500
SSC01165.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 600 | 3 | 42 | 500 | 500
SSC01165.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 600 | 3 | 42 | 500 | 500
SSC01165.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP400G5* | 600 | 3 | - | 400 | 400 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 600 | 3 | 42 | 500 | 500
SSC01166.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 600 | 3 | 42 | 500 | 500
SSC01166.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 600 | 3 | 42 | 500 | 500
SSC01166.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 600 | 3 | 42 | 500 | 500
SSC01166.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 242 | 250 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 600 | 3 | 42 | 500 | 500
SSC01167.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 600 | 3 | 42 | 500 | 500
SSC01167.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 600 | 3 | 42 | 500 | 500
SSC01167.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 600 | 3 | 42 | 500 | 500
SSC01167.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 600 | 3 | 42 | 500 | 500
SSC01168.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 600 | 3 | 42 | 500 | 500
SSC01168.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 600 | 3 | 42 | 500 | 500
SSC01168.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 600 | 3 | 42 | 500 | 500
SSC01168.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 289 | 300 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 600 | 3 | 42 | 500 | 500
SSC01169.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 600 | 3 | 42 | 500 | 500
SSC01169.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 600 | 3 | 42 | 500 | 500
SSC01169.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 600 | 3 | 42 | 500 | 500
SSC01169.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600X6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 600 | 3 | 42 | 500 | 500
SSC01170.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 600 | 3 | 42 | 500 | 500
SSC01170.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 600 | 3 | 42 | 500 | 500
SSC01170.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 600 | 3 | 42 | 500 | 500
SSC01170.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 336 | 350 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 600 | 3 | 42 | 500 | 500
SSC01171.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 600 | 3 | 42 | 500 | 500
SSC01171.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 600 | 3 | 42 | 500 | 500
SSC01171.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 600 | 3 | 42 | 500 | 500
SSC01171.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 600 | 3 | 42 | 500 | 500
SSC01172.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 600 | 3 | 42 | 500 | 500
SSC01172.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 600 | 3 | 42 | 500 | 500
SSC01172.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 600 | 3 | 42 | 500 | 500
SSC01172.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 382 | 400 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 600 | 3 | 42 | 500 | 500
SSC01173.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 600 | 3 | 42 | 500 | 500
SSC01173.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 600 | 3 | 42 | 500 | 500
SSC01173.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 600 | 3 | 42 | 500 | 500
SSC01173.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 600 | 3 | 42 | 500 | 500
SSC01174.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 600 | 3 | 42 | 500 | 500
SSC01174.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 600 | 3 | 42 | 500 | 500
SSC01174.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 600 | 3 | 42 | 500 | 500
SSC01174.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600L6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 412 | 450 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 600 | 3 | 42 | 500 | 500
SSC01175.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 600 | 3 | 42 | 500 | 500
SSC01175.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 600 | 3 | 42 | 500 | 500
SSC01175.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 600 | 3 | 42 | 500 | 500
SSC01175.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP600Y6* | 600 | 3 | - | 600 | 500 | 600 | 3 | 18 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 600 | 3 | 42 | 500 | 500
SSC01176.01 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 500 | 600 | 3 | 18 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801U50N3S | 600 | 3 | 42 | 500 | 500
SSC01176.02 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 500 | 600 | 3 | 18 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S801+U50N3S | 600 | 3 | 42 | 500 | 500
SSC01176.03 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 500 | 600 | 3 | 18 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811U50N3S | 600 | 3 | 42 | 500 | 500
SSC01176.04 | E176513 | Vol. 1, Sec. 4 | D | ICB | Eaton | HMCP800X7* | 600 | 3 | - | 800 | 500 | 600 | 3 | 18 | 472 | 500 | 17437 | 1,2 | n/a
|  |  |  | RVSS | Eaton | S811+U50N3S | 600 | 3 | 42 | 500 | 500
Conditions of Aceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
z

## S752 Softstarter Type D
Issued: 2008-02-05
Last Revised: 2008-02-05
Certification of Combined Components in Combination Motor Controllers for use in Industrial Control Panels
ID Number | Combination Type | Individual Component | [6 empty] | Combination SCCR | [5 empty] | Conditions of Acceptability | Combination UL Starter File | Motor Control Center UL File
|  | Component Type | Manufacturer | Partial Catalog Nos. | Ratings |  |  |  | SCCR kA | Volts | Phase | Hp | NEC FLC | Min. Enclosure Volume (cu. ft.)
[5 empty] | SCCR kA | Max. Amps | Volts | No. Poles
S752D001 | D | ICB | Eaton | HMCP007 | - | 7 | 200 | 3 | 65 | 200 | 3 | 1/2 | 2.5 | 0.69 | (1) (5) (7a) | - - | E47048 Vol.2 Sec. 5
|  | STR |  | S752L04N3S | 5 | 4.4
S752D002 |  | ICB |  | HMCP007 | - | 7 | [5 empty] | 3/4 | 3.7
|  | STR |  | S752L04N3S | 5 | 4.4
S752D003 | D | ICB | Eaton | HMCP007 | - | 7 | 208 | 3 | 65 | 208 | 3 | 1/2 | 2.4 | 0.69 | (1) (5) (7a) | - - | E47048 Vol.2 Sec. 5
|  | STR |  | S752L04N3S | 5 | 4.4
S752D004 |  | ICB |  | HMCP007 | - | 7 | [5 empty] | 3/4 | 3.5
|  | STR |  | S752L04N3S | 5 | 4.4
S752D005 | D | ICB | Eaton | HMCP007 | - | 7 | 230 | 3 | 65 | 230 | 3 | 1/2 | 2.2 | 0.69 | (1) (5) (7a) | - - | E47048 Vol.2 Sec. 5
|  | STR |  | S752L04N3S | 5 | 4.4
S752D006 |  | ICB |  | HMCP007 | - | 7 | [5 empty] | 3/4 | 3.2
|  | STR |  | S752L04N3S | 5 | 4.4
S752D007 | D | ICB | Eaton | HMCP003 | - | 3 | 460 | 3 | 65 | 460 | 3 | 1/2 | 1.1 | 0.69 | (1) (5) (7a) | - - | E47048 Vol.2 Sec. 5
|  | STR |  | S752L04N3S | 5 | 4.4
S752D008 |  | ICB |  | HMCP003 | - | 3 | [5 empty] | 3/4 | 1.6
|  | STR |  | S752L04N3S | 5 | 4.4
S752D009 |  | ICB |  | HMCP007 | - | 7 | [5 empty] | 1 | 2.1
|  | STR |  | S752L04N3S | 5 | 4.4
S752D010 |  | ICB |  | HMCP007 | - | 7 | [5 empty] | 1.5 | 3
|  | STR |  | S752L04N3S | 5 | 4.4
S752D011 |  | ICB |  | HMCP007 | - | 7 | [5 empty] | 2 | 3.4
|  | STR |  | S752L04N3S | 5 | 4.4
S752D012 | D | ICB | Eaton | HMCP015 | - | 15 | 200 | 3 | 65 | 200 | 3 | 1 | 4.8 | 0.69 | (1) (5) (7a) | - - | E47048 Vol.2 Sec. 5
|  | STR |  | S752L09N3S | 5 | 9
S752D013 |  | ICB |  | HMCP015 | - | 15 | [5 empty] | 1-1/2 | 6.9
|  | STR |  | S752L09N3S | 5 | 9
S752D014 |  | ICB |  | HMCP015 | - | 15 | [5 empty] | 2 | 7.8
|  | STR |  | S752L09N3S | 5 | 9
S752D015 | D | ICB | Eaton | HMCP015 | - | 15 | 208 | 3 | 65 | 208 | 3 | 1 | 4.6 | 0.69 | (1) (5) (7a) | - - | E47048 Vol.2 Sec. 5
|  | STR |  | S752L09N3S | 5 | 9
S752D016 |  | ICB |  | HMCP015 | - | 15 | [5 empty] | 1-1/2 | 6.6
|  | STR |  | S752L09N3S | 5 | 9
S752D017 |  | ICB |  | HMCP015 | - | 15 | [5 empty] | 2 | 7.5
|  | STR |  | S752L09N3S | 5 | 9
S752D018 | D | ICB | Eaton | HMCP015 | - | 15 | 230 | 3 | 65 | 230 | 3 | 1 | 4.2 | 0.69 | (1) (5) (7a) | - - | E47048 Vol.2 Sec. 5
|  | STR |  | S752L09N3S | 5 | 9
S752D019 |  | ICB |  | HMCP015 | - | 15 | [5 empty] | 1-1/2 | 6
|  | STR |  | S752L09N3S | 5 | 9
S752D020 |  | ICB |  | HMCP015 | - | 15 | [5 empty] | 2 | 6.8
|  | STR |  | S752L09N3S | 5 | 9
S752D021 | D | ICB | Eaton | HMCP015 | - | 15 | 460 | 3 | 65 | 460 | 3 | 3 | 4.8 | 0.69 | (1) (5) (7a) | - - | E47048 Vol.2 Sec. 5
|  | STR |  | S752L09N3S | 5 | 9
S752D022 |  | ICB |  | HMCP015 | - | 15 | [5 empty] | 5 | 7.6
|  | STR |  | S752L09N3S | 5 | 9
S752D023 | D | ICB | Eaton | HMCP030 | - | 30 | 200 | 3 | 65 | 200 | 3 | 3 | 11 | 0.69 | (1) (5) (7a) | - - | E47048 Vol.2 Sec. 5
|  | STR |  | S752L16N3S | 5 | 16
S752D024 | D | ICB | Eaton | HMCP030 | - | 30 | 208 | 3 | 65 | 208 | 3 | 3 | 10.6 | 0.69 | (1) (5) (7a) | - - | E47048 Vol.2 Sec. 5
|  | STR |  | S752L16N3S | 5 | 16
S752D025 | D | ICB | Eaton | HMCP030 | - | 30 | 230 | 3 | 65 | 230 | 3 | 3 | 9.6 | 0.69 | (1) (5) (7a) | - - | E47048 Vol.2 Sec. 5
|  | STR |  | S752L16N3S | 5 | 16
S752D026 | D | ICB | Eaton | HMCP030 | - | 30 | 460 | 3 | 65 | 460 | 3 | 7.5 | 11 | 0.69 | (1) (5) (7a) | - - | E47048 Vol.2 Sec. 5
|  | STR |  | S752L16N3S | 5 | 16
S752D027 | D | ICB | Eaton | HMCP050 | - | 50 | 200 | 3 | 65 | 200 | 3 | 5 | 17.5 | 0.69 | (1) (5) (7a) | - - | E47048 Vol.2 Sec. 5
|  | STR |  | S752L27N3S | 5 | 27
S752D028 | D | ICB | Eaton | HMCP030 | - | 30 | 208 | 3 | 65 | 208 | 3 | 5 | 16.7 | 0.69 | (1) (5) (7a) | - - | E47048 Vol.2 Sec. 5
|  | STR |  | S752L27N3S | 5 | 27
S752D029 | D | ICB | Eaton | HMCP030 | - | 30 | 230 | 3 | 65 | 230 | 3 | 5 | 15.2 | 0.69 | (1) (5) (7a) | - - | E47048 Vol.2 Sec. 5
|  | STR |  | S752L27N3S | 5 | 27
S752D030 |  | ICB |  | HMCP050 | - | 50 | [5 empty] | 7.5 | 22 | 0.69 | (1) (5) (7a) | - -
|  | STR |  | S752L27N3S | 5 | 27
S752D031 | D | ICB | Eaton | HMCP030 | - | 30 | 460 | 3 | 65 | 460 | 3 | 10 | 14 | 0.69 | (1) (5) (7a) | - - | E47408 Vol.2 Sec. 5
|  | STR |  | S752L27N3S | 5 | 27
S752D032 |  | ICB |  | HMCP050 | - | 50 | [5 empty] | 15 | 21
|  | STR |  | S752L27N3S | 5 | 27
S752D033 | D | ICB | Eaton | HMCP050 | - | 50 | 200 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 0.69 | (1) (5) (7b) | - - | E47048 Vol.2 Sec. 5
|  | STR |  | S752L50N3S | 5 | 50
S752D034 |  | ICB |  | HMCP070 | - | 70 | [5 empty] | 10 | 32.2
|  | STR |  | S752L50N3S | 5 | 50
S752D035 | D | ICB | Eaton | HMCP050 | - | 50 | 208 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 0.69 | (1) (5) (7a) | - - | E47048 Vol.2 Sec. 5
|  | STR |  | S752L50N3S | 5 | 50
S752D036 |  | ICB |  | HMCP050 | - | 50 | [5 empty] | 10 | 30.8 |  | (1) (5) (7b)
|  | STR |  | S752L50N3S | 5 | 50
S752D037 | D | ICB | Eaton | HMCP050 | - | 50 | 230 | 3 | 65 | 230 | 3 | 10 | 28 | 0.69 | (1) (5) (7b) | - - | E47048 Vol.2 Sec. 5
|  | STR |  | S752L50N3S | 5 | 50
S752D038 |  | ICB |  | HMCP100 | - | 100 | [5 empty] | 15 | 42 |  | (1) (5) (7c)
|  | STR |  | S752L50N3S | 5 | 50
S752D039 | D | ICB | Eaton | HMCP050 | - | 50 | 460 | 3 | 65 | 460 | 3 | 20 | 27 | 0.69 | (1) (5) (7b) | - - | E47048 Vol.2 Sec. 5
|  | ICB |  | S752L50N3S | 5 | 50
S752040 |  | ICB |  | HMCP070 | - | 70 | [5 empty] | 25 | 34 |  | (1) (5) (7c)
|  | ICB |  | S752L50N3S | 5 | 50
S752041 |  | ICB |  | HMCP100 | - | 100 | [5 empty] | 30 | 40 |  | (1) (5) (7c)
|  | STR |  | S752L50N3S | 5 | 50
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = Additional Conditions of Acceptability may be specified in the individual Tables.
(7) See Table 7 for internal wiring between load side of short circuit protective device & line side of starter.
Table 7 - Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
|  | Wire Code | Wire Size | Wire Code | Wire Size
|  | 7a | 12 awg. | 7j | 4/0 awg.
|  | 7b | 10 awg. | 7k | 250kcml
|  | 7c | 8 awg. | 7l | 350kcml
|  | 7d | 6 awg. | 7m | 4/0 awg. (3)
|  | 7e | 4 awg. | 7n | 4/0 awg. (4)
|  | 7f | 2 awg. | 7p | 250kcml (2)
|  | 7g | 1/0 awg. | 7r | 350kcml (3)
|  | 7h | 2/0 awg. | 7s | 4/0 awg. (2)