## AM317 - AM357 Type F
Issued: 2006-05-18
Last Revised: 2006-05-18
Combination Motor Controllers for use in Industrial Control Panels
ID Number | Combination Type | Manufacturer | Partial Catalog No. | FLA Dial Range | 1-Ph Hp Ratings |  | 3 Ph. Hp Ratings |  |  | SCCR (kA) 480Y / 277V | Min. Enclosure (cu.-ft.) | Conditions of Acceptability | UL File
[5 empty] | 115V | 230V | 200V | 230V | 460V
AMF01 | F | Eaton | AM317ANS3* | 0.11 - 0.16 | - | - | - | - | - | 65 | 0.148 | 1 | E218618 Vol. 1 Sec. 1
AMF02 |  |  | AM317BNS3* | 0.14 - 0.20 | - | - | - | - | -
AMF03 |  |  | AM317CNS3* | 0.18 - 0.25 | - | - | - | - | -
AMF04 |  |  | AM317DNS3* | 0.22 - 0.32 | - | - | - | - | -
AMF05 | F | Eaton | AM317ENS3* | 0.28 - 0.40 | - | - | - | - | - | 65 | 0.148 | 1 | E218618 Vol. 1 Sec. 1
AMF06 |  |  | AM317FNS3* | 0.35 - 0.50 | - | - | - | - | -
AMF07 |  |  | AM317GNS3* | 0.45 - 0.63 | - | - | - | - | -
AMF08 |  |  | AM317HNS3* | 0.55 - 0.80 | - | - | - | - | 1/4
AMF09 | F | Eaton | AM317JNS3* | 0.70 1.0 | - | - | - | - | 1/2 | 65 | 0.148 | 1 | E218618 Vol. 1 Sec. 1
AMF10 |  |  | AM317KNS3* | 0.9 - 1.25 | - | - | - | 1/4 | 3/4
AMF11 |  |  | AM317LNS3* | 1.1 - 1.6 | - | 1/10 | 1/4 | 1/3 | 3/4
AMF12 |  |  | AM317MNS3* | 1.4 - 2.0 | - | 1/8 | 1/3 | 1/2 | 1
AMF13 | F | Eaton | AM317NNS3* | 1.8 - 2.5 | - | 1/6 | 1/2 | 1/2 | 1-1/2 | 65 | 0.148 | 1 | E218618 Vol. 1 Sec. 1
AMF14 |  |  | AM317PNS3* | 2.2 - 3.2 | 1/10 | 1/4 | 3/4 | 3/4 | 1-1/2
AMF15 |  |  | AM317RNS3* | 2.8 - 4.0 | 1/8 | 1/3 | 3/4 | 1 | 2
AMF16 |  |  | AM317SNS3* | 3.5 - 5.0 | 1/6 | 1/2 | 1 | 1 | 3
AMF17 | F | Eaton | AM317TNS3* | 4.5 - 6.3 | 1/4 | 3/4 | 1-1/2 | 1-1/2 | 5 | 65 | 0.148 | 1 | E218618 Vol. 1 Sec. 1
AMF18 |  |  | AM317UNS3* | 5.5 - 8.0 | 1/3 | 1 | 2 | 2 | 5
AMF19 |  |  | AM317VNS3* | 7.0 - 10 | 1/2 | 1-1/2 | 3 | 3 | 7-1/2
AMF20 | F | Eaton | AM357ANS3* | 0.11 - 0.16 | - | - | - | - | - | 65 | 0.148 | 1 | E218618 Vol. 1 Sec. 1
AMF21 |  |  | AM357BNS3* | 0.14 - 0.20 | - | - | - | - | -
AMF22 |  |  | AM357CNS3* | 0.18 - 0.25 | - | - | - | - | -
AMF23 |  |  | AM357DNS3* | 0.22 - 0.32 | - | - | - | - | -
AMF24 | F | Eaton | AM357ENS3* | 0.28 - 0.40 | - | - | - | - | - | 65 | 0.148 | 1 | E218618 Vol. 1 Sec. 1
AMF25 |  |  | AM357FNS3* | 0.35 - 0.50 | - | - | - | - | -
AMF26 |  |  | AM357GNS3* | 0.45 - 0.63 | - | - | - | - | -
AMF27 |  |  | AM357HNS3* | 0.55 - 0.80 | - | - | - | - | 1/4
AMF28 | F | Eaton | AM357JNS3* | 0.70 1.0 | - | - | - | - | 1/2 | 65 | 0.148 | 1 | E218618 Vol. 1 Sec. 1
AMF29 |  |  | AM357KNS3* | 0.9 - 1.25 | - | - | - | 1/4 | 3/4
AMF30 |  |  | AM357LNS3* | 1.1 - 1.6 | - | 1/10 | 1/4 | 1/3 | 3/4
AMF31 |  |  | AM357MNS3* | 1.4 - 2.0 | - | 1/8 | 1/3 | 1/2 | 1
AMF32 | F | Eaton | AM357NNS3* | 1.8 - 2.5 | - | 1/6 | 1/2 | 1/2 | 1-1/2 | 65 | 0.148 | 1 | E218618 Vol. 1 Sec. 1
AMF33 |  |  | AM357PNS3* | 2.2 - 3.2 | 1/10 | 1/4 | 3/4 | 3/4 | 1-1/2
AMF34 |  |  | AM357RNS3* | 2.8 - 4.0 | 1/8 | 1/3 | 3/4 | 1 | 2
AMF35 |  |  | AM357SNS3* | 3.5 - 5.0 | 1/6 | 1/2 | 1 | 1 | 3
AMF36 | F | Eaton | AM357TNS3* | 4.5 - 6.3 | 1/4 | 3/4 | 1-1/2 | 1-1/2 | 5 | 65 | 0.148 | 1 | E218618 Vol. 1 Sec. 1
AMF37 |  |  | AM357UNS3* | 5.5 - 8.0 | 1/3 | 1 | 2 | 2 | 5
AMF38 |  |  | AM357VNS3* | 7.0 - 10 | 1/2 | 1-1/2 | 3 | 3 | 7-1/2
Conditions of Acceptability:
1 = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.

## Freedom Type F
Issued: 2006-05-18
Last Revised: 2006-05-18
Combination Motor Controllers for use in Industrial Control Panels
ID Number | Combination Type | Manufacturer | Partial Catalog No. | FLA Dial Range | 1-Ph Hp Ratings |  | 3 Ph. Hp Ratings |  |  | SCCR (kA) 480Y / 277V | Min. Enclosure (cu.-ft.) | Conditions of Acceptability | UL File
[5 empty] | 115V | 230V | 200V | 230V | 460V
FRF001 | F | Eaton | AE317ANS3* | 0.11 - 0.16 | - | - | - | - | - | 65 | 0.148 | 1 | E218618 Vol. 1 Sec. 1
FRF002 |  |  | AE317BNS3* | 0.14 - 0.2 | - | - | - | - | -
FRF003 |  |  | AE317CNS3* | 0.18 - 0.25 | - | - | - | - | -
FRF004 |  |  | AE317DNS3* | 0.22 - 0.32 | - | - | - | - | -
FRF005 | F | Eaton | AE317ENS3* | 0.28 - 0.4 | - | - | - | - | - | 65 | 0.148 | 1
FRF006 |  |  | AE317FNS3* | 0.35 - 0.5 | - | - | - | - | -
FRF007 |  |  | AE317GNS3* | 0.45 - 0.63 | - | - | - | - | -
FRF008 |  |  | AE317HNS3* | 0.55 - 0.8 | - | - | - | - | 1/4
FRF009 | F | Eaton | AE317JNS3* | 0.7- 1.0 | - | - | - | - | 1/2 | 65 | 0.148 | 1 | E218618 Vol. 1 Sec. 1
FRF010 |  |  | AE317KNS3* | 0.9 - 1.25 | - | - | - | 1/4 | 3/4
FRF011 |  |  | AE317LNS3* | 1.1 - 1.6 | - | 1/10 | 1/4 | 1/3 | 3/4
FRF012 |  |  | AE317MNS3* | 1.4 - 2.0 | - | 1/8 | 1/3 | 1/2 | 1
FRF013 | F | Eaton | AE317NNS3* | 1.8 - 2.5 | - | 1/6 | 1/2 | 1/2 | 1-1/2 | 65 | 0.148 | 1
FRF014 |  |  | AE317PNS3* | 2.2 - 3.2 | 1/10 | 1/4 | 3/4 | 3/4 | 1-1/2
FRF015 |  |  | AE317RNS3* | 2.8 - 4.0 | 1/8 | 1/3 | 3/4 | 1 | 2
FRF016 |  |  | AE317SNS3* | 3.5 - 5.0 | 1/6 | 1/2 | 1 | 1 | 3
FRF017 | F | Eaton | AE317TNS3* | 4.5 - 6.3 | 1/4 | 3/4 | 1-1/2 | 1-1/2 | 5 | 65 | 0.148 | 1 | E218618 Vol. 1 Sec. 1
FRF018 |  |  | AE317UNS3* | 5.5 - 8.0 | 1/3 | 1 | 2 | 2 | 5
FRF019 |  |  | AE317VNS3* | 7 - 10 | 1/2 | 1-1/2 | 3 | 3 | 7-1/2
FRF020 |  |  | AE317WNS3* | 9 - 12.5 | 1/2 | 2 | 3 | 3 | 7-1/2
FRF021 | F | Eaton | AE317XNS3* | 11 - 16 | 1 | 3 | 5 | 5 | 10 | 65 | 0.148 | 1
FRF022 |  |  | AE317YNS3* | 14 - 20 | 1-1/2 | 3 | 5 | 7-1/2 | 15
FRF023 |  |  | AE317ZNS3* | 17 - 22 | 2 | 3 | 7-1/2 | 7-1/2 | 15
FRF024 | F | Eaton | AE357ANS3* | 0.11 - 0.16 | - | - | - | - | - | 65 | 0.148 | 1 | E218618 Vol. 1 Sec. 1
FRF025 |  |  | AE357BNS3* | 0.14 - 0.2 | - | - | - | - | -
FRF026 |  |  | AE357CNS3* | 0.18 - 0.25 | - | - | - | - | -
FRF027 |  |  | AE357DNS3* | 0.22 - 0.32 | - | - | - | - | -
FRF028 | F | Eaton | AE357ENS3* | 0.28 - 0.4 | - | - | - | - | - | 65 | 0.148 | 1
FRF029 |  |  | AE357FNS3* | 0.35 - 0.5 | - | - | - | - | -
FRF030 |  |  | AE357GNS3* | 0.45 - 0.63 | - | - | - | - | -
FRF031 |  |  | AE357HNS3* | 0.55 - 0.8 | - | - | - | - | 1/4
FRF032 | F | Eaton | AE357JNS3* | 0.7- 1.0 | - | - | - | - | 1/2 | 65 | 0.148 | 1 | E218618 Vol. 1 Sec. 1
FRF033 |  |  | AE357KNS3* | 0.9 - 1.25 | - | - | - | 1/4 | 3/4
FRF034 |  |  | AE357LNS3* | 1.1 - 1.6 | - | 1/10 | 1/4 | 1/3 | 3/4
FRF035 |  |  | AE357MNS3* | 1.4 - 2.0 | - | 1/8 | 1/3 | 1/2 | 1
FRF036 | F | Eaton | AE357NNS3* | 1.8 - 2.5 | - | 1/6 | 1/2 | 1/2 | 1-1/2 | 65 | 0.148 | 1
FRF037 |  |  | AE357PNS3* | 2.2 - 3.2 | 1/10 | 1/4 | 3/4 | 3/4 | 1-1/2
FRF038 |  |  | AE357RNS3* | 2.8 - 4.0 | 1/8 | 1/3 | 3/4 | 1 | 2
FRF039 |  |  | AE357SNS3* | 3.5 - 5.0 | 1/6 | 1/2 | 1 | 1 | 3
FRF040 | F | Eaton | AE357TNS3* | 4.5 - 6.3 | 1/4 | 3/4 | 1-1/2 | 1-1/2 | 5 | 65 | 0.148 | 1 | E218618 Vol. 1 Sec. 1
FRF041 |  |  | AE357UNS3* | 5.5 - 8.0 | 1/3 | 1 | 2 | 2 | 5
FRF042 |  |  | AE357VNS3* | 7 - 10 | 1/2 | 1-1/2 | 3 | 3 | 7-1/2
FRF043 |  |  | AE357WNS3* | 9 - 12.5 | 1/2 | 2 | 3 | 3 | 7-1/2
FRF044 | F | Eaton | AE357XNS3* | 11 - 16 | 1 | 3 | 5 | 5 | 10 | 65 | 0.148 | 1
FRF045 |  |  | AE357YNS3* | 14 - 20 | 1-1/2 | 3 | 5 | 7-1/2 | 15
FRF046 |  |  | AE357ZNS3* | 17 - 22 | 2 | 3 | 7-1/2 | 7-1/2 | 15
FRF047 | F | Eaton | AE318LNS3* | 11 - 16 | 1 | 3 | 5 | 5 | 10 | 65 | 0.329 | 1 | E218618 Vol. 1 Sec. 1
FRF048 |  |  | AE318MNS3* | 14 - 20 | 1-1/2 | 3 | 5 | 7-1/2 | 15
FRF049 |  |  | AE318NNS3* | 18 - 25 | 2 | 5 | 7-1/2 | 10 | 20
FRF050 |  |  | AE318PNS3* | 22 - 32 | 2 | 5 | 10 | 10 | 25
FRF051 | F | Eaton | AE318RNS3* | 28 - 40 | 3 | 7-1/2 | 10 | 15 | 30 | 65 | 0.329 | 1
FRF052 |  |  | AE318SNS3* | 36 - 45 | 3 | 7-1/2 | 15 | 15 | 30
FRF053 |  |  | AE318TNS3* | 40 - 50 | 3 | 10 | 15 | 15 | 40
FRF054 | F | Eaton | AE358LNS3* | 11 - 16 | 1 | 3 | 5 | 5 | 10 | 65 | 0.329 | 1 | E218618 Vol. 1 Sec. 1
FRF055 |  |  | AE358MNS3* | 14 - 20 | 1-1/2 | 3 | 5 | 7-1/2 | 15
FRF056 |  |  | AE358NNS3* | 18 - 25 | 2 | 5 | 7-1/2 | 10 | 20
FRF057 |  |  | AE358PNS3* | 22 - 32 | 2 | 5 | 10 | 10 | 25
FRF058 | F | Eaton | AE358RNS3* | 28 - 40 | 3 | 7-1/2 | 10 | 15 | 30 | 65 | 0.329 | 1
FRF059 |  |  | AE358SNS3* | 36 - 45 | 3 | 7-1/2 | 15 | 15 | 30
FRF060 |  |  | AE358TNS3* | 40 - 50 | 3 | 10 | 15 | 15 | 40
FRF061 | F | Eaton | AE319RNS3* | 28 - 40 | 3 | 7-1/2 | 15 | 15 | 30 | 50 | 1.44 | 1 | E218618 Vol. 1 Sec. 1
FRF062 |  |  | AE319SNS3* | 36 - 50 | 5 | 10 | 15 | 20 | 40
FRF063 |  |  | AE319TNS3* | 45 - 63 | 5 | 15 | 20 | 25 | 50
FRF064 | F | Eaton | AE319UNS3* | 57 - 75 | 7-1/2 | 15 | 25 | 25 | 60 | 50 | 1.44 | 1
FRF065 |  |  | AE319VNS3* | 70 - 90 | 10 | 20 | 30 | 30 | 75
FRF066 |  |  | AE319WNS3* | 80 - 100 | 10 | 20 | 30 | 30 | 75
FRF067 | F | Eaton | AE359RNS3* | 28 - 40 | 3 | 7-1/2 | 15 | 15 | 30 | 50 | 1.44 | 1 | E218618 Vol. 1 Sec. 1
FRF068 |  |  | AE359SNS3* | 36 - 50 | 5 | 10 | 15 | 20 | 40
FRF069 |  |  | AE359TNS3* | 45 - 63 | 5 | 15 | 20 | 25 | 50
FRF070 | F | Eaton | AE359UNS3* | 57 - 75 | 7-1/2 | 15 | 25 | 25 | 60 | 50 | 1.44 | 1
FRF071 |  |  | AE359VNS3* | 70 - 90 | 10 | 20 | 30 | 30 | 75
FRF072 |  |  | AE359WNS3* | 80 - 100 | 10 | 20 | 30 | 30 | 75
FRF073 | F | Eaton | AN317ANS3* | 0.11 - 0.16 | - | - | - | - | - | 65 | 0.148 | 1 | E218618 Vol. 1 Sec. 1
FRF074 |  |  | AN317BNS3* | 0.14 - 0.20 | - | - | - | - | -
FRF075 |  |  | AN317CNS3* | 0.18 - 0.25 | - | - | - | - | -
FRF076 |  |  | AN317DNS3* | 0.22 - 0.32 | - | - | - | - | -
FRF077 | F | Eaton | AN317ENS3* | 0.28 - 0.40 | - | - | - | - | - | 65 | 0.148 | 1
FRF078 |  |  | AN317FNS3* | 0.35 - 0.50 | - | - | - | - | -
FRF079 |  |  | AN317GNS3* | 0.45 - 0.63 | - | - | - | - | -
FRF080 |  |  | AN317HNS3* | 0.55 - 0.80 | - | - | - | - | -
FRF081 | F | Eaton | AN317JNS3* | 0.70 - 1.0 | - | - | - | - | 1/2 | 65 | 0.148 | 1 | E218618 Vol. 1 Sec. 1
FRF082 |  |  | AN317KNS3* | 0.90 - 1.25 | - | - | - | - | 3/4
FRF083 |  |  | AN317LNS3* | 1.1 - 1.6 | - | - | - | - | 3/4
FRF084 |  |  | AN317MNS3* | 1.4 - 2.0 | - | - | - | - | 1
FRF085 | F | Eaton | AN317NNS3* | 1.8 - 2.5 | - | - | 1/2 | 1/2 | 1.5 | 65 | 0.148 | 1
FRF086 |  |  | AN317PNS3* | 2.2 - 3.2 | - | - | 3/4 | 3/4 | 1.5
FRF087 |  |  | AN317RNS3* | 2.8 - 4.0 | - | - | 3/4 | 1 | 2
FRF088 |  |  | AN317SNS3* | 3.5 - 5.0 | - | - | 1 | 1 | 3
FRF089 | F | Eaton | AN317TNS3* | 4.5 - 6.3 | - | - | 1.5 | 1.5 | 5 | 65 | 0.148 | 1 | E218618 Vol. 1 Sec. 1
FRF090 |  |  | AN317UNS3* | 5.5 - 8.0 | - | - | 2 | 2 | 5
FRF091 |  |  | AN317VNS3* | 7.0 - 10 | - | - | 3 | 3 | 7.5
FRF092 |  |  | AN317WNS3* | 9.0 - 12.5 | - | - | 3 | 3 | 7.5
FRF093 | F | Eaton | AN317XNS3* | 11 - 16 | - | - | 5 | 5 | 10 | 65 | 0.148 | 1
FRF094 |  |  | AN317YNS3* | 14 - 20 | - | - | 5 | 7.5 | 15
FRF095 |  |  | AN317ZNS3* | 17 - 22 | - | - | 7.5 | 7.5 | 15
FRF096 | F | Eaton | AN357ANS3* | 0.11 - 0.16 | - | - | - | - | - | 65 | 0.148 | 1 | E218618 Vol. 1 Sec. 1
FRF097 |  |  | AN357BNS3* | 0.14 - 0.20 | - | - | - | - | -
FRF098 |  |  | AN357CNS3* | 0.18 - 0.25 | - | - | - | - | -
FRF099 |  |  | AN357DNS3* | 0.22 - 0.32 | - | - | - | - | -
FRF100 | F | Eaton | AN357ENS3* | 0.28 - 0.40 | - | - | - | - | - | 65 | 0.148 | 1
FRF101 |  |  | AN357FNS3* | 0.35 - 0.50 | - | - | - | - | -
FRF102 |  |  | AN357GNS3* | 0.45 - 0.63 | - | - | - | - | -
FRF103 |  |  | AN357HNS3* | 0.55 - 0.80 | - | - | - | - | -
FRF104 | F | Eaton | AN357JNS3* | 0.70 - 1.0 | - | - | - | - | 1/2 | 65 | 0.148 | 1 | E218618 Vol. 1 Sec. 1
FRF105 |  |  | AN357KNS3* | 0.90 - 1.25 | - | - | - | - | 3/4
FRF106 |  |  | AN357LNS3* | 1.1 - 1.6 | - | - | - | - | 3/4
FRF107 |  |  | AN357MNS3* | 1.4 - 2.0 | - | - | - | - | 1
FRF108 | F | Eaton | AN357NNS3* | 1.8 - 2.5 | - | - | 1/2 | 1/2 | 1.5 | 65 | 0.148 | 1
FRF109 |  |  | AN357PNS3* | 2.2 - 3.2 | - | - | 3/4 | 3/4 | 1.5
FRF110 |  |  | AN357RNS3* | 2.8 - 4.0 | - | - | 3/4 | 1 | 2
FRF111 |  |  | AN357SNS3* | 3.5 - 5.0 | - | - | 1 | 1 | 3
FRF112 | F | Eaton | AN357TNS3* | 4.5 - 6.3 | - | - | 1.5 | 1.5 | 5 | 65 | 0.148 | 1 | E218618 Vol. 1 Sec. 1
FRF113 |  |  | AN357UNS3* | 5.5 - 8.0 | - | - | 2 | 2 | 5
FRF114 |  |  | AN357VNS3* | 7.0 - 10 | - | - | 3 | 3 | 7.5
FRF115 |  |  | AN357WNS3* | 9.0 - 12.5 | - | - | 3 | 3 | 7.5
FRF116 | F | Eaton | AN357XNS3* | 11 - 16 | - | - | 5 | 5 | 10 | 65 | 0.148 | 1
FRF117 |  |  | AN357YNS3* | 14 - 20 | - | - | 5 | 7.5 | 15
FRF118 |  |  | AN357ZNS3* | 17 - 22 | - | - | 7.5 | 7.5 | 15
FRF119 | F | Eaton | AN318LNS3* | 11 - 16 | - | - | 5 | 5 | 10 | 65 | 0.329 | 1 | E218618 Vol. 1 Sec. 1
FRF120 |  |  | AN318MNS3* | 14 - 20 | - | - | 5 | 7.5 | 15
FRF121 |  |  | AN318NNS3* | 18 - 25 | - | - | 7.5 | 10 | 20
FRF122 |  |  | AN318PNS3* | 22 - 31 | - | - | 10 | 10 | 25
FRF123 | F | Eaton | AN318RNS3* | 28 - 40 | - | - | 15 | 15 | 30 | 65 | 0.329 | 1
FRF124 |  |  | AN318SNS3* | 36 - 50 | - | - | 15 | 15 | 30
FRF125 |  |  | AN318TNS3* | 40 - 45 | - | - | 15 | 20 | 40
FRF126 | F | Eaton | AN358LNS3* | 11 - 16 | - | - | 5 | 5 | 10 | 65 | 0.329 | 1 | E218618 Vol. 1 Sec. 1
FRF127 |  |  | AN358MNS3* | 14 - 20 | - | - | 5 | 7.5 | 15
FRF128 |  |  | AN358NNS3* | 18 - 25 | - | - | 7.5 | 10 | 20
FRF129 |  |  | AN358PNS3* | 22 - 31 | - | - | 10 | 10 | 25
FRF130 | F | Eaton | AN358RNS3* | 28 - 40 | - | - | 15 | 15 | 30 | 65 | 0.329 | 1
FRF131 |  |  | AN358SNS3* | 36 - 50 | - | - | 15 | 15 | 30
FRF132 |  |  | AN358TNS3* | 40 - 45 | - | - | 15 | 20 | 40
FRF133 | F | Eaton | AN319RNS3* | 28 - 40 | - | - | 15 | 15 | 30 | 50 | 1.44 | 1 | E218618 Vol. 1 Sec. 1
FRF134 |  |  | AN319SNS3* | 36 - 50 | - | - | 15 | 20 | 40
FRF135 |  |  | AN319TNS3* | 45 - 63 | - | - | 20 | 25 | 50
FRF136 | F | Eaton | AN319UNS3* | 57 - 75 | - | - | 25 | 25 | 60 | 50 | 1.44 | 1
FRF137 |  |  | AN319VNS3* | 70 - 90 | - | - | 30 | 30 | 75
FRF138 |  |  | AN319WNS3* | 80 - 100 | - | - | 40 | 40 | 75
FRF139 | F | Eaton | AN359RNS3* | 28 - 40 | - | - | 15 | 15 | 30 | 50 | 1.44 | 1 | E218618 Vol. 1 Sec. 1
FRF140 |  |  | AN359SNS3* | 36 - 50 | - | - | 15 | 20 | 40
FRF141 |  |  | AN359TNS3* | 45 - 63 | - | - | 20 | 25 | 50
FRF142 | F | Eaton | AN359UNS3* | 57 - 75 | - | - | 25 | 25 | 60 | 50 | 1.44 | 1
FRF143 |  |  | AN359VNS3* | 70 - 90 | - | - | 30 | 30 | 75
FRF144 |  |  | AN359WNS3* | 80 - 100 | - | - | 40 | 40 | 75
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified volume in cubic feet. Additional testing of the combination motor controller is not required when installed in an enclosure having the same or larger volume.

## IT-EM Type F
Issued: 2006-05-18
Last Revised: 2006-05-18
Combination Motor Controllers for use in Industrial Control Panels
ID Number | Combination Type | Manufacturer | Partial Catalog No. | FLA Dial Range | 3 Ph. Hp Ratings |  |  |  | SCCR (kA) |  | Min. Enclosure (cu.-ft.) | Conditions of Acceptability | UL File
[5 empty] | 200V | 230V | 460V | 575V | 480V | 600V
ITF001 | F | Eaton | E307ANAX3N* | 0.11 - 0.16 | - | - | - | - | 65 | 50 | 0.148 | 1 | E218618 Vol. 2 Sec. 1
ITF002 |  |  | E307BNAX3N* | 0.14 - 0.20 | - | - | - | - |  | 30
ITF003 |  |  | E307CNAX3N* | 0.18 - 0.25 | - | - | - | -
ITF004 |  |  | E307DNAX3N* | 0.22 - 0.32 | - | - | - | -
ITF005 | F | Eaton | E307ENAX3N* | 0.28 - 0.40 | - | - | - | - | 65 | 30 | 0.148 | 1
ITF006 |  |  | E307FNAX3N* | 0.35 - 0.50 | - | - | - | -
ITF007 |  |  | E307GNAX3N* | 0.45 - 0.63 | - | - | - | -
ITF008 |  |  | E307HNAX3N* | 0.55 - 0.80 | - | - | - | 1/2
ITF009 | F | Eaton | E307JNAX3N* | 0.7 - 1.0 | - | - | 1/2 | 1/2 | 65 | 30 | 0.148 | 1
ITF010 |  |  | E307KNAX3N* | 0.9 - 1.25 | - | - | 3/4 | 3/4
ITF011 |  |  | E307LNAX3N* | 1.1 - 1.6 | - | - | 3/4 | 1
ITF012 |  |  | E307MNAX3N* | 1.4 - 2.0 | - | - | 1 | 1.5
ITF013 | F | Eaton | E307NNAX3N* | 1.8 - 2.5 | 1/2 | 1/2 | 1.5 | 1.5 | 65 | 30 | 0.148 | 1 | E218618 Vol. 2 Sec. 1
ITF014 |  |  | E307PNAX3N* | 2.2 - 3.2 | 3/4 | 3/4 | 1.5 | 2
ITF015 |  |  | E307RNAX3N* | 2.8 - 4.0 | 3/4 | 1 | 2 | 3
ITF016 |  |  | E307SNAX3N* | 3.5 - 5.0 | 1 | 1 | 3 | 3
ITF017 | F | Eaton | E307TNAX3N* | 4.5 - 6.3 | 1.5 | 1.5 | 5 | 5 | 65 | 30 | 0.148 | 1
ITF018 |  |  | E307UNAX3N* | 5.5 - 8.0 | 2 | 2 | 5 | 5
ITF019 |  |  | E307VNAX3N* | 7 - 10 | 3 | 3 | 7.5 | 10
ITF020 |  |  | E307WNBX3N* | 9 - 12.5 | 3 | 3 | 7.5 | 10 |  | 50 | 0.329
ITF021 | F | Eaton | E307XNBX3N* | 11 - 16 | 5 | 5 | 10 | 15 | 65 | 30 | 0.329 | 1
ITF022 |  |  | E307YNBZ3X* | 14 - 20 | 5 | 7.5 | 15 | 20
ITF023 |  |  | E307ZNBX3N* | 17 - 22 | 7.5 | 7.5 | 15 | 20
ITF024 |  |  | E307Z2BX3N* | 20 - 25 | 7.5 | 7.5 | 15 | 20
ITF025 | F | Eaton | E357ANAX3N* | 0.11 - 0.16 | - | - | - | - | 65 | 50 | 0.148 | 1 | E218618 Vol. 2 Sec. 1
ITF026 |  |  | E357BNAX3N* | 0.14 - 0.20 | - | - | - | - |  | 30
ITF027 |  |  | E357CNAX3N* | 0.18 - 0.25 | - | - | - | -
ITF028 |  |  | E357DNAX3N* | 0.22 - 0.32 | - | - | - | -
ITF029 | F | Eaton | E357ENAX3N* | 0.28 - 0.40 | - | - | - | - | 65 | 30 | 0.148 | 1
ITF030 |  |  | E357FNAX3N* | 0.35 - 0.50 | - | - | - | -
ITF031 |  |  | E357GNAX3N* | 0.45 - 0.63 | - | - | - | -
ITF032 |  |  | E357HNAX3N* | 0.55 - 0.80 | - | - | - | 1/2
ITF033 | F | Eaton | E357JNAX3N* | 0.7 - 1.0 | - | - | 1/2 | 1/2 | 65 | 30 | 0.148 | 1
ITF034 |  |  | E357KNAX3N* | 0.9 - 1.25 | - | - | 3/4 | 3/4
ITF035 |  |  | E357LNAX3N* | 1.1 - 1.6 | - | - | 3/4 | 1
ITF036 |  |  | E357MNAX3N* | 1.4 - 2.0 | - | - | 1 | 1.5
ITF037 | F | Eaton | E357NNAX3N* | 1.8 - 2.5 | 1/2 | 1/2 | 1.5 | 1.5 | 65 | 30 | 0.148 | 1 | E218618 Vol. 2 Sec. 1
ITF038 |  |  | E357PNAX3N* | 2.2 - 3.2 | 3/4 | 3/4 | 1.5 | 2
ITF039 |  |  | E357RNAX3N* | 2.8 - 4.0 | 3/4 | 1 | 2 | 3
ITF040 |  |  | E357SNAX3N* | 3.5 - 5.0 | 1 | 1 | 3 | 3
ITF041 | F | Eaton | E357TNAX3N* | 4.5 - 6.3 | 1.5 | 1.5 | 5 | 5 | 65 | 30 | 0.148 | 1
ITF042 |  |  | E357UNAX3N* | 5.5 - 8.0 | 2 | 2 | 5 | 5
ITF043 |  |  | E357VNAX3N* | 7 - 10 | 3 | 3 | 7.5 | 10
ITF044 |  |  | E357WNBX3N* | 9 - 12.5 | 3 | 3 | 7.5 | 10 |  | 50 | 0.329
ITF045 | F | Eaton | E357XNBX3N* | 11 - 16 | 5 | 5 | 10 | 15 | 65 | 30 | 0.329 | 1
ITF046 |  |  | E357YNBZ3X* | 14 - 20 | 5 | 7.5 | 15 | 20
ITF047 |  |  | E357ZNBX3N* | 17 - 22 | 7.5 | 7.5 | 15 | 20
ITF048 |  |  | E357Z2BX3N* | 20 - 25 | 7.5 | 7.5 | 15 | 20
ITF049 | F | Eaton | E308LNCX3N* | 11 - 16 | 5 | 5 | 10 | 15 | 65 | 50 | 0.65 | 1 | E218618 Vol. 2 Sec. 1
ITF050 |  |  | E308MNCX3N* | 14 - 20 | 5 | 7.5 | 15 | 20
ITF051 |  |  | E308NNCX3N* | 18 - 25 | 7.5 | 10 | 20 | 25
ITF052 |  |  | E308PNCX3N* | 22 - 32 | 7.5 | 10 | 25 | 30
ITF053 | F | Eaton | E308RNCX3N* | 28 - 40 | 10 | 15 | 30 | 40 | 65 | 50 | 0.65 | 1
ITF054 |  |  | E308SNCX3N* | 36 - 45 | 15 | 15 | 30 | 40
ITF055 |  |  | E308TNCX3N* | 40 - 50 | 15 | 20 | 40 | 50
ITF056 | F | Eaton | E358LNCX3N* | 11 - 16 | 5 | 5 | 10 | 15 | 65 | 50 | 0.65 | 1
ITF057 |  |  | E358MNCX3N* | 14 - 20 | 5 | 7.5 | 15 | 20
ITF058 |  |  | E358NNCX3N* | 18 - 25 | 7.5 | 10 | 20 | 25
ITF059 |  |  | E358PNCX3N* | 22 - 32 | 7.5 | 10 | 25 | 30
ITF060 | F | Eaton | E358RNCX3N* | 28 - 40 | 10 | 15 | 30 | 40 | 65 | 50 | 0.65 | 1
ITF061 |  |  | E358SNCX3N* | 36 - 45 | 15 | 15 | 30 | 40
ITF062 |  |  | E358TNCX3N* | 40 - 50 | 15 | 20 | 40 | 50
ITF063 | F | Eaton | E309RNDX3N* | 28 - 40 | 15 | 15 | 30 | 40 | 50 | 50 | 1.44 | 1 | E218618 Vol. 2 Sec. 1
ITF064 |  |  | E309SNDX3N* | 36 - 50 | 20 | 25 | 50 | 50 |  | 30
ITF065 |  |  | E309TNDX3N* | 45 - 63 | 25 | 25 | 50 | 60
ITF066 | F | Eaton | E309UNDX3N* | 57- 75 | 25 | 25 | 60 | 75 | 50 | 30 | 1.44 | 1
ITF067 |  |  | E309VNDX3N* | 70 - 90 | 30 | 30 | 75 | 100
ITF068 |  |  | E309WNDX3N* | 80 - 100 | 40 | 40 | 75 | 100 | 65
ITF069 | F | Eaton | E359RNDX3N* | 28 - 40 | 15 | 15 | 30 | 40 | 50 | 50 | 1.44 | 1
ITF070 |  |  | E359SNDX3N* | 36 - 50 | 20 | 25 | 50 | 50 |  | 30
ITF071 |  |  | E359TNDX3N* | 45 - 63 | 25 | 25 | 50 | 60
ITF072 | F | Eaton | E359UNDX3N* | 57- 75 | 25 | 25 | 60 | 75 | 50 | 30 | 1.44 | 1
ITF073 |  |  | E359VNDX3N* | 70 - 90 | 30 | 30 | 75 | 100
ITF074 |  |  | E359WNDX3N* | 80 - 100 | 40 | 40 | 75 | 100 | 65
ITF075 | F | Eaton | N307DNSAX3N* | 0.22 - 0.32 | - | - | - | - | 65 | 30 | 0.329 | 1 | E218618 Vol. 2 Sec. 1
ITF076 |  |  | N307ENSAX3N* | 0.28 - 0.40 | - | - | - | -
ITF077 |  |  | N307FNSAX3N* | 0.35 - 0.50 | - | - | - | -
ITF078 |  |  | N307GNSAX3N* | 0.45 - 0.63 | - | - | - | -
ITF079 | F | Eaton | N307HNSAX3N* | 0.55 - 0.80 | - | - | - | 1/2 | 65 | 30 | 0.329 | 1
ITF080 |  |  | N307JNSAX3N* | 0.70 - 1.0 | - | - | 1/2 | 1/2
ITF081 |  |  | N307KNSAX3N* | 0.9 - 1.25 | - | - | 3/4 | 3/4
ITF082 |  |  | N307LNSAX3N* | 1.1 - 1.6 | - | - | 3/4 | 1
ITF083 | F | Eaton | N307MNSAX3N* | 1.4 - 2.0 | - | - | 1 | 1.5 | 65 | 30 | 0.329 | 1
ITF084 |  |  | N307NNSAX3N* | 1.8 - 2.5 | 1/2 | 1/2 | 1.5 | 1.5
ITF085 |  |  | N307PNSAX3N* | 2.2 - 3.2 | 3/4 | 3/4 | 1.5 | 2
ITF086 |  |  | N307RNSAX3N* | 2.8 - 4.0 | 3/4 | 1 | 2 | 3
ITF087 | F | Eaton | N307SNSAX3N* | 3.5 - 5.0 | 1 | 1 | 3 | 3 | 65 | 30 | 0.329 | 1
ITF088 |  |  | N307TNSAX3N | 4.5 - 6.3 | 1.5 | 1.5 | 5 | 5
ITF089 |  |  | N307UNSAX3N* | 5.5 - 8.0 | 2 | 2 | 5 | 5
ITF090 |  |  | N307VNS0X3N* | 7 - 10 | 3 | 3 | 7.5 | 10
ITF091 | F | Eaton | N307WNS0X3N* | 9 - 12.5 | 5 | 5 | 10 | 10 | 65 | 50 | 0.329 | 1
ITF092 |  |  | N307XNSA0X3N* | 11 - 16 | 5 | 5 | 10 | 15 |  | 30
ITF093 |  |  | N307YNS0X3N* | 14 - 20 | 5 | 7.5 | 15 | 20
ITF094 | F | Eaton | N357DNSAX3N* | 0.22 - 0.32 | - | - | - | - | 65 | 30 | 0.329 | 1 | E218618 Vol. 2 Sec. 1
ITF095 |  |  | N357ENSAX3N* | 0.28 - 0.40 | - | - | - | -
ITF096 |  |  | N357FNSAX3N* | 0.35 - 0.50 | - | - | - | -
ITF097 |  |  | N357GNSAX3N* | 0.45 - 0.63 | - | - | - | -
ITF098 | F | Eaton | N357HNSAX3N* | 0.55 - 8.0 | - | - | - | 1/2 | 65 | 30 | 0.329 | 1
ITF099 |  |  | N357JNSAX3N* | 0.70 - 1.0 | - | - | 1/2 | 1/2
ITF100 |  |  | N357KNSAX3N* | 0.9 - 1.25 | - | - | 3/4 | 3/4
ITF101 |  |  | N357LNSAX3N* | 1.1 - 1.6 | - | - | 3/4 | 1
ITF102 | F | Eaton | N357MNSAX3N* | 1.4 - 2.0 | - | - | 1 | 1.5 | 65 | 30 | 0.329 | 1
ITF103 |  |  | N357NNSAX3N* | 1.8 - 2.5 | 1/2 | 1/2 | 1.5 | 1.5
ITF104 |  |  | N357PNSAX3N* | 2.2 - 3.2 | 3/4 | 3/4 | 1.5 | 2
ITF105 |  |  | N357RNSAX3N* | 2.8 - 4.0 | 3/4 | 1 | 2 | 3
ITF106 | F | Eaton | N357SNSAX3N* | 3.5 - 5.0 | 1 | 1 | 3 | 3 | 65 | 30 | 0.329 | 1
ITF107 |  |  | N357TNSAX3N | 4.5 - 6.3 | 1.5 | 1.5 | 5 | 5
ITF108 |  |  | N357UNSAX3N* | 5.5 - 8.0 | 2 | 2 | 5 | 5
ITF109 |  |  | N357VNS0X3N* | 7 - 10 | 3 | 3 | 7.5 | 10
ITF110 | F | Eaton | N357WNS0X3N* | 9 - 12.5 | 5 | 5 | 10 | 10 | 65 | 50 | 0.329 | 1
ITF111 |  |  | N357XNSA0X3N* | 11 - 16 | 5 | 5 | 10 | 15 |  | 30
ITF112 |  |  | N357YNS0X3N* | 14 - 20 | 5 | 7.5 | 15 | 20
ITF113 | F | Eaton | N308LNS1X3N | 11 - 16 | 5 | 5 | 10 | 15 | 65 | 50 | 0.65 | 1 | E218618 Vol. 2 Sec. 1
ITF114 |  |  | N308MNS1X3N* | 14 - 20 | 5 | 7.5 | 15 | 20
ITF115 |  |  | N308NNS1X3N* | 18 - 25 | 7.5 | 10 | 20 | 25
ITF116 |  |  | N308PNS1X3N* | 22 - 32 | 7.5 | 10 | 25 | 30
ITF117 | F | Eaton | N358LNS1X3N | 11 - 16 | 5 | 5 | 10 | 15 | 65 | 50 | 0.65 | 1
ITF118 |  |  | N358MNS1X3N* | 14 - 20 | 5 | 7.5 | 15 | 20
ITF119 |  |  | N358NNS1X3N* | 18 - 25 | 7.5 | 10 | 20 | 25
ITF120 |  |  | N358PNS1X3N* | 22 - 32 | 7.5 | 10 | 25 | 30
ITF121 | F | Eaton | N309RNS2X3N* | 28 - 40 | 15 | 15 | 30 | 40 | 50 | 50 | 1.44 | 1
ITF122 |  |  | N309SNS2X3N* | 36 - 50 | 20 | 25 | 50 | 50 |  | 30
ITF123 |  |  | N359RNS2X3N* | 28 - 40 | 15 | 15 | 30 | 40 |  | 50
ITF124 |  |  | N359SNS2X3N* | 36 - 50 | 20 | 25 | 50 | 50 |  | 30
Conditions of Acceptability:
1 = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.

## XT - Type F
Issued: 2007-02-01
Last Revised: 2013-01-04
ID Number | Combination Type | Partial Catalog Number | Component Type | Component Manufacturer | Component Catalog Desgination | Component Ratings |  |  |  | Combination kA | Combination Volts | Combination Phase | Max. Motor HP Ratings (See Note[1]) | Max. Motor FLA (See Note[2]) | Minimum Enclosure Volume (cu in/ cu Ft) |  | Conditions of Acceptability | Combination UL File Reference
[6 empty] | kA | Max Amps | Volts | Poles
XTF001 | F | XTFCP25BB… | MSP | Eaton | XTPRP25BC1 | 50 | 0.2 - 0.25 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | - | 0.25 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 480Y/277V | 3
|  |  | MC | Eaton | XTCE007 | 5 | 7 | 480Y/277V | 3
XTF001a |  |  | MSP | Eaton | XTPRP25BC1 | 50 | 0.2 - 0.25 | 240 | 3 | 50 | 240 | 3 | - | 0.25 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 240 | 3
|  |  | MC | Eaton | XTCE007 | 5 | 7 | 240 | 3
XTF001b |  |  | MSP | Eaton | XTPRP25BC1 | 50 | 0.2 - 0.25 | 208 | 3 | 50 | 208 | 3 | - | 0.25 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 208 | 3
|  |  | MC | Eaton | XTCE007 | 5 | 7 | 208 | 3
XTF002 | F | XTFCP40BB… | MSP | Eaton | XTPRP40BC1 | 50 | 0.3 - 0.4 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | - | 0.4 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 480Y/277V | 3
|  |  | MC | Eaton | XTCE007 | 5 | 7 | 480Y/277V | 3
XTF002a |  |  | MSP | Eaton | XTPRP40BC1 | 50 | 0.3 - 0.4 | 240 | 3 | 50 | 240 | 3 | - | 0.4 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 240 | 3
|  |  | MC | Eaton | XTCE007 | 5 | 7 | 240 | 3
XTF002b |  |  | MSP | Eaton | XTPRP40BC1 | 50 | 0.3 - 0.4 | 208 | 3 | 50 | 208 | 3 | - | 0.4 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 208 | 3
|  |  | MC | Eaton | XTCE007 | 5 | 7 | 208 | 3
XTF003 | F | XTFCP63BB… | MSP | Eaton | XTPRP63BC1 | 50 | 0.4 - 0.63 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | - | 0.6 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 480Y/277V | 3
|  |  | MC | Eaton | XTCE007 | 5 | 7 | 480Y/277V | 3
XTF003a |  |  | MSP | Eaton | XTPRP63BC1 | 50 | 0.4 - 0.63 | 240 | 3 | 50 | 240 | 3 | - | 0.6 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 240 | 3
|  |  | MC | Eaton | XTCE007 | 5 | 7 | 240 | 3
XTF003b |  |  | MSP | Eaton | XTPRP63BC1 | 50 | 0.4 - 0.63 | 208 | 3 | 50 | 208 | 3 | - | 0.6 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 208 | 3
|  |  | MC | Eaton | XTCE007 | 5 | 7 | 208 | 3
XTF004 | F | XTFC001BB… | MSP | Eaton | XTPR001BC1 | 50 | 0.6 - 1 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 0.5 | 1 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 480Y/277V | 3
|  |  | MC | Eaton | XTCE007 | 5 | 7 | 480Y/277V | 3
XTF004a |  |  | MSP | Eaton | XTPR001BC1 | 50 | 0.6 - 1 | 240 | 3 | 50 | 240 | 3 | - | 1 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 240 | 3
|  |  | MC | Eaton | XTCE007 | 5 | 7 | 240 | 3
XTF004b |  |  | MSP | Eaton | XTPR001BC1 | 50 | 0.6 - 1 | 208 | 3 | 50 | 208 | 3 | - | 1 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 208 | 3
|  |  | MC | Eaton | XTCE007 | 5 | 7 | 208 | 3
XTF005 | F | XTFC1P6BB… | MSP | Eaton | XTPR1P6BC1 | 50 | 1 - 1.6 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 0.75 | 1.6 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 480Y/277V | 3
|  |  | MC | Eaton | XTCE007 | 5 | 7 | 480Y/277V | 3
XTF005a |  |  | MSP | Eaton | XTPR1P6BC1 | 50 | 1 - 1.6 | 240 | 3 | 50 | 240 | 3 | - | 1.6 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 240 | 3
|  |  | MC | Eaton | XTCE007 | 5 | 7 | 240 | 3
XTF005b |  |  | MSP | Eaton | XTPR1P6BC1 | 50 | 1 - 1.6 | 208 | 3 | 50 | 208 | 3 | - | 1.6 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 208 | 3
|  |  | MC | Eaton | XTCE007 | 5 | 7 | 208 | 3
XTF006 | F | XTFC2P5BB… | MSP | Eaton | XTPR2P5BC1 | 50 | 1.6 - 2.5 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 1 | 2.1 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 480Y/277V | 3
|  |  | MC | Eaton | XTCE007 | 5 | 7 | 480Y/277V | 3
XTF006a |  |  | MSP | Eaton | XTPR2P5BC1 | 50 | 1.6 - 2.5 | 240 | 3 | 50 | 240 | 3 | 0.5 | 2.2 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 240 | 3
|  |  | MC | Eaton | XTCE007 | 5 | 7 | 240 | 3
XTF006b |  |  | MSP | Eaton | XTPR2P5BC1 | 50 | 1.6 - 2.5 | 208 | 3 | 50 | 208 | 3 | 0.5 | 2.4 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 208 | 3
|  |  | MC | Eaton | XTCE007 | 5 | 7 | 208 | 3
XTF007 | F | XTFC004BB… | MSP | Eaton | XTPR004BC1 | 50 | 2.5 - 4 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 2 | 3.4 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 480Y/277V | 3
|  |  | MC | Eaton | XTCE007 | 5 | 7 | 480Y/277V | 3
XTF007a |  |  | MSP | Eaton | XTPR004BC1 | 50 | 2.5 - 4 | 240 | 3 | 50 | 240 | 3 | 0.75 | 3.2 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 240 | 3
|  |  | MC | Eaton | XTCE007 | 5 | 7 | 240 | 3
XTF007b |  |  | MSP | Eaton | XTPR004BC1 | 50 | 2.5 - 4 | 208 | 3 | 50 | 208 | 3 | 0.75 | 3.5 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 208 | 3
|  |  | MC | Eaton | XTCE007 | 5 | 7 | 208 | 3
XTF008 | F | XTFC6P3BB… | MSP | Eaton | XTPR6P3BC1 | 65 | 4.0 - 6.3 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 3 | 4.8 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 480Y/277V | 3
|  |  | MC | Eaton | XTCE007 | 5 | 7 | 480Y/277V | 3
XTF008a |  |  | MSP | Eaton | XTPR6P3BC1 | 65 | 4.0 - 6.3 | 240 | 3 | 65 | 240 | 3 | 1.5 | 6 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 240 | 3
|  |  | MC | Eaton | XTCE007 | 5 | 7 | 240 | 3
XTF008b |  |  | MSP | Eaton | XTPR6P3BC1 | 65 | 4.0 - 6.3 | 208 | 3 | 65 | 208 | 3 | 1 | 4.6 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 208 | 3
|  |  | MC | Eaton | XTCE007 | 5 | 7 | 208 | 3
XTF009 | F | XTFC010BB… | MSP | Eaton | XTPR010BC1 | 65 | 6.3 - 11 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 5 | 7.6 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 480Y/277V | 3
|  |  | MC | Eaton | XTCE009B | 5 | 9 | 480Y/277V | 3
XTF009a |  |  | MSP | Eaton | XTPR010BC1 | 65 | 6.3 - 11 | 240 | 3 | 65 | 240 | 3 | 2 | 6.8 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 240 | 3
|  |  | MC | Eaton | XTCE009B | 5 | 9 | 240 | 3
XTF009b |  |  | MSP | Eaton | XTPR010BC1 | 65 | 6.3 - 11 | 208 | 3 | 65 | 208 | 3 | 2 | 7.5 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 208 | 3
|  |  | MC | Eaton | XTCE009B | 5 | 9 | 208 | 3
XTF010 | F | XTFC012BB… | MSP | Eaton | XTPR012BC1 | 65 | 8.0 - 12 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 7.5 | 11 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 480Y/277V | 3
|  |  | MC | Eaton | XTCE012B | 5 | 12 | 480Y/277V | 3
XTF010a |  |  | MSP | Eaton | XTPR012BC1 | 65 | 8.0 - 12 | 240 | 3 | 65 | 240 | 3 | 3 | 9.6 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 240 | 3
|  |  | MC | Eaton | XTCE012B | 5 | 12 | 240 | 3
XTF010b |  |  | MSP | Eaton | XTPR012BC1 | 65 | 8.0 - 12 | 208 | 3 | 65 | 208 | 3 | 3 | 10.6 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 208 | 3
|  |  | MC | Eaton | XTCE012B | 5 | 12 | 208 | 3
XTF011 | F | XTFC016BC… | MSP | Eaton | XTPR016BC1 | 18 | 10.0 - 16 | 480Y/277V | 3 | 18 | 480Y/277V | 3 | 10 | 14 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 480Y/277V | 3
|  |  | MC | Eaton | XTCE018C | 5 | 17 | 480Y/277V | 3
XTF011a |  |  | MSP | Eaton | XTPR016BC1 | 18 | 10.0 - 16 | 240 | 3 | 18 | 240 | 3 | 5 | 15.2 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 240 | 3
|  |  | MC | Eaton | XTCE018C | 5 | 17 | 240 | 3
XTF011b |  |  | MSP | Eaton | XTPR016BC1 | 18 | 10.0 - 16 | 208 | 3 | 18 | 208 | 3 | 3 | 10.6 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 208 | 3
|  |  | MC | Eaton | XTCE018C | 5 | 17 | 208 | 3
XTF012 | F | XTFC020BC… | MSP | Eaton | XTPR020BC1 | 18 | 16.0 - 20 | 208 | 3 | 18 | 208 | 3 | 5 | 16.7 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 208 | 3
|  |  | MC | Eaton | XTCE025C | 5 | 25 | 208 | 3
XTF013 | F | XTFC025BC… | MSP | Eaton | XTPR025BC1 | 18 | 20.0 - 25 | 480Y/277V | 3 | 18 | 480Y/277V | 3 | 15 | 21 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 480Y/277V | 3
|  |  | MC | Eaton | XTCE025C | 5 | 25 | 480Y/277V | 3
XTF013a |  |  | MSP | Eaton | XTPR025BC1 | 18 | 20.0 - 25 | 240 | 3 | 18 | 240 | 3 | 7.5 | 22 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 240 | 3
|  |  | MC | Eaton | XTCE025C | 5 | 25 | 240 | 3
XTF0113b |  |  | MSP | Eaton | XTPR025BC1 | 18 | 20.0 - 25 | 208 | 3 | 18 | 208 | 3 | 7.5 | 24.2 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 208 | 3
|  |  | MC | Eaton | XTCE025C | 5 | 25 | 208 | 3
XTF014 | F | XTFC032BC… | MSP | Eaton | XTPR032BC1 | 18 | 25.0 - 30 | 480Y/277V | 3 | 18 | 480Y/277V | 3 | 20 | 27 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 480Y/277V | 3
|  |  | MC | Eaton | XTCE032C | 5 | 32 | 480Y/277V | 3
XTF014a |  |  | MSP | Eaton | XTPR032BC1 | 18 | 25.0 - 30 | 240 | 3 | 18 | 240 | 3 | 10 | 28 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 240 | 3
|  |  | MC | Eaton | XTCE032C | 5 | 32 | 240 | 3
XTF015 | F | XTFC016DC… | MSP | Eaton | XTPR016DC1 | 30 | 10.0 - 16 | 600Y/347V | 3 | 30 | 600Y/347V | 3 | 10 | 11 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSAD | - | 60 | 600Y/347V | 3
|  |  | MC | Eaton | XTCE018C | 5 | 17 | 600Y/347V | 3
XTF015a |  |  | MSP | Eaton | XTPR016DC1 | 65 | 10.0 -16 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 10 | 14 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSAD | - | 60 | 480Y/277V | 3
|  |  | MC | Eaton | XTCE018C | 5 | 17 | 480Y/277V | 3
XTF015b |  |  | MSP | Eaton | XTPR016DC1 | 65 | 10.0 -16 | 240 | 3 | 65 | 240 | 3 | 5 | 15.2 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSAD | - | 60 | 240 | 3
|  |  | MC | Eaton | XTCE018C | 5 | 17 | 240 | 3
XTF015c |  |  | MSP | Eaton | XTPR016DC1 | 65 | 10.0 -16 | 208 | 3 | 65 | 208 | 3 | 3 | 10.6 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | Adapter | Eaton | XTPAXLSAD | - | 60 | 208 | 3
|  |  | MC | Eaton | XTCE018C | 5 | 17 | 208 | 3
XTF016 | F | XTFC025DC… | MSP | Eaton | XTPR025DC1 | 30 | 16 - 25 | 600Y/347V | 3 | 30 | 600Y/347V | 3 | 20 | 22 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSAD | - | 60 | 600Y/347V | 3
|  |  | MC | Eaton | XTCE025C | 5 | 25 | 600Y/347V | 3
XTF016a |  |  | MSP | Eaton | XTPR025DC1 | 65 | 16 - 25 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 15 | 21 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSAD | - | 60 | 480Y/277V | 3
|  |  | MC | Eaton | XTCE025C | 5 | 25 | 480Y/277V | 3
XTF016b |  |  | MSP | Eaton | XTPR025DC1 | 65 | 16 - 25 | 240 | 3 | 65 | 240 | 3 | 7.5 | 22 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSAD | - | 60 | 240 | 3
|  |  | MC | Eaton | XTCE025C | 5 | 25 | 240 | 3
XTF016c |  |  | MSP | Eaton | XTPR025DC1 | 65 | 16 - 25 | 208 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSAD | - | 60 | 208 | 3
|  |  | MC | Eaton | XTCE025C | 5 | 25 | 208 | 3
XTF017 | F | XTFC032DC… | MSP | Eaton | XTPR032DC1 | 50 | 25 - 32 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 25 | 27 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSAD | - | 60 | 600Y/347V | 3
|  |  | MC | Eaton | XTCE032C | 5 | 32 | 600Y/347V | 3
XTF017a |  |  | MSP | Eaton | XTPR032DC1 | 65 | 25 - 32 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 20 | 27 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSAD | - | 60 | 480Y/277V | 3
|  |  | MC | Eaton | XTCE032C | 5 | 32 | 480Y/277V | 3
XTF017b |  |  | MSP | Eaton | XTPR032DC1 | 65 | 25 - 32 | 240 | 3 | 65 | 240 | 3 | 10 | 28 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSAD | - | 60 | 240 | 3
|  |  | MC | Eaton | XTCE032C | 5 | 32 | 240 | 3
XTF017c |  |  | MSP | Eaton | XTPR032DC1 | 65 | 25 - 32 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSAD | - | 60 | 208 | 3
|  |  | MC | Eaton | XTCE032C | 5 | 32 | 208 | 3
XTF018 | F | XTFC040DD… | MSP | Eaton | XTPR040DC1 | 50 | 32.0 - 40 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 30 | 32 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSAD | - | 60 | 600Y/347V | 3
|  |  | MC | Eaton | XTCE040D | 10 | 40 | 600Y/347V | 3
XTF018a |  |  | MSP | Eaton | XTPR040DC1 | 65 | 32.0 - 40 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 30 | 40 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSAD | - | 60 | 480Y/277V | 3
|  |  | MC | Eaton | XTCE040D | 10 | 40 | 480Y/277V | 3
XTF037 | F | XTFC050DD… | MSP | Eaton | XTPR050DC1 | 65 | 40-52 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 30 | 40 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSAD | - | 60 | 480Y/277V | 3
|  |  | MC | Eaton | XTCE050D | 10 | 52 | 480Y/277V | 3
XTF037a |  |  | MSP | Eaton | XTPR050DC1 | 65 | 40-52 | 240 | 3 | 65 | 240 | 3 | 20 | 42 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSAD | - | 60 | 240 | 3
|  |  | MC | Eaton | XTCE050D | 10 | 54 | 240 | 3
XTF037b |  |  | MSP | Eaton | XTPR050DC1 | 65 | 40-52 | 208 | 3 | 65 | 208 | 3 | 15 | 46.2 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSAD | - | 60 | 208 | 3
|  |  | MC | Eaton | XTCE050D | 10 | 49 | 208 | 3
XTF019 | F | XTFRP25BB… | MSP | Eaton | XTPRP25BC1 | 50 | 0.2 - 0.25 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | - | 0.25 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 480Y/277V | 3
|  |  | FOR MC,REV MC | Eaton | XTCE007 | 5 | 7 | 480Y/277V | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF019a |  |  | MSP | Eaton | XTPRP25BC1 | 50 | 0.2 - 0.25 | 230 | 3 | 50 | 240 | 3 | - | 0.25 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 230 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE007 | 5 | 7 | 230 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF019b |  |  | MSP | Eaton | XTPRP25BC1 | 50 | 0.2 - 0.25 | 208 | 3 | 50 | 208 | 3 | - | 0.25 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 208 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE007 | 5 | 7 | 208 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF020 | F | XTFRP40BB… | MSP | Eaton | XTPRP40BC1 | 50 | 0.3 - 0.4 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | - | 0.4 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 480Y/277V | 3
|  |  | FOR MC,REV MC | Eaton | XTCE007 | 5 | 7 | 480Y/277V | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF020a |  |  | MSP | Eaton | XTPRP40BC1 | 50 | 0.3 - 0.4 | 240 | 3 | 50 | 240 | 3 | - | 0.4 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 240 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE007 | - | 7 | 240 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF020b |  |  | MSP | Eaton | XTPRP40BC1 | 50 | 0.3 - 0.4 | 208 | 3 | 50 | 208 | 3 | - | 0.4 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 208 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE007 | 5 | 7 | 208 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF021 | F | XTFRP63BB… | MSP | Eaton | XTPRP63BC1 | 50 | 0.4 - 0.63 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | - | 0.6 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 480Y/277V | 3
|  |  | FOR MC,REV MC | Eaton | XTCE007 | 5 | 7 | 480Y/277V | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF021a |  |  | MSP | Eaton | XTPRP63BC1 | 50 | 0.4 - 0.63 | 240 | 3 | 50 | 240 | 3 | - | 0.6 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 240 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE007 | 5 | 7 | 240 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF021b |  |  | MSP | Eaton | XTPRP63BC1 | 50 | 0.4 - 0.63 | 208 | 3 | 50 | 208 | 3 | - | 0.6 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 240 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE007 | 5 | 7 | 208 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF022 | F | XTFR001BB… | MSP | Eaton | XTPR001BC1 | 50 | 0.6 - 1 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 0.5 | 1 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 480Y/277V | 3
|  |  | FOR MC,REV MC | Eaton | XTCE007 | 5 | 7 | 480Y/277V | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF022a |  |  | MSP | Eaton | XTPR001BC1 | 50 | 0.6 - 1 | 240 | 3 | 50 | 240 | 3 | - | 1 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 240 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE007 | 5 | 7 | 240 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF022b |  |  | MSP | Eaton | XTPR001BC1 | 50 | 0.6 - 1 | 208 | 3 | 50 | 208 | 3 | - | 1 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 208 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE007 | 5 | 7 | 208 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF023 | F | XTFR1P6BB… | MSP | Eaton | XTPR1P6BC1 | 50 | 1 - 1.6 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 0.75 | 1.6 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 480Y/277V | 3
|  |  | FOR MC,REV MC | Eaton | XTCE007 | 5 | 7 | 480Y/277V | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF023a |  |  | MSP | Eaton | XTPR1P6BC1 | 50 | 1 - 1.6 | 240 | 3 | 50 | 240 | 3 | - | 1.6 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 240 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE007 | 5 | 7 | 240 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF023b |  |  | MSP | Eaton | XTPR1P6BC1 | 50 | 1 - 1.6 | 208 | 3 | 50 | 208 | 3 | - | 1.6 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 208 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE007 | 5 | 7 | 208 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF024 | F | XTFR2P5BB… | MSP | Eaton | XTPR2P5BC1 | 50 | 1.6 - 2.5 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 1 | 2.1 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 480Y/277V | 3
|  |  | FOR MC,REV MC | Eaton | XTCE007 | 5 | 7 | 480Y/277V | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF024a |  |  | MSP | Eaton | XTPR2P5BC1 | 50 | 1.6 - 2.5 | 240 | 3 | 50 | 240 | 3 | 0.5 | 2.2 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 240 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE007 | 5 | 7 | 240 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF024b |  |  | MSP | Eaton | XTPR2P5BC1 | 50 | 1.6 - 2.5 | 208 | 3 | 50 | 208 | 3 | 0.5 | 2.4 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 208 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE007 | 5 | 7 | 208 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF025 | F | XTFR004BB… | MSP | Eaton | XTPR004BC1 | 50 | 2.5 - 4 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 2 | 3.4 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 480Y/277V | 3
|  |  | FOR MC,REV MC | Eaton | XTCE007 | 5 | 7 | 480Y/277V | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF025a |  |  | MSP | Eaton | XTPR004BC1 | 50 | 2.5 - 4 | 240 | 3 | 50 | 240 | 3 | 0.75 | 3.2 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 240 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE007 | 5 | 7 | 240 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF025b |  |  | MSP | Eaton | XTPR004BC1 | 50 | 2.5 - 4 | 208 | 3 | 50 | 208 | 3 | 0.75 | 3.5 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 208 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE007 | 5 | 7 | 208 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF026 | F | XTFR6P3BB… | MSP | Eaton | XTPR6P3BC1 | 65 | 4.0 - 6.3 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 3 | 4.8 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 480Y/277V | 3
|  |  | FOR MC,REV MC | Eaton | XTCE007 | 5 | 7 | 480Y/277V | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF026a |  |  | MSP | Eaton | XTPR6P3BC1 | 65 | 4.0 - 6.3 | 240 | 3 | 65 | 240 | 3 | 1.5 | 6 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 240 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE007 | 5 | 7 | 240 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF026b |  |  | MSP | Eaton | XTPR6P3BC1 | 65 | 4.0 - 6.3 | 208 | 3 | 65 | 208 | 3 | 1 | 4.6 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 208 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE007 | 5 | 7 | 208 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF027 | F | XTFR010BB… | MSP | Eaton | XTPR010BC1 | 65 | 6.3 - 11 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 5 | 7.6 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 480Y/277V | 3
|  |  | FOR MC,REV MC | Eaton | XTCE009 | 5 | 9 | 480Y/277V | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF027a |  |  | MSP | Eaton | XTPR010BC1 | 65 | 6.3 - 11 | 240 | 3 | 65 | 240 | 3 | 2 | 6.8 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 240 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE009 | 5 | 9 | 240 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF027b |  |  | MSP | Eaton | XTPR010BC1 | 65 | 6.3 - 11 | 208 | 3 | 65 | 208 | 3 | 2 | 7.5 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 208 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE009 | 5 | 9 | 208 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF028 | F | XTFR012BB… | MSP | Eaton | XTPR012BC1 | 65 | 8.0 - 12 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 7.5 | 11 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 480Y/277V | 3
|  |  | FOR MC,REV MC | Eaton | XTCE012 | 5 | 12 | 480Y/277V | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF028a |  |  | MSP | Eaton | XTPR012BC1 | 65 | 8.0 - 12 | 240 | 3 | 65 | 240 | 3 | 3 | 9.6 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 240 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE012 | 5 | 12 | 240 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF028b |  |  | MSP | Eaton | XTPR012BC1 | 65 | 8.0 - 12 | 208 | 3 | 65 | 208 | 3 | 3 | 10.6 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 208 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE012 | 5 | 12 | 208 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLB | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLB | - | 12 | 600 | 3
XTF029 | F | XTFR016BC… | MSP | Eaton | XTPR016BC1 | 18 | 10.0 - 16 | 480Y/277V | 3 | 18 | 480Y/277V | 3 | 10 | 14 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 480Y/277V | 3
|  |  | FOR MC,REV MC | Eaton | XTCE018 | 5 | 17 | 480Y/277V | 3
|  |  | INTERLOCK | Eaton | XTCEXMLC | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLC | - | 32 | 600 | 3
XTF029a |  |  | MSP | Eaton | XTPR016BC1 | 18 | 10.0 - 16 | 240 | 3 | 18 | 240 | 3 | 5 | 15.2 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 240 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE018 | 5 | 17 | 240 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLC | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLC | - | 32 | 600 | 3
XTF029b |  |  | MSP | Eaton | XTPR016BC1 | 18 | 10.0 - 16 | 208 | 3 | 18 | 208 | 3 | 3 | 10.6 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 208 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE018 | 5 | 17 | 208 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLC | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLC | - | 32 | 600 | 3
XTF030 |  | XTFR020BC… | MSP | Eaton | XTPR020BC1 | 18 | 16.0 - 20 | 208 | 3 | 18 | 208 | 3 | 5 | 16.7 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 208 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE025 | 5 | 25 | 208 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLC | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLC | - | 32 | 600 | 3
XTF031 | F | XTFR025BC… | MSP | Eaton | XTPR025BC1 | 18 | 20.0 - 25 | 480Y/277V | 3 | 18 | 480Y/277V | 3 | 15 | 21 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 480Y/277V | 3
|  |  | FOR MC,REV MC | Eaton | XTCE025 | 5 | 25 | 480Y/277V | 3
|  |  | INTERLOCK | Eaton | XTCEXMLC | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLC | - | 32 | 600 | 3
XTF031a |  |  | MSP | Eaton | XTPR025BC1 | 18 | 20.0 - 25 | 240 | 3 | 18 | 240 | 3 | 7.5 | 22 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 240 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE025 | 5 | 25 | 240 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLC | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLC | - | 32 | 600 | 3
XTF031b |  |  | MSP | Eaton | XTPR025BC1 | 18 | 20.0 - 25 | 208 | 3 | 18 | 208 | 3 | 7.5 | 24.2 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 208 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE025 | 5 | 25 | 208 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLC | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLC | - | 32 | 600 | 3
XTF032 | F | XTFR032BC… | MSP | Eaton | XTPR032BC1 | 18 | 25.0 - 30 | 480Y/277V | 3 | 18 | 480Y/277V | 3 | 20 | 27 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 480Y/277V | 3
|  |  | FOR MC,REV MC | Eaton | XTCE032 | 5 | 32 | 480Y/277V | 3
|  |  | INTERLOCK | Eaton | XTCEXMLC | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCR032C | - | 32 | 600 | 3
XTF032a |  |  | MSP | Eaton | XTPR032BC1 | 18 | 25.0 - 30 | 240 | 3 | 18 | 240 | 3 | 10 | 28 | 915.3562 | 0.52972 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSA | - | 60 | 240 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE032 | 5 | 32 | 240 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLC | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCR032C | - | 32 | 600 | 3
XTF033 | F | XTFR016DC… | MSP | Eaton | XTPR016DC1 | 30 | 10.0 - 16 | 600Y/347V | 3 | 30 | 600Y/347V | 3 | 10 | 11 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSAD | - | 60 | 600Y/347V | 3
|  |  | FOR MC,REV MC | Eaton | XTCE018 | 5 | 17 | 600Y/347V | 3
|  |  | INTERLOCK | Eaton | XTCEXMLC | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLC | - | 32 | 600 | 3
XTF033a |  |  | MSP | Eaton | XTPR016DC1 | 65 | 10.0 -16 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 10 | 14 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSAD | - | 60 | 480Y/277V | 3
|  |  | FOR MC,REV MC | Eaton | XTCE018 | 5 | 17 | 480Y/277V | 3
|  |  | INTERLOCK | Eaton | XTCEXMLC | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLC | - | 32 | 600 | 3
XTF033b |  |  | MSP | Eaton | XTPR016DC1 | 65 | 10.0 -16 | 240 | 3 | 65 | 240 | 3 | 5 | 15.2 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSAD | - | 60 | 240 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE018 | 5 | 17 | 240 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLC | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLC | - | 32 | 600 | 3
XTF033c |  |  | MSP | Eaton | XTPR016DC1 | 65 | 10.0 -16 | 208 | 3 | 65 | 208 | 3 | 3 | 10.6 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSAD | - | 60 | 208 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE018 | 5 | 17 | 208 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLC | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLC | - | 32 | 600 | 3
XTF034 | F | XTFR025DC… | MSP | Eaton | XTPR025DC1 | 30 | 16 - 25 | 600Y/347V | 3 | 30 | 600Y/347V | 3 | 20 | 22 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSAD | - | 60 | 600Y/347V | 3
|  |  | FOR MC,REV MC | Eaton | XTCE025 | 5 | 25 | 600Y/347V | 3
|  |  | INTERLOCK | Eaton | XTCEXMLC | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLC | - | 32 | 600 | 3
XTF034a |  |  | MSP | Eaton | XTPR025DC1 | 65 | 16 - 25 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 15 | 21 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSAD | - | 60 | 480Y/277V | 3
|  |  | FOR MC,REV MC | Eaton | XTCE025 | 5 | 25 | 480Y/277V | 3
|  |  | INTERLOCK | Eaton | XTCEXMLC | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLC | - | 32 | 600 | 3
XTF034b |  |  | MSP | Eaton | XTPR025DC1 | 65 | 16 - 25 | 240 | 3 | 65 | 240 | 3 | 7.5 | 22 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSAD | - | 60 | 240 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE025 | 5 | 25 | 240 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLC | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLC | - | 32 | 600 | 3
XTF034c |  |  | MSP | Eaton | XTPR025DC1 | 65 | 16 - 25 | 208 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSAD | - | 60 | 208 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE025 | 5 | 25 | 208 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLC | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLC | 5 | 32 | 600 | 3
XTF035 | F | XTFR032DC… | MSP | Eaton | XTPR032DC1 | 50 | 25 - 32 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 25 | 27 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSAD | - | 60 | 600Y/347V | 3
|  |  | FOR MC,REV MC | Eaton | XTCE032 | 5 | 32 | 600Y/347V | 3
|  |  | INTERLOCK | Eaton | XTCEXMLC | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLC | - | 32 | 600Y/347V | 3
XTF035a |  |  | MSP | Eaton | XTPR032DC1 | 65 | 25 - 32 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 20 | 27 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSAD | - | 60 | 480Y/277V | 3
|  |  | FOR MC,REV MC | Eaton | XTCE032 | 5 | 32 | 480Y/277V | 3
|  |  | INTERLOCK | Eaton | XTCEXMLC | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLC | - | 32 | 480Y/277V | 3
XTF035b |  |  | MSP | Eaton | XTPR032DC1 | 65 | 25 - 32 | 240 | 3 | 65 | 240 | 3 | 10 | 28 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSAD | - | 60 | 240 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE032 | 5 | 32 | 240 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLC | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLC | - | 32 | 240 | 3
XTF035c |  |  | MSP | Eaton | XTPR032DC1 | 65 | 25 - 32 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | ACC(Adapter) | Eaton | XTPAXLSAD | - | 60 | 208 | 3
|  |  | FOR MC,REV MC | Eaton | XTCE032 | 5 | 32 | 208 | 3
|  |  | INTERLOCK | Eaton | XTCEXMLC | - | - | - | -
|  |  | ACC(REV.LINKS) | Eaton | XTCEXRLC | - | 32 | 208 | 3
XTF036 | F | XTFR040DD… | MSP | Eaton | XTPR040DC1 | 50 | 32.0 - 40 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 30 | 32 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | Adapter | Eaton | XTPAXLSAD | - | 60 | 600Y/347V | 3
|  |  | REVCON | Eaton | XTCR040D | 10 | 40 | 600Y/347V | 3
XTF036a |  |  | MSP | Eaton | XTPR040DC1 | 65 | 32.0 - 40 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 30 | 40 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | Adapter | Eaton | XTPAXLSAD | - | 60 | 480Y/277V | 3
|  |  | REVCON | Eaton | XTCR040D | 10 | 40 | 480Y/277V | 3
XTF038 | F | XTFR050DD… | MSP | Eaton | XTPR050DC1 | 65 | 40-52 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 30 | 40 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | Adapter | Eaton | XTPAXLSAD | - | 60 | 480Y/277V | 3
|  |  | REVCON | Eaton | XTCR050D | 10 | 52 | 480Y/277V | 3
XTF038a |  |  | MSP | Eaton | XTPR050DC1 | 65 | 40-52 | 240 | 3 | 65 | 240 | 3 | 20 | 42 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | Adapter | Eaton | XTPAXLSAD | - | 60 | 240 | 3
|  |  | REVCON | Eaton | XTCR050D | 10 | 54 | 240 | 3
XTF038b |  |  | MSP | Eaton | XTPR050DC1 | 65 | 40-52 | 208 | 3 | 65 | 208 | 3 | 15 | 46.2 | 983.2 | 0.569 | 1, 5 | E218618 V2 S3
|  |  | Adapter | Eaton | XTPAXLSAD | - | 60 | 208 | 3
|  |  | REVCON | Eaton | XTCR050D | 10 | 50 | 208 | 3
Notes:
[1] HP ratings for reference only. Select combination motor controller based on motor full load current and service factor.
[2] Values represent Motor FLC ratings from Table 430-250 or maximum dial setting on combination motor controller.
CONDITIONS OF ACCEPTABILITY Unless specified otherwise in the individual Recognitions, consideration is to be given to the following Conditions of Acceptability when these components are employed as a combination motor controller in the end-use equipment: Specific Conditions of Use - Number refers to specific condition number as defined below and number in parenthesis identifies specific information applicable to the combination motor controller. 1. All of the specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume. 2. When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective devices and other components shall not be installed in this area. 3. When specified, the overload relay heater table number shall be provided with the equipment. 4. Unless otherwise specified, all connections between components are made with insulated wire having an ampacity of 125 percent of the rated motor current and connected to the terminals supplied with the individual components. 5. The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor controllers shall be considered in the end - product application. 6. Additional Conditions of Acceptability may be specified in the individual tables. 7. Type F Combination motor controllers feature pre-fabricated connector links between motor protector and contactor.
8. Units with suffix "/BBA" are mounted on busbar shoes for use in listed and/or recognized busbar systems for ICPs.

## XT + ITEM Type F
Issued: 2011-01-13
Last Revised: 2011-01-13
Database Identification Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Enclosure Volume, cubic inches | Conditions of Use | Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating
XTITF1 | F | MSP | Eaton | XTPR1P6BC1 | 600Y347 | 3 | 50 | 1.3 | 0.75 | 600Y347 | 3 | 35 | 1.3 | 0.75 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E111A06X3N | 600 | 3 | 5 | 3.9 | 3
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 600 | 3 | -- | -- | --
XTITF2 | F | MSP | Eaton | XTPR1P6BC1 | 480Y277 | 3 | 50 | 1.6 | 0.75 | 480Y277 | 3 | 35 | 1.6 | 0.75 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E111A06X3N | 480 | 3 | 5 | 4.8 | 3
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF3 | F | MSP | Eaton | XTPR2P5BC1 | 600Y347 | 3 | 50 | 2.4 | 1.5 | 600Y347 | 3 | 35 | 2.4 | 1.5 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E111A06X3N | 600 | 3 | 5 | 3.9 | 3
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 600 | 3 | -- | -- | --
XTITF4 | F | MSP | Eaton | XTPR2P5BC1 | 480Y277 | 3 | 50 | 2.1 | 1 | 480Y277 | 3 | 35 | 2.1 | 1 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E111A06X3N | 480 | 3 | 5 | 4.8 | 3
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF5 | F | MSP | Eaton | XTPR2P5BC1 | 240 | 3 | 50 | 2.2 | 0.5 | 240 | 3 | 35 | 2.2 | 0.5 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E111A06X3N | 240 | 3 | 5 | 6 | 1.5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 240 | 3 | -- | -- | --
XTITF6 | F | MSP | Eaton | XTPR2P5BC1 | 200 | 3 | 50 | 2.5 | 0.5 | 200 | 3 | 35 | 2.5 | 0.5 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E111A06X3N | 200 | 3 | 5 | 4.8 | 1
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 200 | 3 | -- | -- | --
XTITF7 | F | MSP | Eaton | XTPR004BC1 | 600Y347 | 3 | 50 | 3.9 | 3 | 600Y347 | 3 | 35 | 3.9 | 3 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E111A06X3N | 600 | 3 | 5 | 3.9 | 3
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 600 | 3 | -- | -- | --
XTITF8 | F | MSP | Eaton | XTPR004BC1 | 480Y277 | 3 | 50 | 3.4 | 2 | 480Y277 | 3 | 35 | 3.4 | 2 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E111A06X3N | 480 | 3 | 5 | 4.8 | 3
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF9 | F | MSP | Eaton | XTPR004BC1 | 240 | 3 | 50 | 3.2 | 0.75 | 240 | 3 | 35 | 3.2 | 0.75 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E111A06X3N | 240 | 3 | 5 | 6 | 1.5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 240 | 3 | -- | -- | --
XTITF10 | F | MSP | Eaton | XTPR004BC1 | 200 | 3 | 50 | 3.7 | 0.75 | 200 | 3 | 35 | 3.7 | 0.75 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E111A06X3N | 200 | 3 | 5 | 4.8 | 1
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 200 | 3 | -- | -- | --
XTITF11 | F | MSP | Eaton | XTPR6P3BC1 | 600Y347 | 3 | 50 | 6.1 | 5 | 600Y347 | 3 | 35 | 3.9 | 3 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E111A09X3N | 600 | 3 | 5 | 6.1 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 600 | 3 | -- | -- | --
XTITF12 | F | MSP | Eaton | XTPR6P3BC1 | 480Y277 | 3 | 50 | 4.8 | 3 | 480Y277 | 3 | 35 | 4.8 | 3 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E111A09X3N | 480 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF13 | F | MSP | Eaton | XTPR6P3BC1 | 240 | 3 | 50 | 4.2 | 1 | 240 | 3 | 35 | 4.2 | 1 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E111A09X3N | 240 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 240 | 3 | -- | -- | --
XTITF14 | F | MSP | Eaton | XTPR6P3BC1 | 200 | 3 | 50 | 6.9 | 1.5 | 200 | 3 | 35 | 4.8 | 1 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E111A09X3N | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 200 | 3 | -- | -- | --
XTITF15 | F | MSP | Eaton | XTPR010BC1 | 600Y347 | 3 | 50 | 11 | 10 | 600Y347 | 3 | 35 | 6.1 | 5 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E111A12X3N | 600 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 600 | 3 | -- | -- | --
XTITF16 | F | MSP | Eaton | XTPR010BC1 | 480Y277 | 3 | 50 | 11 | 7.5 | 480Y277 | 3 | 35 | 7.6 | 5 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E111A12X3N | 480 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF17 | F | MSP | Eaton | XTPR010BC1 | 240 | 3 | 50 | 9.6 | 3 | 240 | 3 | 35 | 6.8 | 2 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E111A12X3N | 240 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 240 | 3 | -- | -- | --
XTITF18 | F | MSP | Eaton | XTPR010BC1 | 200 | 3 | 50 | 11 | 3 | 200 | 3 | 35 | 7.8 | 2 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E111A12X3N | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 200 | 3 | -- | -- | --
XTITF19 | F | MSP | Eaton | XTPR012BC1 | 480Y277 | 3 | 65 | 11 | 7.5 | 480Y277 | 3 | 35 | 11 | 7.5 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E111A12X3N | 480 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF20 | F | MSP | Eaton | XTPR012BC1 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 35 | 9.6 | 3 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E111A12X3N | 240 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 240 | 3 | -- | -- | --
XTITF21 | F | MSP | Eaton | XTPR012BC1 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 35 | 11 | 3 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E111A12X3N | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 200 | 3 | -- | -- | --
XTITF22 | F | MSP | Eaton | XTPR1P6BC1 | 600Y347 | 3 | 50 | 1.3 | 0.75 | 600Y347 | 3 | 35 | 1.3 | 0.75 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E511A06X3N | 600 | 3 | 5 | 3.9 | 3
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 600 | 3 | -- | -- | --
XTITF23 | F | MSP | Eaton | XTPR1P6BC1 | 480Y277 | 3 | 50 | 1.6 | 0.75 | 480Y277 | 3 | 35 | 1.6 | 0.75 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E511A06X3N | 480 | 3 | 5 | 4.8 | 3
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF24 | F | MSP | Eaton | XTPR2P5BC1 | 600Y347 | 3 | 50 | 2.4 | 1.5 | 600Y347 | 3 | 35 | 2.4 | 1.5 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E511A06X3N | 600 | 3 | 5 | 3.9 | 3
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 600 | 3 | -- | -- | --
XTITF25 | F | MSP | Eaton | XTPR2P5BC1 | 480Y277 | 3 | 50 | 2.1 | 1 | 480Y277 | 3 | 35 | 2.1 | 1 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E511A06X3N | 480 | 3 | 5 | 4.8 | 3
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF26 | F | MSP | Eaton | XTPR2P5BC1 | 240 | 3 | 50 | 2.2 | 0.5 | 240 | 3 | 35 | 2.2 | 0.5 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E511A06X3N | 240 | 3 | 5 | 6 | 1.5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 240 | 3 | -- | -- | --
XTITF27 | F | MSP | Eaton | XTPR2P5BC1 | 200 | 3 | 50 | 2.5 | 0.5 | 200 | 3 | 35 | 2.5 | 0.5 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E511A06X3N | 200 | 3 | 5 | 4.8 | 1
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 200 | 3 | -- | -- | --
XTITF28 | F | MSP | Eaton | XTPR004BC1 | 600Y347 | 3 | 50 | 3.9 | 3 | 600Y347 | 3 | 35 | 3.9 | 3 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E511A06X3N | 600 | 3 | 5 | 3.9 | 3
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 600 | 3 | -- | -- | --
XTITF29 | F | MSP | Eaton | XTPR004BC1 | 480Y277 | 3 | 50 | 3.4 | 2 | 480Y277 | 3 | 35 | 3.4 | 2 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E511A06X3N | 480 | 3 | 5 | 4.8 | 3
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF30 | F | MSP | Eaton | XTPR004BC1 | 240 | 3 | 50 | 3.2 | 0.75 | 240 | 3 | 35 | 3.2 | 0.75 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E511A06X3N | 240 | 3 | 5 | 6 | 1.5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 240 | 3 | -- | -- | --
XTITF31 | F | MSP | Eaton | XTPR004BC1 | 200 | 3 | 50 | 3.7 | 0.75 | 200 | 3 | 35 | 3.7 | 0.75 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E511A06X3N | 200 | 3 | 5 | 4.8 | 1
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 200 | 3 | -- | -- | --
XTITF32 | F | MSP | Eaton | XTPR6P3BC1 | 600Y347 | 3 | 50 | 6.1 | 5 | 600Y347 | 3 | 35 | 3.9 | 3 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E511A09X3N | 600 | 3 | 5 | 6.1 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 600 | 3 | -- | -- | --
XTITF33 | F | MSP | Eaton | XTPR6P3BC1 | 480Y277 | 3 | 50 | 4.8 | 3 | 480Y277 | 3 | 35 | 4.8 | 3 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E511A09X3N | 480 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF34 | F | MSP | Eaton | XTPR6P3BC1 | 240 | 3 | 50 | 4.2 | 1 | 240 | 3 | 35 | 4.2 | 1 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E511A09X3N | 240 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 240 | 3 | -- | -- | --
XTITF35 | F | MSP | Eaton | XTPR6P3BC1 | 200 | 3 | 50 | 6.9 | 1.5 | 200 | 3 | 35 | 4.8 | 1 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E511A09X3N | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 200 | 3 | -- | -- | --
XTITF36 | F | MSP | Eaton | XTPR010BC1 | 600Y347 | 3 | 50 | 11 | 10 | 600Y347 | 3 | 35 | 6.1 | 5 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E511A12X3N | 600 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 600 | 3 | -- | -- | --
XTITF37 | F | MSP | Eaton | XTPR010BC1 | 480Y277 | 3 | 50 | 11 | 7.5 | 480Y277 | 3 | 35 | 7.6 | 5 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E511A12X3N | 480 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF38 | F | MSP | Eaton | XTPR010BC1 | 240 | 3 | 50 | 9.6 | 3 | 240 | 3 | 35 | 6.8 | 2 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E511A12X3N | 240 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 240 | 3 | -- | -- | --
XTITF39 | F | MSP | Eaton | XTPR010BC1 | 200 | 3 | 50 | 11 | 3 | 200 | 3 | 35 | 7.8 | 2 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E511A12X3N | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 200 | 3 | -- | -- | --
XTITF40 | F | MSP | Eaton | XTPR012BC1 | 480Y277 | 3 | 65 | 11 | 7.5 | 480Y277 | 3 | 35 | 11 | 7.5 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E511A12X3N | 480 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF41 | F | MSP | Eaton | XTPR012BC1 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 35 | 9.6 | 3 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E511A12X3N | 240 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 240 | 3 | -- | -- | --
XTITF42 | F | MSP | Eaton | XTPR012BC1 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 35 | 11 | 3 | 257 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E511A12X3N | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 200 | 3 | -- | -- | --
XTITF43 | F | MSP | Eaton | XTPR1P6BC1 | 600Y347 | 3 | 50 | 1.3 | 0.75 | 600Y347 | 3 | 35 | 1.3 | 0.75 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 600 | 3 | 5 | 11 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 600 | 3 | -- | -- | --
XTITF44 | F | MSP | Eaton | XTPR1P6BC1 | 480Y277 | 3 | 50 | 1.6 | 0.75 | 480Y277 | 3 | 35 | 1.6 | 0.75 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 480 | 3 | 5 | 14 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF45 | F | MSP | Eaton | XTPR2P5BC1 | 600Y347 | 3 | 50 | 2.4 | 1.5 | 600Y347 | 3 | 35 | 2.4 | 1.5 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 600 | 3 | 5 | 11 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 600 | 3 | -- | -- | --
XTITF46 | F | MSP | Eaton | XTPR2P5BC1 | 480Y277 | 3 | 50 | 2.1 | 1 | 480Y277 | 3 | 35 | 2.1 | 1 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 480 | 3 | 5 | 14 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF47 | F | MSP | Eaton | XTPR2P5BC1 | 240 | 3 | 50 | 2.2 | 0.5 | 240 | 3 | 35 | 2.2 | 0.5 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 240 | 3 | 5 | 15.2 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 240 | 3 | -- | -- | --
XTITF48 | F | MSP | Eaton | XTPR2P5BC1 | 200 | 3 | 50 | 2.5 | 0.5 | 200 | 3 | 35 | 2.5 | 0.5 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 200 | 3 | -- | -- | --
XTITF49 | F | MSP | Eaton | XTPR004BC1 | 600Y347 | 3 | 50 | 3.9 | 3 | 600Y347 | 3 | 35 | 3.9 | 3 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 600 | 3 | 5 | 11 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 600 | 3 | -- | -- | --
XTITF50 | F | MSP | Eaton | XTPR004BC1 | 480Y277 | 3 | 50 | 3.4 | 2 | 480Y277 | 3 | 35 | 3.4 | 2 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 480 | 3 | 5 | 14 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF51 | F | MSP | Eaton | XTPR004BC1 | 240 | 3 | 50 | 3.2 | 0.75 | 240 | 3 | 35 | 3.2 | 0.75 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 240 | 3 | 5 | 15.2 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 240 | 3 | -- | -- | --
XTITF52 | F | MSP | Eaton | XTPR004BC1 | 200 | 3 | 50 | 3.7 | 0.75 | 200 | 3 | 35 | 3.7 | 0.75 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 200 | 3 | -- | -- | --
XTITF53 | F | MSP | Eaton | XTPR6P3BC1 | 600Y347 | 3 | 50 | 6.1 | 5 | 600Y347 | 3 | 35 | 6.1 | 5 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 600 | 3 | 5 | 11 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 600 | 3 | -- | -- | --
XTITF54 | F | MSP | Eaton | XTPR6P3BC1 | 480Y277 | 3 | 50 | 4.8 | 3 | 480Y277 | 3 | 35 | 4.8 | 3 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 480 | 3 | 5 | 14 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF55 | F | MSP | Eaton | XTPR6P3BC1 | 240 | 3 | 50 | 4.2 | 1 | 240 | 3 | 35 | 4.2 | 1 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 240 | 3 | 5 | 15.2 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 240 | 3 | -- | -- | --
XTITF56 | F | MSP | Eaton | XTPR6P3BC1 | 200 | 3 | 50 | 6.9 | 1.5 | 200 | 3 | 35 | 6.9 | 1.5 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 200 | 3 | -- | -- | --
XTITF57 | F | MSP | Eaton | XTPR010BC1 | 600Y347 | 3 | 50 | 11 | 10 | 600Y347 | 3 | 35 | 11 | 10 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 600 | 3 | 5 | 11 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 600 | 3 | -- | -- | --
XTITF58 | F | MSP | Eaton | XTPR010BC1 | 480Y277 | 3 | 50 | 11 | 7.5 | 480Y277 | 3 | 35 | 11 | 7.5 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 480 | 3 | 5 | 14 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF59 | F | MSP | Eaton | XTPR010BC1 | 240 | 3 | 50 | 9.6 | 3 | 240 | 3 | 35 | 9.6 | 3 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 240 | 3 | 5 | 15.2 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 240 | 3 | -- | -- | --
XTITF60 | F | MSP | Eaton | XTPR010BC1 | 200 | 3 | 50 | 11 | 3 | 200 | 3 | 35 | 11 | 3 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 200 | 3 | -- | -- | --
XTITF61 | F | MSP | Eaton | XTPR012BC1 | 480Y277 | 3 | 65 | 11 | 7.5 | 480Y277 | 3 | 35 | 11 | 7.5 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 480 | 3 | 5 | 14 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF62 | F | MSP | Eaton | XTPR012BC1 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 35 | 9.6 | 3 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 240 | 3 | 5 | 15.2 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 240 | 3 | -- | -- | --
XTITF63 | F | MSP | Eaton | XTPR012BC1 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 35 | 11 | 3 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 200 | 3 | -- | -- | --
XTITF64 | F | MSP | Eaton | XTPR016BC1 | 480Y277 | 3 | 42 | 14 | 10 | 480Y277 | 3 | 35 | 14 | 10 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 480 | 3 | 5 | 14 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF65 | F | MSP | Eaton | XTPR016BC1 | 240 | 3 | 42 | 15.2 | 5 | 240 | 3 | 35 | 15.2 | 5 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 240 | 3 | 5 | 15.2 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 240 | 3 | -- | -- | --
XTITF66 | F | MSP | Eaton | XTPR016BC1 | 200 | 3 | 42 | 11 | 3 | 200 | 3 | 35 | 11 | 3 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 200 | 3 | -- | -- | --
XTITF67 | F | MSP | Eaton | XTPR020BC1 | 200 | 3 | 18 | 17.5 | 5 | 200 | 3 | 35 | 17.5 | 5 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB25X3N | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 200 | 3 | -- | -- | --
XTITF68 | F | MSP | Eaton | XTPR025BC1 | 480Y277 | 3 | 18 | 21 | 15 | 480Y277 | 3 | 35 | 21 | 15 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB25X3N | 480 | 3 | 5 | 21 | 15
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF69 | F | MSP | Eaton | XTPR025BC1 | 240 | 3 | 18 | 22 | 7.5 | 240 | 3 | 35 | 22 | 7.5 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB25X3N | 240 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 240 | 3 | -- | -- | --
XTITF70 | F | MSP | Eaton | XTPR032BC1 | 480Y277 | 3 | 18 | 27 | 20 | 480Y277 | 3 | 35 | 27 | 20 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB32X3N | 480 | 3 | 5 | 27 | 20
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF71 | F | MSP | Eaton | XTPR032BC1 | 240 | 3 | 18 | 28 | 10 | 240 | 3 | 35 | 28 | 10 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB32X3N | 240 | 3 | 5 | 28 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 240 | 3 | -- | -- | --
XTITF72 | F | MSP | Eaton | XTPR032BC1 | 200 | 3 | 18 | 25.3 | 7.5 | 200 | 3 | 35 | 25.3 | 7.5 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB32X3N | 200 | 3 | 5 | 25.3 | 7.5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 200 | 3 | -- | -- | --
XTITF73 | F | MSP | Eaton | XTPR1P6BC1 | 600Y347 | 3 | 50 | 1.3 | 0.75 | 600Y347 | 3 | 35 | 1.3 | 0.75 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 600 | 3 | 5 | 11 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 600 | 3 | -- | -- | --
XTITF74 | F | MSP | Eaton | XTPR1P6BC1 | 480Y277 | 3 | 50 | 1.6 | 0.75 | 480Y277 | 3 | 35 | 1.6 | 0.75 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 480 | 3 | 5 | 14 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF75 | F | MSP | Eaton | XTPR2P5BC1 | 600Y347 | 3 | 50 | 2.4 | 1.5 | 600Y347 | 3 | 35 | 2.4 | 1.5 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 600 | 3 | 5 | 11 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 600 | 3 | -- | -- | --
XTITF76 | F | MSP | Eaton | XTPR2P5BC1 | 480Y277 | 3 | 50 | 2.1 | 1 | 480Y277 | 3 | 35 | 2.1 | 1 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 480 | 3 | 5 | 14 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF77 | F | MSP | Eaton | XTPR2P5BC1 | 240 | 3 | 50 | 2.2 | 0.5 | 240 | 3 | 35 | 2.2 | 0.5 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 240 | 3 | 5 | 15.2 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 240 | 3 | -- | -- | --
XTITF78 | F | MSP | Eaton | XTPR2P5BC1 | 200 | 3 | 50 | 2.5 | 0.5 | 200 | 3 | 35 | 2.5 | 0.5 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 200 | 3 | -- | -- | --
XTITF79 | F | MSP | Eaton | XTPR004BC1 | 600Y347 | 3 | 50 | 3.9 | 3 | 600Y347 | 3 | 35 | 3.9 | 3 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 600 | 3 | 5 | 11 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 600 | 3 | -- | -- | --
XTITF80 | F | MSP | Eaton | XTPR004BC1 | 480Y277 | 3 | 50 | 3.4 | 2 | 480Y277 | 3 | 35 | 3.4 | 2 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 480 | 3 | 5 | 14 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF81 | F | MSP | Eaton | XTPR004BC1 | 240 | 3 | 50 | 3.2 | 0.75 | 240 | 3 | 35 | 3.2 | 0.75 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 240 | 3 | 5 | 15.2 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 240 | 3 | -- | -- | --
XTITF82 | F | MSP | Eaton | XTPR004BC1 | 200 | 3 | 50 | 3.7 | 0.75 | 200 | 3 | 35 | 3.7 | 0.75 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 200 | 3 | -- | -- | --
XTITF83 | F | MSP | Eaton | XTPR6P3BC1 | 600Y347 | 3 | 50 | 6.1 | 5 | 600Y347 | 3 | 35 | 6.1 | 5 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 600 | 3 | 5 | 11 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 600 | 3 | -- | -- | --
XTITF84 | F | MSP | Eaton | XTPR6P3BC1 | 480Y277 | 3 | 50 | 4.8 | 3 | 480Y277 | 3 | 35 | 4.8 | 3 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 480 | 3 | 5 | 14 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF85 | F | MSP | Eaton | XTPR6P3BC1 | 240 | 3 | 50 | 4.2 | 1 | 240 | 3 | 35 | 4.2 | 1 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 240 | 3 | 5 | 15.2 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 240 | 3 | -- | -- | --
XTITF86 | F | MSP | Eaton | XTPR6P3BC1 | 200 | 3 | 50 | 6.9 | 1.5 | 200 | 3 | 35 | 6.9 | 1.5 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 200 | 3 | -- | -- | --
XTITF87 | F | MSP | Eaton | XTPR010BC1 | 600Y347 | 3 | 50 | 11 | 10 | 600Y347 | 3 | 35 | 11 | 10 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 600 | 3 | 5 | 11 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 600 | 3 | -- | -- | --
XTITF88 | F | MSP | Eaton | XTPR010BC1 | 480Y277 | 3 | 50 | 11 | 7.5 | 480Y277 | 3 | 35 | 11 | 7.5 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 480 | 3 | 5 | 14 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF89 | F | MSP | Eaton | XTPR010BC1 | 240 | 3 | 50 | 9.6 | 3 | 240 | 3 | 35 | 9.6 | 3 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 240 | 3 | 5 | 15.2 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 240 | 3 | -- | -- | --
XTITF90 | F | MSP | Eaton | XTPR010BC1 | 200 | 3 | 50 | 11 | 3 | 200 | 3 | 35 | 11 | 3 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 200 | 3 | -- | -- | --
XTITF91 | F | MSP | Eaton | XTPR012BC1 | 480Y277 | 3 | 65 | 11 | 7.5 | 480Y277 | 3 | 35 | 11 | 7.5 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 480 | 3 | 5 | 14 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF92 | F | MSP | Eaton | XTPR012BC1 | 240 | 3 | 65 | 9.6 | 3 | 240 | 3 | 35 | 9.6 | 3 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 240 | 3 | 5 | 15.2 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 240 | 3 | -- | -- | --
XTITF93 | F | MSP | Eaton | XTPR012BC1 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 35 | 11 | 3 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 200 | 3 | -- | -- | --
XTITF94 | F | MSP | Eaton | XTPR016BC1 | 480Y277 | 3 | 42 | 14 | 10 | 480Y277 | 3 | 35 | 14 | 10 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 480 | 3 | 5 | 14 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF95 | F | MSP | Eaton | XTPR016BC1 | 240 | 3 | 42 | 15.2 | 5 | 240 | 3 | 35 | 15.2 | 5 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 240 | 3 | 5 | 15.2 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 240 | 3 | -- | -- | --
XTITF96 | F | MSP | Eaton | XTPR016BC1 | 200 | 3 | 42 | 11 | 3 | 200 | 3 | 35 | 11 | 3 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB18X3N | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 200 | 3 | -- | -- | --
XTITF97 | F | MSP | Eaton | XTPR020BC1 | 200 | 3 | 18 | 17.5 | 5 | 200 | 3 | 35 | 17.5 | 5 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB25X3N | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 200 | 3 | -- | -- | --
XTITF98 | F | MSP | Eaton | XTPR025BC1 | 480Y277 | 3 | 18 | 21 | 15 | 480Y277 | 3 | 35 | 21 | 15 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB25X3N | 480 | 3 | 5 | 21 | 15
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF99 | F | MSP | Eaton | XTPR025BC1 | 240 | 3 | 18 | 22 | 7.5 | 240 | 3 | 35 | 22 | 7.5 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB25X3N | 240 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 240 | 3 | -- | -- | --
XTITF100 | F | MSP | Eaton | XTPR032BC1 | 480Y277 | 3 | 18 | 27 | 20 | 480Y277 | 3 | 35 | 27 | 20 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB32X3N | 480 | 3 | 5 | 27 | 20
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 480 | 3 | -- | -- | --
XTITF101 | F | MSP | Eaton | XTPR032BC1 | 240 | 3 | 18 | 28 | 10 | 240 | 3 | 35 | 28 | 10 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB32X3N | 240 | 3 | 5 | 28 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 240 | 3 | -- | -- | --
XTITF102 | F | MSP | Eaton | XTPR032BC1 | 200 | 3 | 18 | 25.3 | 7.5 | 200 | 3 | 35 | 25.3 | 7.5 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NB32X3N | 200 | 3 | 5 | 25.3 | 7.5
|  | ACC(ADAPTOR) | Eaton | XTPAXLSA | 200 | 3 | -- | -- | --
XTITF103 | F | MSP | Eaton | XTPR016DC1 | 600Y347 | 3 | 25 | 11 | 10 | 600Y347 | 3 | 5 | 11 | 10 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 600 | 3 | 5 | 27 | 25
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 600 | 3 | -- | -- | --
XTITF104 | F | MSP | Eaton | XTPR016DC1 | 480Y277 | 3 | 65 | 14 | 10 | 480Y277 | 3 | 35 | 14 | 10 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 480 | 3 | 5 | 34 | 25
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 480 | 3 | -- | -- | --
XTITF105 | F | MSP | Eaton | XTPR016DC1 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 35 | 15.2 | 5 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 240 | 3 | 5 | 28 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 240 | 3 | -- | -- | --
XTITF106 | F | MSP | Eaton | XTPR016DC1 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 35 | 11 | 3 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 200 | 3 | 5 | 32.2 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 200 | 3 | -- | -- | --
XTITF107 | F | MSP | Eaton | XTPR025DC1 | 600Y347 | 3 | 25 | 22 | 20 | 600Y347 | 3 | 5 | 27 | 25 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 600 | 3 | 5 | 27 | 25
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 600 | 3 | -- | -- | --
XTITF108 | F | MSP | Eaton | XTPR025DC1 | 480Y277 | 3 | 65 | 21 | 15 | 480Y277 | 3 | 35 | 27 | 20 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 480 | 3 | 5 | 34 | 25
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 480 | 3 | -- | -- | --
XTITF109 | F | MSP | Eaton | XTPR025DC1 | 240 | 3 | 65 | 22 | 7.5 | 240 | 3 | 35 | 22 | 7.5 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 240 | 3 | 5 | 28 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 240 | 3 | -- | -- | --
XTITF110 | F | MSP | Eaton | XTPR025DC1 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 35 | 25.3 | 7.5 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 200 | 3 | 5 | 32.2 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 200 | 3 | -- | -- | --
XTITF111 | F | MSP | Eaton | XTPR032DC1 | 600Y347 | 3 | 25 | 32 | 30 | 600Y347 | 3 | 5 | 27 | 25 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 600 | 3 | 5 | 27 | 25
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 600 | 3 | -- | -- | --
XTITF112 | F | MSP | Eaton | XTPR032DC1 | 480Y277 | 3 | 65 | 27 | 20 | 480Y277 | 3 | 35 | 34 | 25 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 480 | 3 | 5 | 34 | 25
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 480 | 3 | -- | -- | --
XTITF113 | F | MSP | Eaton | XTPR032DC1 | 240 | 3 | 65 | 28 | 10 | 240 | 3 | 35 | 28 | 10 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 240 | 3 | 5 | 28 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 240 | 3 | -- | -- | --
XTITF114 | F | MSP | Eaton | XTPR032DC1 | 200 | 3 | 65 | 25.3 | 7.5 | 200 | 3 | 35 | 32.2 | 10 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 200 | 3 | 5 | 32.2 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 200 | 3 | -- | -- | --
XTITF115 | F | MSP | Eaton | XTPR040DC1 | 600Y347 | 3 | 25 | 32 | 30 | 600Y347 | 3 | 5 | 27 | 25 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 600 | 3 | 5 | 27 | 25
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 600 | 3 | -- | -- | --
XTITF116 | F | MSP | Eaton | XTPR040DC1 | 480Y277 | 3 | 65 | 40 | 30 | 480Y277 | 3 | 35 | 34 | 25 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 480 | 3 | 5 | 34 | 25
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 480 | 3 | -- | -- | --
XTITF117 | F | MSP | Eaton | XTPR040DC1 | 200 | 3 | 65 | 32.2 | 10 | 200 | 3 | 35 | 32.2 | 10 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 200 | 3 | 5 | 32.2 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 200 | 3 | -- | -- | --
XTITF118 | F | MSP | Eaton | XTPR050DC1 | 480Y277 | 3 | 65 | 40 | 30 | 480Y277 | 3 | 35 | 40 | 30 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC50X3N | 480 | 3 | 5 | 40 | 30
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 480 | 3 | -- | -- | --
XTITF119 | F | MSP | Eaton | XTPR050DC1 | 240 | 3 | 65 | 42 | 15 | 240 | 3 | 35 | 42 | 15 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC50X3N | 240 | 3 | 5 | 42 | 15
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 240 | 3 | -- | -- | --
XTITF120 | F | MSP | Eaton | XTPR016DC1 | 600Y347 | 3 | 25 | 11 | 10 | 600Y347 | 3 | 5 | 11 | 10 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 600 | 3 | 5 | 27 | 25
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 600 | 3 | -- | -- | --
XTITF121 | F | MSP | Eaton | XTPR016DC1 | 480Y277 | 3 | 65 | 14 | 10 | 480Y277 | 3 | 35 | 14 | 10 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 480 | 3 | 5 | 34 | 25
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 480 | 3 | -- | -- | --
XTITF122 | F | MSP | Eaton | XTPR016DC1 | 240 | 3 | 65 | 15.2 | 5 | 240 | 3 | 35 | 15.2 | 5 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 240 | 3 | 5 | 28 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 240 | 3 | -- | -- | --
XTITF123 | F | MSP | Eaton | XTPR016DC1 | 200 | 3 | 65 | 11 | 3 | 200 | 3 | 35 | 11 | 3 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 200 | 3 | 5 | 32.2 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 200 | 3 | -- | -- | --
XTITF124 | F | MSP | Eaton | XTPR025DC1 | 600Y347 | 3 | 25 | 22 | 20 | 600Y347 | 3 | 5 | 27 | 25 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 600 | 3 | 5 | 27 | 25
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 600 | 3 | -- | -- | --
XTITF125 | F | MSP | Eaton | XTPR025DC1 | 480Y277 | 3 | 65 | 21 | 15 | 480Y277 | 3 | 35 | 27 | 20 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 480 | 3 | 5 | 34 | 25
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 480 | 3 | -- | -- | --
XTITF126 | F | MSP | Eaton | XTPR025DC1 | 240 | 3 | 65 | 22 | 7.5 | 240 | 3 | 35 | 22 | 7.5 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 240 | 3 | 5 | 28 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 240 | 3 | -- | -- | --
XTITF127 | F | MSP | Eaton | XTPR025DC1 | 200 | 3 | 65 | 17.5 | 5 | 200 | 3 | 35 | 25.3 | 7.5 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 200 | 3 | 5 | 32.2 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 200 | 3 | -- | -- | --
XTITF128 | F | MSP | Eaton | XTPR032DC1 | 600Y347 | 3 | 25 | 32 | 30 | 600Y347 | 3 | 5 | 27 | 25 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 600 | 3 | 5 | 27 | 25
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 600 | 3 | -- | -- | --
XTITF129 | F | MSP | Eaton | XTPR032DC1 | 480Y277 | 3 | 65 | 27 | 20 | 480Y277 | 3 | 35 | 34 | 25 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 480 | 3 | 5 | 34 | 25
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 480 | 3 | -- | -- | --
XTITF130 | F | MSP | Eaton | XTPR032DC1 | 240 | 3 | 65 | 28 | 10 | 240 | 3 | 35 | 28 | 10 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 240 | 3 | 5 | 28 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 240 | 3 | -- | -- | --
XTITF131 | F | MSP | Eaton | XTPR032DC1 | 200 | 3 | 65 | 25.3 | 7.5 | 200 | 3 | 35 | 32.2 | 10 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 200 | 3 | 5 | 32.2 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 200 | 3 | -- | -- | --
XTITF132 | F | MSP | Eaton | XTPR040DC1 | 600Y347 | 3 | 25 | 32 | 30 | 600Y347 | 3 | 5 | 27 | 25 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 600 | 3 | 5 | 27 | 25
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 600 | 3 | -- | -- | --
XTITF133 | F | MSP | Eaton | XTPR040DC1 | 480Y277 | 3 | 65 | 40 | 30 | 480Y277 | 3 | 35 | 34 | 25 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 480 | 3 | 5 | 34 | 25
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 480 | 3 | -- | -- | --
XTITF134 | F | MSP | Eaton | XTPR040DC1 | 200 | 3 | 65 | 32.2 | 10 | 200 | 3 | 35 | 32.2 | 10 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC40X3N | 200 | 3 | 5 | 32.2 | 10
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 200 | 3 | -- | -- | --
XTITF135 | F | MSP | Eaton | XTPR050DC1 | 480Y277 | 3 | 65 | 40 | 30 | 480Y277 | 3 | 35 | 40 | 30 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC50X3N | 480 | 3 | 5 | 40 | 30
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 480 | 3 | -- | -- | --
XTITF136 | F | MSP | Eaton | XTPR050DC1 | 240 | 3 | 65 | 42 | 15 | 240 | 3 | 35 | 42 | 15 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04NC50X3N | 240 | 3 | 5 | 42 | 15
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 240 | 3 | -- | -- | --
XTITF137 | F | MSP | Eaton | XTPR050DC1 | 480Y277 | 3 | 65 | 40 | 30 | 480Y277 | 3 | 35 | 40 | 30 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04ND65X3N | 480 | 3 | 10 | 65 | 50
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 480 | 3 | -- | -- | --
XTITF138 | F | MSP | Eaton | XTPR050DC1 | 240 | 3 | 65 | 42 | 15 | 240 | 3 | 35 | 42 | 15 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04ND65X3N | 240 | 3 | 10 | 54 | 20
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 240 | 3 | -- | -- | --
XTITF139 | F | MSP | Eaton | XTPR058DC1 | 480Y277 | 3 | 65 | 52 | 40 | 480Y277 | 3 | 35 | 52 | 40 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04ND65X3N | 480 | 3 | 10 | 65 | 50
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 480 | 3 | -- | -- | --
XTITF140 | F | MSP | Eaton | XTPR063DC1 | 480Y277 | 3 | 65 | 52 | 40 | 480Y277 | 3 | 35 | 52 | 40 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04ND65X3N | 480 | 3 | 10 | 65 | 50
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 480 | 3 | -- | -- | --
XTITF141 | F | MSP | Eaton | XTPR050DC1 | 480Y277 | 3 | 65 | 40 | 30 | 480Y277 | 3 | 35 | 40 | 30 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04ND65X3N | 480 | 3 | 10 | 65 | 50
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 480 | 3 | -- | -- | --
XTITF142 | F | MSP | Eaton | XTPR050DC1 | 240 | 3 | 65 | 42 | 15 | 240 | 3 | 35 | 42 | 15 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04ND65X3N | 240 | 3 | 10 | 54 | 20
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 240 | 3 | -- | -- | --
XTITF143 | F | MSP | Eaton | XTPR058DC1 | 480Y277 | 3 | 65 | 52 | 40 | 480Y277 | 3 | 35 | 52 | 40 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04ND65X3N | 480 | 3 | 10 | 65 | 50
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 480 | 3 | -- | -- | --
XTITF144 | F | MSP | Eaton | XTPR063DC1 | 480Y277 | 3 | 65 | 52 | 40 | 480Y277 | 3 | 35 | 52 | 40 | 2433 | 1, 2 | E218618, V2 S2
|  | MC | Eaton | E04ND65X3N | 480 | 3 | 10 | 65 | 50
|  | ACC(ADAPTOR) | Eaton | XTPAXLSAD | 480 | 3 | -- | -- | --
Conditions of Use:
1. All of the specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches. Additional testing is not required when installed in an enclosure having the same or larger volume.
2. Interconnect wire size between components are as specified: controllers having 27mm size (A suffix) contactor use No. 12 AWG; controllers having 45mm (B suffix) contactors use No. 10 AWG; controllers having 54mm (C suffix) contactors use No. 8 AWG; controllers having 76mm (D suffix) contactors use No. 6 AWG.