## Fuji Electric - Type E
Issued: 2008-07-28
| Combination motor controllers for use in industrial control panels | [14 empty] | Last Revised: 2008-09-12
ID Number | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component Ratings |  |  |  | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in.) | Conditions of Acceptability | Combination UL File Reference
[5 empty] | kA | Max Amps | Volts | Poles
FEE080001 | E | MSP | Fuji Electric | BM3RSB-P40 | 50 | 0.25 - 0.4 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | - | 0.4 FLA/2.4 LRA | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080002 | E | MSP | Fuji Electric | BM3RSB-P63 | 50 | 0.4 - 0.63 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | - | 0.63 FLA/3.8 LRA | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080003 | E | MSP | Fuji Electric | BM3RSB-001 | 50 | 0.63 - 1.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | - | 1.0 FLA/ 6.0 LRA | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080004 | E | MSP | Fuji Electric | BM3RSB-1P6 | 50 | 1.0 - 1.6 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 0.75 | 1.6 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080005 | E | MSP | Fuji Electric | BM3RSB-2P5 | 50 | 1.6 - 2.5 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 1 | 2.1 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080006 | E | MSP | Fuji Electric | BM3RSB-004 | 50 | 2.5 - 4.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 2 | 3.4 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080007 | E | MSP | Fuji Electric | BM3RSB-6P3 | 50 | 4.0 - 6.3 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 3 | 4.8 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080008 | E | MSP | Fuji Electric | BM3RSB-010 | 22 | 6.3 - 10.0 | 480Y/277 | 3 | 22 | 480Y/277 | 3 | 5 | 7.6 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080009 | E | MSP | Fuji Electric | BM3RSB-013 | 22 | 9.0 - 13.0 | 480Y/277 | 3 | 22 | 480Y/277 | 3 | 7.5 | 11 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080010 | E | MSP | Fuji Electric | BM3RSB-016 | 22 | 11.0 - 16.0 | 480Y/277 | 3 | 22 | 480Y/277 | 3 | 10 | 14 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080011 | E | MSP | Fuji Electric | BM3RSB-020 | 22 | 14.0 - 20.0 | 480Y/277 | 3 | 22 | 480Y/277 | 3 | 10 | 14 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080012 | E | MSP | Fuji Electric | BM3RSB-025 | 22 | 19.0 - 25.0 | 480Y/277 | 3 | 22 | 480Y/277 | 3 | 15 | 21 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080013 | E | MSP | Fuji Electric | BM3RSB-032 | 22 | 24.0 - 32.0 | 480Y/277 | 3 | 22 | 480Y/277 | 3 | 20 | 27 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080014 | E | MSP | Fuji Electric | BM3RSR-P40 | 50 | 0.25 - 0.4 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | - | 0.4 FLA/2.4 LRA | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080015 | E | MSP | Fuji Electric | BM3RSR-P63 | 50 | 0.4 - 0.63 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | - | 0.63 FLA/3.8 LRA | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080016 | E | MSP | Fuji Electric | BM3RSR-001 | 50 | 0.63 - 1.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | - | 1.0 FLA/ 6.0 LRA | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080017 | E | MSP | Fuji Electric | BM3RSR-1P6 | 50 | 1.0 - 1.6 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 0.75 | 1.6 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080018 | E | MSP | Fuji Electric | BM3RSR-2P5 | 50 | 1.6 - 2.5 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 1 | 2.1 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080019 | E | MSP | Fuji Electric | BM3RSR-004 | 50 | 2.5 - 4.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 2 | 3.4 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080020 | E | MSP | Fuji Electric | BM3RSR-6P3 | 50 | 4.0 - 6.3 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 3 | 4.8 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080021 | E | MSP | Fuji Electric | BM3RSR-010 | 22 | 6.3 - 10.0 | 480Y/277 | 3 | 22 | 480Y/277 | 3 | 5 | 7.6 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080022 | E | MSP | Fuji Electric | BM3RSR-013 | 22 | 9.0 - 13.0 | 480Y/277 | 3 | 22 | 480Y/277 | 3 | 7.5 | 11 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080023 | E | MSP | Fuji Electric | BM3RSR-016 | 22 | 11.0 - 16.0 | 480Y/277 | 3 | 22 | 480Y/277 | 3 | 10 | 14 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080024 | E | MSP | Fuji Electric | BM3RSR-020 | 22 | 14.0 - 20.0 | 480Y/277 | 3 | 22 | 480Y/277 | 3 | 10 | 14 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080025 | E | MSP | Fuji Electric | BM3RSR-025 | 22 | 19.0 - 25.0 | 480Y/277 | 3 | 22 | 480Y/277 | 3 | 15 | 21 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080026 | E | MSP | Fuji Electric | BM3RSR-032 | 22 | 24.0 - 32.0 | 480Y/277 | 3 | 22 | 480Y/277 | 3 | 20 | 27 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080027 | E | MSP | Fuji Electric | BM3RHB-P40 | 50 | 0.25 - 0.4 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | - | 0.4 FLA/2.4 LRA | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080028 | E | MSP | Fuji Electric | BM3RHB-P63 | 50 | 0.4 - 0.63 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | - | 0.63 FLA/3.8 LRA | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080029 | E | MSP | Fuji Electric | BM3RHB-001 | 50 | 0.63 - 1.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | - | 1.0 FLA/ 6.0 LRA | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080030 | E | MSP | Fuji Electric | BM3RHB-1P6 | 50 | 1.0 - 1.6 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 0.75 | 1.6 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080031 | E | MSP | Fuji Electric | BM3RHB-2P5 | 50 | 1.6 - 2.5 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 1 | 2.1 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080032 | E | MSP | Fuji Electric | BM3RHB-004 | 50 | 2.5 - 4.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 2 | 3.4 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080033 | E | MSP | Fuji Electric | BM3RHB-6P3 | 50 | 4.0 - 6.3 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 3 | 4.8 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080034 | E | MSP | Fuji Electric | BM3RHB-010 | 50 | 6.3 - 10.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 5 | 7.6 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080035 | E | MSP | Fuji Electric | BM3RHB-013 | 50 | 9.0 - 13.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 7.5 | 11 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080036 | E | MSP | Fuji Electric | BM3RHB-016 | 50 | 11.0 - 16.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 10 | 14 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080037 | E | MSP | Fuji Electric | BM3RHB-020 | 50 | 14.0 - 20.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 10 | 14 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080038 | E | MSP | Fuji Electric | BM3RHB-025 | 50 | 19.0 - 25.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 15 | 21 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080039 | E | MSP | Fuji Electric | BM3RHB-032 | 50 | 24.0 - 32.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 20 | 27 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080040 | E | MSP | Fuji Electric | BM3RHR-P40 | 50 | 0.25 - 0.4 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | - | 0.4 FLA/2.4 LRA | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080041 | E | MSP | Fuji Electric | BM3RHR-P63 | 50 | 0.4 - 0.63 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | - | 0.63 FLA/3.8 LRA | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080042 | E | MSP | Fuji Electric | BM3RHR-001 | 50 | 0.63 - 1.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | - | 1.0 FLA/ 6.0 LRA | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080043 | E | MSP | Fuji Electric | BM3RHR-1P6 | 50 | 1.0 - 1.6 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 0.75 | 1.6 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080044 | E | MSP | Fuji Electric | BM3RHR-2P5 | 50 | 1.6 - 2.5 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 1 | 2.1 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080045 | E | MSP | Fuji Electric | BM3RHR-004 | 50 | 2.5 - 4.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 2 | 3.4 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080046 | E | MSP | Fuji Electric | BM3RHR-6P3 | 50 | 4.0 - 6.3 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 3 | 4.8 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080047 | E | MSP | Fuji Electric | BM3RHR-010 | 50 | 6.3 - 10.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 5 | 7.6 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080048 | E | MSP | Fuji Electric | BM3RHR-013 | 50 | 9.0 - 13.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 7.5 | 11 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080049 | E | MSP | Fuji Electric | BM3RHR-016 | 50 | 11.0 - 16.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 10 | 14 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080050 | E | MSP | Fuji Electric | BM3RHR-020 | 50 | 14.0 - 20.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 10 | 14 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080051 | E | MSP | Fuji Electric | BM3RHR-025 | 50 | 19.0 - 25.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 15 | 21 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080052 | E | MSP | Fuji Electric | BM3RHR-032 | 50 | 24.0 - 32.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 20 | 27 | 148 | 1, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
FEE080053 | E | MSP | Fuji Electric | BM3VSB-010 | 22 | 6.3 - 10.0 | 480Y/277 | 3 | 22 | 480Y/277 | 3 | 5 | 7.6 | 264 | 1, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
-
FEE080054 | E | MSP | Fuji Electric | BM3VSB-013 | 22 | 9.0 - 13.0 | 480Y/277 | 3 | 22 | 480Y/277 | 3 | 7.5 | 11 | 264 | 1, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
-
FEE080055 | E | MSP | Fuji Electric | BM3VSB-016 | 22 | 11.0 - 16.0 | 480Y/277 | 3 | 22 | 480Y/277 | 3 | 10 | 14 | 264 | 1, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
-
FEE080056 | E | MSP | Fuji Electric | BM3VSB-020 | 22 | 14.0 - 20.0 | 480Y/277 | 3 | 22 | 480Y/277 | 3 | 10 | 14 | 264 | 1, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
-
FEE080057 | E | MSP | Fuji Electric | BM3VSB-025 | 22 | 19.0 - 25.0 | 480Y/277 | 3 | 22 | 480Y/277 | 3 | 15 | 21 | 264 | 1, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
-
FEE080058 | E | MSP | Fuji Electric | BM3VSB-032 | 22 | 24.0 - 32.0 | 480Y/277 | 3 | 22 | 480Y/277 | 3 | 20 | 27 | 264 | 1, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
-
FEE080059 | E | MSP | Fuji Electric | BM3VSB-040 | 22 | 28.0 - 40.0 | 480Y/277 | 3 | 22 | 480Y/277 | 3 | 30 | 40 | 264 | 1, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
-
FEE080060 | E | MSP | Fuji Electric | BM3VSB-050 | 22 | 35.0 - 50.0 | 480Y/277 | 3 | 22 | 480Y/277 | 3 | 30 | 40 | 264 | 1, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
-
FEE080061 | E | MSP | Fuji Electric | BM3VSB-063 | 22 | 45.0 - 63.0 | 480Y/277 | 3 | 22 | 480Y/277 | 3 | 40 | 52 | 264 | 1, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
-
FEE080062 | E | MSP | Fuji Electric | BM3VHB-010 | 50 | 6.3 - 10.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 5 | 7.6 | 264 | 1, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
-
FEE080063 | E | MSP | Fuji Electric | BM3VHB-013 | 50 | 9.0 - 13.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 7.5 | 11 | 264 | 1, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
-
FEE080064 | E | MSP | Fuji Electric | BM3VHB-016 | 50 | 11.0 - 16.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 10 | 14 | 264 | 1, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
-
FEE080065 | E | MSP | Fuji Electric | BM3VHB-020 | 50 | 14.0 - 20.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 10 | 14 | 264 | 1, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
-
FEE080066 | E | MSP | Fuji Electric | BM3VHB-025 | 50 | 19.0 - 25.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 15 | 21 | 264 | 1, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
-
FEE080067 | E | MSP | Fuji Electric | BM3VHB-032 | 50 | 24.0 - 32.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 20 | 27 | 264 | 1, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
-
FEE080068 | E | MSP | Fuji Electric | BM3VHB-040 | 50 | 28.0 - 40.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 30 | 40 | 264 | 1, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
-
FEE080069 | E | MSP | Fuji Electric | BM3VHB-050 | 50 | 35.0 - 50.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 30 | 40 | 264 | 1, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
-
FEE080070 | E | MSP | Fuji Electric | BM3VHB-063 | 50 | 45.0 - 63.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 40 | 52 | 264 | 1, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
-
Conditions of Acceptability:
|  | 1 | All of the specified individual components of the combination motor controller have been installed in an enclosure having
a specified internal volume in cubic inches. Additional testing of the combination motor controller is not required when
installed in an enclosure having the same or larger volume.
|  | 2 | When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from
the overcurrent protective devices and other components shall not be installed in this area.
|  | 3 | When specified, the overload relay heater table number shall be provided with the equipment.
|  | 4 | Unless otherwise specified, all connections between components are made with insulated wire having an ampacity of
125 percent of the rated motor current and connected to the terminals supplied with the individual components.
|  | 5 | The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor
controllers shall be considered in the end-product application.

## Fuji Electric - Type F
Issued: 2008-07-28
| Combination motor controllers for use in industrial control panels | [14 empty] | Last Revised: 2008-09-12
ID Number | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component Ratings |  |  |  | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in.) | Conditions of Acceptability | Combination UL File Reference
[5 empty] | kA | Max Amps | Volts | Poles
FEF080001 | F | MSP | Fuji Electric | BM3RSB-P40 | 50 | 0.25 - 0.4 | 480Y/277 | 3 | 65 | 480/277 | 3 | - | 0.4 FLA/2.4 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M01 | 5 | 4.8 | 600 | 3
FEF080002 | F | MSP | Fuji Electric | BM3RSB-P63 | 50 | 0.4 - 0.63 | 480Y/277 | 3 | 65 | 480/277 | 3 | - | 0.63 FLA/3.8 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M01 | 5 | 4.8 | 600 | 3
FEF080003 | F | MSP | Fuji Electric | BM3RSB-001 | 50 | 0.63 - 1.0 | 480Y/277 | 3 | 65 | 480/277 | 3 | - | 1.0 FLA/6.0 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M01 | 5 | 4.8 | 600 | 3
FEF080004 | F | MSP | Fuji Electric | BM3RSB-1P6 | 50 | 1.0 - 1.6 | 480Y/277 | 3 | 65 | 480/277 | 3 | 0.75 | 1.6 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M01 | 5 | 4.8 | 600 | 3
FEF080005 | F | MSP | Fuji Electric | BM3RSB-2P5 | 50 | 1.6 - 2.5 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 1 | 2.1 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M01 | 5 | 4.8 | 600 | 3
FEF080006 | F | MSP | Fuji Electric | BM3RSB-004 | 50 | 2.5 - 4.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 2 | 3.4 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M01 | 5 | 4.8 | 600 | 3
FEF080007 | F | MSP | Fuji Electric | BM3RSB-6P3 | 50 | 4.0 - 6.3 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 3 | 4.8 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M01 | 5 | 4.8 | 600 | 3
FEF080008 | F | MSP | Fuji Electric | BM3RSB-010 | 22 | 6.3 - 10.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 5 | 7.6 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M02 | 5 | 7.6 | 600 | 3
FEF080009 | F | MSP | Fuji Electric | BM3RSB-P40 | 50 | 0.25 - 0.4 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 0.4 FLA/2.4 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080010 | F | MSP | Fuji Electric | BM3RSB-P63 | 50 | 0.4 - 0.63 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 0.63 FLA/3.8 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080011 | F | MSP | Fuji Electric | BM3RSB-001 | 50 | 0.63 - 1.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 1.0 FLA/6.0 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080012 | F | MSP | Fuji Electric | BM3RSB-1P6 | 50 | 1.0 - 1.6 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 0.75 | 1.6 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080013 | F | MSP | Fuji Electric | BM3RSB-2P5 | 50 | 1.6 - 2.5 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 1 | 2.1 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080014 | F | MSP | Fuji Electric | BM3RSB-004 | 50 | 2.5 - 4.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 2 | 3.4 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080015 | F | MSP | Fuji Electric | BM3RSB-6P3 | 50 | 4.0 - 6.3 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 3 | 4.8 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080016 | F | MSP | Fuji Electric | BM3RSB-010 | 22 | 6.3 - 10.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 5 | 7.6 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080017 | F | MSP | Fuji Electric | BM3RSB-013 | 22 | 9.0 - 13.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 7.5 | 11 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E03 | 5 | 11 | 600 | 3
FEF080018 | F | MSP | Fuji Electric | BM3RSB-016 | 22 | 11.0 - 16.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 10 | 14 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E04 | 5 | 14 | 600 | 3
FEF080019 | F | MSP | Fuji Electric | BM3RSB-020 | 22 | 14.0 - 20.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 10 | 14 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E04 | 5 | 14 | 600 | 3
FEF080020 | F | MSP | Fuji Electric | BM3RSB-025 | 22 | 19.0 - 25.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 15 | 21 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E05 | 5 | 21 | 600 | 3
FEF080021 | F | MSP | Fuji Electric | BM3RSB-032 | 22 | 24.0 - 32.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 20 | 27 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1 | 5 | 34 | 600 | 3
FEF080022 | F | MSP | Fuji Electric | BM3RSB-P40 | 50 | 0.25 - 0.4 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 0.4 FLA/2.4 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080023 | F | MSP | Fuji Electric | BM3RSB-P63 | 50 | 0.4 - 0.63 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 0.63 FLA/3.8 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080024 | F | MSP | Fuji Electric | BM3RSB-001 | 50 | 0.63 - 1.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 1.0 FLA/6.0 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080025 | F | MSP | Fuji Electric | BM3RSB-1P6 | 50 | 1.0 - 1.6 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 0.75 | 1.6 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080026 | F | MSP | Fuji Electric | BM3RSB-2P5 | 50 | 1.6 - 2.5 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 1 | 2.1 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080027 | F | MSP | Fuji Electric | BM3RSB-004 | 50 | 2.5 - 4.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 2 | 3.4 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080028 | F | MSP | Fuji Electric | BM3RSB-6P3 | 50 | 4.0 - 6.3 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 3 | 4.8 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080029 | F | MSP | Fuji Electric | BM3RSB-010 | 22 | 6.3 - 10.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 5 | 7.6 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080030 | F | MSP | Fuji Electric | BM3RSB-013 | 22 | 9.0 - 13.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 7.5 | 11 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E03P | 5 | 11 | 600 | 3
FEF080031 | F | MSP | Fuji Electric | BM3RSB-016 | 22 | 11.0 - 16.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 10 | 14 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E04P | 5 | 14 | 600 | 3
FEF080032 | F | MSP | Fuji Electric | BM3RSB-020 | 22 | 14.0 - 20.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 10 | 14 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E04P | 5 | 14 | 600 | 3
FEF080033 | F | MSP | Fuji Electric | BM3RSB-025 | 22 | 19.0 - 25.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 15 | 21 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E05P | 5 | 21 | 600 | 3
FEF080034 | F | MSP | Fuji Electric | BM3RSB-032 | 22 | 24.0 - 32.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 20 | 27 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1P | 5 | 34 | 600 | 3
FEF080035 | F | MSP | Fuji Electric | BM3RSR-P40 | 50 | 0.25 - 0.4 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 0.4 FLA/2.4 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M01 | 5 | 4.8 | 600 | 3
FEF080036 | F | MSP | Fuji Electric | BM3RSR-P63 | 50 | 0.4 - 0.63 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 0.63 FLA/3.8 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M01 | 5 | 4.8 | 600 | 3
FEF080037 | F | MSP | Fuji Electric | BM3RSR-001 | 50 | 0.63 - 1.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 1.0 FLA/6.0 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M01 | 5 | 4.8 | 600 | 3
FEF080038 | F | MSP | Fuji Electric | BM3RSR-1P6 | 50 | 1.0 - 1.6 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 0.75 | 1.6 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M01 | 5 | 4.8 | 600 | 3
FEF080039 | F | MSP | Fuji Electric | BM3RSR-2P5 | 50 | 1.6 - 2.5 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 1 | 2.1 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M01 | 5 | 4.8 | 600 | 3
FEF080040 | F | MSP | Fuji Electric | BM3RSR-004 | 50 | 2.5 - 4.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 2 | 3.4 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M01 | 5 | 4.8 | 600 | 3
FEF080041 | F | MSP | Fuji Electric | BM3RSR-6P3 | 50 | 4.0 - 6.3 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 3 | 4.8 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M01 | 5 | 4.8 | 600 | 3
FEF080042 | F | MSP | Fuji Electric | BM3RSR-010 | 22 | 6.3 - 10.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 5 | 7.6 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M02 | 5 | 7.6 | 600 | 3
FEF080043 | F | MSP | Fuji Electric | BM3RSR-P40 | 50 | 0.25 - 0.4 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 0.4 FLA/2.4 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080044 | F | MSP | Fuji Electric | BM3RSR-P63 | 50 | 0.4 - 0.63 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 0.63 FLA/3.8 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080045 | F | MSP | Fuji Electric | BM3RSR-001 | 50 | 0.63 - 1.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 1.0 FLA/6.0 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080046 | F | MSP | Fuji Electric | BM3RSR-1P6 | 50 | 1.0 - 1.6 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 0.75 | 1.6 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080047 | F | MSP | Fuji Electric | BM3RSR-2P5 | 50 | 1.6 - 2.5 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 1 | 2.1 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080048 | F | MSP | Fuji Electric | BM3RSR-004 | 50 | 2.5 - 4.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 2 | 3.4 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080049 | F | MSP | Fuji Electric | BM3RSR-6P3 | 50 | 4.0 - 6.3 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 3 | 4.8 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080050 | F | MSP | Fuji Electric | BM3RSR-010 | 22 | 6.3 - 10.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 5 | 7.6 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080051 | F | MSP | Fuji Electric | BM3RSR-013 | 22 | 9.0 - 13.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 7.5 | 11 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E03 | 5 | 11 | 600 | 3
FEF080052 | F | MSP | Fuji Electric | BM3RSR-016 | 22 | 11.0 - 16.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 10 | 14 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E04 | 5 | 14 | 600 | 3
FEF080053 | F | MSP | Fuji Electric | BM3RSR-020 | 22 | 14.0 - 20.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 10 | 14 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E04 | 5 | 14 | 600 | 3
FEF080054 | F | MSP | Fuji Electric | BM3RSR-025 | 22 | 19.0 - 25.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 15 | 21 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E05 | 5 | 21 | 600 | 3
FEF080055 | F | MSP | Fuji Electric | BM3RSR-032 | 22 | 24.0 - 32.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 20 | 27 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1 | 5 | 34 | 600 | 3
FEF080056 | F | MSP | Fuji Electric | BM3RSR-P40 | 50 | 0.25 - 0.4 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 0.4 FLA/2.4 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080057 | F | MSP | Fuji Electric | BM3RSR-P63 | 50 | 0.4 - 0.63 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 0.63 FLA/3.8 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080058 | F | MSP | Fuji Electric | BM3RSR-001 | 50 | 0.63 - 1.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 1.0 FLA/6.0 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080059 | F | MSP | Fuji Electric | BM3RSR-1P6 | 50 | 1.0 - 1.6 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 0.75 | 1.6 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080060 | F | MSP | Fuji Electric | BM3RSR-2P5 | 50 | 1.6 - 2.5 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 1 | 2.1 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080061 | F | MSP | Fuji Electric | BM3RSR-004 | 50 | 2.5 - 4.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 2 | 3.4 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080062 | F | MSP | Fuji Electric | BM3RSR-6P3 | 50 | 4.0 - 6.3 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 3 | 4.8 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080063 | F | MSP | Fuji Electric | BM3RSR-010 | 22 | 6.3 - 10.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 5 | 7.6 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080064 | F | MSP | Fuji Electric | BM3RSR-013 | 22 | 9.0 - 13.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 7.5 | 11 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E03P | 5 | 11 | 600 | 3
FEF080065 | F | MSP | Fuji Electric | BM3RSR-016 | 22 | 11.0 - 16.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 10 | 14 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E04P | 5 | 14 | 600 | 3
FEF080066 | F | MSP | Fuji Electric | BM3RSR-020 | 22 | 14.0 - 20.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 10 | 14 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E04P | 5 | 14 | 600 | 3
FEF080067 | F | MSP | Fuji Electric | BM3RSR-025 | 22 | 19.0 - 25.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 15 | 21 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E05P | 5 | 21 | 600 | 3
FEF080068 | F | MSP | Fuji Electric | BM3RSR-032 | 22 | 24.0 - 32.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 20 | 27 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1P | 5 | 34 | 600 | 3
FEF080069 | F | MSP | Fuji Electric | BM3RHB-P40 | 50 | 0.25 - 0.4 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 0.4 FLA/2.4 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M01 | 5 | 4.8 | 600 | 3
FEF080070 | F | MSP | Fuji Electric | BM3RHB-P63 | 50 | 0.4 - 0.63 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 0.63 FLA/3.8 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M01 | 5 | 4.8 | 600 | 3
FEF080071 | F | MSP | Fuji Electric | BM3RHB-001 | 50 | 0.63 - 1.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 1.0 FLA/6.0 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M01 | 5 | 4.8 | 600 | 3
FEF080072 | F | MSP | Fuji Electric | BM3RHB-1P6 | 50 | 1.0 - 1.6 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 0.75 | 1.6 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M01 | 5 | 4.8 | 600 | 3
FEF080073 | F | MSP | Fuji Electric | BM3RHB-2P5 | 50 | 1.6 - 2.5 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 1 | 2.1 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M01 | 5 | 4.8 | 600 | 3
FEF080074 | F | MSP | Fuji Electric | BM3RHB-004 | 50 | 2.5 - 4.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 2 | 3.4 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M01 | 5 | 4.8 | 600 | 3
FEF080075 | F | MSP | Fuji Electric | BM3RHB-6P3 | 50 | 4.0 - 6.3 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 3 | 4.8 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M01 | 5 | 4.8 | 600 | 3
FEF080076 | F | MSP | Fuji Electric | BM3RHB-010 | 50 | 6.3 - 10.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 5 | 7.6 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M02 | 5 | 7.6 | 600 | 3
FEF080077 | F | MSP | Fuji Electric | BM3RHB-P40 | 50 | 0.25 - 0.4 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 0.4 FLA/2.4 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080078 | F | MSP | Fuji Electric | BM3RHB-P63 | 50 | 0.4 - 0.63 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 0.63 FLA/3.8 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080079 | F | MSP | Fuji Electric | BM3RHB-001 | 50 | 0.63 - 1.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 1.0 FLA/6.0 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080080 | F | MSP | Fuji Electric | BM3RHB-1P6 | 50 | 1.0 - 1.6 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 0.75 | 1.6 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080081 | F | MSP | Fuji Electric | BM3RHB-2P5 | 50 | 1.6 - 2.5 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 1 | 2.1 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080082 | F | MSP | Fuji Electric | BM3RHB-004 | 50 | 2.5 - 4.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 2 | 3.4 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080083 | F | MSP | Fuji Electric | BM3RHB-6P3 | 50 | 4.0 - 6.3 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 3 | 4.8 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080084 | F | MSP | Fuji Electric | BM3RHB-010 | 50 | 6.3 - 10.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 5 | 7.6 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080085 | F | MSP | Fuji Electric | BM3RHB-013 | 50 | 9.0 - 13.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 7.5 | 11 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E03 | 5 | 11 | 600 | 3
FEF080086 | F | MSP | Fuji Electric | BM3RHB-016 | 50 | 11.0 - 16.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 10 | 14 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E04 | 5 | 14 | 600 | 3
FEF080087 | F | MSP | Fuji Electric | BM3RHB-020 | 50 | 14.0 - 20.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 10 | 14 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E04 | 5 | 14 | 600 | 3
FEF080088 | F | MSP | Fuji Electric | BM3RHB-025 | 50 | 19.0 - 25.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 15 | 21 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E05 | 5 | 21 | 600 | 3
FEF080089 | F | MSP | Fuji Electric | BM3RHB-032 | 50 | 24.0 - 32.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 20 | 27 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1 | 5 | 34 | 600 | 3
FEF080090 | F | MSP | Fuji Electric | BM3RHB-P40 | 50 | 0.25 - 0.4 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 0.4 FLA/2.4 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080091 | F | MSP | Fuji Electric | BM3RHB-P63 | 50 | 0.4 - 0.63 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 0.63 FLA/3.8 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080092 | F | MSP | Fuji Electric | BM3RHB-001 | 50 | 0.63 - 1.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 1.0 FLA/6.0 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080093 | F | MSP | Fuji Electric | BM3RHB-1P6 | 50 | 1.0 - 1.6 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 0.75 | 1.6 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080094 | F | MSP | Fuji Electric | BM3RHB-2P5 | 50 | 1.6 - 2.5 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 1 | 2.1 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080095 | F | MSP | Fuji Electric | BM3RHB-004 | 50 | 2.5 - 4.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 2 | 3.4 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080096 | F | MSP | Fuji Electric | BM3RHB-6P3 | 50 | 4.0 - 6.3 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 3 | 4.8 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080097 | F | MSP | Fuji Electric | BM3RHB-010 | 50 | 6.3 - 10.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 5 | 7.6 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080098 | F | MSP | Fuji Electric | BM3RHB-013 | 50 | 9.0 - 13.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 7.5 | 11 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E03P | 5 | 11 | 600 | 3
FEF080099 | F | MSP | Fuji Electric | BM3RHB-016 | 50 | 11.0 - 16.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 10 | 14 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E04P | 5 | 14 | 600 | 3
FEF080100 | F | MSP | Fuji Electric | BM3RHB-020 | 50 | 14.0 - 20.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 10 | 14 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E04P | 5 | 14 | 600 | 3
FEF080101 | F | MSP | Fuji Electric | BM3RHB-025 | 50 | 19.0 - 25.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 15 | 21 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E05P | 5 | 21 | 600 | 3
FEF080102 | F | MSP | Fuji Electric | BM3RHB-032 | 50 | 24.0 - 32.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 20 | 27 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0TCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1P | 5 | 34 | 600 | 3
FEF080103 | F | MSP | Fuji Electric | BM3RHR-P40 | 50 | 0.25 - 0.4 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 0.4 FLA/2.4 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M01 | 5 | 4.8 | 600 | 3
FEF080104 | F | MSP | Fuji Electric | BM3RHR-P63 | 50 | 0.4 - 0.63 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 0.63 FLA/3.8 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M01 | 5 | 4.8 | 600 | 3
FEF080105 | F | MSP | Fuji Electric | BM3RHR-001 | 50 | 0.63 - 1.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 1.0 FLA/6.0 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M01 | 5 | 4.8 | 600 | 3
FEF080106 | F | MSP | Fuji Electric | BM3RHR-1P6 | 50 | 1.0 - 1.6 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 0.75 | 1.6 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M01 | 5 | 4.8 | 600 | 3
FEF080107 | F | MSP | Fuji Electric | BM3RHR-2P5 | 50 | 1.6 - 2.5 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 1 | 2.1 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M01 | 5 | 4.8 | 600 | 3
FEF080108 | F | MSP | Fuji Electric | BM3RHR-004 | 50 | 2.5 - 4.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 2 | 3.4 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M01 | 5 | 4.8 | 600 | 3
FEF080109 | F | MSP | Fuji Electric | BM3RHR-6P3 | 50 | 4.0 - 6.3 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 3 | 4.8 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M01 | 5 | 4.8 | 600 | 3
FEF080110 | F | MSP | Fuji Electric | BM3RHR-010 | 50 | 6.3 - 10.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 5 | 7.6 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-M02 | 5 | 7.6 | 600 | 3
FEF080111 | F | MSP | Fuji Electric | BM3RHR-P40 | 50 | 0.25 - 0.4 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 0.4 FLA/2.4 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080112 | F | MSP | Fuji Electric | BM3RHR-P63 | 50 | 0.4 - 0.63 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 0.63 FLA/3.8 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080113 | F | MSP | Fuji Electric | BM3RHR-001 | 50 | 0.63 - 1.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 1.0 FLA/6.0 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080114 | F | MSP | Fuji Electric | BM3RHR-1P6 | 50 | 1.0 - 1.6 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 0.75 | 1.6 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080115 | F | MSP | Fuji Electric | BM3RHR-2P5 | 50 | 1.6 - 2.5 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 1 | 2.1 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080116 | F | MSP | Fuji Electric | BM3RHR-004 | 50 | 2.5 - 4.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 2 | 3.4 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080117 | F | MSP | Fuji Electric | BM3RHR-6P3 | 50 | 4.0 - 6.3 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 3 | 4.8 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080118 | F | MSP | Fuji Electric | BM3RHR-010 | 50 | 6.3 - 10.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 5 | 7.6 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02 | 5 | 7.6 | 600 | 3
FEF080119 | F | MSP | Fuji Electric | BM3RHR-013 | 50 | 9.0 - 13.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 7.5 | 11 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E03 | 5 | 11 | 600 | 3
FEF080120 | F | MSP | Fuji Electric | BM3RHR-016 | 50 | 11.0 - 16.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 10 | 14 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E04 | 5 | 14 | 600 | 3
FEF080121 | F | MSP | Fuji Electric | BM3RHR-020 | 50 | 14.0 - 20.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 10 | 14 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E04 | 5 | 14 | 600 | 3
FEF080122 | F | MSP | Fuji Electric | BM3RHR-025 | 50 | 19.0 - 25.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 15 | 21 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E05 | 5 | 21 | 600 | 3
FEF080123 | F | MSP | Fuji Electric | BM3RHR-032 | 50 | 24.0 - 32.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 20 | 27 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1 | 5 | 34 | 600 | 3
FEF080124 | F | MSP | Fuji Electric | BM3RHR-P40 | 50 | 0.25 - 0.4 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 0.4 FLA/2.4 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080125 | F | MSP | Fuji Electric | BM3RHR-P63 | 50 | 0.4 - 0.63 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 0.63 FLA/3.8 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080126 | F | MSP | Fuji Electric | BM3RHR-001 | 50 | 0.63 - 1.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | - | 1.0 FLA/6.0 LRA | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080127 | F | MSP | Fuji Electric | BM3RHR-1P6 | 50 | 1.0 - 1.6 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 0.75 | 1.6 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080128 | F | MSP | Fuji Electric | BM3RHR-2P5 | 50 | 1.6 - 2.5 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 1 | 2.1 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080129 | F | MSP | Fuji Electric | BM3RHR-004 | 50 | 2.5 - 4.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 2 | 3.4 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080130 | F | MSP | Fuji Electric | BM3RHR-6P3 | 50 | 4.0 - 6.3 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 3 | 4.8 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080131 | F | MSP | Fuji Electric | BM3RHR-010 | 50 | 6.3 - 10.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 5 | 7.6 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E02P | 5 | 7.6 | 600 | 3
FEF080132 | F | MSP | Fuji Electric | BM3RHR-013 | 50 | 9.0 - 13.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 7.5 | 11 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E03P | 5 | 11 | 600 | 3
FEF080133 | F | MSP | Fuji Electric | BM3RHR-016 | 50 | 11.0 - 16.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 10 | 14 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E04P | 5 | 14 | 600 | 3
FEF080134 | F | MSP | Fuji Electric | BM3RHR-020 | 50 | 14.0 - 20.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 10 | 14 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E04P | 5 | 14 | 600 | 3
FEF080135 | F | MSP | Fuji Electric | BM3RHR-025 | 50 | 19.0 - 25.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 15 | 21 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E05P | 5 | 21 | 600 | 3
FEF080136 | F | MSP | Fuji Electric | BM3RHR-032 | 50 | 24.0 - 32.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 20 | 27 | 323 | 1, 4, 5 | E211710 Vol. 1 Sec. 1
|  | Adapter | Fuji Electric | BZ0RTCRE | - | - | - | -
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1P | 5 | 34 | 600 | 3
FEF080137 | F | MSP | Fuji Electric | BM3VSB-010 | 22 | 6.3 - 10.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 5 | 7.6 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1 | 5 | 34 | 600 | 3
FEF080138 | F | MSP | Fuji Electric | BM3VSB-013 | 22 | 9.0 - 13.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 7.5 | 11 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1 | 5 | 34 | 600 | 3
FEF080139 | F | MSP | Fuji Electric | BM3VSB-016 | 22 | 11.0 - 16.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 10 | 14 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1 | 5 | 34 | 600 | 3
FEF080140 | F | MSP | Fuji Electric | BM3VSB-020 | 22 | 14.0 - 20.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 10 | 14 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1 | 5 | 34 | 600 | 3
FEF080141 | F | MSP | Fuji Electric | BM3VSB-025 | 22 | 19.0 - 25.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 15 | 21 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1 | 5 | 34 | 600 | 3
FEF080142 | F | MSP | Fuji Electric | BM3VSB-032 | 22 | 24.0 - 32.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 20 | 27 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1 | 5 | 34 | 600 | 3
FEF080143 | F | MSP | Fuji Electric | BM3VSB-040 | 22 | 28.0 - 40.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 30 | 40 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E2 | 5 | 40 | 600 | 3
FEF080144 | F | MSP | Fuji Electric | BM3VSB-050 | 22 | 35.0 - 50.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 30 | 40 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E2S | 5 | 40 | 600 | 3
FEF080145 | F | MSP | Fuji Electric | BM3VSB-063 | 22 | 45.0 - 63.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 40 | 52 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E3 | 5 | 65 | 600 | 3
FEF080146 | F | MSP | Fuji Electric | BM3VHB-010 | 50 | 6.3 - 10.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 5 | 7.6 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1 | 5 | 34 | 600 | 3
FEF080147 | F | MSP | Fuji Electric | BM3VHB-013 | 50 | 9.0 - 13.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 7.5 | 11 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1 | 5 | 34 | 600 | 3
FEF080148 | F | MSP | Fuji Electric | BM3VHB-016 | 50 | 11.0 - 16.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 10 | 14 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1 | 5 | 34 | 600 | 3
FEF080149 | F | MSP | Fuji Electric | BM3VHB-020 | 50 | 14.0 - 20.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 10 | 14 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1 | 5 | 34 | 600 | 3
FEF080150 | F | MSP | Fuji Electric | BM3VHB-025 | 50 | 19.0 - 25.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 15 | 21 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1 | 5 | 34 | 600 | 3
FEF080151 | F | MSP | Fuji Electric | BM3VHB-032 | 50 | 24.0 - 32.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 20 | 27 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1 | 5 | 34 | 600 | 3
FEF080152 | F | MSP | Fuji Electric | BM3VHB-040 | 50 | 28.0 - 40.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 30 | 40 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E2 | 5 | 40 | 600 | 3
FEF080153 | F | MSP | Fuji Electric | BM3VHB-050 | 50 | 35.0 - 50.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 30 | 40 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E2S | 5 | 40 | 600 | 3
FEF080154 | F | MSP | Fuji Electric | BM3VHB-063 | 50 | 45.0 - 63.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 40 | 52 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E3 | 5 | 65 | 600 | 3
FEF080155 | F | MSP | Fuji Electric | BM3VSB-010 | 22 | 6.3 - 10.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 5 | 7.6 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1P | 5 | 34 | 600 | 3
FEF080156 | F | MSP | Fuji Electric | BM3VSB-013 | 22 | 9.0 - 13.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 7.5 | 11 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1P | 5 | 34 | 600 | 3
FEF080157 | F | MSP | Fuji Electric | BM3VSB-016 | 22 | 11.0 - 16.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 10 | 14 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1P | 5 | 34 | 600 | 3
FEF080158 | F | MSP | Fuji Electric | BM3VSB-020 | 22 | 14.0 - 20.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 10 | 14 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1P | 5 | 34 | 600 | 3
FEF080159 | F | MSP | Fuji Electric | BM3VSB-025 | 22 | 19.0 - 25.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 15 | 21 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1P | 5 | 34 | 600 | 3
FEF080160 | F | MSP | Fuji Electric | BM3VSB-032 | 22 | 24.0 - 32.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 20 | 27 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1P | 5 | 34 | 600 | 3
FEF080161 | F | MSP | Fuji Electric | BM3VSB-040 | 22 | 28.0 - 40.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 30 | 40 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E2P | 5 | 40 | 600 | 3
FEF080162 | F | MSP | Fuji Electric | BM3VSB-050 | 22 | 35.0 - 50.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 30 | 40 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E2SP | 5 | 40 | 600 | 3
FEF080163 | F | MSP | Fuji Electric | BM3VSB-063 | 22 | 45.0 - 63.0 | 480Y/277 | 3 | 25 | 480Y/277 | 3 | 40 | 52 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E3P | 5 | 65 | 600 | 3
FEF080164 | F | MSP | Fuji Electric | BM3VHB-010 | 50 | 6.3 - 10.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 5 | 7.6 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1P | 5 | 34 | 600 | 3
FEF080165 | F | MSP | Fuji Electric | BM3VHB-013 | 50 | 9.0 - 13.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 7.5 | 11 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1P | 5 | 34 | 600 | 3
FEF080166 | F | MSP | Fuji Electric | BM3VHB-016 | 50 | 11.0 - 16.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 10 | 14 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1P | 5 | 34 | 600 | 3
FEF080167 | F | MSP | Fuji Electric | BM3VHB-020 | 50 | 14.0 - 20.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 10 | 14 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1P | 5 | 34 | 600 | 3
FEF080168 | F | MSP | Fuji Electric | BM3VHB-025 | 50 | 19.0 - 25.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 15 | 21 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1P | 5 | 34 | 600 | 3
FEF080169 | F | MSP | Fuji Electric | BM3VHB-032 | 50 | 24.0 - 32.0 | 480Y/277 | 3 | 65 | 480Y/277 | 3 | 20 | 27 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E1P | 5 | 34 | 600 | 3
FEF080170 | F | MSP | Fuji Electric | BM3VHB-040 | 50 | 28.0 - 40.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 30 | 40 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E2P | 5 | 40 | 600 | 3
FEF080171 | F | MSP | Fuji Electric | BM3VHB-050 | 50 | 35.0 - 50.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 30 | 40 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E2SP | 5 | 40 | 600 | 3
FEF080172 | F | MSP | Fuji Electric | BM3VHB-063 | 50 | 45.0 - 63.0 | 480Y/277 | 3 | 50 | 480Y/277 | 3 | 40 | 52 | 504 | 1, 4, 5 | E211710 Vol. 1 Sec. 2
|  | Short Circuit Alarm | Fuji Electric | BZ0TKUAB | - | - | - | -
|  | MC | Fuji Electric | SC-E3P | 5 | 65 | 600 | 3
Conditions of Acceptability:
|  | 1 | All of the specified individual components of the combination motor controller have been installed in an enclosure having
a specified internal volume in cubic inches. Additional testing of the combination motor controller is not required when
installed in an enclosure having the same or larger volume.
|  | 2 | When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from
the overcurrent protective devices and other components shall not be installed in this area.
|  | 3 | When specified, the overload relay heater table number shall be provided with the equipment.
|  | 4 | Unless otherwise specified, all connections between components are made with insulated wire having an ampacity of
125 percent of the rated motor current and connected to the terminals supplied with the individual components.
|  | 5 | The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor
controllers shall be considered in the end-product application.