## Cover sheet
Combination type | Original UL-Text
Type A | Type A combination motor controller consisting of a disconnect switch, fuses, motor controller and overload relay
Type C | Type C combination motor controller consisting of Inverse time circuit breaker, motor controller and overload relay
Type D | Type D combination motor controller consisting of instantaneous trip circuit breaker, motor controller and overload relay
Type E (self protected) | Type E (self-protected) combination motor controller consisting of manual self-protected combination motor controller and motor controller
Type F | Type F combination motor controller consisting of manual self-protected combination motor controller and motor controller
CB | Listed Inverse - time circuit breaker
DS | Listed or Recognized Disconnect switch or Listed Molded-case Switch
F | Listed Fuses
FH | Discrete Fuseholder
ICB | Recognized Instantaneous trip circuit breaker
MC | Listed or Recognized Motor Controller
MSP | Listed Manual Self-Protected combination motor controller
OLR | Listed or Recognized Overload Relay
HP | Horsepower rating for component, if provided
kA | marked short circuit current rating (SCCR) on individual component
Max Amps | Maximum ampere rating of individual component
V | voltage rating of individual component
kA | maximum short circuit current rating for combination motor controller
V | Maximum voltage rating for combination motor controller
Ph | number of phases for combination motor controller
HP or maximum amperes | Maximum horsepower or current at the corresponding voltage rating for combination motor controller
CA | Conditions of Acceptability specific for combination motor controller
CONDITIONS OF ACCEPTABILITY Unless specified otherwise in the individual Recognitions, consideration is to be given to the following Conditions of Acceptability when these components are employed as a combination motor controller in the end-use equipment: Specific Conditions of Use - Number refers to specific condition number as defined below and number in parenthesis identifies specific information applicable to the combination motor controller. 1. All of the specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume. 2. When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective devices and other components shall not be installed in this area. 3. When specified, the overload relay heater table number shall be provided with the equipment. 4. Unless otherwise specified, all connections between components are made with insulated wire having an ampacity of 125 percent of the rated motor current and connected to the terminals supplied with the individual components. 5. The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor controllers shall be considered in the end - product application. 6. Additional Conditions of Acceptability may be specified in the individual tables. 7. Type F Combination motor controllers feature pre-fabricated connector links between motor protector and contactor.
8. Units with suffix "/BBA" are mounted on busbar shoes for use in listed and/or recognized busbar systems for ICPs.

## D-FVNR ICB + Bimetal OLR
Issued: 2008-09-05
Last Revised: 2008-09-12
ID Number | Combination Type | Component Type | Component Manufactuer | Component Catalog Desgination | Component Ratings |  |  |  | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Motor FLC per NEC Table 430-250 | Minimum Enclosure Volume (cu in/ cu Ft) |  | Conditions of Acceptability | Combination UL File Reference
[5 empty] | kA | Max Amps | Volts | Poles
D-M-NZM+ZB 001 | D | ICB | Moeller | NZMB1-S2-CNA | - | 2 | 480Y/277V | 3 | 100 | 480Y/277V | 3 | 0.5 | 1.1 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 480 | 3
|  | OLR | Moeller | ZB32-1.6 | 5 | 1…1,6 | 480 | 3
D-M-NZM+ZB 002 | D | ICB | Moeller | NZMB1-S2-CNA | - | 2 | 480Y/277V | 3 | 100 | 480Y/277V | 3 | 0.75 | 1.6 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 480 | 3
|  | OLR | Moeller | ZB32-1.6 | 5 | 1…1,6 | 480 | 3
D-M-NZM+ZB 003 | D | ICB | Moeller | NZMB1-S3-CNA | - | 3 | 480Y/277V | 3 | 100 | 480Y/277V | 3 | 1 | 2.1 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 480 | 3
|  | OLR | Moeller | ZB32-2.4 | 5 | 1,6…2,4 | 480 | 3
D-M-NZM+ZB 004 | D | ICB | Moeller | NZMB1-S3-CNA | - | 3 | 240 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 240 | 3
|  | OLR | Moeller | ZB32-2.4 | 5 | 1,6…2,4 | 240 | 3
D-M-NZM+ZB 005 | D | ICB | Moeller | NZMB1-S3-CNA | - | 3 | 208 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 208 | 3
|  | OLR | Moeller | ZB32-2.4 | 5 | 1,6…2,4 | 208 | 3
D-M-NZM+ZB 006 | D | ICB | Moeller | NZMB1-S3-CNA | - | 3 | 200 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 200 | 3
|  | OLR | Moeller | ZB32-4 | 5 | 2,4…4 | 200 | 3
D-M-NZM+ZB 007 | D | ICB | Moeller | NZMB1-S5-CNA | - | 5 | 480Y/277V | 3 | 100 | 480Y/277V | 3 | 1.5 | 3 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 480 | 3
|  | OLR | Moeller | ZB32-4 | 5 | 2,4…4 | 480 | 3
D-M-NZM+ZB 008 | D | ICB | Moeller | NZMB1-S5-CNA | - | 5 | 240 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 240 | 3
|  | OLR | Moeller | ZB32-4 | 5 | 2,4…4 | 240 | 3
D-M-NZM+ZB 009 | D | ICB | Moeller | NZMB1-S5-CNA | - | 5 | 480Y/277V | 3 | 100 | 480Y/277V | 3 | 2 | 3.4 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 480 | 3
|  | OLR | Moeller | ZB32-4 | 5 | 2,4…4 | 480 | 3
D-M-NZM+ZB 010 | D | ICB | Moeller | NZMB1-S5-CNA | - | 5 | 208 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 208 | 3
|  | OLR | Moeller | ZB32-4 | 5 | 2,4…4 | 208 | 3
D-M-NZM+ZB 011 | D | ICB | Moeller | NZMB1-S5-CNA | - | 5 | 200 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 200 | 3
|  | OLR | Moeller | ZB32-4 | 5 | 2,4…4 | 200 | 3
D-M-NZM+ZB 012 | D | ICB | Moeller | NZMB1-S5-CNA | - | 5 | 240 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 240 | 3
|  | OLR | Moeller | ZB32-6 | 5 | 4…6 | 240 | 3
D-M-NZM+ZB 013 | D | ICB | Moeller | NZMB1-S8-CNA | - | 8 | 208 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 208 | 3
|  | OLR | Moeller | ZB32-6 | 5 | 4…6 | 208 | 3
D-M-NZM+ZB 014 | D | ICB | Moeller | NZMB1-S8-CNA | - | 8 | 200 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 200 | 3
|  | OLR | Moeller | ZB32-6 | 5 | 4…6 | 200 | 3
D-M-NZM+ZB 015 | D | ICB | Moeller | NZMB1-S8-CNA | - | 8 | 480Y/277V | 3 | 100 | 480Y/277V | 3 | 3 | 4.8 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 480 | 3
|  | OLR | Moeller | ZB32-6 | 5 | 4…6 | 480 | 3
D-M-NZM+ZB 016 | D | ICB | Moeller | NZMB1-S8-CNA | - | 8 | 240 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 240 | 3
|  | OLR | Moeller | ZB32-6 | 5 | 4…6 | 240 | 3
D-M-NZM+ZB 017 | D | ICB | Moeller | NZMB1-S8-CNA | - | 8 | 208 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 208 | 3
|  | OLR | Moeller | ZB32-10 | 5 | 6…10 | 208 | 3
D-M-NZM+ZB 018 | D | ICB | Moeller | NZMB1-S8-CNA | - | 8 | 240 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 240 | 3
|  | OLR | Moeller | ZB32-10 | 5 | 6…10 | 240 | 3
D-M-NZM+ZB 019 | D | ICB | Moeller | NZMB1-S8-CNA | - | 8 | 200 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 200 | 3
|  | OLR | Moeller | ZB32-10 | 5 | 6…10 | 200 | 3
D-M-NZM+ZB 020 | D | ICB | Moeller | NZMB1-S12-CNA | - | 12 | 208 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 208 | 3
|  | OLR | Moeller | ZB32-10 | 5 | 6…10 | 208 | 3
D-M-NZM+ZB 021 | D | ICB | Moeller | NZMB1-S12-CNA | - | 12 | 480Y/277V | 3 | 100 | 480Y/277V | 3 | 5 | 7.6 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 480 | 3
|  | OLR | Moeller | ZB32-10 | 5 | 6…10 | 480 | 3
D-M-NZM+ZB 022 | D | ICB | Moeller | NZMB1-S12-CNA | - | 12 | 200 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 200 | 3
|  | OLR | Moeller | ZB32-10 | 5 | 6…10 | 200 | 3
D-M-NZM+ZB 023 | D | ICB | Moeller | NZMB1-S12-CNA | - | 12 | 240 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 240 | 3
|  | OLR | Moeller | ZB32-10 | 5 | 6…10 | 240 | 3
D-M-NZM+ZB 024 | D | ICB | Moeller | NZMB1-S18-CNA | - | 18 | 208 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 208 | 3
|  | OLR | Moeller | ZB32-16 | 5 | 10…16 | 208 | 3
D-M-NZM+ZB 025 | D | ICB | Moeller | NZMB1-S18-CNA | - | 18 | 200 | 3 | 100 | 200 | 3 | 3 | 11 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 200 | 3
|  | OLR | Moeller | ZB32-16 | 5 | 10…16 | 200 | 3
D-M-NZM+ZB 026 | D | ICB | Moeller | NZMB1-S18-CNA | - | 18 | 480Y/277V | 3 | 100 | 480Y/277V | 3 | 7.5 | 11 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 480 | 3
|  | OLR | Moeller | ZB32-16 | 5 | 10…16 | 480 | 3
D-M-NZM+ZB 027 | D | ICB | Moeller | NZMB1-S18-CNA | - | 18 | 480Y/277V | 3 | 100 | 480Y/277V | 3 | 10 | 14 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 480 | 3
|  | OLR | Moeller | ZB32-16 | 5 | 10…16 | 480 | 3
D-M-NZM+ZB 028 | D | ICB | Moeller | NZMB1-S18-CNA | - | 18 | 240 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 240 | 3
|  | OLR | Moeller | ZB32-16 | 5 | 10…16 | 240 | 3
D-M-NZM+ZB 029 | D | ICB | Moeller | NZMB1-S26-CNA | - | 26 | 208 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 208 | 3
|  | OLR | Moeller | ZB32-24 | 5 | 16…24 | 208 | 3
D-M-NZM+ZB 030 | D | ICB | Moeller | NZMB1-S26-CNA | - | 26 | 200 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 200 | 3
|  | OLR | Moeller | ZB32-24 | 5 | 16…24 | 200 | 3
D-M-NZM+ZB 031 | D | ICB | Moeller | NZMB1-S26-CNA | - | 26 | 480Y/277V | 3 | 100 | 480Y/277V | 3 | 15 | 21 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM25-10 | 5 | 35 | 480 | 3
|  | OLR | Moeller | ZB32-24 | 5 | 16…24 | 480 | 3
D-M-NZM+ZB 032 | D | ICB | Moeller | NZMB1-S26-CNA | - | 26 | 240 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM25-10 | 5 | 35 | 240 | 3
|  | OLR | Moeller | ZB32-24 | 5 | 16…24 | 240 | 3
D-M-NZM+ZB 033 | D | ICB | Moeller | NZMB1-S33-CNA | - | 33 | 208 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM25-10 | 5 | 35 | 208 | 3
|  | OLR | Moeller | ZB32-24 | 5 | 16…24 | 208 | 3
D-M-NZM+ZB 034 | D | ICB | Moeller | NZMB1-S33-CNA | - | 33 | 200 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM25-10 | 5 | 35 | 200 | 3
|  | OLR | Moeller | ZB32-32 | 5 | 24…32 | 200 | 3
D-M-NZM+ZB 035 | D | ICB | Moeller | NZMB1-S33-CNA | - | 33 | 480Y/277V | 3 | 100 | 480Y/277V | 3 | 20 | 27 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM32-10 | 5 | 40 | 480 | 3
|  | OLR | Moeller | ZB32-32 | 5 | 24…32 | 480 | 3
D-M-NZM+ZB 036 | D | ICB | Moeller | NZMB1-S33-CNA | - | 33 | 240 | 3 | 100 | 240 | 3 | 10 | 28 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM32-10 | 5 | 40 | 240 | 3
|  | OLR | Moeller | ZB32-32 | 5 | 24…32 | 240 | 3
D-M-NZM+ZB 037 | D | ICB | Moeller | NZMB1-S40-CNA | - | 40 | 208 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM32-10 | 5 | 40 | 208 | 3
|  | OLR | Moeller | ZB32-32 | 5 | 24…32 | 208 | 3
D-M-NZM+ZB 038 | D | ICB | Moeller | NZMB1-S40-CNA | - | 40 | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1002.24 | 0.58 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM32-10 | 5 | 40 | 200 | 3
|  | OLR | Moeller | ZB32-32 | 5 | 24…32 | 200 | 3
D-M-NZM+ZB 039 | D | ICB | Moeller | NZMB1-S40-CNA | - | 40 | 480Y/277V | 3 | 100 | 480Y/277V | 3 | 25 | 34 | 1335.744 | 0.773 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM40 | 10 | 55 | 480 | 3
|  | OLR | Moeller | ZB65-40 | 5 | 24…40 | 480 | 3
D-M-NZM+ZB 040 | D | ICB | Moeller | NZMB1-S50-CNA | - | 50 | 480Y/277V | 3 | 100 | 480Y/277V | 3 | 30 | 40 | 1335.744 | 0.773 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM40 | 10 | 55 | 480 | 3
|  | OLR | Moeller | ZB65-40 | 5 | 24…40 | 480 | 3
D-M-NZM+ZB 041 | D | ICB | Moeller | NZMB1-S50-CNA | - | 50 | 240 | 3 | 100 | 240 | 3 | 15 | 42 | 1335.6877 | 0.77297 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM40 | 10 | 55 | 240 | 3
|  | OLR | Moeller | ZB65-57 | 10 | 40…57 | 240 | 3
D-M-NZM+ZB 042 | D | ICB | Moeller | NZMB2-S1.6-CNA | - | 1.6 | 600 | 3 | 50 | 600 | 3 | 0.5 | 0.9 | 1335.6877 | 0.77297 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 600 | 3
|  | OLR | Moeller | ZB32-1.0 | 5 | 0,6…1 | 600 | 3
D-M-NZM+ZB 043 | D | ICB | Moeller | NZMB2-S1.6-CNA | - | 1.6 | 600 | 3 | 50 | 600 | 3 | 0.75 | 1.3 | 1335.6877 | 0.77297 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 600 | 3
|  | OLR | Moeller | ZB32-1.6 | 5 | 1…1,6 | 600 | 3
D-M-NZM+ZB 044 | D | ICB | Moeller | NZMB2-S2.4-CNA | - | 2.4 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 1335.6877 | 0.77297 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 600 | 3
|  | OLR | Moeller | ZB32-2.4 | 5 | 1,6…2,4 | 600 | 3
D-M-NZM+ZB 045 | D | ICB | Moeller | NZMB2-S5-CNA | - | 5 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 1335.6877 | 0.77297 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 600 | 3
|  | OLR | Moeller | ZB32-2.4 | 5 | 1,6…2,4 | 600 | 3
D-M-NZM+ZB 046 | D | ICB | Moeller | NZMB2-S5-CNA | - | 5 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 1335.6877 | 0.77297 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 600 | 3
|  | OLR | Moeller | ZB32-4 | 5 | 2,4…4 | 600 | 3
D-M-NZM+ZB 047 | D | ICB | Moeller | NZMB2-S5-CNA | - | 5 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 1335.6877 | 0.77297 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 600 | 3
|  | OLR | Moeller | ZB32-4 | 5 | 2,4…4 | 600 | 3
D-M-NZM+ZB 048 | D | ICB | Moeller | NZMB2-S8-CNA | - | 8 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 1335.6877 | 0.77297 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 600 | 3
|  | OLR | Moeller | ZB32-10 | 5 | 6…10 | 600 | 3
D-M-NZM+ZB 049 | D | ICB | Moeller | NZMB2-S12-CNA | - | 12 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1335.6877 | 0.77297 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 600 | 3
|  | OLR | Moeller | ZB32-10 | 5 | 6…10 | 600 | 3
D-M-NZM+ZB 050 | D | ICB | Moeller | NZMB2-S18-CNA | - | 18 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1335.6877 | 0.77297 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 600 | 3
|  | OLR | Moeller | ZB32-16 | 5 | 10…16 | 600 | 3
D-M-NZM+ZB 051 | D | ICB | Moeller | NZMB2-S26-CNA | - | 26 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1335.6877 | 0.77297 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 600 | 3
|  | OLR | Moeller | ZB32-24 | 5 | 16…24 | 600 | 3
D-M-NZM+ZB 052 | D | ICB | Moeller | NZMB2-S26-CNA | - | 26 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1335.6877 | 0.77297 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM25-10 | 5 | 35 | 600 | 3
|  | OLR | Moeller | ZB32-24 | 5 | 16…24 | 600 | 3
D-M-NZM+ZB 053 | D | ICB | Moeller | NZMB2-S33-CNA | - | 33 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1335.6877 | 0.77297 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM32-10 | 5 | 40 | 600 | 3
|  | OLR | Moeller | ZB32-32 | 5 | 24…32 | 600 | 3
D-M-NZM+ZB 054 | D | ICB | Moeller | NZMB2-S40-CNA | - | 40 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 1335.6877 | 0.77297 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM40 | 10 | 55 | 600 | 3
|  | OLR | Moeller | ZB65-40 | 5 | 24…40 | 600 | 3
D-M-NZM+ZB 055 | D | ICB | Moeller | NZMB2-S50-CNA | - | 50 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 1335.6877 | 0.77297 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM40 | 10 | 55 | 600 | 3
|  | OLR | Moeller | ZB65-57 | 10 | 40…57 | 600 | 3
D-M-NZM+ZB 056 | D | ICB | Moeller | NZMB2-S63-CNA | - | 63 | 208 | 3 | 100 | 208 | 3 | 15 | 46.2 | 1335.6877 | 0.77297 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM50 | 10 | 65 | 208 | 3
|  | OLR | Moeller | ZB65-57 | 10 | 40…57 | 208 | 3
D-M-NZM+ZB 057 | D | ICB | Moeller | NZMB2-S63-CNA | - | 63 | 200 | 3 | 100 | 200 | 3 | 15 | 48.3 | 1335.6877 | 0.77297 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM50 | 10 | 65 | 200 | 3
|  | OLR | Moeller | ZB65-57 | 10 | 40…57 | 200 | 3
D-M-NZM+ZB 058 | D | ICB | Moeller | NZMB2-S63-CNA | - | 63 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 1335.6877 | 0.77297 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM50 | 10 | 65 | 600 | 3
|  | OLR | Moeller | ZB65-57 | 10 | 40…57 | 600 | 3
D-M-NZM+ZB 059 | D | ICB | Moeller | NZMB2-S63-CNA | - | 63 | 480 | 3 | 100 | 480 | 3 | 40 | 52 | 1335.6877 | 0.77297 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM50 | 10 | 65 | 480 | 3
|  | OLR | Moeller | ZB65-57 | 10 | 40…57 | 480 | 3
D-M-NZM+ZB 060 | D | ICB | Moeller | NZMB2-S63-CNA | - | 63 | 240 | 3 | 100 | 240 | 3 | 20 | 54 | 1335.6877 | 0.77297 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM50 | 10 | 65 | 240 | 3
|  | OLR | Moeller | ZB65-57 | 10 | 40…57 | 240 | 3
D-M-NZM+ZB 061 | D | ICB | Moeller | NZMB2-S80-CNA | - | 80 | 208 | 3 | 100 | 208 | 3 | 20 | 59.4 | 1335.6877 | 0.77297 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM65 | 10 | 80 | 208 | 3
|  | OLR | Moeller | ZB65-65 | 10 | 50…65 | 208 | 3
D-M-NZM+ZB 062 | D | ICB | Moeller | NZMB2-S80-CNA | - | 80 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 1335.6877 | 0.77297 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM65 | 10 | 80 | 600 | 3
|  | OLR | Moeller | ZB65-65 | 10 | 50..65 | 600 | 3
D-M-NZM+ZB 063 | D | ICB | Moeller | NZMB2-S80-CNA | - | 80 | 200 | 3 | 100 | 200 | 3 | 20 | 62.1 | 1335.6877 | 0.77297 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM65 | 10 | 80 | 200 | 3
|  | OLR | Moeller | ZB65-65 | 10 | 50…65 | 200 | 3
D-M-NZM+ZB 064 | D | ICB | Moeller | NZMB2-S80-CNA | - | 80 | 480 | 3 | 100 | 480 | 3 | 50 | 65 | 1335.744 | 0.773 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM65 | 10 | 80 | 480 | 3
|  | OLR | Moeller | ZB65-65 | 10 | 50..65 | 480 | 3
D-M-NZM+ZB 065 | D | ICB | Moeller | NZMB2-S80-CNA | - | 80 | 240 | 3 | 100 | 240 | 3 | 25 | 68 | 2671.3754 | 1.5459 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM80 | 10 | 125 | 240 | 3
|  | OLR | Moeller | ZB150-70 | 10 | 50…70 | 240 | 3
D-M-NZM+ZB 066 | D | ICB | Moeller | NZMB2-S100-CNA | - | 100 | 208 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2671.3754 | 1.5459 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM80 | 10 | 125 | 208 | 3
|  | OLR | Moeller | ZB150-100 | 10 | 70…100 | 208 | 3
D-M-NZM+ZB 067 | D | ICB | Moeller | NZMB2-S100-CNA | - | 100 | 480 | 3 | 100 | 480 | 3 | 60 | 77 | 2671.488 | 1.546 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM80 | 10 | 125 | 480 | 3
|  | OLR | Moeller | ZB150-100 | 10 | 70…100 | 480 | 3
D-M-NZM+ZB 068 | D | ICB | Moeller | NZMB2-S100-CNA | - | 100 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 2671.488 | 1.546 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM80 | 10 | 125 | 600 | 3
|  | OLR | Moeller | ZB150-100 | 10 | 70…100 | 600 | 3
D-M-NZM+ZB 069 | D | ICB | Moeller | NZMB2-S100-CNA | - | 100 | 200 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2671.3754 | 1.5459 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM80 | 10 | 125 | 200 | 3
|  | OLR | Moeller | ZB150-100 | 10 | 70…100 | 200 | 3
D-M-NZM+ZB 070 | D | ICB | Moeller | NZMB2-S100-CNA | - | 100 | 240 | 3 | 100 | 240 | 3 | 30 | 80 | 2671.3754 | 1.5459 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM80 | 10 | 125 | 240 | 3
|  | OLR | Moeller | ZB150-100 | 10 | 70…100 | 240 | 3
D-M-NZM+ZB 071 | D | ICB | Moeller | NZMB2-S125-CNA | - | 125 | 208 | 3 | 100 | 208 | 3 | 30 | 88 | 2671.3754 | 1.5459 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM115 | 10 | 160 | 208 | 3
|  | OLR | Moeller | ZB150-100 | 10 | 70…100 | 208 | 3
D-M-NZM+ZB 072 | D | ICB | Moeller | NZMB2-S125-CNA | - | 125 | 200 | 3 | 100 | 200 | 3 | 30 | 92 | 2671.3754 | 1.5459 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM115 | 10 | 160 | 200 | 3
|  | OLR | Moeller | ZB150-100 | 10 | 70…100 | 200 | 3
D-M-NZM+ZB 073 | D | ICB | Moeller | NZMB2-S125-CNA | - | 125 | 480 | 3 | 100 | 480 | 3 | 75 | 96 | 2671.488 | 1.546 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM95 | 10 | 125 | 480 | 3
|  | OLR | Moeller | ZB150-100 | 10 | 70…100 | 480 | 3
D-M-NZM+ZB 074 | D | ICB | Moeller | NZMB2-S125-CNA | - | 125 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 2671.488 | 1.546 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM95 | 10 | 125 | 600 | 3
|  | OLR | Moeller | ZB150-100 | 10 | 70…100 | 600 | 3
D-M-NZM+ZB 075 | D | ICB | Moeller | NZMB2-S125-CNA | - | 125 | 240 | 3 | 100 | 240 | 3 | 40 | 104 | 2671.3754 | 1.5459 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM95 | 10 | 125 | 240 | 3
|  | OLR | Moeller | ZB150-125 | 10 | 95…125 | 240 | 3
D-M-NZM+ZB 076 | D | ICB | Moeller | NZMB2-S160-CNA | - | 160 | 208 | 3 | 100 | 208 | 3 | 40 | 114 | 2671.3754 | 1.5459 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM115 | 10 | 160 | 208 | 3
|  | OLR | Moeller | ZB150-125 | 10 | 95…125 | 208 | 3
D-M-NZM+ZB 077 | D | ICB | Moeller | NZMB2-S160-CNA | - | 160 | 200 | 3 | 100 | 200 | 3 | 40 | 120 | 2671.3754 | 1.5459 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM115 | 10 | 160 | 200 | 3
|  | OLR | Moeller | ZB150-125 | 10 | 95…125 | 200 | 3
D-M-NZM+ZB 078 | D | ICB | Moeller | NZMB2-S160-CNA | - | 160 | 480 | 3 | 100 | 480 | 3 | 100 | 124 | 2671.488 | 1.546 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM115 | 10 | 160 | 480 | 3
|  | OLR | Moeller | ZB150-125 | 10 | 95…125 | 480 | 3
D-M-NZM+ZB 079 | D | ICB | Moeller | NZMB2-S160-CNA | - | 160 | 600 | 3 | 50 | 600 | 3 | 125 | 125 | 2671.488 | 1.546 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM115 | 10 | 160 | 600 | 3
|  | OLR | Moeller | ZB150-125 | 10 | 95…125 | 600 | 3
D-M-NZM+ZB 080 | D | ICB | Moeller | NZMB2-S160-CNA | - | 160 | 240 | 3 | 100 | 240 | 3 | 50 | 130 | 2671.3754 | 1.5459 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM115 | 10 | 160 | 240 | 3
|  | OLR | Moeller | ZB150-150 | 10 | 120…150 | 240 | 3
D-M-NZM+ZB 081 | D | ICB | Moeller | NZMB2-S200-CNA | - | 200 | 208 | 3 | 100 | 208 | 3 | 50 | 143 | 4340.9851 | 2.5121 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM185/22 | 18 | 225 | 208 | 3
|  | OLR | Moeller | Z5-160/FF250 | 10 | 120…160 | 208 | 3
D-M-NZM+ZB 082 | D | ICB | Moeller | NZMB2-S200-CNA | - | 200 | 600 | 3 | 50 | 600 | 3 | 150 | 144 | 4340.736 | 2.512 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM185/22 | 18 | 225 | 600 | 3
|  | OLR | Moeller | Z5-160/FF250 | 10 | 120…160 | 600 | 3
D-M-NZM+ZB 083 | D | ICB | Moeller | NZMB2-S200-CNA | - | 200 | 200 | 3 | 100 | 200 | 3 | 50 | 150 | 4340.9851 | 2.5121 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM185/22 | 18 | 225 | 200 | 3
|  | OLR | Moeller | Z5-160/FF250 | 10 | 120…160 | 200 | 3
D-M-NZM+ZB 084 | D | ICB | Moeller | NZMB2-S200-CNA | - | 200 | 240 | 3 | 100 | 240 | 3 | 60 | 154 | 4340.9851 | 2.5121 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM185/22 | 18 | 225 | 240 | 3
|  | OLR | Moeller | Z5-160/FF250 | 10 | 120…160 | 240 | 3
D-M-NZM+ZB 086 | D | ICB | Moeller | NZMB2-S200-CNA | - | 200 | 208 | 3 | 100 | 208 | 3 | 60 | 169 | 4340.9851 | 2.5121 | 1 , 5 | E51580 V1 S29
|  | MC | Moeller | DILM225/22 | 18 | 225 | 208 | 3
|  | OLR | Moeller | Z5-220/FF250 | 10 | 160…220 | 208 | 3

## D-FVNR ICB + SS OLR
Issued: 2008-09-05
Last Revised: 2008-09-12
ID Number | Combination Type | Component Type | Component Manufactuer | Component Catalog Desgination | Component Ratings |  |  |  | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Motor FLC per NEC Table 430-250 | Minimum Enclosure Volume (cu in/ cu Ft) |  | Conditions of Acceptability | Combination UL File Reference
[5 empty] | kA | Max Amps | Volts | Poles
D-M-NZM+ZEV 001 | D | ICB | Moeller | NZMB2-S1.6-CNA | - | 1.6 | 600 | 3 | 50 | 600 | 3 | 0.5 | 0.9 | 1335.744 | 0.773 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-25 | 5 | 1…25 | 600 | 3
D-M-NZM+ZEV 002 | D | ICB | Moeller | NZMB2-S1.6-CNA | - | 1.6 | 600 | 3 | 50 | 600 | 3 | 0.75 | 1.3 | 1335.744 | 0.773 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-25 | 5 | 1…25 | 600 | 3
D-M-NZM+ZEV 003 | D | ICB | Moeller | NZMB2-S2.4-CNA | - | 2.4 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 1335.744 | 0.773 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-25 | 5 | 1…25 | 600 | 3
D-M-NZM+ZEV 004 | D | ICB | Moeller | NZMB2-S5-CNA | - | 5 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 1335.744 | 0.773 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-25 | 5 | 1…25 | 600 | 3
D-M-NZM+ZEV 005 | D | ICB | Moeller | NZMB2-S5-CNA | - | 5 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 1335.744 | 0.773 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-25 | 5 | 1…25 | 600 | 3
D-M-NZM+ZEV 006 | D | ICB | Moeller | NZMB2-S5-CNA | - | 5 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 1335.744 | 0.773 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-25 | 5 | 1…25 | 600 | 3
D-M-NZM+ZEV 007 | D | ICB | Moeller | NZMB2-S8-CNA | - | 8 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 1335.744 | 0.773 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-25 | 5 | 1…25 | 600 | 3
D-M-NZM+ZEV 008 | D | ICB | Moeller | NZMB2-S12-CNA | - | 12 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1335.744 | 0.773 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-25 | 5 | 1…25 | 600 | 3
D-M-NZM+ZEV 009 | D | ICB | Moeller | NZMB2-S18-CNA | - | 18 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1335.744 | 0.773 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-25 | 5 | 1…25 | 600 | 3
D-M-NZM+ZEV 010 | D | ICB | Moeller | NZMB2-S26-CNA | - | 26 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1335.744 | 0.773 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM17-10 | 5 | 35 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-25 | 5 | 1…25 | 600 | 3
D-M-NZM+ZEV 011 | D | ICB | Moeller | NZMB2-S26-CNA | - | 26 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1335.744 | 0.773 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM25-10 | 5 | 35 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-25 | 5 | 1…25 | 600 | 3
D-M-NZM+ZEV 012 | D | ICB | Moeller | NZMB2-S33-CNA | - | 33 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1335.744 | 0.773 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM32-10 | 5 | 40 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 600 | 3
D-M-NZM+ZEV 013 | D | ICB | Moeller | NZMB2-S40-CNA | - | 40 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 1335.744 | 0.773 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM40 | 10 | 55 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 600 | 3
D-M-NZM+ZEV 014 | D | ICB | Moeller | NZMB2-S50-CNA | - | 50 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 1335.744 | 0.773 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM40 | 10 | 55 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 600 | 3
D-M-NZM+ZEV 015 | D | ICB | Moeller | NZMB2-S63-CNA | - | 63 | 208 | 3 | 100 | 208 | 3 | 15 | 46.2 | 1335.744 | 0.773 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM50 | 10 | 65 | 208 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 208 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 208 | 3
D-M-NZM+ZEV 016 | D | ICB | Moeller | NZMB2-S63-CNA | - | 63 | 200 | 3 | 100 | 200 | 3 | 15 | 48.3 | 1335.744 | 0.773 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM50 | 10 | 65 | 200 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 200 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 200 | 3
D-M-NZM+ZEV 017 | D | ICB | Moeller | NZMB2-S63-CNA | - | 63 | 480 | 3 | 100 | 480 | 3 | 40 | 52 | 1335.744 | 0.773 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM50 | 10 | 65 | 480 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 480 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 480 | 3
D-M-NZM+ZEV 018 | D | ICB | Moeller | NZMB2-S63-CNA | - | 63 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 1335.744 | 0.773 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM50 | 10 | 65 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 600 | 3
D-M-NZM+ZEV 019 | D | ICB | Moeller | NZMB2-S63-CNA | - | 63 | 240 | 3 | 100 | 240 | 3 | 20 | 54 | 1335.744 | 0.773 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM50 | 10 | 65 | 240 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 240 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 240 | 3
D-M-NZM+ZEV 020 | D | ICB | Moeller | NZMB2-S80-CNA | - | 80 | 208 | 3 | 100 | 208 | 3 | 20 | 59.4 | 1335.744 | 0.773 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM65 | 10 | 80 | 208 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 208 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 208 | 3
D-M-NZM+ZEV 021 | D | ICB | Moeller | NZMB2-S80-CNA | - | 80 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 1335.744 | 0.773 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM65 | 10 | 80 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 600 | 3
D-M-NZM+ZEV 022 | D | ICB | Moeller | NZMB2-S80-CNA | - | 80 | 200 | 3 | 100 | 200 | 3 | 20 | 62.1 | 1335.744 | 0.773 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM65 | 10 | 80 | 200 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 200 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 200 | 3
D-M-NZM+ZEV 023 | D | ICB | Moeller | NZMB2-S80-CNA | - | 80 | 480 | 3 | 100 | 480 | 3 | 50 | 65 | 1335.744 | 0.773 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM65 | 10 | 80 | 480 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 480 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 480 | 3
D-M-NZM+ZEV 024 | D | ICB | Moeller | NZMB2-S80-CNA | - | 80 | 240 | 3 | 100 | 240 | 3 | 25 | 68 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM80 | 10 | 125 | 240 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 240 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 240 | 3
D-M-NZM+ZEV 025 | D | ICB | Moeller | NZMB2-S100-CNA | - | 100 | 208 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2672.3754 | 1.5465 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM80 | 10 | 125 | 208 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 208 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 208 | 3
D-M-NZM+ZEV 026 | D | ICB | Moeller | NZMB2-S100-CNA | - | 100 | 480 | 3 | 100 | 480 | 3 | 60 | 77 | 2671.488 | 1.546 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM80 | 10 | 125 | 480 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 480 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 480 | 3
D-M-NZM+ZEV 027 | D | ICB | Moeller | NZMB2-S100-CNA | - | 100 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 2671.488 | 1.546 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM80 | 10 | 125 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 600 | 3
D-M-NZM+ZEV 028 | D | ICB | Moeller | NZMB2-S100-CNA | - | 100 | 200 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2673.3754 | 1.5471 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM80 | 10 | 125 | 200 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 200 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 200 | 3
D-M-NZM+ZEV 029 | D | ICB | Moeller | NZMB2-S100-CNA | - | 100 | 240 | 3 | 100 | 240 | 3 | 30 | 80 | 2674.3754 | 1.5477 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM80 | 10 | 125 | 240 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 240 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 240 | 3
D-M-NZM+ZEV 030 | D | ICB | Moeller | NZMB2-S125-CNA | - | 125 | 208 | 3 | 100 | 208 | 3 | 30 | 88 | 2675.3754 | 1.5482 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM115 | 10 | 160 | 208 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 208 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 208 | 3
D-M-NZM+ZEV 031 | D | ICB | Moeller | NZMB2-S125-CNA | - | 125 | 200 | 3 | 100 | 200 | 3 | 30 | 92 | 2676.3754 | 1.5488 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM115 | 10 | 160 | 200 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 200 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 200 | 3
D-M-NZM+ZEV 032 | D | ICB | Moeller | NZMB2-S125-CNA | - | 125 | 480 | 3 | 100 | 480 | 3 | 75 | 96 | 2671.488 | 1.546 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM95 | 10 | 125 | 480 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 480 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 480 | 3
D-M-NZM+ZEV 033 | D | ICB | Moeller | NZMB2-S125-CNA | - | 125 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 2671.488 | 1.546 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM95 | 10 | 125 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 600 | 3
D-M-NZM+ZEV 034 | D | ICB | Moeller | NZMB2-S125-CNA | - | 125 | 240 | 3 | 100 | 240 | 3 | 40 | 104 | 2677.3754 | 1.5494 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM95 | 10 | 125 | 240 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 240 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 240 | 3
D-M-NZM+ZEV 035 | D | ICB | Moeller | NZMB2-S160-CNA | - | 160 | 208 | 3 | 100 | 208 | 3 | 40 | 114 | 2678.3754 | 1.55 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM115 | 10 | 160 | 208 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 208 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 208 | 3
D-M-NZM+ZEV 036 | D | ICB | Moeller | NZMB2-S160-CNA | - | 160 | 200 | 3 | 100 | 200 | 3 | 40 | 120 | 2679.3754 | 1.5506 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM115 | 10 | 160 | 200 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 200 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 200 | 3
D-M-NZM+ZEV 037 | D | ICB | Moeller | NZMB2-S160-CNA | - | 160 | 480 | 3 | 100 | 480 | 3 | 100 | 124 | 2671.488 | 1.546 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM115 | 10 | 160 | 480 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 480 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 480 | 3
D-M-NZM+ZEV 038 | D | ICB | Moeller | NZMB2-S160-CNA | - | 160 | 600 | 3 | 50 | 600 | 3 | 125 | 125 | 2671.488 | 1.546 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM115 | 10 | 160 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 600 | 3
D-M-NZM+ZEV 039 | D | ICB | Moeller | NZMB2-S160-CNA | - | 160 | 240 | 3 | 100 | 240 | 3 | 50 | 130 | 2680.3754 | 1.5511 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM115 | 10 | 160 | 240 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 240 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 240 | 3
D-M-NZM+ZEV 040 | D | ICB | Moeller | NZMB2-S200-CNA | - | 200 | 208 | 3 | 100 | 208 | 3 | 50 | 143 | 4340.9851 | 2.5121 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM185/22 | 18 | 225 | 208 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 208 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 208 | 3
D-M-NZM+ZEV 041 | D | ICB | Moeller | NZMB2-S200-CNA | - | 200 | 600 | 3 | 50 | 600 | 3 | 150 | 144 | 4340.736 | 2.512 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM185/22 | 18 | 225 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 600 | 3
D-M-NZM+ZEV 042 | D | ICB | Moeller | NZMB2-S200-CNA | - | 200 | 200 | 3 | 100 | 200 | 3 | 50 | 150 | 4341.9851 | 2.5127 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM185/22 | 18 | 225 | 200 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 200 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 200 | 3
D-M-NZM+ZEV 043 | D | ICB | Moeller | NZMB2-S200-CNA | - | 200 | 240 | 3 | 100 | 240 | 3 | 60 | 154 | 4342.9851 | 2.5133 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM185/22 | 18 | 225 | 240 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 240 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 240 | 3
D-M-NZM+ZEV 044 | D | ICB | Moeller | NZMB2-S200-CNA | - | 200 | 480 | 3 | 100 | 480 | 3 | 125 | 156 | 4007.232 | 2.319 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM150 | 10 | 160 | 480 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 480 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 480 | 3
D-M-NZM+ZEV 045 | D | ICB | Moeller | NZMB2-S200-CNA | - | 200 | 208 | 3 | 100 | 208 | 3 | 60 | 169 | 4343.9851 | 2.5139 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM225/22 | 18 | 250 | 208 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 208 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 208 | 3

## D-FVNR SSTrip ICB + Bimetal OLR
Issued: 2008-09-05
Last Revised: 2008-09-12
ID Number | Combination Type | Component Type | Component Manufactuer | Component Catalog Desgination | Component Ratings |  |  |  | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Motor FLC per NEC Table 430-250 | Minimum Enclosure Volume (cu in.) |  | Conditions of Acceptability | Combination UL File Reference
[5 empty] | kA | Max Amps | Volts | Poles
D-M-NZM-SE+ZB 018 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 208 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM25-10 | 5 | 35 | 208 | 3
|  | OLR | Moeller | ZB32-24 | 5 | 16…24 | 208 | 3
D-M-NZM-SE+ZB 019 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 200 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM25-10 | 5 | 35 | 200 | 3
|  | OLR | Moeller | ZB32-32 | 5 | 24…32 | 200 | 3
D-M-NZM-SE+ZB 020 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM32-10 | 5 | 40 | 600 | 3
|  | OLR | Moeller | ZB32-32 | 5 | 24…32 | 600 | 3
D-M-NZM-SE+ZB 021 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 480 | 3 | 100 | 480 | 3 | 20 | 27 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM32-10 | 5 | 40 | 480 | 3
|  | OLR | Moeller | ZB32-32 | 5 | 24…32 | 480 | 3
D-M-NZM-SE+ZB 022 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 240 | 3 | 100 | 240 | 3 | 10 | 28 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM32-10 | 5 | 40 | 240 | 3
|  | OLR | Moeller | ZB32-32 | 5 | 24…32 | 240 | 3
D-M-NZM-SE+ZB 023 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 208 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM32-10 | 5 | 40 | 208 | 3
|  | OLR | Moeller | ZB32-32 | 5 | 24…32 | 208 | 3
D-M-NZM-SE+ZB 024 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM40 | 10 | 55 | 600 | 3
|  | OLR | Moeller | ZB65-40 | 5 | 24…40 | 600 | 3
D-M-NZM-SE+ZB 025 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM32-10 | 5 | 40 | 200 | 3
|  | OLR | Moeller | ZB32-32 | 5 | 24…32 | 200 | 3
D-M-NZM-SE+ZB 026 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 480 | 3 | 100 | 480 | 3 | 25 | 34 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM40 | 10 | 55 | 480 | 3
|  | OLR | Moeller | ZB65-40 | 5 | 24…40 | 480 | 3
D-M-NZM-SE+ZB 027 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 480 | 3 | 100 | 480 | 3 | 30 | 40 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM40 | 10 | 55 | 480 | 3
|  | OLR | Moeller | ZB65-40 | 5 | 24…40 | 480 | 3
D-M-NZM-SE+ZB 028 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM40 | 10 | 55 | 600 | 3
|  | OLR | Moeller | ZB65-57 | 10 | 40…57 | 600 | 3
D-M-NZM-SE+ZB 029 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 240 | 3 | 100 | 240 | 3 | 15 | 42 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM40 | 10 | 55 | 240 | 3
|  | OLR | Moeller | ZB65-57 | 10 | 40…57 | 240 | 3
D-M-NZM-SE+ZB 030 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 208 | 3 | 100 | 208 | 3 | 15 | 46.2 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM50 | 10 | 65 | 208 | 3
|  | OLR | Moeller | ZB65-57 | 10 | 40…57 | 208 | 3
D-M-NZM-SE+ZB 031 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 200 | 3 | 100 | 200 | 3 | 15 | 48.3 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM50 | 10 | 65 | 200 | 3
|  | OLR | Moeller | ZB65-57 | 10 | 40…57 | 200 | 3
D-M-NZM-SE+ZB 032 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 480 | 3 | 100 | 480 | 3 | 40 | 52 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM50 | 10 | 65 | 480 | 3
|  | OLR | Moeller | ZB65-57 | 10 | 40…57 | 480 | 3
D-M-NZM-SE+ZB 033 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM50 | 10 | 65 | 600 | 3
|  | OLR | Moeller | ZB65-57 | 10 | 40…57 | 600 | 3
D-M-NZM-SE+ZB 034 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 240 | 3 | 100 | 240 | 3 | 20 | 54 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM50 | 10 | 65 | 240 | 3
|  | OLR | Moeller | ZB65-57 | 10 | 40…57 | 240 | 3
D-M-NZM-SE+ZB 035 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 208 | 3 | 100 | 208 | 3 | 20 | 59.4 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM65 | 10 | 80 | 208 | 3
|  | OLR | Moeller | ZB65-65 | 10 | 50…65 | 208 | 3
D-M-NZM-SE+ZB 036 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM65 | 10 | 80 | 600 | 3
|  | OLR | Moeller | ZB65-65 | 10 | 50…65 | 600 | 3
D-M-NZM-SE+ZB 037 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 200 | 3 | 100 | 200 | 3 | 20 | 62.1 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM65 | 10 | 80 | 200 | 3
|  | OLR | Moeller | ZB65-65 | 10 | 50…65 | 200 | 3
D-M-NZM-SE+ZB 038 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 480 | 3 | 100 | 480 | 3 | 50 | 65 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM65 | 10 | 80 | 480 | 3
|  | OLR | Moeller | ZB65-65 | 10 | 50…65 | 480 | 3
D-M-NZM-SE+ZB 039 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 240 | 3 | 100 | 240 | 3 | 25 | 68 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM80 | 10 | 125 | 240 | 3
|  | OLR | Moeller | ZB150-70 | 10 | 50…70 | 240 | 3
D-M-NZM-SE+ZB 040 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 208 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM80 | 10 | 125 | 208 | 3
|  | OLR | Moeller | ZB150-100 | 10 | 70…100 | 208 | 3
D-M-NZM-SE+ZB 041 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 480 | 3 | 100 | 480 | 3 | 60 | 77 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM80 | 10 | 125 | 480 | 3
|  | OLR | Moeller | ZB150-100 | 10 | 70…100 | 480 | 3
D-M-NZM-SE+ZB 042 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM80 | 10 | 125 | 600 | 3
|  | OLR | Moeller | ZB150-100 | 10 | 70…100 | 600 | 3
D-M-NZM-SE+ZB 043 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 200 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM80 | 10 | 125 | 200 | 3
|  | OLR | Moeller | ZB150-100 | 10 | 70…100 | 200 | 3
D-M-NZM-SE+ZB 044 | D | ICB | Moeller | NZMN2-SE-140-CNA | - | 140 | 240 | 3 | 100 | 240 | 3 | 30 | 80 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM80 | 10 | 125 | 240 | 3
|  | OLR | Moeller | ZB150-100 | 10 | 70…100 | 240 | 3
D-M-NZM-SE+ZB 045 | D | ICB | Moeller | NZMN2-SE-140-CNA | - | 140 | 208 | 3 | 100 | 208 | 3 | 30 | 88 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM115 | 10 | 160 | 208 | 3
|  | OLR | Moeller | ZB150-100 | 10 | 70…100 | 208 | 3
D-M-NZM-SE+ZB 046 | D | ICB | Moeller | NZMN2-SE-140-CNA | - | 140 | 200 | 3 | 100 | 200 | 3 | 30 | 92 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM115 | 10 | 160 | 200 | 3
|  | OLR | Moeller | ZB150-100 | 10 | 70…100 | 200 | 3
D-M-NZM-SE+ZB 047 | D | ICB | Moeller | NZMN2-SE-140-CNA | - | 140 | 480 | 3 | 100 | 480 | 3 | 75 | 96 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM95 | 10 | 125 | 480 | 3
|  | OLR | Moeller | ZB150-100 | 10 | 70…100 | 480 | 3
D-M-NZM-SE+ZB 048 | D | ICB | Moeller | NZMN2-SE-140-CNA | - | 140 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM95 | 10 | 125 | 600 | 3
|  | OLR | Moeller | ZB150-100 | 10 | 70…100 | 600 | 3
D-M-NZM-SE+ZB 049 | D | ICB | Moeller | NZMN2-SE-140-CNA | - | 140 | 240 | 3 | 100 | 240 | 3 | 40 | 104 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM95 | 10 | 125 | 240 | 3
|  | OLR | Moeller | ZB150-125 | 10 | 95…125 | 240 | 3
D-M-NZM-SE+ZB 050 | D | ICB | Moeller | NZMN2-SE-140-CNA | - | 140 | 208 | 3 | 100 | 208 | 3 | 40 | 114 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM115 | 10 | 160 | 208 | 3
|  | OLR | Moeller | ZB150-125 | 10 | 95…125 | 208 | 3
D-M-NZM-SE+ZB 051 | D | ICB | Moeller | NZMN2-SE-220-CNA | - | 220 | 480 | 3 | 100 | 480 | 3 | 100 | 124 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM115 | 10 | 160 | 480 | 3
|  | OLR | Moeller | ZB150-125 | 10 | 95…125 | 480 | 3
D-M-NZM-SE+ZB 052 | D | ICB | Moeller | NZMN2-SE-220-CNA | - | 220 | 600 | 3 | 50 | 600 | 3 | 125 | 125 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM115 | 10 | 160 | 600 | 3
|  | OLR | Moeller | ZB150-125 | 10 | 95…125 | 600 | 3
D-M-NZM-SE+ZB 053 | D | ICB | Moeller | NZMN2-SE-220-CNA | - | 220 | 240 | 3 | 100 | 240 | 3 | 50 | 130 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM115 | 10 | 160 | 240 | 3
|  | OLR | Moeller | ZB150-150 | 10 | 120…150 | 240 | 3
D-M-NZM-SE+ZB 054 | D | ICB | Moeller | NZMN2-SE-220-CNA | - | 220 | 208 | 3 | 100 | 208 | 3 | 50 | 143 | 4340.9851 | 2.5121 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM185/22 | 18 | 225 | 208 | 3
|  | OLR | Moeller | Z5-160/FF250 | 10 | 120…160 | 208 | 3
D-M-NZM-SE+ZB 055 | D | ICB | Moeller | NZMN2-SE-220-CNA | - | 220 | 600 | 3 | 50 | 600 | 3 | 150 | 144 | 4340.9851 | 2.5121 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM185/22 | 18 | 225 | 600 | 3
|  | OLR | Moeller | Z5-160/FF250 | 10 | 120…160 | 600 | 3
D-M-NZM-SE+ZB 056 | D | ICB | Moeller | NZMN2-SE-220-CNA | - | 220 | 200 | 3 | 100 | 200 | 3 | 50 | 150 | 4340.9851 | 2.5121 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM185/22 | 18 | 225 | 200 | 3
|  | OLR | Moeller | Z5-160/FF250 | 10 | 120…160 | 200 | 3
D-M-NZM-SE+ZB 057 | D | ICB | Moeller | NZMN2-SE-220-CNA | - | 220 | 240 | 3 | 100 | 240 | 3 | 60 | 154 | 4340.9851 | 2.5121 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM185/22 | 18 | 225 | 240 | 3
|  | OLR | Moeller | Z5-160/FF250 | 10 | 120…160 | 240 | 3
D-M-NZM-SE+ZB 059 | D | ICB | Moeller | NZMN2-SE-220-CNA | - | 220 | 208 | 3 | 100 | 208 | 3 | 60 | 169 | 4340.9851 | 2.5121 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM225/22 | 18 | 250 | 208 | 3
|  | OLR | Moeller | Z5-220/FF250 | 10 | 160…220 | 208 | 3
D-M-NZM-SE+ZB 060 | D | ICB | Moeller | NZMN2-SE-220-CNA | - | 220 | 200 | 3 | 100 | 200 | 3 | 60 | 177 | 4340.9851 | 2.5121 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM225/22 | 18 | 250 | 200 | 3
|  | OLR | Moeller | Z5-220/FF250 | 10 | 160…220 | 200 | 3
D-M-NZM-SE+ZB 061 | D | ICB | Moeller | NZMN2-SE-220-CNA | - | 220 | 480 | 3 | 100 | 480 | 3 | 150 | 180 | 4340.9851 | 2.5121 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM225/22 | 18 | 250 | 480 | 3
|  | OLR | Moeller | Z5-220/FF250 | 10 | 160…220 | 480 | 3
D-M-NZM-SE+ZB 062 | D | ICB | Moeller | NZMN2-SE-220-CNA | - | 220 | 240 | 3 | 100 | 240 | 3 | 75 | 192 | 4340.9851 | 2.5121 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM225/22 | 18 | 250 | 240 | 3
|  | OLR | Moeller | Z5-220/FF250 | 10 | 160…220 | 240 | 3
D-M-NZM-SE+ZB 063 | D | ICB | Moeller | NZMN2-SE-220-CNA | - | 220 | 600 | 3 | 50 | 600 | 3 | 200 | 192 | 4340.9851 | 2.5121 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM225/22 | 18 | 250 | 600 | 3
|  | OLR | Moeller | Z5-220/FF250 | 10 | 160…220 | 600 | 3
D-M-NZM-SE+ZB 064 | D | ICB | Moeller | NZMN3-SE-350-CNA | - | 350 | 208 | 3 | 100 | 208 | 3 | 75 | 211 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM250/22 | 18 | 350 | 208 | 3
|  | OLR | Moeller | Z5-220/FF250 | 10 | 160…220 | 208 | 3
D-M-NZM-SE+ZB 065 | D | ICB | Moeller | NZMN3-SE-350-CNA | - | 350 | 200 | 3 | 100 | 200 | 3 | 75 | 221 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM250/22 | 18 | 350 | 200 | 3
|  | OLR | Moeller | Z5-250/FF250 | 10 | 200…250 | 200 | 3
D-M-NZM-SE+ZB 066 | D | ICB | Moeller | NZMN3-SE-350-CNA | - | 350 | 480 | 3 | 100 | 480 | 3 | 200 | 240 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM250/22 | 18 | 350 | 480 | 3
|  | OLR | Moeller | Z5-250/FF250 | 10 | 200…250 | 480 | 3
D-M-NZM-SE+ZB 067 | D | ICB | Moeller | NZMN3-SE-350-CNA | - | 350 | 600 | 3 | 50 | 600 | 3 | 250 | 242 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM250/22 | 18 | 350 | 600 | 3
|  | OLR | Moeller | Z5-250/FF250 | 10 | 200…250 | 600 | 3
D-M-NZM-SE+ZB 068 | D | ICB | Moeller | NZMN3-SE-350-CNA | - | 350 | 240 | 3 | 100 | 240 | 3 | 100 | 248 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM250/22 | 18 | 350 | 240 | 3
|  | OLR | Moeller | Z5-250/FF250 | 10 | 200…250 | 240 | 3
D-M-NZM-SE+ZB 069 | D | ICB | Moeller | NZMN3-SE-350-CNA | - | 350 | 208 | 3 | 100 | 208 | 3 | 100 | 273 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM300/22 | 30 | 350 | 208 | 3
|  | OLR | Moeller | ZW7-290 | - | 190…290 | 208 | 3
D-M-NZM-SE+ZB 070 | D | ICB | Moeller | NZMN3-SE-350-CNA | - | 350 | 200 | 3 | 100 | 200 | 3 | 100 | 285 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM300/22 | 30 | 350 | 200 | 3
|  | OLR | Moeller | ZW7-290 | - | 190…290 | 200 | 3
D-M-NZM-SE+ZB 071 | D | ICB | Moeller | NZMN3-SE-350-CNA | - | 350 | 600 | 3 | 50 | 600 | 3 | 300 | 289 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM300/22 | 30 | 350 | 600 | 3
|  | OLR | Moeller | ZW7-290 | - | 190…290 | 600 | 3
D-M-NZM-SE+ZB 072 | D | ICB | Moeller | NZMN3-SE-350-CNA | - | 350 | 480 | 3 | 100 | 480 | 3 | 250 | 302 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM300/22 | 30 | 350 | 480 | 3
|  | OLR | Moeller | ZW7-400 | - | 270…400 | 480 | 3
D-M-NZM-SE+ZB 073 | D | ICB | Moeller | NZMN3-SE-450-CNA | - | 450 | 240 | 3 | 100 | 240 | 3 | 125 | 312 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM300/22 | 30 | 350 | 240 | 3
|  | OLR | Moeller | ZW7-400 | - | 270…400 | 240 | 3
D-M-NZM-SE+ZB 074 | D | ICB | Moeller | NZMN3-SE-450-CNA | - | 450 | 600 | 3 | 50 | 600 | 3 | 350 | 336 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM400/22 | 30 | 450 | 600 | 3
|  | OLR | Moeller | ZW7-400 | - | 270…400 | 600 | 3
D-M-NZM-SE+ZB 075 | D | ICB | Moeller | NZMN3-SE-450-CNA | - | 450 | 208 | 3 | 100 | 208 | 3 | 125 | 343 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM400/22 | 30 | 450 | 208 | 3
|  | OLR | Moeller | ZW7-400 | - | 270…400 | 208 | 3
D-M-NZM-SE+ZB 076 | D | ICB | Moeller | NZMN3-SE-450-CNA | - | 450 | 200 | 3 | 100 | 200 | 3 | 125 | 359 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM400/22 | 30 | 450 | 200 | 3
|  | OLR | Moeller | ZW7-400 | - | 270…400 | 200 | 3
D-M-NZM-SE+ZB 077 | D | ICB | Moeller | NZMN3-SE-450-CNA | - | 450 | 240 | 3 | 100 | 240 | 3 | 150 | 360 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM400/22 | 30 | 450 | 240 | 3
|  | OLR | Moeller | ZW7-400 | - | 270…400 | 240 | 3
D-M-NZM-SE+ZB 078 | D | ICB | Moeller | NZMN3-SE-450-CNA | - | 450 | 480 | 3 | 100 | 480 | 3 | 300 | 361 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM400/22 | 30 | 450 | 480 | 3
|  | OLR | Moeller | ZW7-400 | - | 270…400 | 480 | 3
D-M-NZM-SE+ZB 079 | D | ICB | Moeller | NZMN3-SE-450-CNA | - | 450 | 600 | 3 | 50 | 600 | 3 | 400 | 382 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM400/22 | 30 | 450 | 600 | 3
|  | OLR | Moeller | ZW7-400 | - | 270…400 | 600 | 3

## D-FVNR SS Trip ICB + SS OLR
Issued: 2008-09-05
Last Revised: 2008-09-12
ID Number | Combination Type | Component Type | Component Manufactuer | Component Catalog Desgination | Component Ratings |  |  |  | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Motor FLC per NEC Table 430-250 | Minimum Enclosure Volume (cu in/ cu Ft) |  | Conditions of Acceptability | Combination UL File Reference
[5 empty] | kA | Max Amps | Volts | Poles
D-M-NZM-SE+ZEV 018 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 208 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM25-10 | 5 | 35 | 208 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 208 | 3
|  | Current Sensor | Moeller | ZEV-XSW-25 | 5 | 1…25 | 208 | 3
D-M-NZM-SE+ZEV 019 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 200 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM25-10 | 5 | 35 | 200 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 200 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 200 | 3
D-M-NZM-SE+ZEV 020 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 480 | 3 | 100 | 480 | 3 | 20 | 27 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM32-10 | 5 | 40 | 480 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 480 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 480 | 3
D-M-NZM-SE+ZEV 021 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM32-10 | 5 | 40 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 600 | 3
D-M-NZM-SE+ZEV 022 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 240 | 3 | 100 | 240 | 3 | 10 | 28 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM32-10 | 5 | 40 | 240 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 240 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 240 | 3
D-M-NZM-SE+ZEV 023 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 208 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM32-10 | 5 | 40 | 208 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 208 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 208 | 3
D-M-NZM-SE+ZEV 024 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM40 | 10 | 55 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 600 | 3
D-M-NZM-SE+ZEV 025 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 200 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM32-10 | 5 | 40 | 200 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 200 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 200 | 3
D-M-NZM-SE+ZEV 026 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 480 | 3 | 100 | 480 | 3 | 25 | 34 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM40 | 10 | 55 | 480 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 480 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 480 | 3
D-M-NZM-SE+ZEV 027 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 480 | 3 | 100 | 480 | 3 | 30 | 40 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM40 | 10 | 55 | 480 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 480 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 480 | 3
D-M-NZM-SE+ZEV 028 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM40 | 10 | 55 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 600 | 3
D-M-NZM-SE+ZEV 029 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 240 | 3 | 100 | 240 | 3 | 15 | 42 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM40 | 10 | 55 | 240 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 240 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 240 | 3
D-M-NZM-SE+ZEV 030 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 208 | 3 | 100 | 208 | 3 | 15 | 46.2 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM50 | 10 | 65 | 208 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 208 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 208 | 3
D-M-NZM-SE+ZEV 031 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 200 | 3 | 100 | 200 | 3 | 15 | 48.3 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM50 | 10 | 65 | 200 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 200 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 200 | 3
D-M-NZM-SE+ZEV 032 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM50 | 10 | 65 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 600 | 3
D-M-NZM-SE+ZEV 033 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 480 | 3 | 100 | 480 | 3 | 40 | 52 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM50 | 10 | 65 | 480 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 480 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 480 | 3
D-M-NZM-SE+ZEV 034 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 240 | 3 | 100 | 240 | 3 | 20 | 54 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM50 | 10 | 65 | 240 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 240 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 240 | 3
D-M-NZM-SE+ZEV 035 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 208 | 3 | 100 | 208 | 3 | 20 | 59.4 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM65 | 10 | 80 | 208 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 208 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 208 | 3
D-M-NZM-SE+ZEV 036 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM65 | 10 | 80 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 600 | 3
D-M-NZM-SE+ZEV 037 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 200 | 3 | 100 | 200 | 3 | 20 | 62.1 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM65 | 10 | 80 | 200 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 200 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 200 | 3
D-M-NZM-SE+ZEV 038 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 480 | 3 | 100 | 480 | 3 | 50 | 65 | 1335.6877 | 0.77297 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM65 | 10 | 80 | 480 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 480 | 3
|  | Current Sensor | Moeller | ZEV-XSW-65 | 10 | 3…65 | 480 | 3
D-M-NZM-SE+ZEV 039 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 240 | 3 | 100 | 240 | 3 | 25 | 68 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM80 | 10 | 125 | 240 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 240 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 240 | 3
D-M-NZM-SE+ZEV 040 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 208 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM80 | 10 | 125 | 208 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 208 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 208 | 3
D-M-NZM-SE+ZEV 041 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 480 | 3 | 100 | 480 | 3 | 60 | 77 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM80 | 10 | 125 | 480 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 480 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 480 | 3
D-M-NZM-SE+ZEV 042 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM80 | 10 | 125 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 600 | 3
D-M-NZM-SE+ZEV 043 | D | ICB | Moeller | NZMN2-SE-90-CNA | - | 90 | 200 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM80 | 10 | 125 | 200 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 200 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 200 | 3
D-M-NZM-SE+ZEV 044 | D | ICB | Moeller | NZMN2-SE-140-CNA | - | 140 | 240 | 3 | 100 | 240 | 3 | 30 | 80 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM80 | 10 | 125 | 240 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 240 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 240 | 3
D-M-NZM-SE+ZEV 045 | D | ICB | Moeller | NZMN2-SE-140-CNA | - | 140 | 208 | 3 | 100 | 208 | 3 | 30 | 88 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM115 | 10 | 160 | 208 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 208 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 208 | 3
D-M-NZM-SE+ZEV 046 | D | ICB | Moeller | NZMN2-SE-140-CNA | - | 140 | 200 | 3 | 100 | 200 | 3 | 30 | 92 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM115 | 10 | 160 | 200 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 200 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 200 | 3
D-M-NZM-SE+ZEV 047 | D | ICB | Moeller | NZMN2-SE-140-CNA | - | 140 | 480 | 3 | 100 | 480 | 3 | 75 | 96 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM95 | 10 | 125 | 480 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 480 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 480 | 3
D-M-NZM-SE+ZEV 048 | D | ICB | Moeller | NZMN2-SE-140-CNA | - | 140 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM95 | 10 | 125 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 600 | 3
D-M-NZM-SE+ZEV 049 | D | ICB | Moeller | NZMN2-SE-140-CNA | - | 140 | 240 | 3 | 100 | 240 | 3 | 40 | 104 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM95 | 10 | 125 | 240 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 240 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 240 | 3
D-M-NZM-SE+ZEV 050 | D | ICB | Moeller | NZMN2-SE-140-CNA | - | 140 | 208 | 3 | 100 | 208 | 3 | 40 | 114 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM115 | 10 | 160 | 208 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 208 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 208 | 3
D-M-NZM-SE+ZEV 051 | D | ICB | Moeller | NZMN2-SE-140-CNA | - | 140 | 200 | 3 | 100 | 200 | 3 | 40 | 120 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM115 | 10 | 160 | 200 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 200 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 200 | 3
D-M-NZM-SE+ZEV 052 | D | ICB | Moeller | NZMN2-SE-220-CNA | - | 220 | 480 | 3 | 100 | 480 | 3 | 100 | 124 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM115 | 10 | 160 | 480 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 480 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 480 | 3
D-M-NZM-SE+ZEV 053 | D | ICB | Moeller | NZMN2-SE-220-CNA | - | 220 | 600 | 3 | 50 | 600 | 3 | 125 | 125 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM115 | 10 | 160 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 600 | 3
D-M-NZM-SE+ZEV 054 | D | ICB | Moeller | NZMN2-SE-220-CNA | - | 220 | 240 | 3 | 100 | 240 | 3 | 50 | 130 | 2671.3754 | 1.5459 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM115 | 10 | 160 | 240 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 240 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 240 | 3
D-M-NZM-SE+ZEV 055 | D | ICB | Moeller | NZMN2-SE-220-CNA | - | 220 | 208 | 3 | 100 | 208 | 3 | 50 | 143 | 4340.9851 | 2.5121 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM185/22 | 18 | 225 | 208 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 208 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 208 | 3
D-M-NZM-SE+ZEV 056 | D | ICB | Moeller | NZMN2-SE-220-CNA | - | 220 | 600 | 3 | 50 | 600 | 3 | 150 | 144 | 4340.9851 | 2.5121 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM185/22 | 18 | 225 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-145 | 10 | 10…145 | 600 | 3
D-M-NZM-SE+ZEV 057 | D | ICB | Moeller | NZMN2-SE-220-CNA | - | 220 | 200 | 3 | 100 | 200 | 3 | 50 | 150 | 4340.9851 | 2.5121 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM185/22 | 18 | 225 | 200 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 200 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 200 | 3
D-M-NZM-SE+ZEV 058 | D | ICB | Moeller | NZMN2-SE-220-CNA | - | 220 | 240 | 3 | 100 | 240 | 3 | 60 | 154 | 4340.9851 | 2.5121 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM185/22 | 18 | 225 | 240 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 240 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 240 | 3
D-M-NZM-SE+ZEV 059 | D | ICB | Moeller | NZMN2-SE-220-CNA | - | 220 | 480 | 3 | 100 | 480 | 3 | 125 | 156 | 4340.9851 | 2.5121 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM150 | 10 | 160 | 480 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 480 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 480 | 3
D-M-NZM-SE+ZEV 060 | D | ICB | Moeller | NZMN2-SE-220-CNA | - | 220 | 208 | 3 | 100 | 208 | 3 | 60 | 169 | 4340.9851 | 2.5121 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM225/22 | 18 | 250 | 208 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 208 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 208 | 3
D-M-NZM-SE+ZEV 061 | D | ICB | Moeller | NZMN2-SE-220-CNA | - | 220 | 200 | 3 | 100 | 200 | 3 | 60 | 177 | 4340.9851 | 2.5121 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM225/22 | 18 | 250 | 200 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 200 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 200 | 3
D-M-NZM-SE+ZEV 062 | D | ICB | Moeller | NZMN2-SE-220-CNA | - | 220 | 480 | 3 | 100 | 480 | 3 | 150 | 180 | 4340.9851 | 2.5121 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM225/22 | 18 | 250 | 480 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 480 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 480 | 3
D-M-NZM-SE+ZEV 063 | D | ICB | Moeller | NZMN2-SE-220-CNA | - | 220 | 240 | 3 | 100 | 240 | 3 | 75 | 192 | 4340.9851 | 2.5121 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM225/22 | 18 | 250 | 240 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 240 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 240 | 3
D-M-NZM-SE+ZEV 064 | D | ICB | Moeller | NZMN2-SE-220-CNA | - | 220 | 600 | 3 | 50 | 600 | 3 | 200 | 192 | 4340.9851 | 2.5121 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM225/22 | 18 | 250 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 600 | 3
D-M-NZM-SE+ZEV 065 | D | ICB | Moeller | NZMN3-SE-350-CNA | - | 350 | 208 | 3 | 100 | 208 | 3 | 75 | 211 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM250/22 | 18 | 350 | 208 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 208 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 208 | 3
D-M-NZM-SE+ZEV 066 | D | ICB | Moeller | NZMN3-SE-350-CNA | - | 350 | 200 | 3 | 100 | 200 | 3 | 75 | 221 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM250/22 | 18 | 350 | 200 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 200 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 200 | 3
D-M-NZM-SE+ZEV 067 | D | ICB | Moeller | NZMN3-SE-350-CNA | - | 350 | 480 | 3 | 100 | 480 | 3 | 200 | 240 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM250/22 | 18 | 350 | 480 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 480 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 480 | 3
D-M-NZM-SE+ZEV 068 | D | ICB | Moeller | NZMN3-SE-350-CNA | - | 350 | 600 | 3 | 50 | 600 | 3 | 250 | 242 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM250/22 | 18 | 350 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 600 | 3
D-M-NZM-SE+ZEV 069 | D | ICB | Moeller | NZMN3-SE-350-CNA | - | 350 | 240 | 3 | 100 | 240 | 3 | 100 | 248 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM250/22 | 18 | 350 | 240 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 240 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 240 | 3
D-M-NZM-SE+ZEV 070 | D | ICB | Moeller | NZMN3-SE-350-CNA | - | 350 | 208 | 3 | 100 | 208 | 3 | 100 | 273 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM300/22 | 30 | 350 | 208 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 208 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 208 | 3
D-M-NZM-SE+ZEV 071 | D | ICB | Moeller | NZMN3-SE-350-CNA | - | 350 | 200 | 3 | 100 | 200 | 3 | 100 | 285 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM300/22 | 30 | 350 | 200 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 200 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 200 | 3
D-M-NZM-SE+ZEV 072 | D | ICB | Moeller | NZMN3-SE-350-CNA | - | 350 | 600 | 3 | 50 | 600 | 3 | 300 | 289 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM300/22 | 30 | 350 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 600 | 3
D-M-NZM-SE+ZEV 073 | D | ICB | Moeller | NZMN3-SE-350-CNA | - | 350 | 480 | 3 | 100 | 480 | 3 | 250 | 302 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM300/22 | 30 | 350 | 480 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 480 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 480 | 3
D-M-NZM-SE+ZEV 074 | D | ICB | Moeller | NZMN2-SE-450-CNA | - | 450 | 240 | 3 | 100 | 240 | 3 | 125 | 312 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM300/22 | 30 | 350 | 240 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 240 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 240 | 3
D-M-NZM-SE+ZEV 075 | D | ICB | Moeller | NZMN3-SE-450-CNA | - | 450 | 600 | 3 | 50 | 600 | 3 | 350 | 336 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM400/22 | 30 | 450 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 600 | 3
D-M-NZM-SE+ZEV 076 | D | ICB | Moeller | NZMN3-SE-450-CNA | - | 450 | 208 | 3 | 100 | 208 | 3 | 125 | 343 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM400/22 | 30 | 450 | 208 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 208 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 208 | 3
D-M-NZM-SE+ZEV 077 | D | ICB | Moeller | NZMN3-SE-450-CNA | - | 450 | 200 | 3 | 100 | 200 | 3 | 125 | 359 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM400/22 | 30 | 450 | 200 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 200 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 200 | 3
D-M-NZM-SE+ZEV 078 | D | ICB | Moeller | NZMN3-SE-450-CNA | - | 450 | 240 | 3 | 100 | 240 | 3 | 150 | 360 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM400/22 | 30 | 450 | 240 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 240 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 240 | 3
D-M-NZM-SE+ZEV 079 | D | ICB | Moeller | NZMN3-SE-450-CNA | - | 450 | 480 | 3 | 100 | 480 | 3 | 300 | 361 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM400/22 | 30 | 450 | 480 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 480 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 480 | 3
D-M-NZM-SE+ZEV 080 | D | ICB | Moeller | NZMN3-SE-450-CNA | - | 450 | 600 | 3 | 50 | 600 | 3 | 400 | 382 | 5008.8289 | 2.8986 | 1, 5 | E51580 V1 S29
|  | MC | Moeller | DILM400/22 | 30 | 450 | 600 | 3
|  | OLR | Moeller | ZEV | - | 1…820 | 600 | 3
|  | Current Sensor | Moeller | ZEV-XSW-820 | 42 | 40…820 | 600 | 3

## E-Self-Protected + MSP
Issued: 2008-09-05
Last Revised: 2011-09-06
ID Number | Combination Type | Component Type | Component Manufactuer | Component Catalog Desgination | Component Ratings |  |  |  | Combination kA | Combination Volts | Combination Phase | Max. Motor HP Ratings (See Note[1]) | Max. Motor FLC (See Note[2]) | Minimum Enclosure Volume (cu in/ cu Ft) |  | Conditions of Acceptability | Combination UL File Reference
[5 empty] | kA | Max Amps | Volts | Poles
E-M-PKZ2 S-SP 000 | E | MSP | Moeller | PKZ2/ZM-0,6/S-SP | - | 0.6 | 600Y/347V | 3 | 42 | 600Y/347V | 3 | - | 0.6 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 001 | E | MSP | Moeller | PKZ2/ZM-1/S-SP | - | 1 | 600Y/347V | 3 | 42 | 600Y/347V | 3 | 0.5 | 0.9 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 002 | E | MSP | Moeller | PKZ2/ZM-1,6/S-SP | - | 1.6 | 600Y/347V | 3 | 42 | 600Y/347V | 3 | 0.75 | 1.3 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 003 | E | MSP | Moeller | PKZ2/ZM-2,4/S-SP | - | 2.4 | 600Y/347V | 3 | 42 | 600Y/347V | 3 | 1.5 | 2.4 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 004 | E | MSP | Moeller | PKZ2/ZM-4/S-SP | - | 4 | 600Y/347V | 3 | 42 | 600Y/347V | 3 | 3 | 3.9 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 006 | E | MSP | Moeller | PKZ2/ZM-10/S-SP | - | 10 | 600Y/347V | 3 | 42 | 600Y/347V | 3 | 7.5 | 9 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 007 | E | MSP | Moeller | PKZ2/ZM-16/S-SP | - | 16 | 600Y/347V | 3 | 42 | 600Y/347V | 3 | 10 | 11 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 008 | E | MSP | Moeller | PKZ2/ZM-25/S-SP | - | 27 | 600Y/347V | 3 | 42 | 600Y/347V | 3 | 25 | 27 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 009 | E | MSP | Moeller | PKZ2/ZM-0,6/S-SP | - | 0.6 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | - | 0.6 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 010 | E | MSP | Moeller | PKZ2/ZM-1,6/S-SP | - | 1.6 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 0.75 | 1.6 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 011 | E | MSP | Moeller | PKZ2/ZM-2,4/S-SP | - | 2.4 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 1 | 2.1 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 012 | E | MSP | Moeller | PKZ2/ZM-4/S-SP | - | 4 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 2 | 3.4 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 013 | E | MSP | Moeller | PKZ2/ZM-6/S-SP | - | 6 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 3 | 4.8 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 014 | E | MSP | Moeller | PKZ2/ZM-10/S-SP | - | 10 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 5 | 7.6 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 015 | E | MSP | Moeller | PKZ2/ZM-16/S-SP | - | 16 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 10 | 14 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 016 | E | MSP | Moeller | PKZ2/ZM-25/S-SP | - | 27 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 20 | 27 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 017 | E | MSP | Moeller | PKZ2/ZM-32/S-SP | - | 32 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 20 | 27 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 018 | E | MSP | Moeller | PKZ2/ZM-40/S-SP | - | 42 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 30 | 40 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 019 | E | MSP | Moeller | PKZ2/ZM-0,6/S-SP | - | 0.6 | 240V | 3 | 100 | 240V | 3 | - | 0.6 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 020 | E | MSP | Moeller | PKZ2/ZM-1/S-SP | - | 1 | 240V | 3 | 100 | 240V | 3 | - | 1 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 021 | E | MSP | Moeller | PKZ2/ZM-1,6/S-SP | - | 1.6 | 240V | 3 | 100 | 240V | 3 | - | 1.6 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 022 | E | MSP | Moeller | PKZ2/ZM-2,4/S-SP | - | 2.4 | 240V | 3 | 100 | 240V | 3 | 0.5 | 2.2 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 023 | E | MSP | Moeller | PKZ2/ZM-6/S-SP | - | 6 | 240V | 3 | 100 | 240V | 3 | 1.5 | 6 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 024 | E | MSP | Moeller | PKZ2/ZM-10/S-SP | - | 10 | 240V | 3 | 100 | 240V | 3 | 3 | 9.6 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 025 | E | MSP | Moeller | PKZ2/ZM-16/S-SP | - | 16 | 240V | 3 | 100 | 240V | 3 | 5 | 15.2 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 026 | E | MSP | Moeller | PKZ2/ZM-25/S-SP | - | 25 | 240V | 3 | 100 | 240V | 3 | 7.5 | 22 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 027 | E | MSP | Moeller | PKZ2/ZM-32/S-SP | - | 32 | 240V | 3 | 100 | 240V | 3 | 10 | 28 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 028 | E | MSP | Moeller | PKZ2/ZM-40/S-SP | - | 42 | 240V | 3 | 100 | 240V | 3 | 15 | 42 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 029 | E | MSP | Moeller | PKZ2/ZMR-0,6/S-SP | - | 0.6 | 600Y/347V | 3 | 42 | 600Y/347V | 3 | - | 0.6 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 030 | E | MSP | Moeller | PKZ2/ZMR-1/S-SP | - | 1 | 600Y/347V | 3 | 42 | 600Y/347V | 3 | 0.5 | 0.9 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 031 | E | MSP | Moeller | PKZ2/ZMR-1,6/S-SP | - | 1.6 | 600Y/347V | 3 | 42 | 600Y/347V | 3 | 0.75 | 1.3 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 032 | E | MSP | Moeller | PKZ2/ZMR-2,4/S-SP | - | 2.4 | 600Y/347V | 3 | 42 | 600Y/347V | 3 | 1.5 | 2.4 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 033 | E | MSP | Moeller | PKZ2/ZMR-4/S-SP | - | 4 | 600Y/347V | 3 | 42 | 600Y/347V | 3 | 3 | 3.9 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 034 | E | MSP | Moeller | PKZ2/ZMR-10/S-SP | - | 10 | 600Y/347V | 3 | 42 | 600Y/347V | 3 | 7.5 | 9 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 035 | E | MSP | Moeller | PKZ2/ZMR-16/S-SP | - | 16 | 600Y/347V | 3 | 42 | 600Y/347V | 3 | 10 | 11 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 036 | E | MSP | Moeller | PKZ2/ZMR-25/S-SP | - | 27 | 600Y/347V | 3 | 42 | 600Y/347V | 3 | 25 | 27 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
983.2
E-M-PKZ2 S-SP 037 | E | MSP | Moeller | PKZ2/ZMR-0,6/S-SP | - | 0.6 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | - | 0.6 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 038 | E | MSP | Moeller | PKZ2/ZMR-1,6/S-SP | - | 1.6 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 0.75 | 1.6 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 039 | E | MSP | Moeller | PKZ2/ZMR-2,4/S-SP | - | 2.4 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 1 | 2.1 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 040 | E | MSP | Moeller | PKZ2/ZMR-4/S-SP | - | 4 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 2 | 3.4 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 041 | E | MSP | Moeller | PKZ2/ZMR-6/S-SP | - | 6 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 3 | 4.8 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 042 | E | MSP | Moeller | PKZ2/ZMR-10/S-SP | - | 10 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 5 | 7.6 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 043 | E | MSP | Moeller | PKZ2/ZMR-16/S-SP | - | 16 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 10 | 14 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 044 | E | MSP | Moeller | PKZ2/ZMR-25/S-SP | - | 27 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 20 | 27 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 045 | E | MSP | Moeller | PKZ2/ZMR-32/S-SP | - | 32 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 20 | 27 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 046 | E | MSP | Moeller | PKZ2/ZMR-40/S-SP | - | 42 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 30 | 40 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 047 | E | MSP | Moeller | PKZ2/ZMR-0,6/S-SP | - | 0.6 | 240V | 3 | 100 | 240V | 3 | - | 0.6 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 048 | E | MSP | Moeller | PKZ2/ZMR-1/S-SP | - | 1 | 240V | 3 | 100 | 240V | 3 | - | 1 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 049 | E | MSP | Moeller | PKZ2/ZMR-1,6/S-SP | - | 1.6 | 240V | 3 | 100 | 240V | 3 | - | 1.6 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 050 | E | MSP | Moeller | PKZ2/ZMR-2,4/S-SP | - | 2.4 | 240V | 3 | 100 | 240V | 3 | 0.5 | 2.2 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 051 | E | MSP | Moeller | PKZ2/ZMR-6/S-SP | - | 6 | 240V | 3 | 100 | 240V | 3 | 1.5 | 6 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 052 | E | MSP | Moeller | PKZ2/ZMR-10/S-SP | - | 10 | 240V | 3 | 100 | 240V | 3 | 3 | 9.6 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 053 | E | MSP | Moeller | PKZ2/ZMR-16/S-SP | - | 16 | 240V | 3 | 100 | 240V | 3 | 5 | 15.2 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 054 | E | MSP | Moeller | PKZ2/ZMR-25/S-SP | - | 25 | 240V | 3 | 100 | 240V | 3 | 7.5 | 22 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 055 | E | MSP | Moeller | PKZ2/ZMR-32/S-SP | - | 32 | 240V | 3 | 100 | 240V | 3 | 10 | 28 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZ2 S-SP 056 | E | MSP | Moeller | PKZ2/ZMR-40/S-SP | - | 42 | 240V | 3 | 100 | 240V | 3 | 15 | 42 | 983.2 | 0.569 | 1, 5 | E123500 V1 S1
E-M-PKZM0 001 | E | MSP | Moeller | PKZM0-0,16 | - | 0.16 | 240 | 3 | 65 | 240V | 3 | - | 0.16 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 240 | 3
E-M-PKZM0 002 | E | MSP | Moeller | PKZM0-0,16 | - | 0.16 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | - | 0.16 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 480Y/277V | 3
E-M-PKZM0 003 | E | MSP | Moeller | PKZM0-0,16 | - | 0.16 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | - | 0.16 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 600Y/347V | 3
E-M-PKZM0 004 | E | MSP | Moeller | PKZM0-0,25 | - | 0.25 | 240 | 3 | 65 | 240V | 3 | - | 0.25 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 240 | 3
E-M-PKZM0 005 | E | MSP | Moeller | PKZM0-0,25 | - | 0.25 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | - | 0.25 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 480Y/277V | 3
E-M-PKZM0 006 | E | MSP | Moeller | PKZM0-0,25 | - | 0.25 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | - | 0.25 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 600Y/347V | 3
E-M-PKZM0 007 | E | MSP | Moeller | PKZM0-0,4 | - | 0.4 | 240 | 3 | 65 | 240V | 3 | - | 0.4 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 240 | 3
E-M-PKZM0 008 | E | MSP | Moeller | PKZM0-0,4 | - | 0.4 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | - | 0.4 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 480Y/277V | 3
E-M-PKZM0 009 | E | MSP | Moeller | PKZM0-0,4 | - | 0.4 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | - | 0.4 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 600Y/347V | 3
E-M-PKZM0 010 | E | MSP | Moeller | PKZM0-0,63 | - | 0.63 | 240 | 3 | 65 | 240V | 3 | - | 0.63 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 240 | 3
E-M-PKZM0 011 | E | MSP | Moeller | PKZM0-0,63 | - | 0.63 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | - | 0.63 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 480Y/277V | 3
E-M-PKZM0 012 | E | MSP | Moeller | PKZM0-0,63 | - | 0.63 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | - | 0.63 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 600Y/347V | 3
E-M-PKZM0 013 | E | MSP | Moeller | PKZM0-1 | - | 1 | 240 | 3 | 65 | 240V | 3 | - | 1 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 240 | 3
E-M-PKZM0 014 | E | MSP | Moeller | PKZM0-1 | - | 1 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 0.5 | 0.9 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 600Y/347V | 3
E-M-PKZM0 015 | E | MSP | Moeller | PKZM0-1,6 | - | 1.6 | 240 | 3 | 65 | 240V | 3 | - | 1.6 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 240 | 3
E-M-PKZM0 016 | E | MSP | Moeller | PKZM0-1,6 | - | 1.6 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 0.75 | 1.6 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 480Y/277V | 3
E-M-PKZM0 017 | E | MSP | Moeller | PKZM0-2,5 | - | 2.5 | 240 | 3 | 50 | 240V | 3 | 0.5 | 2.2 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 240 | 3
E-M-PKZM0 018 | E | MSP | Moeller | PKZM0-2,5 | - | 2.5 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 1 | 2.1 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 480Y/277V | 3
E-M-PKZM0 019 | E | MSP | Moeller | PKZM0-2,5 | - | 2.5 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 1.5 | 2.4 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 600Y/347V | 3
E-M-PKZM0 020 | E | MSP | Moeller | PKZM0-4 | - | 4 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 2 | 3.4 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 480Y/277V | 3
E-M-PKZM0 021 | E | MSP | Moeller | PKZM0-4 | - | 4 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 3 | 3.9 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 600Y/347V | 3
E-M-PKZM0 022 | E | MSP | Moeller | PKZM0-6,3 | - | 6.3 | 240 | 3 | 50 | 240V | 3 | 1.5 | 6 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 240 | 3
E-M-PKZM0 023 | E | MSP | Moeller | PKZM0-6,3 | - | 6.3 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 3 | 4.8 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 480Y/277V | 3
E-M-PKZM0 024 | E | MSP | Moeller | PKZM0-6,3 | - | 6.3 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 5 | 6.1 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 600Y/347V | 3
E-M-PKZM0 025 | E | MSP | Moeller | PKZM0-10 | - | 11 | 240 | 3 | 65 | 240V | 3 | 3 | 9.6 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 240 | 3
E-M-PKZM0 026 | E | MSP | Moeller | PKZM0-10 | - | 11 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 7.5 | 11 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 480Y/277V | 3
E-M-PKZM0 027 | E | MSP | Moeller | PKZM0-10 | - | 11 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 10 | 11 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 600Y/347V | 3
E-M-PKZM0 028 | E | MSP | Moeller | PKZM0-12 | - | 12 | 240 | 3 | 18 | 240V | 3 | 3 | 9.6 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 240 | 3
E-M-PKZM0 029 | E | MSP | Moeller | PKZM0-12 | - | 12 | 480Y/277V | 3 | 18 | 480Y/277V | 3 | 7.5 | 11 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 480Y/277V | 3
E-M-PKZM0 030 | E | MSP | Moeller | PKZM0-16 | - | 16 | 240 | 3 | 42 | 240V | 3 | 5 | 15.2 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 240 | 3
E-M-PKZM0 031 | E | MSP | Moeller | PKZM0-16 | - | 16 | 480Y/277V | 3 | 42 | 480Y/277V | 3 | 10 | 14 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 480Y/277V | 3
E-M-PKZM0 032 | E | MSP | Moeller | PKZM0-25 | - | 25 | 240 | 3 | 18 | 240 | 3 | 7.5 | 22 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 240 | 3
E-M-PKZM0 033 | E | MSP | Moeller | PKZM0-25 | - | 25 | 480Y/277V | 3 | 18 | 480Y/277V | 3 | 15 | 21 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 480Y/277V | 3
E-M-PKZM0 034 | E | MSP | Moeller | PKZM0-32 | - | 32 | 240 | 3 | 18 | 240 | 3 | 10 | 28 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 240 | 3
E-M-PKZM0 035 | E | MSP | Moeller | PKZM0-32 | - | 32 | 480Y/277V | 3 | 18 | 480Y/277V | 3 | 20 | 27 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E |  | 60 | 480Y/277V | 3
E-M-PKZM4 001 | E | MSP | Moeller | PKZM4-16 | - | 16 | 240 | 3 | 65 | 240V | 3 | 5 | 15.2 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S2
|  | Adapter | Moeller | BK50/3-PKZ4-E |  | 60 | 240 | 3
E-M-PKZM4 002 | E | MSP | Moeller | PKZM4-16 | - | 16 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 10 | 14 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S2
|  | Adapter | Moeller | BK50/3-PKZ4-E |  | 60 | 480Y/277V | 3
E-M-PKZM4 003 | E | MSP | Moeller | PKZM4-16 | - | 16 | 600Y/347V | 3 | 25 | 600Y/347V | 3 | 10 | 11 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S2
|  | Adapter | Moeller | BK50/3-PKZ4-E |  | 60 | 600Y/347V | 3
E-M-PKZM4 004 | E | MSP | Moeller | PKZM4-25 | - | 27 | 240 | 3 | 65 | 240V | 3 | 7.5 | 22 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S2
|  | Adapter | Moeller | BK50/3-PKZ4-E |  | 60 | 240 | 3
E-M-PKZM4 005 | E | MSP | Moeller | PKZM4-25 | - | 27 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 20 | 27 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S2
|  | Adapter | Moeller | BK50/3-PKZ4-E |  | 60 | 480Y/277V | 3
E-M-PKZM4 006 | E | MSP | Moeller | PKZM4-25 | - | 27 | 600Y/347V | 3 | 25 | 600Y/347V | 3 | 25 | 27 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S2
|  | Adapter | Moeller | BK50/3-PKZ4-E |  | 60 | 600Y/347V | 3
E-M-PKZM4 007 | E | MSP | Moeller | PKZM4-32 | - | 32 | 240 | 3 | 65 | 240V | 3 | 10 | 28 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S2
|  | Adapter | Moeller | BK50/3-PKZ4-E |  | 60 | 240 | 3
E-M-PKZM4 008 | E | MSP | Moeller | PKZM4-32 | - | 32 | 600Y/347V | 3 | 25 | 600Y/347V | 3 | 30 | 32 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S2
|  | Adapter | Moeller | BK50/3-PKZ4-E |  | 60 | 600Y/347V | 3
E-M-PKZM4 009 | E | MSP | Moeller | PKZM4-40 | - | 40 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 30 | 40 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S2
|  | Adapter | Moeller | BK50/3-PKZ4-E |  | 60 | 480Y/277V | 3
E-M-PKZM4 010 | E | MSP | Moeller | PKZM4-40 | - | 40 | 600Y/347V | 3 | 25 | 600Y/347V | 3 | 40 | 40 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S2
|  | Adapter | Moeller | BK50/3-PKZ4-E |  | 60 | 600Y/347V | 3
E-M-PKZM4 011 | E | MSP | Moeller | PKZM4-50 | - | 52 | 240V | 3 | 65 | 240V | 3 | 15 | 42 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S2
|  | Adapter | Moeller | BK50/3-PKZ4-E |  | 60 | 240V | 3
E-M-PKZM4 012 | E | MSP | Moeller | PKZM4-50 | - | 52 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 30 | 40 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S2
|  | Adapter | Moeller | BK50/3-PKZ4-E |  | 60 | 480Y/277V | 3
E-M-PKZM4 013 | E | MSP | Moeller | PKZM4-58 | - | 56 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 40 | 52 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S2
|  | Adapter | Moeller | BK50/3-PKZ4-E |  | 60 | 480Y/277V | 3
E-M-PKZM4 014 | E | MSP | Moeller | PKZM4-63 | - | 58 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 40 | 52 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S2
|  | Adapter | Moeller | BK50/3-PKZ4-E |  | 60 | 480Y/277V | 3
E-M-PKZM4 015 | E | MSP | Moeller | PKZM4-25 | - | 27 | 208 | 3 | 65 | 208V | 3 | 7.5 | 24.2 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S2
|  | Adapter | Moeller | BK50/3-PKZ4-E |  | 60 | 208 | 3
E-M-PKZM4 016 | E | MSP | Moeller | PKZM4-32 | - | 32 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S2
|  | Adapter | Moeller | BK50/3-PKZ4-E |  | 60 | 208 | 3
E-M-PKZM4 017 | E | MSP | Moeller | PKZM4-50 | - | 52 | 208 | 3 | 65 | 208 | 3 | 15 | 46.2 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S2
|  | Adapter | Moeller | BK50/3-PKZ4-E |  | 60 | 208 | 3
Notes:
[1] HP ratings for reference only. Select combination motor controller based on motor full load current and service factor.
[2] Values represent Motor FLC ratings from NEC Table 430-250 or maximum dial setting on combination motor controller
All Starters are FVNR, Full Voltage Non-Reversing
Type PKZ2/ZM-.../S-SP starters are Self-protected Combination Motor Controllers incl. magnetic contactor portion
Type PKZM0 and PKZM4 are manual Self-protected Combination Motor Controllers

## F-MSP + Wiring Adapter
Issued: 2008-09-05
Last Revised: 2008-09-12
ID Number | Combination Type | Component Type | Component Manufactuer | Component Catalog Desgination | Component Ratings |  |  |  | Combination kA | Combination Volts | Combination Phase | Max. Motor HP Ratings (See Note[1]) | Max. Motor FLC (See Note[2]) | Minimum Enclosure Volume (cu in/ cu Ft) |  | Conditions of Acceptability | Combination UL File Reference
[5 empty] | kA | Max Amps | Volts | Poles
F-M-MSC/BBA 001 | F | MSP + MC | Moeller | MSC-D-0,25-M7/BBA | - | 0.25 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | - | 0.25 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC/BBA 002 | F | MSP + MC | Moeller | MSC-D-0,4-M7/BBA | - | 0.4 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | - | 0.4 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC/BBA 003 | F | MSP + MC | Moeller | MSC-D-0,63-M7/BBA | - | 0.63 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | - | 0.63 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC/BBA 004 | F | MSP + MC | Moeller | MSC-D-1-M7/BBA | - | 1 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | - | 1 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC/BBA 005 | F | MSP + MC | Moeller | MSC-D-1,6-M7/BBA | - | 1.6 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 0.75 | 1.6 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC/BBA 006 | F | MSP + MC | Moeller | MSC-D-2,5-M7/BBA | - | 2.5 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 1 | 2.1 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC/BBA 007 | F | MSP + MC | Moeller | MSC-D-4-M7/BBA | - | 4 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 2 | 3.4 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC/BBA 008 | F | MSP + MC | Moeller | MSC-D-6,3-M7/BBA | - | 6.3 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 3 | 4.8 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC/BBA 009 | F | MSP + MC | Moeller | MSC-D-10-M9/BBA | - | 11 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 5 | 7.6 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC/BBA 010 | F | MSP + MC | Moeller | MSC-D-12-M12/BBA | - | 12 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 7.5 | 11 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC/BBA 011 | F | MSP + MC | Moeller | MSC-D-16-M17/BBA | - | 16 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 10 | 14 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC/BBA 012 | F | MSP + MC | Moeller | MSC-D-20-M25/BBA | - | 20 | 480Y/277V | 3 | 18 | 480Y/277V | 3 | 10 | 14 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC/BBA 013 | F | MSP + MC | Moeller | MSC-D-25-M25/BBA | - | 25 | 480Y/277V | 3 | 18 | 480Y/277V | 3 | 15 | 21 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC/BBA 014 | F | MSP + MC | Moeller | MSC-D-32-M32/BBA | - | 32 | 480Y/277V | 3 | 18 | 480Y/277V | 3 | 20 | 27 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC/BBA 015 | F | MSP + MC | Moeller | MSC-D-0,25-M7/BBA | - | 0.25 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | - | 0.25 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-M-MSC/BBA 016 | F | MSP + MC | Moeller | MSC-D-0,4-M7/BBA | - | 0.4 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | - | 0.4 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-M-MSC/BBA 017 | F | MSP + MC | Moeller | MSC-D-0,63-M7/BBA | - | 0.63 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | - | 0.63 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-M-MSC/BBA 018 | F | MSP + MC | Moeller | MSC-D-1-M7/BBA | - | 1 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 0.5 | 0.9 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-M-MSC/BBA 019 | F | MSP + MC | Moeller | MSC-D-1,6-M7/BBA | - | 1.6 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 0.75 | 1.3 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-M-MSC/BBA 020 | F | MSP + MC | Moeller | MSC-D-2,5-M7/BBA | - | 2.5 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 1.5 | 2.4 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-M-MSC/BBA 021 | F | MSP + MC | Moeller | MSC-D-4-M7/BBA | - | 4 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 3 | 3.9 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-M-MSC/BBA 022 | F | MSP + MC | Moeller | MSC-D-6,3-M7/BBA | - | 6.3 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 5 | 6.1 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-M-MSC/BBA 023 | F | MSP + MC | Moeller | MSC-D-10-M9/BBA | - | 11 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 7.5 | 9 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-MW-MSC/BBA 001 | F | MSP + REVCON | Moeller | MSC-R-0,25-M7/BBA | - | 0.25 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | - | 0.25 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-MW-MSC/BBA 002 | F | MSP + REVCON | Moeller | MSC-R-0,4-M7/BBA | - | 0.4 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | - | 0.4 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-MW-MSC/BBA 003 | F | MSP + REVCON | Moeller | MSC-R-0,63-M7/BBA | - | 0.63 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | - | 0.63 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-MW-MSC/BBA 004 | F | MSP + REVCON | Moeller | MSC-R-1,6-M7/BBA | - | 1.6 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 0.75 | 1.6 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-MW-MSC/BBA 005 | F | MSP + REVCON | Moeller | MSC-R-2,5-M7/BBA | - | 2.5 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 1 | 2.5 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-MW-MSC/BBA 006 | F | MSP + REVCON | Moeller | MSC-R-4-M7/BBA | - | 4 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 2 | 3.4 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-MW-MSC/BBA 007 | F | MSP + REVCON | Moeller | MSC-R-6,3-M7/BBA | - | 6.3 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 3 | 4.8 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-MW-MSC/BBA 008 | F | MSP + REVCON | Moeller | MSC-R-10-M7/BBA | - | 11 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 3 | 4.8 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-MW-MSC/BBA 009 | F | MSP + REVCON | Moeller | MSC-R-10-M9/BBA | - | 11 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 5 | 7.6 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-MW-MSC/BBA 010 | F | MSP + REVCON | Moeller | MSC-R-10-M17/BBA | - | 11 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 7.5 | 11 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-MW-MSC/BBA 011 | F | MSP + REVCON | Moeller | MSC-R-12-M17/BBA | - | 12 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 7.5 | 11 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-MW-MSC/BBA 012 | F | MSP + REVCON | Moeller | MSC-R-16-M17/BBA | - | 16 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 10 | 14 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-MW-MSC/BBA 013 | F | MSP + REVCON | Moeller | MSC-R-25-M25/BBA | - | 25 | 480Y/277V | 3 | 18 | 480Y/277V | 3 | 15 | 21 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-MW-MSC/BBA 014 | F | MSP + REVCON | Moeller | MSC-R-32-M32/BBA | - | 32 | 480Y/277V | 3 | 18 | 480Y/277V | 3 | 20 | 27 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-MW-MSC/BBA 015 | F | MSP + REVCON | Moeller | MSC-R-0,25-M7/BBA | - | 0.25 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | - | 0.25 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-MW-MSC/BBA 016 | F | MSP + REVCON | Moeller | MSC-R-0,4-M7/BBA | - | 0.4 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | - | 0.4 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-MW-MSC/BBA 017 | F | MSP + REVCON | Moeller | MSC-R-0,63-M7/BBA | - | 0.63 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | - | 0.63 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-MW-MSC/BBA 018 | F | MSP + REVCON | Moeller | MSC-R-1-M7/BBA | - | 1 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 0.5 | 0.9 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-MW-MSC/BBA 019 | F | MSP + REVCON | Moeller | MSC-R-2,5-M7/BBA | - | 2.5 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 1.5 | 2.4 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-MW-MSC/BBA 020 | F | MSP + REVCON | Moeller | MSC-R-4-M7/BBA | - | 4 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 3 | 3.9 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-MW-MSC/BBA 021 | F | MSP + REVCON | Moeller | MSC-R-6,3-M7/BBA | - | 6.3 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 5 | 6.1 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-MW-MSC/BBA 022 | F | MSP + REVCON | Moeller | MSC-R-10-M7/BBA | - | 11 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 5 | 6.1 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-MW-MSC/BBA 023 | F | MSP + REVCON | Moeller | MSC-R-10-M9/BBA | - | 11 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 7.5 | 9 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-MW-MSC/BBA 024 | F | MSP + REVCON | Moeller | MSC-R-10-M17/BBA | - | 11 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 10 | 11 | 10984.2739 | 6.3566 | 1, 5, 7, 8 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-M-MSC 001 | F | MSP + MC | Moeller | MSC-D-0,25-M7 | - | 0.25 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | - | 0.25 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC 002 | F | MSP + MC | Moeller | MSC-D-0,4-M7 (SOND516) | - | 0.4 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | - | 0.4 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC 003 | F | MSP + MC | Moeller | MSC-D-0,63-M7 | - | 0.63 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | - | 0.63 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC 005 | F | MSP + MC | Moeller | MSC-D-1,6-M7 (SOND516) | - | 1.6 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 0.75 | 1.6 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC 006 | F | MSP + MC | Moeller | MSC-D-2,5-M7 | - | 2.5 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 1 | 2.1 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC 007 | F | MSP + MC | Moeller | MSC-D-4-M7 (SOND516) | - | 4 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 2 | 3.4 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC 008 | F | MSP + MC | Moeller | MSC-D-6,3-M7 (SOND516) | - | 6.3 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 3 | 4.8 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC 009 | F | MSP + MC | Moeller | MSC-D-10-M7 | - | 11 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 3 | 4.8 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC 010 | F | MSP + MC | Moeller | MSC-D-10-M9 | - | 11 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 5 | 7.6 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC 011 | F | MSP + MC | Moeller | MSC-D-12-M12 (SOND516) | - | 12 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 7.5 | 11 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC 012 | F | MSP + MC | Moeller | MSC-D-10-M17 | - | 11 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 7.5 | 11 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC 013 | F | MSP + MC | Moeller | MSC-D-12-M17 | - | 12 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 7.5 | 11 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC 014 | F | MSP + MC | Moeller | MSC-D-16-M15 | - | 16 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 10 | 14 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC 015 | F | MSP + MC | Moeller | MSC-D-25-M25 | - | 25 | 480Y/277V | 3 | 18 | 480Y/277V | 3 | 15 | 21 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC 016 | F | MSP + MC | Moeller | MSC-D-32-M32 | - | 32 | 480Y/277V | 3 | 18 | 480Y/277V | 3 | 20 | 27 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-M-MSC 017 | F | MSP + MC | Moeller | MSC-D-0,25-M7 | - | 0.25 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | - | 0.25 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-M-MSC 018 | F | MSP + MC | Moeller | MSC-D-0,4-M7 (SOND516) | - | 0.4 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | - | 0.4 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-M-MSC 019 | F | MSP + MC | Moeller | MSC-D-0,63-M7 | - | 0.63 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | - | 0.63 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-M-MSC 020 | F | MSP + MC | Moeller | MSC-D-1-M7 (SOND516) | - | 1 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 0.5 | 0.9 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-M-MSC 021 | F | MSP + MC | Moeller | MSC-D-1,6-M7 (SOND516) | - | 1.6 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 3/4 | 1.6 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-M-MSC 022 | F | MSP + MC | Moeller | MSC-D-2,5-M7 | - | 2.5 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 1 | 2.1 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-M-MSC 023 | F | MSP + MC | Moeller | MSC-D-4-M7 (SOND516) | - | 4 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 2 | 3.4 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-M-MSC 024 | F | MSP + MC | Moeller | MSC-D-6,3-M7 (SOND516) | - | 6.3 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 3 | 4.8 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-M-MSC 025 | F | MSP + MC | Moeller | MSC-D-10-M7 | - | 11 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 5 | 6.1 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-M-MSC 026 | F | MSP + MC | Moeller | MSC-D-10-M9 | - | 11 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 7.5 | 9 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-MW-MSC 001 | F | MSP + REVCON | Moeller | MSC-R-0,25-M7 | - | 0.25 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | - | 0.25 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-MW-MSC 002 | F | MSP + REVCON | Moeller | MSC-R-0,4-M7 | - | 0.4 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | - | 0.4 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-MW-MSC 003 | F | MSP + REVCON | Moeller | MSC-R-0,63-M7 | - | 0.63 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | - | 0.63 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-MW-MSC 005 | F | MSP + REVCON | Moeller | MSC-R-1,6-M7 | - | 1.6 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 0.75 | 1.6 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-MW-MSC 006 | F | MSP + REVCON | Moeller | MSC-R-2,5-M7 | - | 2.5 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 1 | 2.1 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-MW-MSC 007 | F | MSP + REVCON | Moeller | MSC-R-4-M7 | - | 4 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 2 | 3.4 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-MW-MSC 008 | F | MSP + REVCON | Moeller | MSC-R-6,3-M7 | - | 6.3 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 3 | 4.8 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-MW-MSC 009 | F | MSP + REVCON | Moeller | MSC-R-10-M7 | - | 11 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 3 | 4.8 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-MW-MSC 010 | F | MSP + REVCON | Moeller | MSC-R-10-M9 | - | 11 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 5 | 7.6 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-MW-MSC 011 | F | MSP + REVCON | Moeller | MSC-R-12-M12 | - | 12 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 7.5 | 11 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-MW-MSC 014 | F | MSP + REVCON | Moeller | MSC-R-16-M17 | - | 16 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 10 | 14 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-MW-MSC 015 | F | MSP + REVCON | Moeller | MSC-R-25-M25 | - | 25 | 480Y/277V | 3 | 18 | 480Y/277V | 3 | 15 | 21 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-MW-MSC 016 | F | MSP + REVCON | Moeller | MSC-R-32-M32 | - | 32 | 480Y/277V | 3 | 18 | 480Y/277V | 3 | 20 | 27 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
F-MW-MSC 017 | F | MSP + REVCON | Moeller | MSC-R-0,25-M7 | - | 0.25 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | - | 0.25 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-MW-MSC 018 | F | MSP + REVCON | Moeller | MSC-R-0,4-M7 | - | 0.4 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | - | 0.4 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-MW-MSC 019 | F | MSP + REVCON | Moeller | MSC-R-0,63-M7 | - | 0.63 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | - | 0.63 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-MW-MSC 020 | F | MSP + REVCON | Moeller | MSC-R-1-M7 | - | 1 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 0.5 | 0.9 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-MW-MSC 021 | F | MSP + REVCON | Moeller | MSC-R-2,5-M7 | - | 2.5 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 1 1/2 | 2.4 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-MW-MSC 022 | F | MSP + REVCON | Moeller | MSC-R-4-M7 | - | 4 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 3 | 3.9 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-MW-MSC 023 | F | MSP + REVCON | Moeller | MSC-R-6,3-M7 | - | 6.3 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 5 | 6.1 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-MW-MSC 024 | F | MSP + REVCON | Moeller | MSC-R-10-M7 | - | 11 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 5 | 6.1 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-MW-MSC 025 | F | MSP + REVCON | Moeller | MSC-R-10-M9 | - | 11 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 10 | 9 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
F-MW-MSC 026 | F | MSP + REVCON | Moeller | MSC-R-10-M17 | - | 11 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 10 | 9 | 915.3562 | 0.52972 | 1, 5, 7 | E36332 V17 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 600Y/347V | 3
Notes:
[1] HP ratings for reference only. Select combination motor controller based on motor full load current and service factor.
[2] Values represent Motor FLC ratings from Table 430-250 or maximum dial setting on combination motor controller

## F-MSP + MC
Issued: 2009-08-13
Last Revised: 2009-08-13
ID Number | Combination Type | Component Type | Component Manufactuer | Component Catalog Desgination | Component Ratings |  |  |  | Combination kA | Combination Volts | Combination Phase | Max. Motor HP Ratings (See Note[1]) | Max. Motor FLC (See Note[2]) | Minimum Enclosure Volume (cu in/ cu Ft) |  | Conditions of Acceptability | Combination UL File Reference
[5 empty] | kA | Max Amps | Volts | Poles
F-M-PKZ+DILM 001 | F | MSP | Moeller | PKZM0-0,16 | 65 | 0,1 - 0,16 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | - | 0.16 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
|  | MC | Moeller | DILM7 | 5 | 7 | 480Y/277V | 3
F-M-PKZ+DILM 002 | F | MSP | Moeller | PKZM0-0,25 | 65 | 0,2 - 0,25 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | - | 0.25 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
|  | MC | Moeller | DILM 7 | 5 | 7 | 480Y/277V | 3
F-M-PKZ+DILM 003 | F | MSP | Moeller | PKZM0-0,4 | 65 | 0,3 - 0,4 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | - | 0.4 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
|  | MC | Moeller | DILM 7 | 5 | 7 | 480Y/277V | 3
F-M-PKZ+DILM 004 | F | MSP | Moeller | PKZM0-0,63 | 65 | 0,4 - 0,63 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | - | 0.6 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
|  | MC | Moeller | DILM 7 | 5 | 7 | 480Y/277V | 3
F-M-PKZ+DILM 005 | F | MSP | Moeller | PKZM0-1 | 65 | 0,6 - 1 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 0.5 | 1 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
|  | MC | Moeller | DILM 7 | 5 | 7 | 480Y/277V | 3
F-M-PKZ+DILM 006 | F | MSP | Moeller | PKZM0-1,6 | 65 | 1 - 1,6 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 0.75 | 1.6 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
|  | MC | Moeller | DILM 7 | 5 | 7 | 480Y/277V | 3
F-M-PKZ+DILM 007 | F | MSP | Moeller | PKZM0-2,5 | 65 | 1,6 - 2,5 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 1 | 2.1 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
|  | MC | Moeller | DILM 7 | 5 | 7 | 480Y/277V | 3
F-M-PKZ+DILM 008 | F | MSP | Moeller | PKZM0-4 | 65 | 2,5 - 4 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 2 | 3.4 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
|  | MC | Moeller | DILM 7 | 5 | 7 | 480Y/277V | 3
F-M-PKZ+DILM 009 | F | MSP | Moeller | PKZM0-6,3 | 65 | 4,0 - 6,3 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 3 | 4.8 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
|  | MC | Moeller | DILM 7 | 5 | 7 | 480Y/277V | 3
F-M-PKZ+DILM 010 | F | MSP | Moeller | PKZM0-10 | 65 | 6,3 - 11 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 5 | 7.6 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
|  | MC | Moeller | DILM 9 | 5 | 9 | 480Y/277V | 3
F-M-PKZ+DILM 011 | F | MSP | Moeller | PKZM0-12 | 18 | 8,0 - 12 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 7.5 | 11 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
|  | MC | Moeller | DILM 12 | 5 | 12 | 480Y/277V | 3
F-M-PKZ+DILM 012 | F | MSP | Moeller | PKZM0-12 | 18 | 8,0 - 12 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 7.5 | 11 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
|  | MC | Moeller | DILM 15 | 5 | 15 | 480Y/277V | 3
F-M-PKZ+DILM 013 | F | MSP | Moeller | PKZM0-16 | 42 | 10,0 - 16 | 480Y/277V | 3 | 18 | 480Y/277V | 3 | 10 | 14 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
|  | MC | Moeller | DILM 17 | 5 | 17 | 480Y/277V | 3
F-M-PKZ+DILM 014 | F | MSP | Moeller | PKZM0-20 | 18 | 16,0 - 20 | 480Y/277V | 3 | 18 | 480Y/277V | 3 | 10 | 14 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
|  | MC | Moeller | DILM 25 | 5 | 25 | 480Y/277V | 3
F-M-PKZ+DILM 015 | F | MSP | Moeller | PKZM0-25 | 18 | 20,0 - 25 | 480Y/277V | 3 | 18 | 480Y/277V | 3 | 15 | 21 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
|  | MC | Moeller | DILM 25 | 5 | 25 | 480Y/277V | 3
F-M-PKZ+DILM 016 | F | MSP | Moeller | PKZM0-32 | 18 | 25,0 - 30 | 480Y/277V | 3 | 18 | 480Y/277V | 3 | 20 | 27 | 915.3562 | 0.52972 | 1, 5 | E123500 V2 S1
|  | Adapter | Moeller | BK25/3-PKZ0-E | - | 60 | 480Y/277V | 3
|  | MC | Moeller | DILM 32 | 5 | 32 | 480Y/277V | 3
F-M-PKZ+DILM026 | F | MSP | Moeller | PKZM4-16 | 50 | 10,0 -16 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 10 | 14 |  | 0.569 | 1, 5 | E123500 V2 S2
|  | Adapter | Moeller | BK50/3-PKZ4-E | - | 60 | 480Y/277V | 3
|  | MC | Moeller | DILM 17 | 5 | 17 | 480Y/277V | 3
F-M-PKZ+DILM027 | F | MSP | Moeller | PKZM4-25 | 50 | 16 - 25 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 15 | 21 |  | 0.569 | 1, 5 | E123500 V2 S2
|  | Adapter | Moeller | BK50/3-PKZ4-E | - | 60 | 480Y/277V | 3
|  | MC | Moeller | DILM 25 | 5 | 25 | 480Y/277V | 3
F-M-PKZ+DILM028 | F | MSP | Moeller | PKZM4-32 | 50 | 25 - 32 | 480Y/277V | 3 | 50 | 480Y/277V | 3 | 20 | 27 |  | 0.569 | 1, 5 | E123500 V2 S2
|  | Adapter | Moeller | BK50/3-PKZ4-E | - | 60 | 480Y/277V | 3
|  | MC | Moeller | DILM 32 | 5 | 32 | 480Y/277V | 3
F-M-PKZ+DILM029 | F | MSP | Moeller | PKZM4-40 | 50 | 32,0 - 40 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 30 | 40 |  | 0.569 | 1, 5 | E123500 V2 S2
|  | Adapter | Moeller | BK50/3-PKZ4-E | - | 60 | 480Y/277V | 3
|  | MC | Moeller | DILM 40 | 10 | 40 | 480Y/277V | 3
F-M-PKZ+DILM030 | F | MSP | Moeller | PKZM4-50 | 65 | 40 - 42 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 30 | 40 |  | 0.569 | 1, 5 | E123500 V2 S2
|  | Adapter | Moeller | BK50/3-PKZ4-E | - | 60 | 480Y/277V | 3
|  | MC | Moeller | DILM 50 | 10 | 50 | 480Y/277V | 3
F-M-PKZ+DILM031 | F | MSP | Moeller | PKZM4-58 | 65 | 50 - 56 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 40 | 52 |  | 0.569 | 1, 5 | E123500 V2 S2
|  | Adapter | Moeller | BK50/3-PKZ4-E | - | 60 | 480Y/277V | 3
|  | MC | Moeller | DILM 65 | 10 | 65 | 480Y/277V | 3
F-M-PKZ+DILM032 | F | MSP | Moeller | PKZM4-63 | 65 | 52 - 58 | 480Y/277V | 3 | 65 | 480Y/277V | 3 | 40 | 52 |  | 0.569 | 1, 5 | E123500 V2 S2
|  | Adapter | Moeller | BK50/3-PKZ4-E | - | 60 | 480Y/277V | 3
|  | MC | Moeller | DILM 65 | 10 | 65 | 480Y/277V | 3
F-M-PKZ+DILM033 | F | MSP | Moeller | PKZM4-16 | 25 | 10,0 - 16 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 10 | 11 |  | 0.569 | 1, 5 | E123500 V2 S2
|  | Adapter | Moeller | BK50/3-PKZ4-E | - | 60 | 600Y/347V | 3
|  | MC | Moeller | DILM 17 | 5 | 17 | 600Y/347V | 3
F-M-PKZ+DILM034 | F | MSP | Moeller | PKZM4-25 | 25 | 16 - 25 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 20 | 22 |  | 0.569 | 1, 5 | E123500 V2 S2
|  | Adapter | Moeller | BK50/3-PKZ4-E | - | 60 | 600Y/347V | 3
|  | MC | Moeller | DILM 25 | 5 | 25 | 600Y/347V | 3
F-M-PKZ+DILM035 | F | MSP | Moeller | PKZM4-32 | 25 | 25 - 32 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 25 | 27 |  | 0.569 | 1, 5 | E123500 V2 S2
|  | Adapter | Moeller | BK50/3-PKZ4-E | - | 60 | 600Y/347V | 3
|  | MC | Moeller | DILM 32 | 5 | 32 | 600Y/347V | 3
F-M-PKZ+DILM036 | F | MSP | Moeller | PKZM4-40 | 25 | 32,0 - 40 | 600Y/347V | 3 | 50 | 600Y/347V | 3 | 30 | 32 |  | 0.569 | 1, 5 | E123500 V2 S2
|  | Adapter | Moeller | BK50/3-PKZ4-E | - | 60 | 600Y/347V | 3
|  | MC | Moeller | DILM 40 | 10 | 40 | 600Y/347V | 3
Notes:
[1] HP ratings for reference only. Select combination motor controller based on motor full load current and service factor.
[2] Values represent Motor FLC ratings from Table 430-250 or maximum dial setting on combination motor controller.
CONDITIONS OF ACCEPTABILITY Unless specified otherwise in the individual Recognitions, consideration is to be given to the following Conditions of Acceptability when these components are employed as a combination motor controller in the end-use equipment: Specific Conditions of Use - Number refers to specific condition number as defined below and number in parenthesis identifies specific information applicable to the combination motor controller. 1. All of the specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume. 2. When specified, the motor controller and overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective devices and other components shall not be installed in this area. 3. When specified, the overload relay heater table number shall be provided with the equipment. 4. Unless otherwise specified, all connections between components are made with insulated wire having an ampacity of 125 percent of the rated motor current and connected to the terminals supplied with the individual components. 5. The need for cautionary markings applicable to high fault short circuit current ratings, Type D and Type E combination motor controllers shall be considered in the end - product application. 6. Additional Conditions of Acceptability may be specified in the individual tables. 7. Type F Combination motor controllers feature pre-fabricated connector links between motor protector and contactor.
8. Units with suffix "/BBA" are mounted on busbar shoes for use in listed and/or recognized busbar systems for ICPs.