## Cont E w MCP (CLT7-CLU7)
Issued: 2010-04-15
Last Revised: 2010-11-08
Database Identification Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability | Combination UL File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP rating | Enclosure Volume, CU inches
CLT7-9…-B2S0.4…-D1AB 200 | E | MSP | Sprecher + Schuh | KTB7-25S-0.4A | 200 | 3 | 65 | 0.4 | - | 200 | 3 | 65 | 0.4/2.4 | - | 665 | 1, 5 and 6a | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | OLR | Sprecher + Schuh | CEP7-ED1AB | 200 | 3 | 5 | 0.5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLT7-9…-B2S0.4…-D1AB 230 | E | MSP | Sprecher + Schuh | KTB7-25S-0.4A | 230 | 3 | 65 | 0.4 | - | 230 | 3 | 65 | 0.4/2.4 | - | 665 | 1, 5 and 6a | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | OLR | Sprecher + Schuh | CEP7-ED1AB | 230 | 3 | 5 | 0.5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLT7-9…-B2S0.4…-D1AB 460 | E | MSP | Sprecher + Schuh | KTB7-25S-0.4A | 460 | 3 | 65 | 0.4 | - | 480Y/277 | 3 | 65 | 0.4/2.4 | - | 665 | 1, 5 and 6a | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | OLR | Sprecher + Schuh | CEP7-ED1AB | 460 | 3 | 5 | 0.5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLT7-9…-B2S0.4…-D1AB 575 | E | MSP | Sprecher + Schuh | KTB7-25S-0.4A | 575 | 3 | 47 | 0.4 | - | 600Y/347 | 3 | 47 | 0.4/2.4 | - | 665 | 1, 5 and 6a | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-9 | 575 | 3 | 5 | 9 | 7.5
|  | OLR | Sprecher + Schuh | CEP7-ED1AB | 575 | 3 | 5 | 0.5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLT7-9…-B2S0.4…-EAB 200 | E | MSP | Sprecher + Schuh | KTB7-25S-0.4A | 200 | 3 | 65 | 0.4 | - | 200 | 3 | 65 | 0.4/2.4 | - | 665 | 1, 5 and 6a | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | OLR | Sprecher + Schuh | CEP7-EEAB | 200 | 3 | 5 | 0.5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLT7-9…-B2S0.4…-EAB 230 | E | MSP | Sprecher + Schuh | KTB7-25S-0.4A | 230 | 3 | 65 | 0.4 | - | 230 | 3 | 65 | 0.4/2.4 | - | 665 | 1, 5 and 6a | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | OLR | Sprecher + Schuh | CEP7-EEAB | 230 | 3 | 5 | 0.5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLT7-9…-B2S0.4…-EAB 460 | E | MSP | Sprecher + Schuh | KTB7-25S-0.4A | 460 | 3 | 65 | 0.4 | - | 480Y/277 | 3 | 65 | 0.4/2.4 | - | 665 | 1, 5 and 6a | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | OLR | Sprecher + Schuh | CEP7-EEAB | 460 | 3 | 5 | 0.5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLT7-9…-B2S0.4…-EAB 575 | E | MSP | Sprecher + Schuh | KTB7-25S-0.4A | 575 | 3 | 47 | 0.4 | - | 600Y/347 | 3 | 47 | 0.4/2.4 | - | 665 | 1, 5 and 6a | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-9 | 575 | 3 | 5 | 9 | 7.5
|  | OLR | Sprecher + Schuh | CEP7-EEAB | 575 | 3 | 5 | 0.5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLT7-9…-B2S1.0…-D1BB 200 | E | MSP | Sprecher + Schuh | KTB7-25S-1.0A | 200 | 3 | 65 | 1 | - | 200 | 3 | 65 | 2010-01-06 | - | 665 | 1, 5 and 6a | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | OLR | Sprecher + Schuh | CEP7-ED1BB | 200 | 3 | 5 | 1 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLT7-9…-B2S1.0…-D1BB 230 | E | MSP | Sprecher + Schuh | KTB7-25S-1.0A | 230 | 3 | 65 | 1 | - | 230 | 3 | 65 | 2010-01-06 | - | 665 | 1, 5 and 6a | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | OLR | Sprecher + Schuh | CEP7-ED1BB | 230 | 3 | 5 | 1 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLT7-9…-B2S1.0…-D1BB 460 | E | MSP | Sprecher + Schuh | KTB7-25S-1.0A | 460 | 3 | 65 | 1 | 0.5 | 480Y/277 | 3 | 65 | 2010-01-06 | - | 665 | 1, 5 and 6a | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | OLR | Sprecher + Schuh | CEP7-ED1BB | 460 | 3 | 5 | 1 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLT7-9…-B2S1.0…-D1BB 575 | E | MSP | Sprecher + Schuh | KTB7-25S-1.0A | 575 | 3 | 47 | 1 | 0.75 | 600Y/347 | 3 | 47 | 0.9 | 2010-01-02 | 665 | 1, 5 and 6a | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-9 | 575 | 3 | 5 | 9 | 7.5
|  | OLR | Sprecher + Schuh | CEP7-ED1BB | 575 | 3 | 5 | 1 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLT7-9…-B2S1.0…-EBB 200 | E | MSP | Sprecher + Schuh | KTB7-25S-1.0A | 200 | 3 | 65 | 1 | - | 200 | 3 | 65 | 2010-01-06 | - | 665 | 1, 5 and 6a | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | OLR | Sprecher + Schuh | CEP7-EEBB | 200 | 3 | 5 | 1 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLT7-9…-B2S1.0…-EBB 230 | E | MSP | Sprecher + Schuh | KTB7-25S-1.0A | 230 | 3 | 65 | 1 | - | 230 | 3 | 65 | 2010-01-06 | - | 665 | 1, 5 and 6a | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | OLR | Sprecher + Schuh | CEP7-EEBB | 230 | 3 | 5 | 1 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLT7-9…-B2S1.0…-EBB 460 | E | MSP | Sprecher + Schuh | KTB7-25S-1.0A | 460 | 3 | 65 | 1 | 0.5 | 480Y/277 | 3 | 65 | 2010-01-06 | - | 665 | 1, 5 and 6a | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | OLR | Sprecher + Schuh | CEP7-EEBB | 460 | 3 | 5 | 1 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLT7-9…-B2S1.0…-EBB 575 | E | MSP | Sprecher + Schuh | KTB7-25S-1.0A | 575 | 3 | 47 | 1 | 0.75 | 600Y/347 | 3 | 47 | 0.9 | 2010-01-02 | 665 | 1, 5 and 6a | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-9 | 575 | 3 | 5 | 9 | 7.5
|  | OLR | Sprecher + Schuh | CEP7-EEBB | 575 | 3 | 5 | 1 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLT7-9…-B2S2.5…-D1CB 200 | E | MSP | Sprecher + Schuh | KTB7-25S-2.5A | 200 | 3 | 65 | 2.5 | - | 200 | 3 | 65 | 2.5 | 2010-01-02 | 665 | 1, 5 and 6a | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | OLR | Sprecher + Schuh | CEP7-ED1CB | 200 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLT7-9…-B2S2.5…-D1CB 230 | E | MSP | Sprecher + Schuh | KTB7-25S-2.5A | 230 | 3 | 65 | 2.5 | 0.75 | 230 | 3 | 65 | 2.2 | 2010-01-02 | 665 | 1, 5 and 6a | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | OLR | Sprecher + Schuh | CEP7-ED1CB | 230 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLT7-9…-B2S2.5…-D1CB 460 | E | MSP | Sprecher + Schuh | KTB7-25S-2.5A | 460 | 3 | 65 | 2.5 | 1.5 | 480Y/277 | 3 | 65 | 2.1 | 1 | 665 | 1, 5 and 6a | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | OLR | Sprecher + Schuh | CEP7-ED1CB | 460 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLT7-9…-B2S2.5…-ECB 200 | E | MSP | Sprecher + Schuh | KTB7-25S-2.5A | 200 | 3 | 65 | 2.5 | - | 200 | 3 | 65 | 2.5 | 2010-01-02 | 665 | 1, 5 and 6a | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | OLR | Sprecher + Schuh | CEP7-EECB | 200 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLT7-9…-B2S2.5…-ECB 230 | E | MSP | Sprecher + Schuh | KTB7-25S-2.5A | 230 | 3 | 65 | 2.5 | 0.75 | 230 | 3 | 65 | 2.2 | 2010-01-02 | 665 | 1, 5 and 6a | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | OLR | Sprecher + Schuh | CEP7-EECB | 230 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLT7-9…-B2S2.5…-ECB 460 | E | MSP | Sprecher + Schuh | KTB7-25S-2.5A | 460 | 3 | 65 | 2.5 | 1.5 | 480Y/277 | 3 | 65 | 2.1 | 1 | 665 | 1, 5 and 6a | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | OLR | Sprecher + Schuh | CEP7-EECB | 460 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLT7-23…-B2H2.5…-D1CB 200 | E | MSP | Sprecher + Schuh | KTB7-25H-2.5A | 200 | 3 | 65 | 2.5 | - | 200 | 3 | 65 | 2.5 | 0.5 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-23 | 200 | 3 | 5 | 17.5 | 5
|  | OLR | Sprecher + Schuh | CEP7-ED1CB | 200 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLT7-23…-B2H2.5…-D1CB 230 | E | MSP | Sprecher + Schuh | KTB7-25H-2.5A | 230 | 3 | 65 | 2.5 | 0.75 | 230 | 3 | 65 | 2.2 | 0.5 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-23 | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Sprecher + Schuh | CEP7-ED1CB | 230 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLT7-23…-B2H2.5…-D1CB 460 | E | MSP | Sprecher + Schuh | KTB7-25H-2.5A | 460 | 3 | 65 | 2.5 | 1.5 | 480Y/277 | 3 | 65 | 2.1 | 1 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-23 | 460 | 3 | 5 | 21 | 15
|  | OLR | Sprecher + Schuh | CEP7-ED1CB | 460 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLT7-23…-B2H2.5…-ECB 200 | E | MSP | Sprecher + Schuh | KTB7-25H-2.5A | 200 | 3 | 65 | 2.5 | - | 200 | 3 | 65 | 2.5 | 0.5 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-23 | 200 | 3 | 5 | 17.5 | 5
|  | OLR | Sprecher + Schuh | CEP7-EECB | 200 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLT7-23…-B2H2.5…-ECB 230 | E | MSP | Sprecher + Schuh | KTB7-25H-2.5A | 230 | 3 | 65 | 2.5 | 0.75 | 230 | 3 | 65 | 2.2 | 0.5 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-23 | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Sprecher + Schuh | CEP7-EECB | 230 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLT7-23…-B2H2.5…-ECB 460 | E | MSP | Sprecher + Schuh | KTB7-25H-2.5A | 460 | 3 | 65 | 2.5 | 1.5 | 480Y/277 | 3 | 65 | 2.1 | 1 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-23 | 460 | 3 | 5 | 21 | 15
|  | OLR | Sprecher + Schuh | CEP7-EECB | 460 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLT7-23…-B2H4.0…-D1CB 200 | E | MSP | Sprecher + Schuh | KTB7-25H-4A | 200 | 3 | 65 | 4 | - | 200 | 3 | 65 | 3.7 | 0.75 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-23 | 200 | 3 | 5 | 17.5 | 5
|  | OLR | Sprecher + Schuh | CEP7-ED1CB | 200 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLT7-23…-B2H4.0…-D1CB 230 | E | MSP | Sprecher + Schuh | KTB7-25H-4A | 230 | 3 | 65 | 4 | 1 | 230 | 3 | 65 | 3.2 | 0.75 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-23 | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Sprecher + Schuh | CEP7-ED1CB | 230 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLT7-23…-B2H4.0…-D1CB 460 | E | MSP | Sprecher + Schuh | KTB7-25H-4A | 460 | 3 | 65 | 4 | 3 | 480Y/277 | 3 | 65 | 3.4 | 2 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-23 | 460 | 3 | 5 | 21 | 15
|  | OLR | Sprecher + Schuh | CEP7-ED1CB | 460 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLT7-23…-B2H4.0…-D1CB 575 | E | MSP | Sprecher + Schuh | KTB7-25H-4A | 575 | 3 | 30 | 4 | 3 | 600Y/347 | 3 | 30 | 3.9 | 3 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-23 | 575 | 3 | 5 | 17 | 15
|  | OLR | Sprecher + Schuh | CEP7-ED1CB | 575 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLT7-23…-B2H4.0…-ECB 200 | E | MSP | Sprecher + Schuh | KTB7-25H-4A | 200 | 3 | 65 | 4 | - | 200 | 3 | 65 | 3.7 | 0.75 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-23 | 200 | 3 | 5 | 17.5 | 5
|  | OLR | Sprecher + Schuh | CEP7-EECB | 200 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLT7-23…-B2H4.0…-ECB 230 | E | MSP | Sprecher + Schuh | KTB7-25H-4A | 230 | 3 | 65 | 4 | 1 | 230 | 3 | 65 | 3.2 | 0.75 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-23 | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Sprecher + Schuh | CEP7-EECB | 230 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLT7-23…-B2H4.0…-ECB 460 | E | MSP | Sprecher + Schuh | KTB7-25H-4A | 460 | 3 | 65 | 4 | 3 | 480Y/277 | 3 | 65 | 3.4 | 2 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-23 | 460 | 3 | 5 | 21 | 15
|  | OLR | Sprecher + Schuh | CEP7-EECB | 460 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLT7-23…-B2H4.0…-ECB 575 | E | MSP | Sprecher + Schuh | KTB7-25H-4A | 575 | 3 | 30 | 4 | 3 | 600Y/347 | 3 | 30 | 3.9 | 3 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-23 | 575 | 3 | 5 | 17 | 15
|  | OLR | Sprecher + Schuh | CEP7-EECB | 575 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLT7-30…B2H10…-EED 200 | E | MSP | Sprecher + Schuh | KTB7-25H-10A | 200 | 3 | 65 | 10 | - | 200 | 3 | 65 | 7.8 | 2 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Sprecher + Schuh | CEP7-EEED | 200 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B2H10…-EED 230 | E | MSP | Sprecher + Schuh | KTB7-25H-10A | 230 | 3 | 65 | 10 | 3 | 230 | 3 | 65 | 9.6 | 3 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Sprecher + Schuh | CEP7-EEED | 230 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B2H10…-EED 460 | E | MSP | Sprecher + Schuh | KTB7-25H-10A | 460 | 3 | 65 | 10 | 7.5 | 480Y/277 | 3 | 65 | 7.6 | 5 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 460 | 3 | 5 | 27 | 20
|  | OLR | Sprecher + Schuh | CEP7-EEED | 460 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B2H10…-EED 575 | E | MSP | Sprecher + Schuh | KTB7-25H-10A | 575 | 3 | 30 | 10 | 10 | 600Y/347 | 3 | 30 | 9 | 7.5 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 575 | 3 | 5 | 27 | 25
|  | OLR | Sprecher + Schuh | CEP7-EEED | 575 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B2H16…-EED 200 | E | MSP | Sprecher + Schuh | KTB7-25H-16A | 200 | 3 | 65 | 16 | - | 200 | 3 | 65 | 11 | 3 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Sprecher + Schuh | CEP7-EEED | 200 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B2H16…-EED 230 | E | MSP | Sprecher + Schuh | KTB7-25H-16A | 230 | 3 | 65 | 16 | 5 | 230 | 3 | 65 | 15.2 | 5 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Sprecher + Schuh | CEP7-EEED | 230 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B2H16…-EED 460 | E | MSP | Sprecher + Schuh | KTB7-25H-16A | 460 | 3 | 65 | 16 | 10 | 480Y/277 | 3 | 65 | 14 | 10 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 460 | 3 | 5 | 27 | 20
|  | OLR | Sprecher + Schuh | CEP7-EEED | 460 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B2H16…-EED 575 | E | MSP | Sprecher + Schuh | KTB7-25H-16A | 575 | 3 | 30 | 16 | 15 | 600Y/347 | 3 | 30 | 11 | 10 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 575 | 3 | 5 | 27 | 25
|  | OLR | Sprecher + Schuh | CEP7-EEED | 575 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B2H25…-EED 200 | E | MSP | Sprecher + Schuh | KTB7-25H-25A | 200 | 3 | 30 | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Sprecher + Schuh | CEP7-EEED | 200 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B2H25…-EED 230 | E | MSP | Sprecher + Schuh | KTB7-25H-25A | 230 | 3 | 30 | 25 | 7.5 | 230 | 3 | 65 | 22 | 7.5 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Sprecher + Schuh | CEP7-EEED | 230 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B2H25…-EED 460 | E | MSP | Sprecher + Schuh | KTB7-25H-25A | 460 | 3 | 30 | 25 | 15 | 480Y/277 | 3 | 65 | 21 | 15 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 460 | 3 | 5 | 27 | 20
|  | OLR | Sprecher + Schuh | CEP7-EEED | 460 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLT7-37…B2H25…-EED 200 | E | MSP | Sprecher + Schuh | KTB7-25H-25A | 200 | 3 | 30 | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Sprecher + Schuh | CEP7-EEED | 200 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLT7-37…B2H25…-EED 230 | E | MSP | Sprecher + Schuh | KTB7-25H-25A | 230 | 3 | 30 | 25 | 7.5 | 230 | 3 | 65 | 22 | 7.5 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Sprecher + Schuh | CEP7-EEED | 230 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLT7-37…B2H25…-EED 460 | E | MSP | Sprecher + Schuh | KTB7-25H-25A | 460 | 3 | 30 | 25 | 15 | 480Y/277 | 3 | 65 | 21 | 15 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 460 | 3 | 5 | 27 | 20
|  | OLR | Sprecher + Schuh | CEP7-EEED | 460 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B4H25…-EED 200 | E | MSP | Sprecher + Schuh | KTB7-45H-25A | 200 | 3 | 65 | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 665 | 1, 5 and 6c | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Sprecher + Schuh | CEP7-EEED | 200 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B4H25…-EED 230 | E | MSP | Sprecher + Schuh | KTB7-45H-25A | 230 | 3 | 65 | 25 | 10 | 230 | 3 | 65 | 22 | 7.5 | 665 | 1, 5 and 6c | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Sprecher + Schuh | CEP7-EEED | 230 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B4H25…-EED 460 | E | MSP | Sprecher + Schuh | KTB7-45H-25A | 460 | 3 | 65 | 25 | 20 | 480Y/277 | 3 | 65 | 21 | 15 | 665 | 1, 5 and 6c | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 460 | 3 | 5 | 27 | 20
|  | OLR | Sprecher + Schuh | CEP7-EEED | 460 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B4H25…-EED 575 | E | MSP | Sprecher + Schuh | KTB7-45H-25A | 575 | 3 | 30 | 25 | 25 | 600Y/347 | 3 | 30 | 22 | 20 | 665 | 1, 5 and 6c | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 575 | 3 | 5 | 27 | 25
|  | OLR | Sprecher + Schuh | CEP7-EEED | 575 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B4H32…-EFD 200 | E | MSP | Sprecher + Schuh | KTB7-45H-32A | 200 | 3 | 65 | 32 | - | 200 | 3 | 65 | 25.3 | 7.5 | 665 | 1, 5 and 6c | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Sprecher + Schuh | CEP7-EEFD | 200 | 3 | 5 | 45 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B4H32…-EFD 230 | E | MSP | Sprecher + Schuh | KTB7-45H-32A | 230 | 3 | 65 | 32 | 10 | 230 | 3 | 65 | 28 | 10 | 665 | 1, 5 and 6c | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Sprecher + Schuh | CEP7-EEFD | 230 | 3 | 5 | 45 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B4H32…-EFD 460 | E | MSP | Sprecher + Schuh | KTB7-45H-32A | 460 | 3 | 65 | 32 | 25 | 480Y/277 | 3 | 65 | 27 | 20 | 665 | 1, 5 and 6c | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 460 | 3 | 5 | 27 | 20
|  | OLR | Sprecher + Schuh | CEP7-EEFD | 460 | 3 | 5 | 45 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B4H32…-EFD 575 | E | MSP | Sprecher + Schuh | KTB7-45H-32A | 575 | 3 | 30 | 32 | 30 | 600Y/347 | 3 | 30 | 27 | 25 | 665 | 1, 5 and 6c | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 575 | 3 | 5 | 27 | 25
|  | OLR | Sprecher + Schuh | CEP7-EEFD | 575 | 3 | 5 | 45 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLT7-37…B4H32…-EFD 200 | E | MSP | Sprecher + Schuh | KTB7-45H-32A | 200 | 3 | 65 | 32 | - | 200 | 3 | 65 | 25.3 | 7.5 | 665 | 1, 5 and 6c | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Sprecher + Schuh | CEP7-EEFD | 200 | 3 | 5 | 45 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLT7-37…B4H32…-EFD 230 | E | MSP | Sprecher + Schuh | KTB7-45H-32A | 230 | 3 | 65 | 32 | 10 | 230 | 3 | 65 | 28 | 10 | 665 | 1, 5 and 6c | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Sprecher + Schuh | CEP7-EEFD | 230 | 3 | 5 | 45 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLT7-37…B4H32…-EFD 460 | E | MSP | Sprecher + Schuh | KTB7-45H-32A | 460 | 3 | 65 | 32 | 25 | 480Y/277 | 3 | 65 | 27 | 20 | 665 | 1, 5 and 6c | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-37 | 460 | 3 | 5 | 34 | 25
|  | OLR | Sprecher + Schuh | CEP7-EEFD | 460 | 3 | 5 | 45 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLT7-37…B4H32…-EFD 575 | E | MSP | Sprecher + Schuh | KTB7-45H-32A | 575 | 3 | 30 | 32 | 30 | 600Y/347 | 3 | 30 | 32 | 30 | 665 | 1, 5 and 6c | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-37 | 575 | 3 | 5 | 32 | 30
|  | OLR | Sprecher + Schuh | CEP7-EEFD | 575 | 3 | 5 | 45 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLT7-37…B4H45…-EFD 200 | E | MSP | Sprecher + Schuh | KTB7-45H-45A | 200 | 3 | 65 | 45 | - | 200 | 3 | 65 | 32.2 | 10 | 665 | 1, 5 and 6c | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Sprecher + Schuh | CEP7-EEFD | 200 | 3 | 5 | 45 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLT7-37…B4H45…-EFD 230 | E | MSP | Sprecher + Schuh | KTB7-45H-45A | 230 | 3 | 65 | 45 | 15 | 230 | 3 | 65 | 28 | 10 | 665 | 1, 5 and 6c | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Sprecher + Schuh | CEP7-EEFD | 230 | 3 | 5 | 45 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLT7-37…B4H45…-EFD 460 | E | MSP | Sprecher + Schuh | KTB7-45H-45A | 460 | 3 | 65 | 45 | 30 | 480Y/277 | 3 | 65 | 34 | 25 | 665 | 1, 5 and 6c | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-37 | 460 | 3 | 5 | 34 | 25
|  | OLR | Sprecher + Schuh | CEP7-EEFD | 460 | 3 | 5 | 45 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLT7-43…-B4H45…-EFD 200 | E | MSP | Sprecher + Schuh | KTB7-45H-45A | 200 | 3 | 65 | 45 | 15 | 200 | 3 | 65 | 32.2 | 10 | 665 | 1, 5 and 6c | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Sprecher + Schuh | CEP7-EEFD | 200 | 3 | 5 | 45 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC43 | 600 | 3 | - | - | -
CLT7-43…-B4H45…-EFD 230 | E | MSP | Sprecher + Schuh | KTB7-45H-45A | 230 | 3 | 65 | 45 | 15 | 230 | 3 | 65 | 42 | 15 | 665 | 1, 5 and 6c | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Sprecher + Schuh | CEP7-EEFD | 230 | 3 | 5 | 45 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC43 | 600 | 3 | - | - | -
CLT7-43…-B4H45…-EFD 460 | E | MSP | Sprecher + Schuh | KTB7-45H-45A | 460 | 3 | 65 | 45 | 30 | 480Y/277 | 3 | 65 | 40 | 30 | 665 | 1, 5 and 6c | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-43 | 460 | 3 | 5 | 40 | 30
|  | OLR | Sprecher + Schuh | CEP7-EEFD | 460 | 3 | 5 | 45 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC43 | 600 | 3 | - | - | -
CLUT7-9…-B2S0.4…-D1AB 200 | E | MSP | Sprecher + Schuh | KTB7-25S-0.4A | 200 | 3 | 65 | 0.4 | - | 200 | 3 | 65 | 0.4/2.4 | - | 1008 | 1, 5 and 6a | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | OLR | Sprecher + Schuh | CEP7-ED1AB | 200 | 3 | 5 | 0.5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLUT7-9…-B2S0.4…-D1AB 230 | E | MSP | Sprecher + Schuh | KTB7-25S-0.4A | 230 | 3 | 65 | 0.4 | - | 230 | 3 | 65 | 0.4/2.4 | - | 1008 | 1, 5 and 6a | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | OLR | Sprecher + Schuh | CEP7-ED1AB | 230 | 3 | 5 | 0.5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLUT7-9…-B2S0.4…-D1AB 460 | E | MSP | Sprecher + Schuh | KTB7-25S-0.4A | 460 | 3 | 65 | 0.4 | - | 480Y/277 | 3 | 65 | 0.4/2.4 | - | 1008 | 1, 5 and 6a | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | OLR | Sprecher + Schuh | CEP7-ED1AB | 460 | 3 | 5 | 0.5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLUT7-9…-B2S0.4…-D1AB 575 | E | MSP | Sprecher + Schuh | KTB7-25S-0.4A | 575 | 3 | 47 | 0.4 | - | 600Y/347 | 3 | 47 | 0.4/2.4 | - | 1008 | 1, 5 and 6a | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 575 | 3 | 5 | 9 | 7.5
|  | OLR | Sprecher + Schuh | CEP7-ED1AB | 575 | 3 | 5 | 0.5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLUT7-9…-B2S0.4…-EAB 200 | E | MSP | Sprecher + Schuh | KTB7-25S-0.4A | 200 | 3 | 65 | 0.4 | - | 200 | 3 | 65 | 0.4/2.4 | - | 1008 | 1, 5 and 6a | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | OLR | Sprecher + Schuh | CEP7-EEAB | 200 | 3 | 5 | 0.5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLUT7-9…-B2S0.4…-EAB 230 | E | MSP | Sprecher + Schuh | KTB7-25S-0.4A | 230 | 3 | 65 | 0.4 | - | 230 | 3 | 65 | 0.4/2.4 | - | 1008 | 1, 5 and 6a | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | OLR | Sprecher + Schuh | CEP7-EEAB | 230 | 3 | 5 | 0.5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLUT7-9…-B2S0.4…-EAB 460 | E | MSP | Sprecher + Schuh | KTB7-25S-0.4A | 460 | 3 | 65 | 0.4 | - | 480Y/277 | 3 | 65 | 0.4/2.4 | - | 1008 | 1, 5 and 6a | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | OLR | Sprecher + Schuh | CEP7-EEAB | 460 | 3 | 5 | 0.5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLUT7-9…-B2S0.4…-EAB 575 | E | MSP | Sprecher + Schuh | KTB7-25S-0.4A | 575 | 3 | 47 | 0.4 | - | 600Y/347 | 3 | 47 | 0.4/2.4 | - | 1008 | 1, 5 and 6a | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 575 | 3 | 5 | 9 | 7.5
|  | OLR | Sprecher + Schuh | CEP7-EEAB | 575 | 3 | 5 | 0.5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLUT7-9…-B2S1.0…-D1BB 200 | E | MSP | Sprecher + Schuh | KTB7-25S-1.0A | 200 | 3 | 65 | 1 | - | 200 | 3 | 65 | 2010-01-06 | - | 1008 | 1, 5 and 6a | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | OLR | Sprecher + Schuh | CEP7-ED1BB | 200 | 3 | 5 | 1 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLUT7-9…-B2S1.0…-D1BB 230 | E | MSP | Sprecher + Schuh | KTB7-25S-1.0A | 230 | 3 | 65 | 1 | - | 230 | 3 | 65 | 2010-01-06 | - | 1008 | 1, 5 and 6a | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | OLR | Sprecher + Schuh | CEP7-ED1BB | 230 | 3 | 5 | 1 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLUT7-9…-B2S1.0…-D1BB 460 | E | MSP | Sprecher + Schuh | KTB7-25S-1.0A | 460 | 3 | 65 | 1 | 0.5 | 480Y/277 | 3 | 65 | 2010-01-06 | - | 1008 | 1, 5 and 6a | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | OLR | Sprecher + Schuh | CEP7-ED1BB | 460 | 3 | 5 | 1 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLUT7-9…-B2S1.0…-D1BB 575 | E | MSP | Sprecher + Schuh | KTB7-25S-1.0A | 575 | 3 | 47 | 1 | 0.75 | 600Y/347 | 3 | 47 | 0.9 | 2010-01-02 | 1008 | 1, 5 and 6a | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 575 | 3 | 5 | 9 | 7.5
|  | OLR | Sprecher + Schuh | CEP7-ED1BB | 575 | 3 | 5 | 1 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLUT7-9…-B2S1.0…-EBB 200 | E | MSP | Sprecher + Schuh | KTB7-25S-1.0A | 200 | 3 | 65 | 1 | - | 200 | 3 | 65 | 2010-01-06 | - | 1008 | 1, 5 and 6a | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | OLR | Sprecher + Schuh | CEP7-EEBB | 200 | 3 | 5 | 1 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLUT7-9…-B2S1.0…-EBB 230 | E | MSP | Sprecher + Schuh | KTB7-25S-1.0A | 230 | 3 | 65 | 1 | - | 230 | 3 | 65 | 2010-01-06 | - | 1008 | 1, 5 and 6a | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | OLR | Sprecher + Schuh | CEP7-EEBB | 230 | 3 | 5 | 1 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLUT7-9…-B2S1.0…-EBB 460 | E | MSP | Sprecher + Schuh | KTB7-25S-1.0A | 460 | 3 | 65 | 1 | 0.5 | 480Y/277 | 3 | 65 | 2010-01-06 | - | 1008 | 1, 5 and 6a | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | OLR | Sprecher + Schuh | CEP7-EEBB | 460 | 3 | 5 | 1 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLUT7-9…-B2S1.0…-EBB 575 | E | MSP | Sprecher + Schuh | KTB7-25S-1.0A | 575 | 3 | 47 | 1 | 0.75 | 600Y/347 | 3 | 47 | 0.9 | 2010-01-02 | 1008 | 1, 5 and 6a | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 575 | 3 | 5 | 9 | 7.5
|  | OLR | Sprecher + Schuh | CEP7-EEBB | 575 | 3 | 5 | 1 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLUT7-9…-B2S2.5…-D1CB 200 | E | MSP | Sprecher + Schuh | KTB7-25S-2.5A | 200 | 3 | 65 | 2.5 | - | 200 | 3 | 65 | 2.5 | 2010-01-02 | 1008 | 1, 5 and 6a | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | OLR | Sprecher + Schuh | CEP7-ED1CB | 200 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLUT7-9…-B2S2.5…-D1CB 230 | E | MSP | Sprecher + Schuh | KTB7-25S-2.5A | 230 | 3 | 65 | 2.5 | 0.75 | 230 | 3 | 65 | 2.2 | 2010-01-02 | 1008 | 1, 5 and 6a | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | OLR | Sprecher + Schuh | CEP7-ED1CB | 230 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLUT7-9…-B2S2.5…-D1CB 460 | E | MSP | Sprecher + Schuh | KTB7-25S-2.5A | 460 | 3 | 65 | 2.5 | 1.5 | 480Y/277 | 3 | 65 | 2.1 | 1 | 1008 | 1, 5 and 6a | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | OLR | Sprecher + Schuh | CEP7-ED1CB | 460 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLUT7-9…-B2S2.5…-ECB 200 | E | MSP | Sprecher + Schuh | KTB7-25S-2.5A | 200 | 3 | 65 | 2.5 | - | 200 | 3 | 65 | 2.5 | 2010-01-02 | 1008 | 1, 5 and 6a | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | OLR | Sprecher + Schuh | CEP7-EECB | 200 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLUT7-9…-B2S2.5…-ECB 230 | E | MSP | Sprecher + Schuh | KTB7-25S-2.5A | 230 | 3 | 65 | 2.5 | 0.75 | 230 | 3 | 65 | 2.2 | 2010-01-02 | 1008 | 1, 5 and 6a | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | OLR | Sprecher + Schuh | CEP7-EECB | 230 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLUT7-9…-B2S2.5…-ECB 460 | E | MSP | Sprecher + Schuh | KTB7-25S-2.5A | 460 | 3 | 65 | 2.5 | 1.5 | 480Y/277 | 3 | 65 | 2.1 | 1 | 1008 | 1, 5 and 6a | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | OLR | Sprecher + Schuh | CEP7-EECB | 460 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLUT7-23…-B2H2.5…-D1CB 200 | E | MSP | Sprecher + Schuh | KTB7-25H-2.5A | 200 | 3 | 65 | 2.5 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1008 | 1, 5 and 6b | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 200 | 3 | 5 | 17.5 | 5
|  | OLR | Sprecher + Schuh | CEP7-ED1CB | 200 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLUT7-23…-B2H2.5…-D1CB 230 | E | MSP | Sprecher + Schuh | KTB7-25H-2.5A | 230 | 3 | 65 | 2.5 | 0.75 | 230 | 3 | 65 | 2.2 | 0.5 | 1008 | 1, 5 and 6b | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Sprecher + Schuh | CEP7-ED1CB | 230 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLUT7-23…-B2H2.5…-D1CB 460 | E | MSP | Sprecher + Schuh | KTB7-25H-2.5A | 460 | 3 | 65 | 2.5 | 1.5 | 480Y/277 | 3 | 65 | 2.1 | 1 | 1008 | 1, 5 and 6b | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 460 | 3 | 5 | 21 | 15
|  | OLR | Sprecher + Schuh | CEP7-ED1CB | 460 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLUT7-23…-B2H2.5.…-ECB 200 | E | MSP | Sprecher + Schuh | KTB7-25H-2.5A | 200 | 3 | 65 | 2.5 | - | 200 | 3 | 65 | 2.5 | 0.5 | 1008 | 1, 5 and 6b | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 200 | 3 | 5 | 17.5 | 5
|  | OLR | Sprecher + Schuh | CEP7-EECB | 200 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLUT7-23…-B2H2.5…-ECB 230 | E | MSP | Sprecher + Schuh | KTB7-25H-2.5A | 230 | 3 | 65 | 2.5 | 0.75 | 230 | 3 | 65 | 2.2 | 0.5 | 1008 | 1, 5 and 6b | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Sprecher + Schuh | CEP7-EECB | 230 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLUT7-23…-B2H2.5…-ECB 460 | E | MSP | Sprecher + Schuh | KTB7-25H-2.5A | 460 | 3 | 65 | 2.5 | 1.5 | 480Y/277 | 3 | 65 | 2.1 | 1 | 1008 | 1, 5 and 6b | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 460 | 3 | 5 | 21 | 15
|  | OLR | Sprecher + Schuh | CEP7-EECB | 460 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLUT7-23…-B2H4.0…-D1CB 200 | E | MSP | Sprecher + Schuh | KTB7-25H-4A | 200 | 3 | 65 | 4 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1008 | 1, 5 and 6b | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 200 | 3 | 5 | 17.5 | 5
|  | OLR | Sprecher + Schuh | CEP7-ED1CB | 200 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLUT7-23…-B2H4.0…-D1CB 230 | E | MSP | Sprecher + Schuh | KTB7-25H-4A | 230 | 3 | 65 | 4 | 1 | 230 | 3 | 65 | 3.2 | 0.75 | 1008 | 1, 5 and 6b | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Sprecher + Schuh | CEP7-ED1CB | 230 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLUT7-23…-B2H4.0…-D1CB 460 | E | MSP | Sprecher + Schuh | KTB7-25H-4A | 460 | 3 | 65 | 4 | 3 | 480Y/277 | 3 | 65 | 3.4 | 2 | 1008 | 1, 5 and 6b | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 460 | 3 | 5 | 21 | 15
|  | OLR | Sprecher + Schuh | CEP7-ED1CB | 460 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLUT7-23…-B2H4.0…-D1CB 575 | E | MSP | Sprecher + Schuh | KTB7-25H-4A | 575 | 3 | 30 | 4 | 3 | 600Y/347 | 3 | 30 | 3.9 | 3 | 1008 | 1, 5 and 6b | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 575 | 3 | 5 | 17 | 15
|  | OLR | Sprecher + Schuh | CEP7-ED1CB | 575 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLUT7-23…-B2H4.0…-ECB 200 | E | MSP | Sprecher + Schuh | KTB7-25H-4A | 200 | 3 | 65 | 4 | - | 200 | 3 | 65 | 3.7 | 0.75 | 1008 | 1, 5 and 6b | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 200 | 3 | 5 | 17.5 | 5
|  | OLR | Sprecher + Schuh | CEP7-EECB | 200 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLUT7-23…-B2H4.0…-ECB 230 | E | MSP | Sprecher + Schuh | KTB7-25H-4A | 230 | 3 | 65 | 4 | 1 | 230 | 3 | 65 | 3.2 | 0.75 | 1008 | 1, 5 and 6b | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 230 | 3 | 5 | 22 | 7.5
|  | OLR | Sprecher + Schuh | CEP7-EECB | 230 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLUT7-23…-B2H4.0…-ECB 460 | E | MSP | Sprecher + Schuh | KTB7-25H-4A | 460 | 3 | 65 | 4 | 3 | 480Y/277 | 3 | 65 | 3.4 | 2 | 1008 | 1, 5 and 6b | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 460 | 3 | 5 | 21 | 15
|  | OLR | Sprecher + Schuh | CEP7-EECB | 460 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLUT7-23…-B2H4.0…-ECB 575 | E | MSP | Sprecher + Schuh | KTB7-25H-4A | 575 | 3 | 30 | 4 | 3 | 600Y/347 | 3 | 30 | 3.9 | 3 | 1008 | 1, 5 and 6b | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 575 | 3 | 5 | 17 | 15
|  | OLR | Sprecher + Schuh | CEP7-EECB | 575 | 3 | 5 | 5 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLT7-30…B2H10…-EED 200 | E | MSP | Sprecher + Schuh | KTB7-25H-10A | 200 | 3 | 65 | 10 | - | 200 | 3 | 65 | 7.8 | 2 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Sprecher + Schuh | CEP7-EEED | 200 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B2H10…-EED 230 | E | MSP | Sprecher + Schuh | KTB7-25H-10A | 230 | 3 | 65 | 10 | 3 | 230 | 3 | 65 | 9.6 | 3 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Sprecher + Schuh | CEP7-EEED | 230 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B2H10…-EED 460 | E | MSP | Sprecher + Schuh | KTB7-25H-10A | 460 | 3 | 65 | 10 | 7.5 | 480Y/277 | 3 | 65 | 7.6 | 5 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 460 | 3 | 5 | 27 | 20
|  | OLR | Sprecher + Schuh | CEP7-EEED | 460 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B2H10…-EED 575 | E | MSP | Sprecher + Schuh | KTB7-25H-10A | 575 | 3 | 30 | 10 | 10 | 600Y/347 | 3 | 30 | 9 | 7.5 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 575 | 3 | 5 | 27 | 25
|  | OLR | Sprecher + Schuh | CEP7-EEED | 575 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B2H16…-EED 200 | E | MSP | Sprecher + Schuh | KTB7-25H-16A | 200 | 3 | 65 | 16 | - | 200 | 3 | 65 | 11 | 3 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Sprecher + Schuh | CEP7-EEED | 200 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B2H16…-EED 230 | E | MSP | Sprecher + Schuh | KTB7-25H-16A | 230 | 3 | 65 | 16 | 5 | 230 | 3 | 65 | 15.2 | 5 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Sprecher + Schuh | CEP7-EEED | 230 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B2H16…-EED 460 | E | MSP | Sprecher + Schuh | KTB7-25H-16A | 460 | 3 | 65 | 16 | 10 | 480Y/277 | 3 | 65 | 14 | 10 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 460 | 3 | 5 | 27 | 20
|  | OLR | Sprecher + Schuh | CEP7-EEED | 460 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B2H16…-EED 575 | E | MSP | Sprecher + Schuh | KTB7-25H-16A | 575 | 3 | 30 | 16 | 15 | 600Y/347 | 3 | 30 | 11 | 10 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 575 | 3 | 5 | 27 | 25
|  | OLR | Sprecher + Schuh | CEP7-EEED | 575 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B2H25…-EED 200 | E | MSP | Sprecher + Schuh | KTB7-25H-25A | 200 | 3 | 30 | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Sprecher + Schuh | CEP7-EEED | 200 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B2H25…-EED 230 | E | MSP | Sprecher + Schuh | KTB7-25H-25A | 230 | 3 | 30 | 25 | 7.5 | 230 | 3 | 65 | 22 | 7.5 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Sprecher + Schuh | CEP7-EEED | 230 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B2H25…-EED 460 | E | MSP | Sprecher + Schuh | KTB7-25H-25A | 460 | 3 | 30 | 25 | 15 | 480Y/277 | 3 | 65 | 21 | 15 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 460 | 3 | 5 | 27 | 10
|  | OLR | Sprecher + Schuh | CEP7-EEED | 460 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B2H25…-EED 200 | E | MSP | Sprecher + Schuh | KTB7-25H-25A | 200 | 3 | 30 | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Sprecher + Schuh | CEP7-EEED | 200 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B2H25…-EED 230 | E | MSP | Sprecher + Schuh | KTB7-25H-25A | 230 | 3 | 30 | 25 | 7.5 | 230 | 3 | 65 | 22 | 7.5 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Sprecher + Schuh | CEP7-EEED | 230 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLT7-30…B2H25…-EED 460 | E | MSP | Sprecher + Schuh | KTB7-25H-25A | 460 | 3 | 30 | 25 | 15 | 480Y/277 | 3 | 65 | 21 | 15 | 665 | 1, 5 and 6b | E125316 V3 S3
|  | MC | Sprecher + Schuh | CA7-30 | 460 | 3 | 5 | 27 | 20
|  | OLR | Sprecher + Schuh | CEP7-EEED | 460 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLUT7-30…B4H25…-EED 200 | E | MSP | Sprecher + Schuh | KTB7-45H-25A | 200 | 3 | 65 | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 1008 | 1, 5 and 6c | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Sprecher + Schuh | CEP7-EEED | 200 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLTU7-30…B4H25…-EED 230 | E | MSP | Sprecher + Schuh | KTB7-45H-25A | 230 | 3 | 65 | 25 | 10 | 230 | 3 | 65 | 22 | 7.5 | 1008 | 1, 5 and 6c | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Sprecher + Schuh | CEP7-EEED | 230 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLUT7-30…B4H25…-EED 460 | E | MSP | Sprecher + Schuh | KTB7-45H-25A | 460 | 3 | 65 | 25 | 20 | 480Y/277 | 3 | 65 | 21 | 15 | 1008 | 1, 5 and 6c | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-30 | 460 | 3 | 5 | 27 | 20
|  | OLR | Sprecher + Schuh | CEP7-EEED | 460 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLUT7-30…B4H25…-EED 575 | E | MSP | Sprecher + Schuh | KTB7-45H-25A | 575 | 3 | 30 | 25 | 25 | 600Y/347 | 3 | 30 | 22 | 20 | 1008 | 1, 5 and 6c | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-30 | 575 | 3 | 5 | 27 | 25
|  | OLR | Sprecher + Schuh | CEP7-EEED | 575 | 3 | 5 | 27 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLUT7-30…B4H32…-EFD 200 | E | MSP | Sprecher + Schuh | KTB7-45H-32A | 200 | 3 | 65 | 32 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1008 | 1, 5 and 6c | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | OLR | Sprecher + Schuh | CEP7-EEFD | 200 | 3 | 5 | 45 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLUT7-30…B4H32…-EFD 230 | E | MSP | Sprecher + Schuh | KTB7-45H-32A | 230 | 3 | 65 | 32 | 10 | 230 | 3 | 65 | 28 | 10 | 1008 | 1, 5 and 6c | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-30 | 230 | 3 | 5 | 28 | 10
|  | OLR | Sprecher + Schuh | CEP7-EEFD | 230 | 3 | 5 | 45 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLUT7-30…B4H32…-EFD 460 | E | MSP | Sprecher + Schuh | KTB7-45H-32A | 460 | 3 | 65 | 32 | 25 | 480Y/277 | 3 | 65 | 27 | 20 | 1008 | 1, 5 and 6c | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-30 | 460 | 3 | 5 | 27 | 20
|  | OLR | Sprecher + Schuh | CEP7-EEFD | 460 | 3 | 5 | 45 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLUT7-30…B4H32…-EFD 575 | E | MSP | Sprecher + Schuh | KTB7-45H-32A | 575 | 3 | 30 | 32 | 30 | 600Y/347 | 3 | 30 | 27 | 25 | 1008 | 1, 5 and 6c | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-30 | 575 | 3 | 5 | 27 | 25
|  | OLR | Sprecher + Schuh | CEP7-EEFD | 575 | 3 | 5 | 45 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLUT7-37…B4H32…-EFD 200 | E | MSP | Sprecher + Schuh | KTB7-45H-32A | 200 | 3 | 65 | 32 | - | 200 | 3 | 65 | 25.3 | 7.5 | 1008 | 1, 5 and 6c | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Sprecher + Schuh | CEP7-EEFD | 200 | 3 | 5 | 45 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLUT7-37…B4H32…-EFD 230 | E | MSP | Sprecher + Schuh | KTB7-45H-32A | 230 | 3 | 65 | 32 | 10 | 230 | 3 | 65 | 28 | 10 | 1008 | 1, 5 and 6c | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Sprecher + Schuh | CEP7-EEFD | 230 | 3 | 5 | 45 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLUT7-37…B4H32…-EFD 460 | E | MSP | Sprecher + Schuh | KTB7-45H-32A | 460 | 3 | 65 | 32 | 25 | 480Y/277 | 3 | 65 | 27 | 20 | 1008 | 1, 5 and 6c | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-37 | 460 | 3 | 5 | 34 | 25
|  | OLR | Sprecher + Schuh | CEP7-EEFD | 460 | 3 | 5 | 45 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLUT7-37…B4H32…-EFD 575 | E | MSP | Sprecher + Schuh | KTB7-45H-32A | 575 | 3 | 30 | 32 | 30 | 600Y/347 | 3 | 30 | 32 | 30 | 1008 | 1, 5 and 6c | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-37 | 575 | 3 | 5 | 32 | 30
|  | OLR | Sprecher + Schuh | CEP7-EEFD | 575 | 3 | 5 | 45 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLUT7-37…B4H45…-EFD 200 | E | MSP | Sprecher + Schuh | KTB7-45H-45A | 200 | 3 | 65 | 45 | - | 200 | 3 | 65 | 32.2 | 10 | 1008 | 1, 5 and 6c | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-37 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Sprecher + Schuh | CEP7-EEFD | 200 | 3 | 5 | 45 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLUT7-37…B4H45…-EFD 230 | E | MSP | Sprecher + Schuh | KTB7-45H-45A | 230 | 3 | 65 | 45 | 10 | 230 | 3 | 65 | 28 | 10 | 1008 | 1, 5 and 6c | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-37 | 230 | 3 | 5 | 28 | 10
|  | OLR | Sprecher + Schuh | CEP7-EEFD | 230 | 3 | 5 | 45 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLUT7-37…B4H45…-EFD 460 | E | MSP | Sprecher + Schuh | KTB7-45H-45A | 460 | 3 | 65 | 45 | 30 | 480Y/277 | 3 | 65 | 34 | 25 | 1008 | 1, 5 and 6c | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-37 | 460 | 3 | 5 | 34 | 25
|  | OLR | Sprecher + Schuh | CEP7-EEFD | 460 | 3 | 5 | 45 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLUT7-43…-B4H45…-EFD 200 | E | MSP | Sprecher + Schuh | KTB7-45H-45A | 200 | 3 | 65 | 45 | - | 200 | 3 | 65 | 32.2 | 10 | 1008 | 1, 5 and 6c | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-43 | 200 | 3 | 5 | 32.2 | 10
|  | OLR | Sprecher + Schuh | CEP7-EEFD | 200 | 3 | 5 | 45 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC43 | 600 | 3 | - | - | -
CLUT7-43…-B4H45…-EFD 230 | E | MSP | Sprecher + Schuh | KTB7-45H-45A | 230 | 3 | 65 | 45 | 15 | 230 | 3 | 65 | 42 | 15 | 1008 | 1, 5 and 6c | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-43 | 230 | 3 | 5 | 42 | 15
|  | OLR | Sprecher + Schuh | CEP7-EEFD | 230 | 3 | 5 | 45 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC43 | 600 | 3 | - | - | -
CLUT7-43…-B4H45…-EFD 460 | E | MSP | Sprecher + Schuh | KTB7-45H-45A | 460 | 3 | 65 | 45 | 30 | 480Y/277 | 3 | 65 | 40 | 30 | 1008 | 1, 5 and 6c | E125316 V3 S3
|  | REVCON | Sprecher + Schuh | CAU7-43 | 460 | 3 | 5 | 40 | 30
|  | OLR | Sprecher + Schuh | CEP7-EEFD | 460 | 3 | 5 | 45 | -
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC43 | 600 | 3 | - | - | -
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = Connection module may be replaced with the wiring indicated in Table 6 for minimum internal power wiring.
Table 6 - Minimum Internal Power Wiring
1/32 in. thick thermoplastic insulation, 600V, rated 105C
|  | Wire Code |  | Wire Size
|  | 6a |  | 12 AWG
|  | 6b |  | 10 AWG
|  | 6c |  | 6 AWG

## Cont. E_F w MCPB (CL7-CLU7)
Issued: 2010-04-23
Last Revised: 2010-11-08
Database Identification Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability | Combination UL File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP rating | Enclosure Volume, CU inches
CL7-9-10-*-AS0.16A-A10 200 | E | MSP | Sprecher + Schuh | KTA7-25S-0.16A | 200 | 3 | 65 | 0.16 | - | 200 | 3 | 65 | 0.16 / 0.96 | - | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.16A-A10 230 | E | MSP | Sprecher + Schuh | KTA7-25S-0.16A | 230 | 3 | 65 | 0.16 | - | 230 | 3 | 65 | 0.16 / 0.96 | - | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.16A-A10 460 | E | MSP | Sprecher + Schuh | KTA7-25S-0.16A | 460 | 3 | 65 | 0.16 | - | 480Y/277 | 3 | 65 | 0.16 / 0.96 | - | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.16A-A10 575 | E | MSP | Sprecher + Schuh | KTA7-25S-0.16A | 575 | 3 | 47 | 0.16 | - | 600Y/347 | 3 | 47 | 0.16 / 0.96 | - | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.25A-A10 200 | E | MSP | Sprecher + Schuh | KTA7-25S-0.25A | 200 | 3 | 65 | 0.25 | - | 200 | 3 | 65 | 0.25 / 1.5 | - | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.25A-A10 230 | E | MSP | Sprecher + Schuh | KTA7-25S-0.25A | 230 | 3 | 65 | 0.25 | - | 230 | 3 | 65 | 0.25 / 1.5 | - | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.25A-A10 460 | E | MSP | Sprecher + Schuh | KTA7-25S-0.25A | 460 | 3 | 65 | 0.25 | - | 480Y/277 | 3 | 65 | 0.25 / 1.5 | - | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.25A-A10 575 | E | MSP | Sprecher + Schuh | KTA7-25S-0.25A | 575 | 3 | 47 | 0.25 | - | 600Y/347 | 3 | 47 | 0.25 / 1.5 | - | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.40A-A10 200 | E | MSP | Sprecher + Schuh | KTA7-25S-0.4A | 200 | 3 | 65 | 0.4 | - | 200 | 3 | 65 | 0.4 / 2.4 | - | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.40A-A10 230 | E | MSP | Sprecher + Schuh | KTA7-25S-0.4A | 230 | 3 | 65 | 0.4 | - | 230 | 3 | 65 | 0.4 / 2.4 | - | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.40A-A10 460 | E | MSP | Sprecher + Schuh | KTA7-25S-0.4A | 460 | 3 | 65 | 0.4 | - | 480Y/277 | 3 | 65 | 0.4 / 2.4 | - | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.40A-A10 575 | E | MSP | Sprecher + Schuh | KTA7-25S-0.4A | 575 | 3 | 47 | 0.4 | - | 600Y/347 | 3 | 47 | 0.4 / 2.4 | - | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.63A-A10 200 | E | MSP | Sprecher + Schuh | KTA7-25S-0.63A | 200 | 3 | 65 | 0.63 | - | 200 | 3 | 65 | 0.63 / 3.78 | - | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.63A-A10 230 | E | MSP | Sprecher + Schuh | KTA7-25S-0.63A | 230 | 3 | 65 | 0.63 | - | 230 | 3 | 65 | 0.63 / 3.78 | - | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.63A-A10 460 | E | MSP | Sprecher + Schuh | KTA7-25S-0.63A | 460 | 3 | 65 | 0.63 | - | 480Y/277 | 3 | 65 | 0.63 / 3.78 | - | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.63A-A10 575 | E | MSP | Sprecher + Schuh | KTA7-25S-0.63A | 575 | 3 | 47 | 0.63 | - | 600Y/347 | 3 | 47 | 0.63 / 3.78 | - | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS1.0A-A10 200 | E | MSP | Sprecher + Schuh | KTA7-25S-1.0A | 200 | 3 | 65 | 1 | - | 200 | 3 | 65 | 1.0 / 6.0 | - | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS1.0A-A10 230 | E | MSP | Sprecher + Schuh | KTA7-25S-1.0A | 230 | 3 | 65 | 1 | - | 230 | 3 | 65 | 1.0 / 6.0 | - | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS1.0A-A10 460 | E | MSP | Sprecher + Schuh | KTA7-25S-1.0A | 460 | 3 | 65 | 1 | 0.5 | 480Y/277 | 3 | 65 | 1 | 0.5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS1.0A-A10 575 | E | MSP | Sprecher + Schuh | KTA7-25S-1.0A | 575 | 3 | 47 | 1 | 0.75 | 600Y/347 | 3 | 47 | 1 | 0.75 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS1.6A-A10 200 | E | MSP | Sprecher + Schuh | KTA7-25S-1.6A | 200 | 3 | 65 | 1.6 | - | 200 | 3 | 65 | 1.6 / 9.6 | - | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS1.6A-A10 230 | E | MSP | Sprecher + Schuh | KTA7-25S-1.6A | 230 | 3 | 65 | 1.6 | - | 230 | 3 | 65 | 1.6 / 9.6 | - | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS1.6A-A10 460 | E | MSP | Sprecher + Schuh | KTA7-25S-1.6A | 460 | 3 | 65 | 1.6 | 1 | 480Y/277 | 3 | 65 | 1.6 | 1 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS1.6A-A10 575 | E | MSP | Sprecher + Schuh | KTA7-25S-1.6A | 575 | 3 | 47 | 1.6 | 1 | 600Y/347 | 3 | 47 | 1.6 | 1 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS2.5A-A10 200 | E | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 200 | 3 | 65 | 2.5 | - | 200 | 3 | 65 | 2.5 | 0.5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS2.5A-A10 230 | E | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 230 | 3 | 65 | 2.5 | 0.75 | 230 | 3 | 65 | 2.5 | 0.75 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS2.5A-A10 460 | E | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 460 | 3 | 65 | 2.5 | 1.5 | 480Y/277 | 3 | 65 | 2.5 | 1.5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS2.5A-A10 575 | F | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 575 | 3 | 30 | 2.5 | 2 | 600Y/347 | 3 | 30 | 2.5 | 2 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS4.0A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 200 | 3 | 65 | 4 | - | 200 | 3 | 65 | 4 | 1 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS4.0A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 230 | 3 | 65 | 4 | 1 | 230 | 3 | 65 | 4 | 1 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS4.0A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 460 | 3 | 65 | 4 | 3 | 480Y/277 | 3 | 65 | 4 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS4.0A-A10 575 | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 575 | 3 | 25 | 4 | 3 | 600Y/347 | 3 | 30 | 3.9 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS6.3A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25S-6.3A | 200 | 3 | 65 | 6.3 | - | 200 | 3 | 65 | 6.3 | 1.5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS6.3A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25S-6.3A | 230 | 3 | 65 | 6.3 | 2 | 230 | 3 | 65 | 6.3 | 2 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS6.3A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25S-6.3A | 460 | 3 | 65 | 6.3 | 5 | 480Y/277 | 3 | 65 | 6.3 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS10A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 200 | 3 | 65 | 10 | - | 200 | 3 | 65 | 7.8 | 2 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS10A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 230 | 3 | 65 | 10 | 3 | 230 | 3 | 65 | 6.8 | 2 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS10A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 460 | 3 | 65 | 10 | 7.5 | 480Y/277 | 3 | 65 | 7.6 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-12-10-*-AS10A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 200 | 3 | 65 | 10 | - | 200 | 3 | 65 | 10 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-12-10-*-AS10A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 230 | 3 | 65 | 10 | 3 | 230 | 3 | 65 | 9.6 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-12 | 230 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-12-10-*-AS10A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 460 | 3 | 65 | 10 | 7.5 | 480Y/277 | 3 | 65 | 10 | 7.5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-16-10-*-AS10A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 200 | 3 | 65 | 10 | - | 200 | 3 | 65 | 10 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-16 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-16-10-*-AS10A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 230 | 3 | 65 | 10 | 3 | 230 | 3 | 65 | 9.6 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | KTA7-25S-10A | 230 | 3 | 5 | 15.2 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-16-10-*-AS10A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 460 | 3 | 65 | 10 | 7.5 | 480Y/277 | 3 | 65 | 10 | 7.5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-16 | 460 | 3 | 5 | 14 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-12-10-*-AS16A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 200 | 3 | 30 | 10 | - | 200 | 3 | 30 | 11 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-12-10-*-AS16A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 230 | 3 | 30 | 10 | 5 | 230 | 3 | 30 | 9.6 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-12 | 230 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-12-10-*-AS16A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 460 | 3 | 30 | 10 | 10 | 480Y/277 | 3 | 30 | 11 | 7.5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-16-10-*-AS16A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 200 | 3 | 30 | 16 | - | 200 | 3 | 30 | 16 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-16 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-16-10-*-AS16A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 230 | 3 | 30 | 16 | 5 | 230 | 3 | 30 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-16 | 230 | 3 | 5 | 15.2 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-16-10-*-AS16A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 460 | 3 | 30 | 16 | 10 | 480Y/277 | 3 | 30 | 14 | 10 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-16 | 460 | 3 | 5 | 14 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-23-10-*-AS16A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 200 | 3 | 30 | 16 | - | 200 | 3 | 30 | 16 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-23 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-23-10-*-AS16A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 230 | 3 | 30 | 16 | 5 | 230 | 3 | 30 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-23 | 230 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-23-10-*-AS16A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 460 | 3 | 30 | 16 | 10 | 480Y/277 | 3 | 30 | 14 | 10 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-23 | 460 | 3 | 5 | 21 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-23-10-*-AS20A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25S-20A | 200 | 3 | 10 | 20 | - | 200 | 3 | 10 | 17.5 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-23 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-23-10-*-AS20A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25S-20A | 230 | 3 | 10 | 20 | 7.5 | 230 | 3 | 10 | 20 | 7.5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-23 | 230 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-23-10-*-AS20A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25S-20A | 460 | 3 | 10 | 20 | 15 | 480Y/277 | 3 | 10 | 20 | 15 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-23 | 460 | 3 | 5 | 21 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH2.5A-A10 200 | E | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 200 | 3 | 65 | 2.5 | - | 200 | 3 | 65 | 2.5 | 0.5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH2.5A-A10 230 | E | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 230 | 3 | 65 | 2.5 | 0.75 | 230 | 3 | 65 | 2.5 | 0.75 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH2.5A-A10 460 | E | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 460 | 3 | 65 | 2.5 | 1.5 | 480Y/277 | 3 | 65 | 2.5 | 1.5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH2.5A-A10 575 | F | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 575 | 3 | 30 | 2.5 | 2 | 600Y/347 | 3 | 30 | 2.5 | 2 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH2.5A-A10 200 | E | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 200 | 3 | 65 | 2.5 | - | 200 | 3 | 65 | 2.5 | 0.5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-23 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH2.5A-A10 230 | E | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 230 | 3 | 65 | 2.5 | 0.75 | 230 | 3 | 65 | 2.5 | 0.75 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-23 | 230 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH2.5A-A10 460 | E | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 460 | 3 | 65 | 2.5 | 1.5 | 480Y/277 | 3 | 65 | 2.5 | 1.5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-23 | 460 | 3 | 5 | 21 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH2.5A-A10 575 | E | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 575 | 3 | 30 | 2.5 | 2 | 600Y/347 | 3 | 30 | 2.5 | 2 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-23 | 575 | 3 | 5 | 17 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH4.0A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 200 | 3 | 65 | 4 | - | 200 | 3 | 65 | 4 | 1 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH4.0A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 230 | 3 | 65 | 4 | 1 | 230 | 3 | 65 | 4 | 1 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH4.0A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 460 | 3 | 65 | 4 | 3 | 480Y/277 | 3 | 65 | 4 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH4.0A-A10 575 | F | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 575 | 3 | 30 | 4 | 3 | 600Y/347 | 3 | 30 | 3.9 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH4.0A-A10 200 | E | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 200 | 3 | 65 | 4 | - | 200 | 3 | 65 | 4 | 1 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-23 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH4.0A-A10 230 | E | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 230 | 3 | 65 | 4 | 1 | 230 | 3 | 65 | 4 | 1 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-23 | 230 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH4.0A-A10 460 | E | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 460 | 3 | 65 | 4 | 3 | 480Y/277 | 3 | 65 | 4 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-23 | 460 | 3 | 5 | 21 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH4.0A-A10 575 | E | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 575 | 3 | 30 | 4 | 3 | 600Y/347 | 3 | 30 | 3.9 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-23 | 575 | 3 | 5 | 17 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH6.3A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25H-6.3A | 200 | 3 | 65 | 6.3 | - | 200 | 3 | 65 | 6.3 | 1.5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH6.3A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25H-6.3A | 230 | 3 | 65 | 6.3 | 2 | 230 | 3 | 65 | 6.3 | 2 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH6.3A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25H-6.3A | 460 | 3 | 65 | 6.3 | 5 | 480Y/277 | 3 | 65 | 6.3 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH6.3A-A10 575 | F | MSP | Sprecher + Schuh | KTA7-25H-6.3A | 575 | 3 | 30 | 6.3 | 5 | 600Y/347 | 3 | 30 | 6.1 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH10A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 200 | 3 | 65 | 9 | - | 200 | 3 | 65 | 7.8 | 2 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH10A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 230 | 3 | 65 | 9 | 3 | 230 | 3 | 65 | 6.8 | 2 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH10A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 460 | 3 | 65 | 9 | 7.5 | 480Y/277 | 3 | 65 | 7.6 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH10A-A10 575 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 575 | 3 | 30 | 9 | 10 | 600Y/347 | 3 | 30 | 9 | 7.5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-12-10-*-AH10A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 200 | 3 | 65 | 10 | - | 200 | 3 | 65 | 10 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-12-10-*-AH10A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 230 | 3 | 65 | 10 | 3 | 230 | 3 | 65 | 9.6 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-12 | 230 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-12-10-*-AH10A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 460 | 3 | 65 | 10 | 7.5 | 480Y/277 | 3 | 65 | 10 | 7.5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-12-10-*-AH10A-A10 575 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 575 | 3 | 30 | 10 | 10 | 600Y/347 | 1 | 30 | 10 | 10 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-12 | 575 | 3 | 5 | 11 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-16-10-*-AH10A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 200 | 3 | 65 | 10 | - | 200 | 3 | 65 | 10 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-16 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-16-10-*-AH10A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 230 | 3 | 65 | 10 | 3 | 230 | 3 | 65 | 9.6 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-16 | 230 | 3 | 5 | 15.2 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-16-10-*-AH10A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 460 | 3 | 65 | 10 | 7.5 | 480Y/277 | 3 | 65 | 10 | 7.5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-16 | 460 | 3 | 5 | 14 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-16-10-*-AH10A-A10 575 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 575 | 3 | 30 | 10 | 10 | 600Y/347 | 3 | 30 | 10 | 10 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-16 | 575 | 3 | 5 | 17 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-12-10-*-AH16A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 200 | 3 | 65 | 12 | - | 200 | 3 | 65 | 11 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-12-10-*-AH16A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 230 | 3 | 65 | 12 | 5 | 230 | 3 | 65 | 9.6 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-12 | 230 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-12-10-*-AH16A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 460 | 3 | 65 | 12 | 10 | 480Y/277 | 3 | 65 | 11 | 7.5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-12-10-*-AH16A-A10 575 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 575 | 3 | 30 | 12 | 15 | 600Y/347 | 3 | 30 | 11 | 10 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-12 | 575 | 3 | 5 | 11 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-16-10-*-AH16A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 200 | 3 | 65 | 16 | - | 200 | 3 | 65 | 16 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-16 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-16-10-*-AH16A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 230 | 3 | 65 | 16 | 5 | 230 | 3 | 65 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-16 | 230 | 3 | 5 | 15.2 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-16-10-*-AH16A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 460 | 3 | 65 | 16 | 10 | 480Y/277 | 3 | 65 | 14 | 10 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-16 | 460 | 3 | 5 | 14 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-16-10-*-AH16A-A10 575 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 575 | 3 | 30 | 16 | 15 | 600Y/347 | 3 | 30 | 11 | 10 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-16 | 575 | 3 | 5 | 17 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH16A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 200 | 3 | 65 | 16 | - | 200 | 3 | 65 | 16 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-23 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH16A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 230 | 3 | 65 | 16 | 5 | 230 | 3 | 65 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-23 | 230 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH16A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 460 | 3 | 65 | 16 | 10 | 480Y/277 | 3 | 65 | 14 | 10 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-23 | 460 | 3 | 5 | 21 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH16A-A10 575 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 575 | 3 | 30 | 16 | 15 | 600Y/347 | 3 | 30 | 16 | 15 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-23 | 575 | 3 | 5 | 17 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH20A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25H-20A | 200 | 3 | 65 | 20 | - | 200 | 3 | 65 | 17.5 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-23 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH20A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25H-20A | 230 | 3 | 65 | 20 | 7.5 | 230 | 3 | 65 | 20 | 7.5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-23 | 230 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH20A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25H-20A | 460 | 3 | 65 | 20 | 15 | 480Y/277 | 3 | 65 | 20 | 15 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-23 | 460 | 3 | 5 | 21 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH25A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25H-25A | 200 | 3 | 65 | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-23 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH25A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25H-25A | 230 | 3 | 65 | 25 | 7.5 | 230 | 3 | 65 | 22 | 7.5 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-23 | 230 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH25A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25H-25A | 460 | 3 | 65 | 25 | 15 | 480Y/277 | 3 | 65 | 21 | 15 | 665 | 1, 5 | E205542 V2 S3
|  | MC | Sprecher + Schuh | CA7-23 | 460 | 3 | 5 | 21 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.16A-A10 200 | E | MSP | Sprecher + Schuh | KTA7-25S-0.16A | 200 | 3 | 65 | 0.16 | - | 200 | 3 | 65 | 0.16 / 0.96 | - | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.16A-A10 230 | E | MSP | Sprecher + Schuh | KTA7-25S-0.16A | 230 | 3 | 65 | 0.16 | - | 230 | 3 | 65 | 0.16 / 0.96 | - | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.16A-A10 460 | E | MSP | Sprecher + Schuh | KTA7-25S-0.16A | 460 | 3 | 65 | 0.16 | - | 480Y/277 | 3 | 65 | 0.16 / 0.96 | - | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.16A-A10 575 | E | MSP | Sprecher + Schuh | KTA7-25S-0.16A | 575 | 3 | 47 | 0.16 | - | 600Y/347 | 3 | 47 | 0.16 / 0.96 | - | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.25A-A10 200 | E | MSP | Sprecher + Schuh | KTA7-25S-0.25A | 200 | 3 | 65 | 0.25 | - | 200 | 3 | 65 | 0.25 / 1.5 | - | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.25A-A10 230 | E | MSP | Sprecher + Schuh | KTA7-25S-0.25A | 230 | 3 | 65 | 0.25 | - | 230 | 3 | 65 | 0.25 / 1.5 | - | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.25A-A10 460 | E | MSP | Sprecher + Schuh | KTA7-25S-0.25A | 460 | 3 | 65 | 0.25 | - | 480Y/277 | 3 | 65 | 0.25 / 1.5 | - | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.25A-A10 575 | E | MSP | Sprecher + Schuh | KTA7-25S-0.25A | 575 | 3 | 47 | 0.25 | - | 600Y/347 | 3 | 47 | 0.25 / 1.5 | - | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.40A-A10 200 | E | MSP | Sprecher + Schuh | KTA7-25S-0.4A | 200 | 3 | 65 | 0.4 | - | 200 | 3 | 65 | 0.4 / 2.4 | - | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.40A-A10 230 | E | MSP | Sprecher + Schuh | KTA7-25S-0.4A | 230 | 3 | 65 | 0.4 | - | 230 | 3 | 65 | 0.4 / 2.4 | - | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.40A-A10 460 | E | MSP | Sprecher + Schuh | KTA7-25S-0.4A | 460 | 3 | 65 | 0.4 | - | 480Y/277 | 3 | 65 | 0.4 / 2.4 | - | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.40A-A10 575 | E | MSP | Sprecher + Schuh | KTA7-25S-0.4A | 575 | 3 | 47 | 0.4 | - | 600Y/347 | 3 | 47 | 0.4 / 2.4 | - | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.63A-A10 200 | E | MSP | Sprecher + Schuh | KTA7-25S-0.63A | 200 | 3 | 65 | 0.63 | - | 200 | 3 | 65 | 0.63 / 3.78 | - | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.63A-A10 230 | E | MSP | Sprecher + Schuh | KTA7-25S-0.63A | 230 | 3 | 65 | 0.63 | - | 230 | 3 | 65 | 0.63 / 3.78 | - | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.63A-A10 460 | E | MSP | Sprecher + Schuh | KTA7-25S-0.63A | 460 | 3 | 65 | 0.63 | - | 480Y/277 | 3 | 65 | 0.63 / 3.78 | - | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.63A-A10 575 | E | MSP | Sprecher + Schuh | KTA7-25S-0.63A | 575 | 3 | 47 | 0.63 | - | 600Y/347 | 3 | 47 | 0.63 / 3.78 | - | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS1.0A-A10 200 | E | MSP | Sprecher + Schuh | KTA7-25S-1.0A | 200 | 3 | 65 | 1 | - | 200 | 3 | 65 | 1.0 / 6.0 | - | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS1.0A-A10 230 | E | MSP | Sprecher + Schuh | KTA7-25S-1.0A | 230 | 3 | 65 | 1 | - | 230 | 3 | 65 | 1.0 / 6.0 | - | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS1.0A-A10 460 | E | MSP | Sprecher + Schuh | KTA7-25S-1.0A | 460 | 3 | 65 | 1 | 0.5 | 480Y/277 | 3 | 65 | 1 | 0.5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS1.0A-A10 575 | E | MSP | Sprecher + Schuh | KTA7-25S-1.0A | 575 | 3 | 47 | 1 | 0.75 | 600Y/347 | 3 | 47 | 1 | 0.75 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS1.6A-A10 200 | E | MSP | Sprecher + Schuh | KTA7-25S-1.6A | 200 | 3 | 65 | 1.6 | - | 200 | 3 | 65 | 1.6 / 9.6 | - | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS1.6A-A10 230 | E | MSP | Sprecher + Schuh | KTA7-25S-1.6A | 230 | 3 | 65 | 1.6 | - | 230 | 3 | 65 | 1.6 / 9.6 | - | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS1.6A-A10 460 | E | MSP | Sprecher + Schuh | KTA7-25S-1.6A | 460 | 3 | 65 | 1.6 | 1 | 480Y/277 | 3 | 65 | 1.6 | 1 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS1.6A-A10 575 | E | MSP | Sprecher + Schuh | KTA7-25S-1.6A | 575 | 3 | 47 | 1.6 | 1 | 600Y/347 | 3 | 47 | 1.6 | 1 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS2.5A-A10 200 | E | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 200 | 3 | 65 | 2.5 | - | 200 | 3 | 65 | 2.5 | 0.5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS2.5A-A10 230 | E | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 230 | 3 | 65 | 2.5 | 0.75 | 230 | 3 | 65 | 2.5 | 0.75 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS2.5A-A10 460 | E | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 460 | 3 | 65 | 2.5 | 1.5 | 480Y/277 | 3 | 65 | 2.5 | 1.5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS2.5A-A10 575 | F | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 575 | 3 | 30 | 2.5 | 2 | 600Y/347 | 3 | 30 | 2.5 | 2 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS4.0A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 200 | 3 | 65 | 4 | - | 200 | 3 | 65 | 4 | 1 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS4.0A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 230 | 3 | 65 | 4 | 1 | 230 | 3 | 65 | 4 | 1 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS4.0A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 460 | 3 | 65 | 4 | 3 | 480Y/277 | 3 | 65 | 4 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS4.0A-A10 575 | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 575 | 3 | 30 | 4 | 3 | 600Y/347 | 3 | 30 | 3.9 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS6.3A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25S-6.3A | 200 | 3 | 65 | 6.3 | - | 200 | 3 | 65 | 6.3 | 1.5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS6.3A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25S-6.3A | 230 | 3 | 65 | 6.3 | 2 | 230 | 3 | 65 | 6.3 | 2 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS6.3A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25S-6.3A | 460 | 3 | 65 | 6.3 | 5 | 480Y/277 | 3 | 65 | 6.3 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS10A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 200 | 3 | 65 | 10 | - | 200 | 3 | 65 | 7.8 | 2 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS10A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 230 | 3 | 65 | 10 | 3 | 230 | 3 | 65 | 6.8 | 2 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS10A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 460 | 3 | 65 | 10 | 7.5 | 480Y/277 | 3 | 65 | 7.6 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-12-10-*-AS10A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 200 | 3 | 65 | 10 | - | 200 | 3 | 65 | 10 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-12-10-*-AS10A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 230 | 3 | 65 | 10 | 3 | 230 | 3 | 65 | 9.6 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-12 | 230 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-12-10-*-AS10A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 460 | 3 | 65 | 10 | 7.5 | 480Y/277 | 3 | 65 | 10 | 7.5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-16-10-*-AS10A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 200 | 3 | 65 | 10 | - | 200 | 3 | 65 | 10 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-16 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-16-10-*-AS10A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 230 | 3 | 65 | 10 | 3 | 230 | 3 | 65 | 9.6 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-16 | 230 | 3 | 5 | 15.2 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-16-10-*-AS10A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 460 | 3 | 65 | 10 | 7.5 | 480Y/277 | 3 | 65 | 10 | 7.5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-16 | 460 | 3 | 5 | 14 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-12-10-*-AS16A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 200 | 3 | 30 | 10 | - | 200 | 3 | 30 | 11 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-12-10-*-AS16A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 230 | 3 | 30 | 10 | 5 | 230 | 3 | 30 | 9.6 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-12 | 230 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-12-10-*-AS16A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 460 | 3 | 30 | 10 | 10 | 480Y/277 | 3 | 30 | 11 | 7.5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-16-10-*-AS16A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 200 | 3 | 30 | 16 | - | 200 | 3 | 30 | 16 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-16 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-16-10-*-AS16A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 230 | 3 | 30 | 16 | 5 | 230 | 3 | 30 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-16 | 230 | 3 | 5 | 15.2 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-16-10-*-AS16A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 460 | 3 | 30 | 16 | 10 | 480Y/277 | 3 | 30 | 14 | 10 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-16 | 460 | 3 | 5 | 14 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AS16A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 200 | 3 | 30 | 16 | - | 200 | 3 | 30 | 16 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AS16A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 230 | 3 | 30 | 16 | 5 | 230 | 3 | 30 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 230 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AS16A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 460 | 3 | 30 | 16 | 10 | 480Y/277 | 3 | 30 | 14 | 10 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 460 | 3 | 5 | 21 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AS20A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25S-20A | 200 | 3 | 10 | 20 | - | 200 | 3 | 10 | 17.5 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AS20A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25S-20A | 230 | 3 | 10 | 20 | 7.5 | 230 | 3 | 10 | 20 | 7.5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 230 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AS20A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25S-20A | 460 | 3 | 10 | 20 | 15 | 480Y/277 | 3 | 10 | 20 | 15 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 460 | 3 | 5 | 21 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH2.5A-A10 200 | E | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 200 | 3 | 65 | 2.5 | - | 200 | 3 | 65 | 2.5 | 0.5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH2.5A-A10 230 | E | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 230 | 3 | 65 | 2.5 | 0.75 | 230 | 3 | 65 | 2.5 | 0.75 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH2.5A-A10 460 | E | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 460 | 3 | 65 | 2.5 | 1.5 | 480Y/277 | 3 | 65 | 2.5 | 1.5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH2.5A-A10 575 | F | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 575 | 3 | 30 | 2.5 | 2 | 600Y/347 | 3 | 30 | 2.5 | 2 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH2.5A-A10 200 | E | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 200 | 3 | 65 | 2.5 | - | 200 | 3 | 65 | 2.5 | 0.5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH2.5A-A10 230 | E | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 230 | 3 | 65 | 2.5 | 0.75 | 230 | 3 | 65 | 2.5 | 0.75 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 230 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH2.5A-A10 460 | E | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 600 | 3 | 65 | 2.5 | 1.5 | 480Y/277 | 3 | 65 | 2.5 | 1.5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 460 | 3 | 5 | 21 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH2.5A-A10 575 | E | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 600 | 3 | 30 | 2.5 | 2 | 600Y/347 | 3 | 30 | 2.5 | 2 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 575 | 3 | 5 | 17 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH4.0A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 200 | 3 | 65 | 4 | - | 200 | 3 | 65 | 4 | 1 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH4.0A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 230 | 3 | 65 | 4 | 1 | 230 | 3 | 65 | 4 | 1 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH4.0A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 460 | 3 | 65 | 4 | 3 | 480Y/277 | 3 | 65 | 4 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH4.0A-A10 575 | F | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 575 | 3 | 30 | 4 | 3 | 600Y/347 | 3 | 30 | 3.9 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH4.0A-A10 200 | E | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 200 | 3 | 65 | 4 | - | 200 | 3 | 65 | 4 | 1 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH4.0A-A10 230 | E | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 230 | 3 | 65 | 4 | 1 | 230 | 3 | 65 | 4 | 1 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 230 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH4.0A-A10 460 | E | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 460 | 3 | 65 | 4 | 3 | 480Y/277 | 3 | 65 | 4 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 460 | 3 | 5 | 21 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH4.0A-A10 575 | E | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 575 | 3 | 30 | 4 | 3 | 600Y/347 | 3 | 30 | 3.9 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 575 | 3 | 5 | 17 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH6.3A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25H-6.3A | 200 | 3 | 65 | 6.3 | - | 200 | 3 | 65 | 6.3 | 1.5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH6.3A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25H-6.3A | 230 | 3 | 65 | 6.3 | 2 | 230 | 3 | 65 | 6.3 | 2 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH6.3A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25H-6.3A | 460 | 3 | 65 | 6.3 | 5 | 480Y/277 | 3 | 65 | 6.3 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH6.3A-A10 575 | F | MSP | Sprecher + Schuh | KTA7-25H-6.3A | 575 | 3 | 30 | 6.3 | 5 | 600Y/347 | 3 | 30 | 6.3 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH10A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 200 | 3 | 65 | 9 | - | 200 | 3 | 65 | 7.8 | 2 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH10A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 230 | 3 | 65 | 9 | 3 | 230 | 3 | 65 | 6.8 | 2 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH10A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 460 | 3 | 65 | 9 | 7.5 | 480Y/277 | 3 | 65 | 7.6 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH10A-A10 575 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 575 | 3 | 30 | 9 | 10 | 600Y/347 | 3 | 30 | 9 | 7.5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-12-10-*-AH10A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 200 | 3 | 65 | 10 | - | 200 | 3 | 65 | 10 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-12-10-*-AH10A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 230 | 3 | 65 | 10 | 3 | 230 | 3 | 65 | 9.6 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-12 | 230 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-12-10-*-AH10A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 460 | 3 | 65 | 10 | 7.5 | 480Y/277 | 3 | 65 | 10 | 7.5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-12-10-*-AH10A-A10 575 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 575 | 3 | 30 | 10 | 10 | 600Y/347 | 1 | 30 | 10 | 10 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-12 | 575 | 3 | 5 | 11 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-16-10-*-AH10A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 200 | 3 | 65 | 10 | - | 200 | 3 | 65 | 10 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-16 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-16-10-*-AH10A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 230 | 3 | 65 | 10 | 3 | 230 | 3 | 65 | 9.6 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-16 | 230 | 3 | 5 | 15.2 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-16-10-*-AH10A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 460 | 3 | 65 | 10 | 7.5 | 480Y/277 | 3 | 65 | 10 | 7.5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-16 | 460 | 3 | 5 | 14 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-16-10-*-AH10A-A10 575 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 575 | 3 | 30 | 10 | 10 | 600Y/347 | 3 | 30 | 10 | 10 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-16 | 575 | 3 | 5 | 17 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-12-10-*-AH16A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 200 | 3 | 65 | 12 | - | 200 | 3 | 65 | 11 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-12-10-*-AH16A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 230 | 3 | 65 | 12 | 5 | 230 | 3 | 65 | 9.6 | 3 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-12 | 230 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-12-10-*-AH16A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 460 | 3 | 65 | 12 | 10 | 480Y/277 | 3 | 65 | 11 | 7.5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-12-10-*-AH16A-A10 575 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 575 | 3 | 30 | 12 | 15 | 600Y/347 | 3 | 30 | 11 | 10 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-12 | 575 | 3 | 5 | 11 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-16-10-*-AH16A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 200 | 3 | 65 | 16 | - | 200 | 3 | 65 | 16 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-16 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-16-10-*-AH16A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 230 | 3 | 65 | 16 | 5 | 230 | 3 | 65 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-16 | 230 | 3 | 5 | 15.2 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-16-10-*-AH16A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 460 | 3 | 65 | 16 | 10 | 480Y/277 | 3 | 65 | 14 | 10 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-16 | 460 | 3 | 5 | 14 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-16-10-*-AH16A-A10 575 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 575 | 3 | 30 | 16 | 15 | 600Y/347 | 3 | 30 | 11 | 10 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-16 | 575 | 3 | 5 | 17 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH16A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 200 | 3 | 65 | 16 | - | 200 | 3 | 65 | 16 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH16A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 230 | 3 | 65 | 16 | 5 | 230 | 3 | 65 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 230 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH16A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 460 | 3 | 65 | 16 | 10 | 480Y/277 | 3 | 65 | 14 | 10 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 460 | 3 | 5 | 21 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH16A-A10 575 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 575 | 3 | 30 | 16 | 15 | 600Y/347 | 3 | 30 | 16 | 15 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 575 | 3 | 5 | 17 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH20A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25H-20A | 200 | 3 | 65 | 20 | - | 200 | 3 | 65 | 17.5 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH20A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25H-20A | 230 | 3 | 65 | 20 | 7.5 | 230 | 3 | 65 | 20 | 7.5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 230 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH20A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25H-20A | 460 | 3 | 65 | 20 | 15 | 480Y/277 | 3 | 65 | 20 | 15 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 460 | 3 | 5 | 21 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH25A-A10 200 | F | MSP | Sprecher + Schuh | KTA7-25H-25A | 200 | 3 | 65 | 25 | - | 200 | 3 | 65 | 17.5 | 5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH25A-A10 230 | F | MSP | Sprecher + Schuh | KTA7-25H-25A | 230 | 3 | 65 | 25 | 7.5 | 230 | 3 | 65 | 22 | 7.5 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 230 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH25A-A10 460 | F | MSP | Sprecher + Schuh | KTA7-25H-25A | 460 | 3 | 65 | 25 | 15 | 480Y/277 | 3 | 65 | 21 | 15 | 665 | 1, 5 | E205542 V2 S3
|  | REVCON | Sprecher + Schuh | CAU7-23 | 460 | 3 | 5 | 21 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PEC23 | 600 | 3 | - | - | -
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches.
Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).

## Cont. E_F w MCPB (CL+7-CLU+7)
Issued: 2010-05-24
Last Revised: 2010-11-08
Database Identification Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability | Combination UL File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP rating | Enclosure Volume, CU inches
CL7-9-10-*-AS0.16A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25S-0.16A | 200 | 3 | 65 | 0.16 | - | 200 | 3 | 65 | 0.16 / 0.96 | - | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.16A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25S-0.16A | 230 | 3 | 65 | 0.16 | - | 230 | 3 | 65 | 0.16 / 0.96 | - | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.16A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-25S-0.16A | 460 | 3 | 65 | 0.16 | - | 480Y/277 | 3 | 65 | 0.16 / 0.96 | - | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.16A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-25S-0.16A | 575 | 3 | 47 | 0.16 | - | 600Y/347 | 3 | 47 | 0.16 / 0.96 | - | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.25A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25S-0.25A | 200 | 3 | 65 | 0.25 | - | 200 | 3 | 65 | 0.25 / 1.5 | - | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.25A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25S-0.25A | 230 | 3 | 65 | 0.25 | - | 230 | 3 | 65 | 0.25 / 1.5 | - | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.25A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-25S-0.25A | 460 | 3 | 65 | 0.25 | - | 480Y/277 | 3 | 65 | 0.25 / 1.5 | - | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.25A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-25S-0.25A | 575 | 3 | 47 | 0.25 | - | 600Y/347 | 3 | 47 | 0.25 / 1.5 | - | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.40A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25S-0.4A | 200 | 3 | 65 | 0.4 | - | 200 | 3 | 65 | 0.4 / 2.4 | - | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.40A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25S-0.4A | 230 | 3 | 65 | 0.4 | - | 230 | 3 | 65 | 0.4 / 2.4 | - | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.40A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-25S-0.4A | 460 | 3 | 65 | 0.4 | - | 480Y/277 | 3 | 65 | 0.4 / 2.4 | - | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.40A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-25S-0.4A | 575 | 3 | 47 | 0.4 | - | 600Y/347 | 3 | 47 | 0.4 / 2.4 | - | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.63A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25S-0.63A | 200 | 3 | 65 | 0.63 | - | 200 | 3 | 65 | 0.63 / 3.78 | - | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.63A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25S-0.63A | 230 | 3 | 65 | 0.63 | - | 230 | 3 | 65 | 0.63 / 3.78 | - | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.63A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-25S-0.63A | 460 | 3 | 65 | 0.63 | - | 480Y/277 | 3 | 65 | 0.63 / 3.78 | - | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS0.63A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-25S-0.63A | 575 | 3 | 47 | 0.63 | - | 600Y/347 | 3 | 47 | 0.63 / 3.78 | - | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS1.0A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25S-1.0A | 200 | 3 | 65 | 1 | - | 200 | 3 | 65 | 1.0 / 6.0 | - | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS1.0A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25S-1.0A | 230 | 3 | 65 | 1 | - | 230 | 3 | 65 | 1.0 / 6.0 | - | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS1.0A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-25S-1.0A | 460 | 3 | 65 | 1 | - | 480Y/277 | 3 | 65 | 1.0 / 6.0 | - | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS1.0A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-25S-1.0A | 575 | 3 | 47 | 1 | - | 600Y/347 | 3 | 47 | 1 | 0.75 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS1.6A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25S-1.6A | 200 | 3 | 65 | 1.6 | - | 200 | 3 | 65 | 1.6 / 9.6 | - | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS1.6A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25S-1.6A | 230 | 3 | 65 | 1.6 | - | 230 | 3 | 65 | 1.6 / 9.6 | - | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS1.6A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-25S-1.6A | 460 | 3 | 65 | 1.6 | - | 480Y/277 | 3 | 65 | 1.6 | 0.75 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS1.6A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-25S-1.6A | 575 | 3 | 47 | 1.6 | - | 600Y/347 | 3 | 47 | 1.3 | 0.75 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS2.5A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 200 | 3 | 65 | 2.5 | - | 200 | 3 | 65 | 2.5 | 0.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS2.5A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 230 | 3 | 65 | 2.5 | - | 230 | 3 | 65 | 2.2 | 0.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS2.5A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 460 | 3 | 65 | 2.5 | - | 480Y/277 | 3 | 65 | 2.1 | 1 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS2.5A-A10-W 575 | F | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 575 | 3 | 30 | 2.5 | - | 600Y/347 | 3 | 30 | 2.4 | 1.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS4.0A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 200 | 3 | 65 | 4 | - | 200 | 3 | 65 | 3.7 | 0.75 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS4.0A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 230 | 3 | 65 | 4 | - | 230 | 3 | 65 | 3.2 | 0.75 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS4.0A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 460 | 3 | 65 | 4 | - | 480Y/277 | 3 | 65 | 3.4 | 2 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS4.0A-A10-W 575 | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 575 | 3 | 30 | 4 | - | 600Y/347 | 3 | 30 | 3.9 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS6.3A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25S-6.3A | 200 | 3 | 65 | 6.3 | - | 200 | 3 | 65 | 4.8 | 1 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS6.3A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25S-6.3A | 230 | 3 | 65 | 6.3 | - | 230 | 3 | 65 | 6 | 1.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS6.3A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25S-6.3A | 460 | 3 | 65 | 6.3 | - | 480Y/277 | 3 | 65 | 4.8 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS10A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 200 | 3 | 65 | 10 | - | 200 | 3 | 65 | 7.8 | 2 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS10A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 230 | 3 | 65 | 10 | - | 230 | 3 | 65 | 6.8 | 2 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AS10A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 460 | 3 | 65 | 10 | - | 480Y/277 | 3 | 65 | 7.6 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-12-10-*-AS10A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 200 | 3 | 65 | 10 | - | 200 | 3 | 65 | 7.8 | 2 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-12-10-*-AS10A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 230 | 3 | 65 | 10 | - | 230 | 3 | 65 | 9.6 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-12 | 230 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-12-10-*-AS10A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 460 | 3 | 65 | 10 | - | 480Y/277 | 3 | 65 | 7.6 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-16-10-*-AS10A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 200 | 3 | 65 | 10 | - | 200 | 3 | 65 | 7.8 | 2 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-16 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-16-10-*-AS10A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 230 | 3 | 65 | 10 | - | 230 | 3 | 65 | 9.6 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-16 | 230 | 3 | 5 | 15.2 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-16-10-*-AS10A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 460 | 3 | 65 | 10 | - | 480Y/277 | 3 | 65 | 7.6 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-16 | 460 | 3 | 5 | 14 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-12-10-*-AS16A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 200 | 3 | 30 | 16 | 5 | 200 | 3 | 30 | 11 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-12-10-*-AS16A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 460 | 3 | 30 | 16 | 10 | 480Y/277 | 3 | 30 | 11 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-16-10-*-AS16A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 200 | 3 | 30 | 16 | 5 | 200 | 3 | 30 | 11 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-16 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-16-10-*-AS16A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 230 | 3 | 30 | 16 | 5 | 230 | 3 | 30 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-16 | 230 | 3 | 5 | 15.2 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-16-10-*-AS16A-A16-W 460 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 460 | 3 | 30 | 16 | 10 | 480Y/277 | 3 | 30 | 14 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-16 | 460 | 3 | 5 | 14 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-23-10-*-AS16A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 200 | 3 | 30 | 16 | - | 200 | 3 | 30 | 11 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-23 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-23-10-*-AS16A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 230 | 3 | 30 | 16 | - | 230 | 3 | 30 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-23 | 230 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-23-10-*-AS16A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 460 | 3 | 30 | 16 | - | 480Y/277 | 3 | 30 | 14 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-23 | 460 | 3 | 5 | 21 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-23-10-*-AS20A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25S-20A | 200 | 3 | 10 | 20 | - | 200 | 3 | 10 | 17.5 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-23 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-23-10-*-AS20A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25S-20A | 230 | 3 | 10 | 20 | - | 230 | 3 | 10 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-23 | 230 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH2.5A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 200 | 3 | 65 | 2.5 | - | 200 | 3 | 65 | 2.5 | 0.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH2.5A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 230 | 3 | 65 | 2.5 | - | 230 | 3 | 65 | 2.2 | 0.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH2.5A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 460 | 3 | 65 | 2.5 | - | 480Y/277 | 3 | 65 | 2.1 | 1 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH2.5A-A10-W 575 | F | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 575 | 3 | 30 | 2.5 | - | 600Y/347 | 3 | 30 | 2.4 | 1.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH2.5A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 200 | 3 | 65 | 2.5 | - | 200 | 3 | 65 | 2.5 | 0.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-23 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH2.5A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 230 | 3 | 65 | 2.5 | - | 230 | 3 | 65 | 2.2 | 0.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-23 | 230 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH2.5A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 460 | 3 | 65 | 2.5 | - | 480Y/277 | 3 | 65 | 2.1 | 1 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-23 | 460 | 3 | 5 | 21 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH2.5A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 575 | 3 | 30 | 2.5 | - | 600Y/347 | 3 | 30 | 2.4 | 1.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-23 | 575 | 3 | 5 | 17 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH4.0A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 200 | 3 | 65 | 4 | - | 200 | 3 | 65 | 3.7 | 0.75 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH4.0A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 230 | 3 | 65 | 4 | - | 230 | 3 | 65 | 3.2 | 0.75 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH4.0A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 460 | 3 | 65 | 4 | - | 480Y/277 | 3 | 65 | 3.4 | 2 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH4.0A-A10-W 575 | F | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 575 | 3 | 30 | 4 | - | 600Y/347 | 3 | 30 | 3.9 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH4.0A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 200 | 3 | 65 | 4 | - | 200 | 3 | 65 | 3.7 | 0.75 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-23 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH4.0A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 230 | 3 | 65 | 4 | - | 230 | 3 | 65 | 3.2 | 0.75 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-23 | 230 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH4.0A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 460 | 3 | 65 | 4 | - | 480Y/277 | 3 | 65 | 3.4 | 2 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-23 | 460 | 3 | 5 | 21 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH4.0A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 575 | 3 | 30 | 4 | - | 600Y/347 | 3 | 30 | 3.9 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-23 | 575 | 3 | 5 | 17 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH6.3A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25H-6.3A | 200 | 3 | 65 | 6.3 | - | 200 | 3 | 65 | 4.8 | 1 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH6.3A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25H-6.3A | 230 | 3 | 65 | 6.3 | - | 230 | 3 | 65 | 6 | 1.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH6.3A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25H-6.3A | 460 | 3 | 65 | 6.3 | - | 480Y/277 | 3 | 65 | 4.8 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH6.3A-A10-W 575 | F | MSP | Sprecher + Schuh | KTA7-25H-6.3A | 575 | 3 | 30 | 6.3 | - | 600Y/347 | 3 | 30 | 6.1 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-30-10-*-A2H6.3A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25H-6.3A | 200 | 3 | 65 | 6.3 | 2 | 200 | 3 | 65 | 4.8 | 1 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 200 | 3 | 5 | 25.2 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-A2H6.3A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25H-6.3A | 230 | 3 | 65 | 6.3 | 2 | 230 | 3 | 65 | 6 | 1.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 230 | 3 | 5 | 28 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-A2H6.3A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-25H-6.3A | 460 | 3 | 65 | 6.3 | 5 | 480Y/277 | 3 | 65 | 4.8 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 460 | 3 | 5 | 27 | 20
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-A2H6.3A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-25H-6.3A | 575 | 3 | 30 | 6.3 | 5 | 600Y/347 | 3 | 30 | 6.1 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 575 | 3 | 5 | 27 | 25
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CL7-9-10-*-AH10A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 200 | 3 | 65 | 9 | - | 200 | 3 | 65 | 7.8 | 2 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH10A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 230 | 3 | 65 | 9 | - | 230 | 3 | 65 | 6.8 | 2 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH10A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 460 | 3 | 65 | 9 | - | 480Y/277 | 3 | 65 | 7.6 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-9-10-*-AH10A-A10-W 575 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 575 | 3 | 30 | 9 | - | 600Y/347 | 3 | 30 | 9 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-12-10-*-AH10A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 200 | 3 | 65 | 10 | - | 200 | 3 | 65 | 7.8 | 2 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-12-10-*-AH10A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 230 | 3 | 65 | 10 | - | 230 | 3 | 65 | 9.6 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-12 | 230 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-12-10-*-AH10A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 460 | 3 | 65 | 10 | - | 480Y/277 | 3 | 65 | 7.6 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-12-10-*-AH10A-A10-W 575 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 575 | 3 | 30 | 10 | - | 600Y/347 | 1 | 30 | 9 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-12 | 575 | 3 | 5 | 11 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-16-10-*-AH10A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 200 | 3 | 65 | 10 | - | 200 | 3 | 65 | 7.8 | 2 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-16 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-16-10-*-AH10A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 230 | 3 | 65 | 10 | - | 230 | 3 | 65 | 9.6 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-16 | 230 | 3 | 5 | 15.2 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-16-10-*-AH10A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 460 | 3 | 65 | 10 | - | 480Y/277 | 3 | 65 | 7.6 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-16 | 460 | 3 | 5 | 14 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-16-10-*-AH10A-A10-W 575 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 575 | 3 | 30 | 10 | - | 600Y/347 | 3 | 30 | 9 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-16 | 575 | 3 | 5 | 17 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-30-10-*-A2H10A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25H-10A | 200 | 3 | 65 | 10 | 3 | 200 | 3 | 65 | 7.8 | 2 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-A2H10A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25H-10A | 230 | 3 | 65 | 10 | 3 | 230 | 3 | 65 | 9.6 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 230 | 3 | 5 | 28 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-A2H10A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-25H-10A | 460 | 3 | 65 | 10 | 7.5 | 480Y/277 | 3 | 65 | 7.6 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 460 | 3 | 5 | 27 | 20
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-A2H10A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-25H-10A | 575 | 3 | 30 | 10 | 10 | 600Y/347 | 3 | 30 | 9 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 575 | 3 | 5 | 27 | 25
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CL7-12-10-*-AH16A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 200 | 3 | 65 | 12 | - | 200 | 3 | 65 | 11 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-12-10-*-AH16A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 460 | 3 | 65 | 12 | - | 480Y/277 | 3 | 65 | 11 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-12-10-*-AH16A-A10-W 575 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 575 | 3 | 30 | 12 | - | 600Y/347 | 3 | 30 | 11 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-12 | 575 | 3 | 5 | 11 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-16-10-*-AH16A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 200 | 3 | 65 | 16 | - | 200 | 3 | 65 | 11 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-16 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-16-10-*-AH16A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 230 | 3 | 65 | 16 | - | 230 | 3 | 65 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-16 | 230 | 3 | 5 | 15.2 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-16-10-*-AH16A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 460 | 3 | 65 | 16 | - | 480Y/277 | 3 | 65 | 14 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-16 | 460 | 3 | 5 | 14 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-16-10-*-AH16A-A10-W 575 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 575 | 3 | 30 | 16 | - | 600Y/347 | 3 | 30 | 11 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-16 | 575 | 3 | 5 | 17 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH16A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 200 | 3 | 65 | 16 | - | 200 | 3 | 65 | 11 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-23 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH16A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 230 | 3 | 65 | 16 | - | 230 | 3 | 65 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-23 | 230 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH16A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 460 | 3 | 65 | 16 | - | 480Y/277 | 3 | 65 | 14 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-23 | 460 | 3 | 5 | 21 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH16A-A10-W 575 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 575 | 3 | 30 | 16 | - | 600Y/347 | 3 | 30 | 11 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-23 | 575 | 3 | 5 | 17 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-30-10-*-A2H16A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25H-16A | 200 | 3 | 65 | 16 | 5 | 200 | 3 | 65 | 11 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-A2H16A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25H-16A | 230 | 3 | 65 | 16 | 5 | 230 | 3 | 65 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 230 | 3 | 5 | 28 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-A2H16A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-25H-16A | 460 | 3 | 65 | 16 | 10 | 480Y/277 | 3 | 65 | 14 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 460 | 3 | 5 | 27 | 20
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-A2H16A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-25H-16A | 575 | 3 | 30 | 16 | 15 | 600Y/347 | 3 | 30 | 11 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 575 | 3 | 5 | 27 | 25
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CL7-23-10-*-AH20A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25H-20A | 200 | 3 | 65 | 20 | - | 200 | 3 | 65 | 17.5 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-23 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH20A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25H-20A | 230 | 3 | 65 | 20 | - | 230 | 3 | 65 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-23 | 230 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-30-10-*-A2H20A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25H-20A | 200 | 3 | 65 | 20 | 7.5 | 200 | 3 | 65 | 17.5 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-A2H20A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25H-20A | 230 | 3 | 65 | 20 | 7.5 | 230 | 3 | 65 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 230 | 3 | 5 | 28 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CL7-23-10-*-AH25A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25H-25A | 230 | 3 | 65 | 25 | - | 230 | 3 | 65 | 22 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-23 | 230 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-23-10-*-AH25A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25H-25A | 460 | 3 | 65 | 25 | - | 480Y/277 | 3 | 65 | 21 | 15 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-23 | 460 | 3 | 5 | 21 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CL7-30-10-*-A2H25A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25H-25A | 200 | 3 | 30 | 25 | 7.5 | 200 | 3 | 65 | 25 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-A2H25A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25H-25A | 230 | 3 | 30 | 25 | 7.5 | 230 | 3 | 65 | 22 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 230 | 3 | 5 | 28 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-A2H25A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-25H-25A | 460 | 3 | 30 | 25 | 15 | 480Y/277 | 3 | 65 | 21 | 15 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 460 | 3 | 5 | 27 | 20
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-AH10A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-45H-10A | 200 | 3 | 65 | 10 | 3 | 200 | 3 | 65 | 7.8 | 2 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-AH10A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-45H-10A | 230 | 3 | 65 | 10 | 3 | 230 | 3 | 65 | 9.6 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 230 | 3 | 5 | 28 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-AH10A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-45H-10A | 460 | 3 | 65 | 10 | 7.5 | 480Y/277 | 3 | 65 | 7.6 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 460 | 3 | 5 | 27 | 20
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-AH10A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-45H-10A | 575 | 3 | 30 | 10 | 10 | 600Y/347 | 3 | 30 | 9 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 575 | 3 | 5 | 27 | 25
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-AH16A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-45H-16A | 200 | 3 | 65 | 16 | 5 | 200 | 3 | 65 | 11 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-AH16A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-45H-16A | 230 | 3 | 65 | 16 | 5 | 230 | 3 | 65 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 230 | 3 | 5 | 28 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-AH16A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-45H-16A | 460 | 3 | 65 | 16 | 10 | 480Y/277 | 3 | 65 | 14 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 460 | 3 | 5 | 27 | 20
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-AH16A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-45H-16A | 575 | 3 | 30 | 16 | 15 | 600Y/347 | 3 | 30 | 11 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 575 | 3 | 5 | 27 | 25
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-AH20A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-45H-20A | 200 | 3 | 65 | 20 | 7.5 | 200 | 3 | 65 | 17.5 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-AH20A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-45H-20A | 230 | 3 | 65 | 20 | 7.5 | 230 | 3 | 65 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 230 | 3 | 5 | 28 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-AH20A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-45H-20A | 575 | 3 | 30 | 20 | 20 | 600Y/347 | 3 | 30 | 17 | 15 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 575 | 3 | 5 | 27 | 25
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-37-10-*-AH20A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-45H-20A | 200 | 3 | 65 | 20 | 7.5 | 200 | 3 | 65 | 17.5 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-37 | 200 | 3 | 5 | 32.2 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-37-10-*-AH20A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-45H-20A | 230 | 3 | 65 | 20 | 7.5 | 230 | 3 | 65 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-37 | 230 | 3 | 5 | 28 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-37-10-*-AH20A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-45H-20A | 575 | 3 | 30 | 20 | 20 | 600Y/347 | 3 | 30 | 17 | 15 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-37 | 575 | 3 | 5 | 32 | 30
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-AH25A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-45H-25A | 200 | 3 | 65 | 25 | 15 | 200 | 3 | 65 | 25 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-AH25A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-45H-25A | 230 | 3 | 65 | 25 | 15 | 230 | 3 | 65 | 22 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 230 | 3 | 5 | 28 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-AH25A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-45H-25A | 460 | 3 | 65 | 25 | 30 | 480Y/277 | 3 | 65 | 21 | 15 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 460 | 3 | 5 | 27 | 20
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-AH25A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-45H-25A | 575 | 3 | 30 | 25 | 25 | 600Y/347 | 3 | 30 | 22 | 20 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 575 | 3 | 5 | 27 | 25
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-37-10-*-AH25A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-45H-25A | 200 | 3 | 65 | 25 | 10 | 200 | 3 | 65 | 25 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-37 | 200 | 3 | 5 | 32.2 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-37-10-*-AH25A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-45H-25A | 230 | 3 | 65 | 25 | 10 | 230 | 3 | 65 | 22 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-37 | 230 | 3 | 5 | 28 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-37-10-*-AH25A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-45H-25A | 460 | 3 | 65 | 25 | 20 | 480Y/277 | 3 | 65 | 21 | 15 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-37 | 460 | 3 | 5 | 34 | 25
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-37-10-*-AH25A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-45H-25A | 575 | 3 | 30 | 25 | 25 | 600Y/347 | 3 | 30 | 22 | 20 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-37 | 575 | 3 | 5 | 32 | 30
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-43-10-*-AH25A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-45H-25A | 200 | 3 | 65 | 25 | 7.5 | 200 | 3 | 65 | 25 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-43 | 200 | 3 | 5 | 32.2 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC43 | 600 | 3 | - | - | -
CL7-43-10-*-AH25A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-45H-25A | 230 | 3 | 65 | 25 | 7.5 | 230 | 3 | 65 | 22 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-43 | 230 | 3 | 5 | 42 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC43 | 600 | 3 | - | - | -
CL7-43-10-*-AH25A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-45H-25A | 460 | 3 | 65 | 25 | 15 | 480Y/277 | 3 | 65 | 21 | 15 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-43 | 460 | 3 | 5 | 40 | 30
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC43 | 600 | 3 | - | - | -
CL7-43-10-*-AH25A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-45H-25A | 575 | 3 | 30 | 25 | 20 | 600Y/347 | 3 | 30 | 22 | 20 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-43 | 575 | 3 | 5 | 32 | 30
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC43 | 600 | 3 | - | - | -
CL7-30-10-*-AH32A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-45H-32A | 200 | 3 | 65 | 32 | 10 | 200 | 3 | 65 | 25.3 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-AH32A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-45H-32A | 230 | 3 | 65 | 32 | 10 | 230 | 3 | 65 | 28 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 230 | 3 | 5 | 28 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-AH32A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-45H-32A | 460 | 3 | 65 | 32 | 25 | 480Y/277 | 3 | 65 | 27 | 20 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 460 | 3 | 5 | 27 | 20
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-30-10-*-AH32A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-45H-32A | 575 | 3 | 0 | 32 | 30 | 600Y/347 | 3 | 30 | 27 | 25 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-30 | 575 | 3 | 5 | 27 | 25
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-37-10-*-AH32A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-45H-32A | 200 | 3 | 65 | 32 | 10 | 200 | 3 | 65 | 32 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-37 | 200 | 3 | 5 | 32.2 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-37-10-*-AH32A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-45H-32A | 230 | 3 | 65 | 32 | 10 | 230 | 3 | 65 | 28 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-37 | 230 | 3 | 5 | 28 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-37-10-*-AH32A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-45H-32A | 460 | 3 | 65 | 32 | 25 | 480Y/277 | 3 | 65 | 27 | 20 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-37 | 460 | 3 | 5 | 34 | 25
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-37-10-*-AH32A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-45H-32A | 575 | 3 | 30 | 32 | 30 | 600Y/347 | 3 | 30 | 32 | 30 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-37 | 575 | 3 | 5 | 32 | 30
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-43-10-*-AH32A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-45H-32A | 200 | 3 | 65 | 32 | 10 | 200 | 3 | 65 | 32 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-43 | 200 | 3 | 5 | 32.2 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC43 | 600 | 3 | - | - | -
CL7-43-10-*-AH32A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-45H-32A | 230 | 3 | 65 | 32 | 10 | 230 | 3 | 65 | 28 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-43 | 230 | 3 | 5 | 42 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC43 | 600 | 3 | - | - | -
CL7-43-10-*-AH32A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-45H-32A | 460 | 3 | 65 | 32 | 25 | 480Y/277 | 3 | 65 | 27 | 20 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-43 | 460 | 3 | 5 | 40 | 30
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC43 | 600 | 3 | - | - | -
CL7-43-10-*-AH32A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-45H-32A | 575 | 3 | 30 | 32 | 20 | 600Y/347 | 3 | 30 | 32 | 30 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-43 | 575 | 3 | 5 | 32 | 30
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC43 | 600 | 3 | - | - | -
CL7-37-10-*-AH45A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-45H-45A | 200 | 3 | 65 | 45 | 15 | 200 | 3 | 65 | 32.2 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-37 | 200 | 3 | 5 | 32.2 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-37-10-*-AH45A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-45H-45A | 460 | 3 | 65 | 45 | 30 | 480Y/277 | 3 | 65 | 34 | 25 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-37 | 460 | 3 | 5 | 34 | 25
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CL7-43-10-*-AH45A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-45H-45A | 200 | 3 | 65 | 45 | 15 | 200 | 3 | 65 | 32 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-43 | 200 | 3 | 5 | 32.2 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC43 | 600 | 3 | - | - | -
CL7-43-10-*-AH45A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-45H-45A | 230 | 3 | 65 | 45 | 15 | 230 | 3 | 65 | 42 | 15 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-43 | 230 | 3 | 5 | 42 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC43 | 600 | 3 | - | - | -
CL7-43-10-*-AH45A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-45H-45A | 460 | 3 | 65 | 45 | 30 | 480Y/277 | 3 | 65 | 40 | 30 | 665 | 1, 5 | E205542 V2 S2
|  | MC | Sprecher + Schuh | CA7-43 | 460 | 3 | 5 | 40 | 30
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC43 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.16A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25S-0.16A | 200 | 3 | 65 | 0.16 | - | 200 | 3 | 65 | 0.16 / 0.96 | - | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.16A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25S-0.16A | 230 | 3 | 65 | 0.16 | - | 230 | 3 | 65 | 0.16 / 0.96 | - | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.16A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-25S-0.16A | 460 | 3 | 65 | 0.16 | - | 480Y/277 | 3 | 65 | 0.16 / 0.96 | - | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.16A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-25S-0.16A | 575 | 3 | 47 | 0.16 | - | 600Y/347 | 3 | 47 | 0.16 / 0.96 | - | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.25A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25S-0.25A | 200 | 3 | 65 | 0.25 | - | 200 | 3 | 65 | 0.25 / 1.5 | - | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.25A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25S-0.25A | 230 | 3 | 65 | 0.25 | - | 230 | 3 | 65 | 0.25 / 1.5 | - | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.25A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-25S-0.25A | 460 | 3 | 65 | 0.25 | - | 480Y/277 | 3 | 65 | 0.25 / 1.5 | - | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.25A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-25S-0.25A | 575 | 3 | 47 | 0.25 | - | 600Y/347 | 3 | 47 | 0.25 / 1.5 | - | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.40A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25S-0.4A | 200 | 3 | 65 | 0.4 | - | 200 | 3 | 65 | 0.4 / 2.4 | - | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.40A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25S-0.4A | 230 | 3 | 65 | 0.4 | - | 230 | 3 | 65 | 0.4 / 2.4 | - | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.40A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-25S-0.4A | 460 | 3 | 65 | 0.4 | - | 480Y/277 | 3 | 65 | 0.4 / 2.4 | - | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.40A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-25S-0.4A | 575 | 3 | 47 | 0.4 | - | 600Y/347 | 3 | 47 | 0.4 / 2.4 | - | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.63A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25S-0.63A | 200 | 3 | 65 | 0.63 | - | 200 | 3 | 65 | 0.63 / 3.78 | - | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.63A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25S-0.63A | 230 | 3 | 65 | 0.63 | - | 230 | 3 | 65 | 0.63 / 3.78 | - | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.63A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-25S-0.63A | 460 | 3 | 65 | 0.63 | - | 480Y/277 | 3 | 65 | 0.63 / 3.78 | - | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS0.63A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-25S-0.63A | 575 | 3 | 47 | 0.63 | - | 600Y/347 | 3 | 47 | 0.63 / 3.78 | - | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS1.0A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25S-1.0A | 200 | 3 | 65 | 1 | - | 200 | 3 | 65 | 1.0 / 6.0 | - | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS1.0A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25S-1.0A | 230 | 3 | 65 | 1 | - | 230 | 3 | 65 | 1.0 / 6.0 | - | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS1.0A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-25S-1.0A | 460 | 3 | 65 | 1 | - | 480Y/277 | 3 | 65 | 1.0 / 6.0 | - | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS1.0A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-25S-1.0A | 575 | 3 | 47 | 1 | - | 600Y/347 | 3 | 47 | 0.9 | 0.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS1.6A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25S-1.6A | 200 | 3 | 65 | 1.6 | - | 200 | 3 | 65 | 1.6 / 9.6 | - | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS1.6A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25S-1.6A | 230 | 3 | 65 | 1.6 | - | 230 | 3 | 65 | 1.6 / 9.6 | - | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS1.6A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-25S-1.6A | 460 | 3 | 65 | 1.6 | - | 480Y/277 | 3 | 65 | 1.6 | 0.75 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS1.6A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-25S-1.6A | 575 | 3 | 47 | 1.6 | - | 600Y/347 | 3 | 47 | 1.3 | 0.75 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS2.5A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 200 | 3 | 65 | 2.5 | - | 200 | 3 | 65 | 2.5 | 0.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS2.5A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 230 | 3 | 65 | 2.5 | - | 230 | 3 | 65 | 2.2 | 0.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS2.5A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 460 | 3 | 65 | 2.5 | - | 480Y/277 | 3 | 65 | 2.1 | 1 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS2.5A-A10-W 575 | F | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 575 | 3 | 30 | 2.5 | - | 600Y/347 | 3 | 30 | 2.4 | 1.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS4.0A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 200 | 3 | 65 | 4 | - | 200 | 3 | 65 | 3.7 | 0.75 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS4.0A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 230 | 3 | 65 | 4 | - | 230 | 3 | 65 | 3.2 | 0.75 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS4.0A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 460 | 3 | 65 | 4 | - | 480Y/277 | 3 | 65 | 3.4 | 2 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS4.0A-A10-W 575 | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 575 | 3 | 30 | 4 | - | 600Y/347 | 3 | 30 | 3.9 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS6.3A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25S-6.3A | 200 | 3 | 65 | 6.3 | - | 200 | 3 | 65 | 4.8 | 1 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS6.3A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25S-6.3A | 230 | 3 | 65 | 6.3 | - | 230 | 3 | 65 | 6 | 1.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS6.3A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25S-6.3A | 460 | 3 | 65 | 6.3 | - | 480Y/277 | 3 | 65 | 4.8 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS10A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 200 | 3 | 65 | 10 | - | 200 | 3 | 65 | 7.8 | 2 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS10A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 230 | 3 | 65 | 10 | - | 230 | 3 | 65 | 6.8 | 2 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AS10A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 460 | 3 | 65 | 10 | - | 480Y/277 | 3 | 65 | 7.6 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-12-10-*-AS10A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 200 | 3 | 65 | 10 | - | 200 | 3 | 65 | 7.8 | 2 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-12-10-*-AS10A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 230 | 3 | 65 | 10 | - | 230 | 3 | 65 | 9.6 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-12 | 230 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-12-10-*-AS10A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 460 | 3 | 65 | 10 | - | 480Y/277 | 3 | 65 | 7.6 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-16-10-*-AS10A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 200 | 3 | 65 | 10 | - | 200 | 3 | 65 | 7.8 | 2 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-16 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-16-10-*-AS10A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 230 | 3 | 65 | 10 | - | 230 | 3 | 65 | 9.6 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-16 | 230 | 3 | 5 | 15.2 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-16-10-*-AS10A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 460 | 3 | 65 | 10 | - | 480Y/277 | 3 | 65 | 7.6 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-16 | 460 | 3 | 5 | 14 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-12-10-*-AS16A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 200 | 3 | 30 | 16 | 5 | 200 | 3 | 30 | 11 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-12-10-*-AS16A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 460 | 3 | 30 | 16 | 10 | 480Y/277 | 3 | 30 | 11 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-16-10-*-AS16A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 200 | 3 | 30 | 16 | 5 | 200 | 3 | 30 | 11 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-16 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-16-10-*-AS16A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 230 | 3 | 30 | 16 | 5 | 230 | 3 | 30 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-16 | 230 | 3 | 5 | 15.2 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-16-10-*-AS16A-A16-W 460 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 460 | 3 | 30 | 16 | 10 | 480Y/277 | 3 | 30 | 14 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-16 | 460 | 3 | 5 | 14 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AS16A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 200 | 3 | 30 | 16 | - | 200 | 3 | 30 | 11 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-23 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AS16A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 230 | 3 | 30 | 16 | - | 230 | 3 | 30 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-23 | 230 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AS16A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 460 | 3 | 30 | 16 | - | 480Y/277 | 3 | 30 | 14 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-23 | 460 | 3 | 5 | 21 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AS20A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25S-20A | 200 | 3 | 10 | 20 | - | 200 | 3 | 10 | 17.5 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-23 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AS20A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25S-20A | 230 | 3 | 10 | 20 | - | 230 | 3 | 10 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-23 | 230 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH2.5A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 200 | 3 | 65 | 2.5 | - | 200 | 3 | 65 | 2.5 | 0.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH2.5A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 230 | 3 | 65 | 2.5 | - | 230 | 3 | 65 | 2.2 | 0.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH2.5A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 460 | 3 | 65 | 2.5 | - | 480Y/277 | 3 | 65 | 2.1 | 1 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH2.5A-A10-W 575 | F | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 575 | 3 | 30 | 2.5 | - | 600Y/347 | 3 | 30 | 2.4 | 1.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH2.5A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 200 | 3 | 65 | 2.5 | - | 200 | 3 | 65 | 2.5 | 0.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-23 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH2.5A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 230 | 3 | 65 | 2.5 | - | 230 | 3 | 65 | 2.2 | 0.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-23 | 230 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH2.5A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 460 | 3 | 65 | 2.5 | - | 480Y/277 | 3 | 65 | 2.1 | 1 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-23 | 460 | 3 | 5 | 21 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH2.5A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-25H-2.5A | 575 | 3 | 30 | 2.5 | - | 600Y/347 | 3 | 30 | 2.4 | 1.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-23 | 575 | 3 | 5 | 17 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH4.0A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 200 | 3 | 65 | 4 | - | 200 | 3 | 65 | 3.7 | 0.75 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH4.0A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 230 | 3 | 65 | 4 | - | 230 | 3 | 65 | 3.2 | 0.75 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH4.0A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 460 | 3 | 65 | 4 | - | 480Y/277 | 3 | 65 | 3.4 | 2 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH4.0A-A10-W 575 | F | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 575 | 3 | 30 | 4 | - | 600Y/347 | 3 | 30 | 3.9 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH4.0A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 200 | 3 | 65 | 4 | - | 200 | 3 | 65 | 3.7 | 0.75 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-23 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH4.0A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 230 | 3 | 65 | 4 | - | 230 | 3 | 65 | 3.2 | 0.75 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-23 | 230 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH4.0A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 460 | 3 | 65 | 4 | - | 480Y/277 | 3 | 65 | 3.4 | 2 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-23 | 460 | 3 | 5 | 21 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH4.0A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-25H-4.0A | 575 | 3 | 30 | 4 | - | 600Y/347 | 3 | 30 | 3.9 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-23 | 575 | 3 | 5 | 17 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH6.3A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25H-6.3A | 200 | 3 | 65 | 6.3 | - | 200 | 3 | 65 | 4.8 | 1 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH6.3A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25H-6.3A | 230 | 3 | 65 | 6.3 | - | 230 | 3 | 65 | 6 | 1.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH6.3A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25H-6.3A | 460 | 3 | 65 | 6.3 | - | 480Y/277 | 3 | 65 | 4.8 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH6.3A-A10-W 575 | F | MSP | Sprecher + Schuh | KTA7-25H-6.3A | 575 | 3 | 30 | 6.3 | - | 600Y/347 | 3 | 30 | 6.1 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-30-10-*-A2H6.3A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25H-6.3A | 200 | 3 | 65 | 6.3 | 2 | 200 | 3 | 65 | 4.8 | 1 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 200 | 3 | 5 | 25.2 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-A2H6.3A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25H-6.3A | 230 | 3 | 65 | 6.3 | 2 | 230 | 3 | 65 | 6 | 1.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 230 | 3 | 5 | 28 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-A2H6.3A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-25H-6.3A | 460 | 3 | 65 | 6.3 | 5 | 480Y/277 | 3 | 65 | 4.8 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 460 | 3 | 5 | 27 | 20
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-A2H6.3A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-25H-6.3A | 575 | 3 | 30 | 6.3 | 5 | 600Y/347 | 3 | 30 | 6.1 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 575 | 3 | 5 | 27 | 25
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLU7-9-10-*-AH10A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 200 | 3 | 65 | 9 | - | 200 | 3 | 65 | 7.8 | 2 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH10A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 230 | 3 | 65 | 9 | - | 230 | 3 | 65 | 6.8 | 2 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH10A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 460 | 3 | 65 | 9 | - | 480Y/277 | 3 | 65 | 7.6 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-9-10-*-AH10A-A10-W 575 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 575 | 3 | 30 | 9 | - | 600Y/347 | 3 | 30 | 9 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-9 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-12-10-*-AH10A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 200 | 3 | 65 | 10 | - | 200 | 3 | 65 | 7.8 | 2 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-12-10-*-AH10A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 230 | 3 | 65 | 10 | - | 230 | 3 | 65 | 9.6 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-12 | 230 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-12-10-*-AH10A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 460 | 3 | 65 | 10 | - | 480Y/277 | 3 | 65 | 7.6 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-12-10-*-AH10A-A10-W 575 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 575 | 3 | 30 | 10 | - | 600Y/347 | 1 | 30 | 9 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-12 | 575 | 3 | 5 | 11 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-16-10-*-AH10A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 200 | 3 | 65 | 10 | - | 200 | 3 | 65 | 7.8 | 2 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-16 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-16-10-*-AH10A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 230 | 3 | 65 | 10 | - | 230 | 3 | 65 | 9.6 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-16 | 230 | 3 | 5 | 15.2 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-16-10-*-AH10A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 460 | 3 | 65 | 10 | - | 480Y/277 | 3 | 65 | 7.6 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-16 | 460 | 3 | 5 | 14 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-16-10-*-AH10A-A10-W 575 | F | MSP | Sprecher + Schuh | KTA7-25H-10A | 575 | 3 | 30 | 10 | - | 600Y/347 | 3 | 30 | 9 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-16 | 575 | 3 | 5 | 17 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-30-10-*-A2H10A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25H-10A | 200 | 3 | 65 | 10 | 3 | 200 | 3 | 65 | 7.8 | 2 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-A2H10A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25H-10A | 230 | 3 | 65 | 10 | 3 | 230 | 3 | 65 | 9.6 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 230 | 3 | 5 | 28 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-A2H10A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-25H-10A | 460 | 3 | 65 | 10 | 7.5 | 480Y/277 | 3 | 65 | 7.6 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 460 | 3 | 5 | 27 | 20
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-A2H10A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-25H-10A | 575 | 3 | 30 | 10 | 10 | 600Y/347 | 3 | 30 | 9 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 575 | 3 | 5 | 27 | 25
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLU7-12-10-*-AH16A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 200 | 3 | 65 | 12 | - | 200 | 3 | 65 | 11 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-12-10-*-AH16A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 460 | 3 | 65 | 12 | - | 480Y/277 | 3 | 65 | 11 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-12-10-*-AH16A-A10-W 575 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 575 | 3 | 30 | 12 | - | 600Y/347 | 3 | 30 | 11 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-12 | 575 | 3 | 5 | 11 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-16-10-*-AH16A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 200 | 3 | 65 | 16 | - | 200 | 3 | 65 | 11 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-16 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-16-10-*-AH16A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 230 | 3 | 65 | 16 | - | 230 | 3 | 65 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-16 | 230 | 3 | 5 | 15.2 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-16-10-*-AH16A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 460 | 3 | 65 | 16 | - | 480Y/277 | 3 | 65 | 14 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-16 | 460 | 3 | 5 | 14 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-16-10-*-AH16A-A10-W 575 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 575 | 3 | 30 | 16 | - | 600Y/347 | 3 | 30 | 11 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-16 | 575 | 3 | 5 | 17 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH16A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 200 | 3 | 65 | 16 | - | 200 | 3 | 65 | 11 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-23 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH16A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 230 | 3 | 65 | 16 | - | 230 | 3 | 65 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-23 | 230 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH16A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 460 | 3 | 65 | 16 | - | 480Y/277 | 3 | 65 | 14 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-23 | 460 | 3 | 5 | 21 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH16A-A10-W 575 | F | MSP | Sprecher + Schuh | KTA7-25H-16A | 575 | 3 | 30 | 16 | - | 600Y/347 | 3 | 30 | 11 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-23 | 575 | 3 | 5 | 17 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-30-10-*-A2H16A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25H-16A | 200 | 3 | 65 | 16 | 5 | 200 | 3 | 65 | 11 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-A2H16A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25H-16A | 230 | 3 | 65 | 16 | 5 | 230 | 3 | 65 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 230 | 3 | 5 | 28 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-A2H16A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-25H-16A | 460 | 3 | 65 | 16 | 10 | 480Y/277 | 3 | 65 | 14 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 460 | 3 | 5 | 27 | 20
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-A2H16A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-25H-16A | 575 | 3 | 30 | 16 | 15 | 600Y/347 | 3 | 30 | 11 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 575 | 3 | 5 | 27 | 25
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLU7-23-10-*-AH20A-A10-W 200 | F | MSP | Sprecher + Schuh | KTA7-25H-20A | 200 | 3 | 65 | 20 | - | 200 | 3 | 65 | 17.5 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-23 | 200 | 3 | 5 | 17.5 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH20A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25H-20A | 230 | 3 | 65 | 20 | - | 230 | 3 | 65 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-23 | 230 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-30-10-*-A2H20A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25H-20A | 200 | 3 | 65 | 20 | 7.5 | 200 | 3 | 65 | 17.5 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-A2H20A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25H-20A | 230 | 3 | 65 | 20 | 7.5 | 230 | 3 | 65 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 230 | 3 | 5 | 28 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLU7-23-10-*-AH25A-A10-W 230 | F | MSP | Sprecher + Schuh | KTA7-25H-25A | 230 | 3 | 65 | 25 | - | 230 | 3 | 65 | 22 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-23 | 230 | 3 | 5 | 22 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-23-10-*-AH25A-A10-W 460 | F | MSP | Sprecher + Schuh | KTA7-25H-25A | 460 | 3 | 65 | 25 | - | 480Y/277 | 3 | 65 | 21 | 15 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-23 | 460 | 3 | 5 | 21 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC23 | 600 | 3 | - | - | -
CLU7-30-10-*-A2H25A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-25H-25A | 200 | 3 | 30 | 25 | 7.5 | 200 | 3 | 65 | 25 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-A2H25A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-25H-25A | 230 | 3 | 30 | 25 | 7.5 | 230 | 3 | 65 | 22 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 230 | 3 | 5 | 28 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-A2H25A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-25H-25A | 460 | 3 | 30 | 25 | 15 | 480Y/277 | 3 | 65 | 21 | 15 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 460 | 3 | 5 | 27 | 20
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-AH10A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-45H-10A | 200 | 3 | 65 | 10 | 3 | 200 | 3 | 65 | 7.8 | 2 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-AH10A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-45H-10A | 230 | 3 | 65 | 10 | 3 | 230 | 3 | 65 | 9.6 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 230 | 3 | 5 | 28 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-AH10A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-45H-10A | 460 | 3 | 65 | 10 | 7.5 | 480Y/277 | 3 | 65 | 7.6 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 460 | 3 | 5 | 27 | 20
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-AH10A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-45H-10A | 575 | 3 | 30 | 10 | 10 | 600Y/347 | 3 | 30 | 9 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 575 | 3 | 5 | 27 | 25
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-AH16A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-45H-16A | 200 | 3 | 65 | 16 | 5 | 200 | 3 | 65 | 11 | 3 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-AH16A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-45H-16A | 230 | 3 | 65 | 16 | 5 | 230 | 3 | 65 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 230 | 3 | 5 | 28 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-AH16A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-45H-16A | 460 | 3 | 65 | 16 | 10 | 480Y/277 | 3 | 65 | 14 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 460 | 3 | 5 | 27 | 20
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-AH16A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-45H-16A | 575 | 3 | 30 | 16 | 15 | 600Y/347 | 3 | 30 | 11 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 575 | 3 | 5 | 27 | 25
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-AH20A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-45H-20A | 200 | 3 | 65 | 20 | 7.5 | 200 | 3 | 65 | 17.5 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-AH20A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-45H-20A | 230 | 3 | 65 | 20 | 7.5 | 230 | 3 | 65 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 230 | 3 | 5 | 28 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-AH20A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-45H-20A | 575 | 3 | 30 | 20 | 20 | 600Y/347 | 3 | 30 | 17 | 15 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 575 | 3 | 5 | 27 | 25
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-37-10-*-AH20A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-45H-20A | 200 | 3 | 65 | 20 | 7.5 | 200 | 3 | 65 | 17.5 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-37 | 200 | 3 | 5 | 32.2 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-37-10-*-AH20A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-45H-20A | 230 | 3 | 65 | 20 | 7.5 | 230 | 3 | 65 | 15.2 | 5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-37 | 230 | 3 | 5 | 28 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-37-10-*-AH20A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-45H-20A | 575 | 3 | 30 | 20 | 20 | 600Y/347 | 3 | 30 | 17 | 15 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-37 | 575 | 3 | 5 | 32 | 30
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-AH25A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-45H-25A | 200 | 3 | 65 | 25 | 15 | 200 | 3 | 65 | 25 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-AH25A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-45H-25A | 230 | 3 | 65 | 25 | 15 | 230 | 3 | 65 | 22 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 230 | 3 | 5 | 28 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-AH25A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-45H-25A | 460 | 3 | 65 | 25 | 30 | 480Y/277 | 3 | 65 | 21 | 15 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 460 | 3 | 5 | 27 | 20
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-AH25A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-45H-25A | 575 | 3 | 30 | 25 | 25 | 600Y/347 | 3 | 30 | 22 | 20 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 575 | 3 | 5 | 27 | 25
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-37-10-*-AH25A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-45H-25A | 200 | 3 | 65 | 25 | 10 | 200 | 3 | 65 | 25 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-37 | 200 | 3 | 5 | 32.2 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-37-10-*-AH25A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-45H-25A | 230 | 3 | 65 | 25 | 10 | 230 | 3 | 65 | 22 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-37 | 230 | 3 | 5 | 28 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-37-10-*-AH25A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-45H-25A | 460 | 3 | 65 | 25 | 20 | 480Y/277 | 3 | 65 | 21 | 15 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-37 | 460 | 3 | 5 | 34 | 25
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-37-10-*-AH25A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-45H-25A | 575 | 3 | 30 | 25 | 25 | 600Y/347 | 3 | 30 | 22 | 20 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-37 | 575 | 3 | 5 | 32 | 30
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-43-10-*-AH25A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-45H-25A | 200 | 3 | 65 | 25 | 7.5 | 200 | 3 | 65 | 25 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-43 | 200 | 3 | 5 | 32.2 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC43 | 600 | 3 | - | - | -
CLU7-43-10-*-AH25A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-45H-25A | 230 | 3 | 65 | 25 | 7.5 | 230 | 3 | 65 | 22 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-43 | 230 | 3 | 5 | 42 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC43 | 600 | 3 | - | - | -
CLU7-43-10-*-AH25A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-45H-25A | 460 | 3 | 65 | 25 | 15 | 480Y/277 | 3 | 65 | 21 | 15 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-43 | 460 | 3 | 5 | 40 | 30
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC43 | 600 | 3 | - | - | -
CLU7-43-10-*-AH25A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-45H-25A | 575 | 3 | 30 | 25 | 20 | 600Y/347 | 3 | 30 | 22 | 20 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-43 | 575 | 3 | 5 | 32 | 30
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC43 | 600 | 3 | - | - | -
CLU7-30-10-*-AH32A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-45H-32A | 200 | 3 | 65 | 32 | 10 | 200 | 3 | 65 | 25.3 | 7.5 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 200 | 3 | 5 | 25.3 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-AH32A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-45H-32A | 230 | 3 | 65 | 32 | 10 | 230 | 3 | 65 | 28 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 230 | 3 | 5 | 28 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-AH32A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-45H-32A | 460 | 3 | 65 | 32 | 25 | 480Y/277 | 3 | 65 | 27 | 20 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 460 | 3 | 5 | 27 | 20
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-30-10-*-AH32A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-45H-32A | 575 | 3 | 0 | 32 | 30 | 600Y/347 | 3 | 30 | 27 | 25 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-30 | 575 | 3 | 5 | 27 | 25
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-37-10-*-AH32A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-45H-32A | 200 | 3 | 65 | 32 | 10 | 200 | 3 | 65 | 32 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-37 | 200 | 3 | 5 | 32.2 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-37-10-*-AH32A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-45H-32A | 230 | 3 | 65 | 32 | 10 | 230 | 3 | 65 | 28 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-37 | 230 | 3 | 5 | 28 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-37-10-*-AH32A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-45H-32A | 460 | 3 | 65 | 32 | 25 | 480Y/277 | 3 | 65 | 27 | 20 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-37 | 460 | 3 | 5 | 34 | 25
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-37-10-*-AH32A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-45H-32A | 575 | 3 | 30 | 32 | 30 | 600Y/347 | 3 | 30 | 32 | 30 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-37 | 575 | 3 | 5 | 32 | 30
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-43-10-*-AH32A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-45H-32A | 200 | 3 | 65 | 32 | 10 | 200 | 3 | 65 | 32 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-43 | 200 | 3 | 5 | 32.2 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC43 | 600 | 3 | - | - | -
CLU7-43-10-*-AH32A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-45H-32A | 230 | 3 | 65 | 32 | 10 | 230 | 3 | 65 | 28 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-43 | 230 | 3 | 5 | 42 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC43 | 600 | 3 | - | - | -
CLU7-43-10-*-AH32A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-45H-32A | 460 | 3 | 65 | 32 | 25 | 480Y/277 | 3 | 65 | 27 | 20 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-43 | 460 | 3 | 5 | 40 | 30
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC43 | 600 | 3 | - | - | -
CLU7-43-10-*-AH32A-A10-W 575 | E | MSP | Sprecher + Schuh | KTA7-45H-32A | 575 | 3 | 30 | 32 | 20 | 600Y/347 | 3 | 30 | 32 | 30 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-43 | 575 | 3 | 5 | 32 | 30
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC43 | 600 | 3 | - | - | -
CLU7-37-10-*-AH45A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-45H-45A | 200 | 3 | 65 | 45 | 15 | 200 | 3 | 65 | 32.2 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-37 | 200 | 3 | 5 | 32.2 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-37-10-*-AH45A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-45H-45A | 460 | 3 | 65 | 45 | 30 | 480Y/277 | 3 | 65 | 34 | 25 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-37 | 460 | 3 | 5 | 34 | 25
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC37 | 600 | 3 | - | - | -
CLU7-43-10-*-AH45A-A10-W 200 | E | MSP | Sprecher + Schuh | KTA7-45H-45A | 200 | 3 | 65 | 45 | 15 | 200 | 3 | 65 | 32.2 | 10 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-43 | 200 | 3 | 5 | 32.2 | 10
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC43 | 600 | 3 | - | - | -
CLU7-43-10-*-AH45A-A10-W 230 | E | MSP | Sprecher + Schuh | KTA7-45H-45A | 230 | 3 | 65 | 45 | 15 | 230 | 3 | 65 | 42 | 15 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-43 | 230 | 3 | 5 | 42 | 15
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC43 | 600 | 3 | - | - | -
CLU7-43-10-*-AH45A-A10-W 460 | E | MSP | Sprecher + Schuh | KTA7-45H-45A | 460 | 3 | 65 | 45 | 30 | 480Y/277 | 3 | 65 | 40 | 30 | 665 | 1, 5 | E205542 V2 S2
|  | REVCON | Sprecher + Schuh | CAU7-43 | 460 | 3 | 5 | 40 | 30
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-45-TE | 600 | 3 | - | - | -
|  | ACC (MOUNTING BASE) | Woehner | EEP | - | - | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-45H-PNC43 | 600 | 3 | - | - | -
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches.
Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).

## Cont. F w MCPB (CL8-CLU8)
Issued: 2010-09-10
Last Revised: 2010-09-10
Database Identification Number | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings | [5 empty] | Conditions of Acceptability | Combination UL File Reference
|  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating FLA or FLA/LRA, A | HP rating | Enclosure Volume, CU inches
CL8-09-10-*-AS0.16A-X 200 | F | MSP | Sprecher + Schuh | KTA7-25S-0.16A | 200 | 3 | 65 | 0.16 | - | 200 | 3 | 65 | 0.16 FLA / 0.96 LRA | - | 773 | 1,5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CL8-09-10-*-AS0.16A-X 230 | F | MSP | Sprecher + Schuh | KTA7-25S-0.16A | 230 | 3 | 65 | 0.16 | - | 230 | 3 | 65 | 0.16 FLA / 0.96 LRA | - | 773 | 1,5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 230 | 3 | - | - | -
CL8-09-10-*-AS0.16A-X 460 | F | MSP | Sprecher + Schuh | KTA7-25S-0.16A | 460 | 3 | 65 | 0.16 | - | 480Y/277 | 3 | 65 | 0.16 FLA / 0.96 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CL8-09-10-*-AS0.16A-X 575 | F | MSP | Sprecher + Schuh | KTA7-25S-0.16A | 575 | 3 | 47 | 0.16 | - | 600Y/347 | 3 | 47 | 0.16 FLA / 0.96 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 575 | 3 | 5 | 6.1 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEC23 | 575 | 3 | - | - | -
CL8-09-10-*-AS0.25A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-0.25A | 200 | 3 | 65 | 0.25 | - | 200 | 3 | 65 | 0.25 FLA / 1.5 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-05 | 200 | 3 | 5 | 6.9 | 1.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CL8-09-10-*-AS0.25A-X.-..230V | F | MSP | Sprecher + Schuh | KTA7-25S-0.25A | 230 | 3 | 65 | 0.25 | - | 230 | 3 | 65 | 0.25 FLA / 1.5 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 230 | 3 | - | - | -
CL8-09-10-*-AS0.25A-X.-..460V | F | MSP | Sprecher + Schuh | KTA7-25S-0.25A | 460 | 3 | 65 | 0.25 | - | 480Y/277 | 3 | 65 | 0.25 FLA / 1.5 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CL8-09-10-*-AS0.25A-X.-..575V | F | MSP | Sprecher + Schuh | KTA7-25S-0.25A | 575 | 3 | 47 | 0.25 | - | 600Y/347 | 3 | 47 | 0.25 FLA / 1.5 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 575 | 3 | 5 | 6.1 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 575 | 3 | - | - | -
CL8-09-10-*-AS0.40A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-0.4A | 200 | 3 | 65 | 0.4 | - | 200 | 3 | 65 | 0.4 FLA / 2.4 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-05 | 200 | 3 | 5 | 6.9 | 1.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CL8-09-10-*-AS0.40A-X.-..230V | F | MSP | Sprecher + Schuh | KTA7-25S-0.4A | 230 | 3 | 65 | 0.4 | - | 230 | 3 | 65 | 0.4 FLA / 2.4 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 230 | 3 | - | - | -
CL8-09-10-*-AS0.40A-X.-..460V | F | MSP | Sprecher + Schuh | KTA7-25S-0.4A | 460 | 3 | 65 | 0.4 | - | 480Y/277 | 3 | 65 | 0.4 FLA / 2.4 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CL8-09-10-*-AS0.40A-X.-..575V | F | MSP | Sprecher + Schuh | KTA7-25S-0.4A | 575 | 3 | 47 | 0.4 | - | 600Y/347 | 3 | 47 | 0.4 FLA / 2.4 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 575 | 3 | 5 | 6.1 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 575 | 3 | - | - | -
CL8-09-10-*-AS0.63A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-0.63A | 200 | 3 | 65 | 0.63 | - | 200 | 3 | 65 | 0.63 FLA / 3.78 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-05 | 200 | 3 | 5 | 6.9 | 1.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CL8-09-10-*-AS0.63A-X.-..230V | F | MSP | Sprecher + Schuh | KTA7-25S-0.63A | 230 | 3 | 65 | 0.63 | - | 230 | 3 | 65 | 0.63 FLA / 3.78 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 230 | 3 | - | - | -
CL8-09-10-*-AS0.63A-X.-..460V | F | MSP | Sprecher + Schuh | KTA7-25S-0.63A | 460 | 3 | 65 | 0.63 | - | 480Y/277 | 3 | 65 | 0.63 FLA / 3.78 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CL8-09-10-*-AS0.63A-X.-..575V | F | MSP | Sprecher + Schuh | KTA7-25S-0.63A | 575 | 3 | 47 | 0.63 | - | 600Y/347 | 3 | 47 | 0.63 FLA / 3.78 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 575 | 3 | 5 | 6.1 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 575 | 3 | - | - | -
CL8-09-10-*-AS1.0A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-1.0A | 200 | 3 | 65 | 1 | - | 200 | 3 | 65 | 1.0 FLA / 6.0 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-05 | 200 | 3 | 5 | 6.9 | 1.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CL8-09-10-*-AS1.0A-X.-..230V | F | MSP | Sprecher + Schuh | KTA7-25S-1.0A | 230 | 3 | 65 | 1 | - | 230 | 3 | 65 | 1.0 FLA / 6.0 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 230 | 3 | - | - | -
CL8-09-10-*-AS1.0A-X.-..460V | F | MSP | Sprecher + Schuh | KTA7-25S-1.0A | 460 | 3 | 65 | 1 | 0.5 | 480Y/277 | 3 | 65 | 1 | 0.5 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CL8-09-10-*-AS1.0A-X.-..575V | F | MSP | Sprecher + Schuh | KTA7-25S-1.0A | 575 | 3 | 47 | 1 | 0.75 | 600Y/347 | 3 | 47 | 1 | 0.75 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 575 | 3 | 5 | 6.1 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 575 | 3 | - | - | -
CL8-09-10-*-AS1.6A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-1.6A | 200 | 3 | 65 | 1.6 | - | 200 | 3 | 65 | 1.6 FLA / 9.6 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-05 | 200 | 3 | 5 | 6.9 | 1.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CL8-09-10-*-AS1.6A-X.-..230V | F | MSP | Sprecher + Schuh | KTA7-25S-1.6A | 230 | 3 | 65 | 1.6 | - | 230 | 3 | 65 | 1.6 FLA / 9.6 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 230 | 3 | - | - | -
CL8-09-10-*-AS1.6A-X.-..460V | F | MSP | Sprecher + Schuh | KTA7-25S-1.6A | 460 | 3 | 65 | 1.6 | 1 | 480Y/277 | 3 | 65 | 1.6 | 1 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CL8-09-10-*-AS1.6A-X.-..575V | F | MSP | Sprecher + Schuh | KTA7-25S-1.6A | 575 | 3 | 47 | 1.6 | 1 | 600Y/347 | 3 | 47 | 1.6 | 1 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 575 | 3 | 5 | 6.1 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 575 | 3 | - | - | -
CL8-09-10-*-AS2.5A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 200 | 3 | 65 | 2.5 | 0.5 | 200 | 3 | 65 | 2.5 | 0.5 | 773 | 1, 5 | E205542 V2 S4 | does not include the CA8-05 with the 2.5, 4.0 and 6.3 MSP?
|  | MC | Sprecher + Schuh | CA8-09 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CL8-09-10-*-AS2.5A-X.-..230V | F | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 230 | 3 | 65 | 2.5 | 0.75 | 230 | 3 | 65 | 2.5 | 0.75 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 230 | 3 | - | - | -
CL8-09-10-*-AS2.5A-X.-..460V | F | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 460 | 3 | 65 | 2.5 | 1.5 | 480Y/277 | 3 | 65 | 2.5 | 1.5 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CL8-09-10-*-AS2.5A-X.-..575V | F | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 575 | 3 | 30 | 2.5 | 2 | 600Y/347 | 3 | 30 | 2.5 | 2 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 575 | 3 | 5 | 6.1 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 575 | 3 | - | - | -
CL8-09-10-*-AS4.0A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 200 | 3 | 65 | 4 | 1 | 200 | 3 | 65 | 4 | 1 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CL8-09-10-*-AS4.0A-X.-..230V | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 230 | 3 | 65 | 4 | 1 | 230 | 3 | 65 | 4 | 1 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 230 | 3 | - | - | -
CL8-09-10-*-AS4.0A-X.-..460V | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 460 | 3 | 65 | 4 | 3 | 480Y/277 | 3 | 65 | 4 | 3 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CL8-09-10-*-AS4.0A-X.-..575V | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 575 | 3 | 25 | 4 | 3 | 600Y/347 | 3 | 30 | 3.9 | 3 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 575 | 3 | 5 | 6.1 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 575 | 3 | - | - | -
CL8-09-10-*-AS6.3A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-6.3A | 200 | 3 | 65 | 6.3 | 1.5 | 200 | 3 | 65 | 6.3 | 1.5 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CL8-09-10-*-AS6.3A-X.-..230V | F | MSP | Sprecher + Schuh | KTA7-25S-6.3A | 230 | 3 | 65 | 6.3 | 2 | 230 | 3 | 65 | 6.3 | 2 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 230 | 3 | - | - | -
CL8-09-10-*-AS6.3A-X.-..460V | F | MSP | Sprecher + Schuh | KTA7-25S-6.3A | 460 | 3 | 65 | 6.3 | 5 | 480Y/277 | 3 | 65 | 6.3 | 5 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CL8-09-10-*-AS10A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 200 | 3 | 65 | 10 | 3 | 200 | 3 | 65 | 7.8 | 2 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CL8-09-10-*-AS10A-X.-.230V | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 230 | 3 | 65 | 10 | 3 | 230 | 3 | 65 | 6.8 | 2 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 230 | 3 | - | - | -
CL8-09-10-*-AS10A-X.-.460V | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 460 | 3 | 65 | 10 | 7.5 | 480Y/277 | 3 | 65 | 7.6 | 5 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-09 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CL8-12-10-*-AS10A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 200 | 3 | 65 | 2.5 | 0.5 | 200 | 3 | 65 | 2.5 | 0.5 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CL8-12-10-*-AS2.5A-X.-..230V | F | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 230 | 3 | 65 | 2.5 | 0.75 | 230 | 3 | 65 | 2.5 | 0.75 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-12 | 230 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 230 | 3 | - | - | -
CL8-12-10-*-AS2.5A-X.-..460V | F | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 460 | 3 | 65 | 2.5 | 1.5 | 480Y/277 | 3 | 65 | 2.5 | 1.5 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CL8-12-10-*-AS2.5A-X.-..575V | F | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 575 | 3 | 30 | 2.5 | 2 | 600Y/347 | 3 | 30 | 2.5 | 2 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-12 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 575 | 3 | - | - | -
CL8-12-10-*-AS4.0A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 200 | 3 | 65 | 4 | 1 | 200 | 3 | 65 | 4 | 1 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CL8-12-10-*-AS4.0A-X.-..230V | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 230 | 3 | 65 | 4 | 1 | 230 | 3 | 65 | 4 | 1 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-12 | 230 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 230 | 3 | - | - | -
CL8-12-10-*-AS4.0A-X.-..460V | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 460 | 3 | 65 | 4 | 3 | 480Y/277 | 3 | 65 | 4 | 3 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CL8-12-10-*-AS4.0A-X.-..575V | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 575 | 3 | 25 | 4 | 3 | 600Y/347 | 3 | 30 | 3.9 | 3 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-12 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 575 | 3 | - | - | -
CL8-12-10-*-AS6.3A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-6.3A | 200 | 3 | 65 | 6.3 | 1.5 | 200 | 3 | 65 | 6.3 | 1.5 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CL8-12-10-*-AS6.3A-X.-..230V | F | MSP | Sprecher + Schuh | KTA7-25S-6.3A | 230 | 3 | 65 | 6.3 | 2 | 230 | 3 | 65 | 6.3 | 2 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-12 | 230 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 230 | 3 | - | - | -
CL8-12-10-*-AS6.3A-X.-..460V | F | MSP | Sprecher + Schuh | KTA7-25S-6.3A | 460 | 3 | 65 | 6.3 | 5 | 480Y/277 | 3 | 65 | 6.3 | 5 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CL8-12-10-*-AS10A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 200 | 3 | 65 | 10 | 3 | 200 | 3 | 65 | 10 | 3 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CL8-12-10-*-AS10A-X.-..230V | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 230 | 3 | 65 | 10 | 3 | 230 | 3 | 65 | 9.6 | 3 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-12 | 230 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 230 | 3 | - | - | -
CL8-12-10-*-AS10A-X.-..460V | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 460 | 3 | 65 | 10 | 7.5 | 480Y/277 | 3 | 65 | 10 | 7.5 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CL8-12-10-*-AS16A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 200 | 3 | 30 | 16 | 5 | 200 | 3 | 30 | 11 | 3 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CL8-12-10-*-AS16A-X.-..460V | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 460 | 3 | 30 | 16 | 10 | 480Y/277 | 3 | 30 | 11 | 7.5 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CA8-12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CLU8-09-02-*-AS0.16A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-0.16A | 200 | 3 | 65 | 0.16 | - | 200 | 3 | 65 | 0.16 FLA / 0.96 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CLU8-09-02-*-AS0.16A-X.-..230V | F | MSP | Sprecher + Schuh | KTA7-25S-0.16A | 230 | 3 | 65 | 0.16 | - | 230 | 3 | 65 | 0.16 FLA / 0.96 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 230 | 3 | - | - | -
CLU8-09-02-*-AS0.16A-X.-..460V | F | MSP | Sprecher + Schuh | KTA7-25S-0.16A | 460 | 3 | 65 | 0.16 | - | 480Y/277 | 3 | 65 | 0.16 FLA / 0.96 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CLU8-09-02-*-AS0.16A-X.-..575V | F | MSP | Sprecher + Schuh | KTA7-25S-0.16A | 575 | 3 | 47 | 0.16 | - | 600Y/347 | 3 | 47 | 0.16 FLA / 0.96 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 575 | 3 | 5 | 6.1 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 575 | 3 | - | - | -
CLU8-09-02-*-AS0.25A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-0.25A | 200 | 3 | 65 | 0.25 | - | 200 | 3 | 65 | 0.25 FLA / 1.5 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CLU8-09-02-*-AS0.25A-X.-..230V | F | MSP | Sprecher + Schuh | KTA7-25S-0.25A | 230 | 3 | 65 | 0.25 | - | 230 | 3 | 65 | 0.25 FLA / 1.5 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 230 | 3 | - | - | -
CLU8-09-02-*-AS0.25A-X.-..460V | F | MSP | Sprecher + Schuh | KTA7-25S-0.25A | 460 | 3 | 65 | 0.25 | - | 480Y/277 | 3 | 65 | 0.25 FLA / 1.5 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CLU8-09-02-*-AS0.25A-X.-..575V | F | MSP | Sprecher + Schuh | KTA7-25S-0.25A | 575 | 3 | 47 | 0.25 | - | 600Y/347 | 3 | 47 | 0.25 FLA / 1.5 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 575 | 3 | 5 | 6.1 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 575 | 3 | - | - | -
CLU8-09-02-*-AS0.40A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-0.4A | 200 | 3 | 65 | 0.4 | - | 200 | 3 | 65 | 0.4 FLA / 2.4 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CLU8-09-02-*-AS0.40A-X.-..230V | F | MSP | Sprecher + Schuh | KTA7-25S-0.4A | 230 | 3 | 65 | 0.4 | - | 230 | 3 | 65 | 0.4 FLA / 2.4 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 230 | 3 | - | - | -
CLU8-09-02-*-AS0.40A-X.-..460V | F | MSP | Sprecher + Schuh | KTA7-25S-0.4A | 460 | 3 | 65 | 0.4 | - | 480Y/277 | 3 | 65 | 0.4 FLA / 2.4 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CLU8-09-02-*-AS0.40A-X.-..575V | F | MSP | Sprecher + Schuh | KTA7-25S-0.4A | 575 | 3 | 47 | 0.4 | - | 600Y/347 | 3 | 47 | 0.4 FLA / 2.4 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 575 | 3 | 5 | 6.1 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 575 | 3 | - | - | -
CLU8-09-02-*-AS0.63A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-0.63A | 200 | 3 | 65 | 0.63 | - | 200 | 3 | 65 | 0.63 FLA / 3.78 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CLU8-09-02-*-AS0.63A-X.-..230V | F | MSP | Sprecher + Schuh | KTA7-25S-0.63A | 230 | 3 | 65 | 0.63 | - | 230 | 3 | 65 | 0.63 FLA / 3.78 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 230 | 3 | - | - | -
CLU8-09-02-*-AS0.63A-X.-..460V | F | MSP | Sprecher + Schuh | KTA7-25S-0.63A | 460 | 3 | 65 | 0.63 | - | 480Y/277 | 3 | 65 | 0.63 FLA / 3.78 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CLU8-09-02-*-AS0.63A-X.-..575V | F | MSP | Sprecher + Schuh | KTA7-25S-0.63A | 575 | 3 | 47 | 0.63 | - | 600Y/347 | 3 | 47 | 0.63 FLA / 3.78 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 575 | 3 | 5 | 6.1 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 575 | 3 | - | - | -
CLU8-09-02-*-AS1.0A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-1.0A | 200 | 3 | 65 | 1 | - | 200 | 3 | 65 | 1.0 FLA / 6.0 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CLU8-09-02-*-AS1.0A-X.-..230V | F | MSP | Sprecher + Schuh | KTA7-25S-1.0A | 230 | 3 | 65 | 1 | - | 230 | 3 | 65 | 1.0 FLA / 6.0 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 230 | 3 | - | - | -
CLU8-09-02-*-AS1.0A-X.-..460V | F | MSP | Sprecher + Schuh | KTA7-25S-1.0A | 460 | 3 | 65 | 1 | 0.5 | 480Y/277 | 3 | 65 | 1 | 0.5 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CLU8-09-02-*-AS1.0A-X.-..575V | F | MSP | Sprecher + Schuh | KTA7-25S-1.0A | 575 | 3 | 47 | 1 | 0.75 | 600Y/347 | 3 | 47 | 1 | 0.75 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 575 | 3 | 5 | 6.1 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 575 | 3 | - | - | -
CLU8-09-02-*-AS1.6A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-1.6A | 200 | 3 | 65 | 1.6 | - | 200 | 3 | 65 | 1.6 FLA / 9.6 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CLU8-09-02-*-AS1.6A-X.-..230V | F | MSP | Sprecher + Schuh | KTA7-25S-1.6A | 230 | 3 | 65 | 1.6 | - | 230 | 3 | 65 | 1.6 FLA / 9.6 LRA | - | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 230 | 3 | - | - | -
CLU8-09-02-*-AS1.6A-X.-..460V | F | MSP | Sprecher + Schuh | KTA7-25S-1.6A | 460 | 3 | 65 | 1.6 | 1 | 480Y/277 | 3 | 65 | 1.6 | 1 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CLU8-09-02-*-AS1.6A-X.-..575V | F | MSP | Sprecher + Schuh | KTA7-25S-1.6A | 575 | 3 | 47 | 1.6 | 1 | 600Y/347 | 3 | 47 | 1.6 | 1 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 575 | 3 | 5 | 6.1 | 5 | [8 empty] | does not include the CAU8-05 with the 2.5, 4.0 and 6.3A MSP?
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 575 | 3 | - | - | -
CLU8-09-02-*-AS2.5A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 200 | 3 | 65 | 2.5 | 0.5 | 200 | 3 | 65 | 2.5 | 0.5 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CLU8-09-02-*-AS2.5A-X.-..230V | F | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 230 | 3 | 65 | 2.5 | 0.75 | 230 | 3 | 65 | 2.5 | 0.75 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 230 | 3 | - | - | -
CLU8-09-02-*-AS2.5A-X.-..460V | F | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 460 | 3 | 65 | 2.5 | 1.5 | 480Y/277 | 3 | 65 | 2.5 | 1.5 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CLU8-09-02-*-AS2.5A-X.-..575V | F | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 575 | 3 | 30 | 2.5 | 2 | 600Y/347 | 3 | 30 | 2.5 | 2 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 575 | 3 | 5 | 6.1 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 575 | 3 | - | - | -
CLU8-09-02-*-AS4.0A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 200 | 3 | 65 | 4 | 1 | 200 | 3 | 65 | 4 | 1 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CLU8-09-02-*-AS4.0A-X.-..230V | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 230 | 3 | 65 | 4 | 1 | 230 | 3 | 65 | 4 | 1 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 230 | 3 | - | - | -
CLU8-09-02-*-AS4.0A-X.-..460V | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 460 | 3 | 65 | 4 | 3 | 480Y/277 | 3 | 65 | 4 | 3 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CLU8-09-02-*-AS4.0A-X.-..575V | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 575 | 3 | 25 | 4 | 3 | 600Y/347 | 3 | 30 | 3.9 | 3 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 575 | 3 | 5 | 6.1 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 575 | 3 | - | - | -
CLU8-09-02-*-AS6.3A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-6.3A | 200 | 3 | 65 | 6.3 | 1.5 | 200 | 3 | 65 | 6.3 | 1.5 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CLU8-09-02-*-AS6.3A-X.-..230V | F | MSP | Sprecher + Schuh | KTA7-25S-6.3A | 230 | 3 | 65 | 6.3 | 2 | 230 | 3 | 65 | 6.3 | 2 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 230 | 3 | - | - | -
CLU8-09-02-*-AS6.3A-X.-..460V | F | MSP | Sprecher + Schuh | KTA7-25S-6.3A | 460 | 3 | 65 | 6.3 | 5 | 480Y/277 | 3 | 65 | 6.3 | 5 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CLU8-09-02-*-AS10A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 200 | 3 | 65 | 10 | 3 | 200 | 3 | 65 | 7.8 | 2 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 200 | 3 | 5 | 7.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CLU8-09-02-*-AS10A-X.-..230V | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 230 | 3 | 65 | 10 | 3 | 230 | 3 | 65 | 6.8 | 2 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 230 | 3 | 5 | 6.8 | 2
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 230 | 3 | - | - | -
CLU8-09-02-*-AS10A-X.-..460V | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 460 | 3 | 65 | 10 | 7.5 | 480Y/277 | 3 | 65 | 7.6 | 5 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-09 | 460 | 3 | 5 | 7.6 | 5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CLU8-12-02-*-AS2.5A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 200 | 3 | 65 | 2.5 | 0.5 | 200 | 3 | 65 | 2.5 | 0.5 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CLU8-12-02-*-AS2.5A-X.-..230V | F | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 230 | 3 | 65 | 2.5 | 0.75 | 230 | 3 | 65 | 2.5 | 0.75 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-12 | 230 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 230 | 3 | - | - | -
CLU8-12-02-*-AS2.5A-X.-..460V | F | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 460 | 3 | 65 | 2.5 | 1.5 | 480Y/277 | 3 | 65 | 2.5 | 1.5 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CLU8-12-02-*-AS2.5A-X.-..575V | F | MSP | Sprecher + Schuh | KTA7-25S-2.5A | 575 | 3 | 30 | 2.5 | 2 | 600Y/347 | 3 | 30 | 2.5 | 2 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-12 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 575 | 3 | - | - | -
CLU8-12-02-*-AS4.0A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 200 | 3 | 65 | 4 | 1 | 200 | 3 | 65 | 4 | 1 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CLU8-12-02-*-AS4.0A-X.-..230V | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 230 | 3 | 65 | 4 | 1 | 230 | 3 | 65 | 4 | 1 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-12 | 230 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 230 | 3 | - | - | -
CLU8-12-02-*-AS4.0A-X.-..460V | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 460 | 3 | 65 | 4 | 3 | 480Y/277 | 3 | 65 | 4 | 3 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CLU8-12-02-*-AS4.0A-X.-..575V | F | MSP | Sprecher + Schuh | KTA7-25S-4.0A | 575 | 3 | 25 | 4 | 3 | 600Y/347 | 3 | 30 | 3.9 | 3 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-12 | 575 | 3 | 5 | 9 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 575 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 575 | 3 | - | - | -
CLU8-12-02-*-AS6.3A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-6.3A | 200 | 3 | 65 | 6.3 | 1.5 | 200 | 3 | 65 | 6.3 | 1.5 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CLU8-12-02-*-AS6.3A-X.-..230V | F | MSP | Sprecher + Schuh | KTA7-25S-6.3A | 230 | 3 | 65 | 6.3 | 2 | 230 | 3 | 65 | 6.3 | 2 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-12 | 230 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 230 | 3 | - | - | -
CLU8-12-02-*-AS6.3A-X.-..460V | F | MSP | Sprecher + Schuh | KTA7-25S-6.3A | 460 | 3 | 65 | 6.3 | 5 | 480Y/277 | 3 | 65 | 6.3 | 5 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CLU8-12-02-*-AS10A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 200 | 3 | 65 | 10 | 3 | 200 | 3 | 65 | 10 | 3 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CLU8-12-02-*-AS10A-X.-..230V | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 230 | 3 | 65 | 10 | 3 | 230 | 3 | 65 | 9.6 | 3 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-12 | 230 | 3 | 5 | 9.6 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 230 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 230 | 3 | - | - | -
CLU8-12-02-*-AS10A-X.-..460V | F | MSP | Sprecher + Schuh | KTA7-25S-10A | 460 | 3 | 65 | 10 | 7.5 | 480Y/277 | 3 | 65 | 10 | 7.5 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
CLU8-12-02-*-AS16A-X.-..200V | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 200 | 3 | 30 | 16 | 5 | 200 | 3 | 30 | 11 | 3 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-12 | 200 | 3 | 5 | 11 | 3
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 200 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 200 | 3 | - | - | -
CLU8-12-02-*-AS16A-X.-..460V | F | MSP | Sprecher + Schuh | KTA7-25S-16A | 460 | 3 | 30 | 16 | 10 | 480Y/277 | 3 | 30 | 11 | 7.5 | 773 | 1, 5 | E205542 V2 S4
|  | MC | Sprecher + Schuh | CAU8-12 | 460 | 3 | 5 | 11 | 7.5
|  | ACC(ADAPTER) | Sprecher + Schuh | KT7-25-TE1 | 460 | 3 | - | - | -
|  | ACC(CONNECTION MODULE) | Sprecher + Schuh | KT7-25S-PEK12 | 460 | 3 | - | - | -
Conditions of Acceptability
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic inches. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type E & F Combination Motor Controllers).