## Type C - FA TM
Issued: 2006-08-11
Last Revised: 2006-11-16
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in.) | Conditions of Acceptability | Combination UL File
SE304390 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 200 | 3 | 0.5 | 2.5 | 1832 | 1 | E40610 V12 S15
SE304390 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 10 | 200 | 3 | 0.5 | 2.5 | 1832 | 1 | E40610 V12 S15
SE304390 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 10 | 200 | 3 | 0.5 | 2.5 | 1832 | 1 | E40610 V12 S15
SE304400 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 208 | 3 | 0.5 | 2.4 | 1832 | 1 | E40610 V12 S15
SE304400 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 10 | 208 | 3 | 0.5 | 2.4 | 1832 | 1 | E40610 V12 S15
SE304400 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 10 | 208 | 3 | 0.5 | 2.4 | 1832 | 1 | E40610 V12 S15
SE304410 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 240 | 3 | 0.5 | 2.2 | 1832 | 1 | E40610 V12 S15
SE304410 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 10 | 240 | 3 | 0.5 | 2.2 | 1832 | 1 | E40610 V12 S15
SE304410 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 10 | 240 | 3 | 0.5 | 2.2 | 1832 | 1 | E40610 V12 S15
SE304420 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 200 | 3 | 0.75 | 3.7 | 1832 | 1 | E40610 V12 S15
SE304420 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 10 | 200 | 3 | 0.75 | 3.7 | 1832 | 1 | E40610 V12 S15
SE304420 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 10 | 200 | 3 | 0.75 | 3.7 | 1832 | 1 | E40610 V12 S15
SE304430 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 208 | 3 | 0.75 | 3.5 | 1832 | 1 | E40610 V12 S15
SE304430 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 10 | 208 | 3 | 0.75 | 3.5 | 1832 | 1 | E40610 V12 S15
SE304430 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 10 | 208 | 3 | 0.75 | 3.5 | 1832 | 1 | E40610 V12 S15
SE304440 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 240 | 3 | 0.75 | 3.2 | 1832 | 1 | E40610 V12 S15
SE304440 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 10 | 240 | 3 | 0.75 | 3.2 | 1832 | 1 | E40610 V12 S15
SE304440 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 10 | 240 | 3 | 0.75 | 3.2 | 1832 | 1 | E40610 V12 S15
SE304450 | C | CB | Square D | FAL34015 | 18 | 15 | 480 | 3 | 18 | 480 | 3 | 0.75 | 1.6 | 1832 | 1 | E40610 V12 S15
SE304450 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 18 | 480 | 3 | 0.75 | 1.6 | 1832 | 1 | E40610 V12 S15
SE304450 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 18 | 480 | 3 | 0.75 | 1.6 | 1832 | 1 | E40610 V12 S15
SE304460 | C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 0.75 | 1.3 | 1832 | 1 | E40610 V12 S15
SE304460 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 14 | 600 | 3 | 0.75 | 1.3 | 1832 | 1 | E40610 V12 S15
SE304460 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 14 | 600 | 3 | 0.75 | 1.3 | 1832 | 1 | E40610 V12 S15
SE304470 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 200 | 3 | 1 | 4.8 | 1832 | 1 | E40610 V12 S15
SE304470 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 10 | 200 | 3 | 1 | 4.8 | 1832 | 1 | E40610 V12 S15
SE304470 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 10 | 200 | 3 | 1 | 4.8 | 1832 | 1 | E40610 V12 S15
SE304480 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 208 | 3 | 1 | 4.6 | 1832 | 1 | E40610 V12 S15
SE304480 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 10 | 208 | 3 | 1 | 4.6 | 1832 | 1 | E40610 V12 S15
SE304480 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 10 | 208 | 3 | 1 | 4.6 | 1832 | 1 | E40610 V12 S15
SE304490 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 240 | 3 | 1 | 4.2 | 1832 | 1 | E40610 V12 S15
SE304490 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 10 | 240 | 3 | 1 | 4.2 | 1832 | 1 | E40610 V12 S15
SE304490 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 10 | 240 | 3 | 1 | 4.2 | 1832 | 1 | E40610 V12 S15
SE304500 | C | CB | Square D | FAL34015 | 18 | 15 | 480 | 3 | 18 | 480 | 3 | 1 | 2.1 | 1832 | 1 | E40610 V12 S15
SE304500 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 18 | 480 | 3 | 1 | 2.1 | 1832 | 1 | E40610 V12 S15
SE304500 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 18 | 480 | 3 | 1 | 2.1 | 1832 | 1 | E40610 V12 S15
SE304510 | C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 1 | 1.7 | 1832 | 1 | E40610 V12 S15
SE304510 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 14 | 600 | 3 | 1 | 1.7 | 1832 | 1 | E40610 V12 S15
SE304510 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 14 | 600 | 3 | 1 | 1.7 | 1832 | 1 | E40610 V12 S15
SE304520 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 200 | 3 | 1.5 | 6.9 | 1832 | 1 | E40610 V12 S15
SE304520 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 10 | 200 | 3 | 1.5 | 6.9 | 1832 | 1 | E40610 V12 S15
SE304520 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 10 | 200 | 3 | 1.5 | 6.9 | 1832 | 1 | E40610 V12 S15
SE304530 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 208 | 3 | 1.5 | 6.6 | 1832 | 1 | E40610 V12 S15
SE304530 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 10 | 208 | 3 | 1.5 | 6.6 | 1832 | 1 | E40610 V12 S15
SE304530 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 10 | 208 | 3 | 1.5 | 6.6 | 1832 | 1 | E40610 V12 S15
SE304540 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 240 | 3 | 1.5 | 6 | 1832 | 1 | E40610 V12 S15
SE304540 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 10 | 240 | 3 | 1.5 | 6 | 1832 | 1 | E40610 V12 S15
SE304540 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 10 | 240 | 3 | 1.5 | 6 | 1832 | 1 | E40610 V12 S15
SE304550 | C | CB | Square D | FAL34015 | 18 | 15 | 480 | 3 | 18 | 480 | 3 | 1.5 | 3 | 1832 | 1 | E40610 V12 S15
SE304550 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 18 | 480 | 3 | 1.5 | 3 | 1832 | 1 | E40610 V12 S15
SE304550 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 18 | 480 | 3 | 1.5 | 3 | 1832 | 1 | E40610 V12 S15
SE304560 | C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 1.5 | 2.4 | 1832 | 1 | E40610 V12 S15
SE304560 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 14 | 600 | 3 | 1.5 | 2.4 | 1832 | 1 | E40610 V12 S15
SE304560 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 14 | 600 | 3 | 1.5 | 2.4 | 1832 | 1 | E40610 V12 S15
SE304570 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 200 | 3 | 2 | 7.82 | 1832 | 1 | E40610 V12 S15
SE304570 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 10 | 200 | 3 | 2 | 7.82 | 1832 | 1 | E40610 V12 S15
SE304570 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 10 | 200 | 3 | 2 | 7.82 | 1832 | 1 | E40610 V12 S15
SE304580 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 208 | 3 | 2 | 7.5 | 1832 | 1 | E40610 V12 S15
SE304580 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 10 | 208 | 3 | 2 | 7.5 | 1832 | 1 | E40610 V12 S15
SE304580 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 10 | 208 | 3 | 2 | 7.5 | 1832 | 1 | E40610 V12 S15
SE304590 | C | CB | Square D | FAL32020 | 10 | 20 | 240 | 3 | 10 | 200 | 3 | 2 | 7.82 | 1832 | 1 | E40610 V12 S15
SE304590 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 10 | 200 | 3 | 2 | 7.82 | 1832 | 1 | E40610 V12 S15
SE304590 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 10 | 200 | 3 | 2 | 7.82 | 1832 | 1 | E40610 V12 S15
SE304600 | C | CB | Square D | FAL32020 | 10 | 20 | 240 | 3 | 10 | 208 | 3 | 2 | 7.5 | 1832 | 1 | E40610 V12 S15
SE304600 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 10 | 208 | 3 | 2 | 7.5 | 1832 | 1 | E40610 V12 S15
SE304600 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 10 | 208 | 3 | 2 | 7.5 | 1832 | 1 | E40610 V12 S15
SE304610 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 240 | 3 | 2 | 6.8 | 1832 | 1 | E40610 V12 S15
SE304610 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 10 | 240 | 3 | 2 | 6.8 | 1832 | 1 | E40610 V12 S15
SE304610 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 10 | 240 | 3 | 2 | 6.8 | 1832 | 1 | E40610 V12 S15
SE304620 | C | CB | Square D | FAL34015 | 18 | 15 | 480 | 3 | 18 | 480 | 3 | 2 | 3.4 | 1832 | 1 | E40610 V12 S15
SE304620 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 18 | 480 | 3 | 2 | 3.4 | 1832 | 1 | E40610 V12 S15
SE304620 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 18 | 480 | 3 | 2 | 3.4 | 1832 | 1 | E40610 V12 S15
SE304630 | C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 2 | 2.7 | 1832 | 1 | E40610 V12 S15
SE304630 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 14 | 600 | 3 | 2 | 2.7 | 1832 | 1 | E40610 V12 S15
SE304630 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 14 | 600 | 3 | 2 | 2.7 | 1832 | 1 | E40610 V12 S15
SE304640 | C | CB | Square D | FAL32020 | 10 | 20 | 240 | 3 | 10 | 200 | 3 | 3 | 11 | 1832 | 1 | E40610 V12 S15
SE304640 |  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3 | 10 | 200 | 3 | 3 | 11 | 1832 | 1 | E40610 V12 S15
SE304640 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 10 | 200 | 3 | 3 | 11 | 1832 | 1 | E40610 V12 S15
SE304650 | C | CB | Square D | FAL32020 | 10 | 20 | 240 | 3 | 10 | 208 | 3 | 3 | 10.6 | 1832 | 1 | E40610 V12 S15
SE304650 |  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3 | 10 | 208 | 3 | 3 | 10.6 | 1832 | 1 | E40610 V12 S15
SE304650 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 10 | 208 | 3 | 3 | 10.6 | 1832 | 1 | E40610 V12 S15
SE304660 | C | CB | Square D | FAL32025 | 10 | 25 | 240 | 3 | 10 | 200 | 3 | 3 | 11 | 1832 | 1 | E40610 V12 S15
SE304660 |  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3 | 10 | 200 | 3 | 3 | 11 | 1832 | 1 | E40610 V12 S15
SE304660 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 10 | 200 | 3 | 3 | 11 | 1832 | 1 | E40610 V12 S15
SE304670 | C | CB | Square D | FAL32025 | 10 | 25 | 240 | 3 | 10 | 208 | 3 | 3 | 10.6 | 1832 | 1 | E40610 V12 S15
SE304670 |  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3 | 10 | 208 | 3 | 3 | 10.6 | 1832 | 1 | E40610 V12 S15
SE304670 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 10 | 208 | 3 | 3 | 10.6 | 1832 | 1 | E40610 V12 S15
SE304680 | C | CB | Square D | FAL32020 | 10 | 20 | 240 | 3 | 10 | 240 | 3 | 3 | 9.6 | 1832 | 1 | E40610 V12 S15
SE304680 |  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3 | 10 | 240 | 3 | 3 | 9.6 | 1832 | 1 | E40610 V12 S15
SE304680 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 10 | 240 | 3 | 3 | 9.6 | 1832 | 1 | E40610 V12 S15
SE304690 | C | CB | Square D | FAL34015 | 18 | 15 | 480 | 3 | 18 | 480 | 3 | 3 | 4.8 | 1832 | 1 | E40610 V12 S15
SE304690 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 18 | 480 | 3 | 3 | 4.8 | 1832 | 1 | E40610 V12 S15
SE304690 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 18 | 480 | 3 | 3 | 4.8 | 1832 | 1 | E40610 V12 S15
SE304700 | C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 3 | 3.9 | 1832 | 1 | E40610 V12 S15
SE304700 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 14 | 600 | 3 | 3 | 3.9 | 1832 | 1 | E40610 V12 S15
SE304700 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 14 | 600 | 3 | 3 | 3.9 | 1832 | 1 | E40610 V12 S15
SE304710 | C | CB | Square D | FAL32035 | 10 | 35 | 240 | 3 | 10 | 200 | 3 | 5 | 17.5 | 1832 | 1 | E40610 V12 S15
SE304710 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 10 | 200 | 3 | 5 | 17.5 | 1832 | 1 | E40610 V12 S15
SE304710 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 10 | 200 | 3 | 5 | 17.5 | 1832 | 1 | E40610 V12 S15
SE304720 | C | CB | Square D | FAL32035 | 10 | 35 | 240 | 3 | 10 | 208 | 3 | 5 | 16.7 | 1832 | 1 | E40610 V12 S15
SE304720 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 10 | 208 | 3 | 5 | 16.7 | 1832 | 1 | E40610 V12 S15
SE304720 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 10 | 208 | 3 | 5 | 16.7 | 1832 | 1 | E40610 V12 S15
SE304730 | C | CB | Square D | FAL32030 | 10 | 30 | 240 | 3 | 10 | 240 | 3 | 5 | 15.2 | 1832 | 1 | E40610 V12 S15
SE304730 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 10 | 240 | 3 | 5 | 15.2 | 1832 | 1 | E40610 V12 S15
SE304730 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 10 | 240 | 3 | 5 | 15.2 | 1832 | 1 | E40610 V12 S15
SE304740 | C | CB | Square D | FAL34015 | 18 | 15 | 480 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1 | E40610 V12 S15
SE304740 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1 | E40610 V12 S15
SE304740 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1 | E40610 V12 S15
SE304750 | C | CB | Square D | FAL32035 | 10 | 35 | 240 | 3 | 10 | 240 | 3 | 5 | 15.2 | 1832 | 1 | E40610 V12 S15
SE304750 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 10 | 240 | 3 | 5 | 15.2 | 1832 | 1 | E40610 V12 S15
SE304750 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 10 | 240 | 3 | 5 | 15.2 | 1832 | 1 | E40610 V12 S15
SE304760 | C | CB | Square D | FAL34020 | 18 | 20 | 480 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1 | E40610 V12 S15
SE304760 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1 | E40610 V12 S15
SE304760 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1 | E40610 V12 S15
SE304770 | C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 5 | 6.1 | 1832 | 1 | E40610 V12 S15
SE304770 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 14 | 600 | 3 | 5 | 6.1 | 1832 | 1 | E40610 V12 S15
SE304770 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 14 | 600 | 3 | 5 | 6.1 | 1832 | 1 | E40610 V12 S15
SE304780 | C | CB | Square D | FAL32050 | 10 | 50 | 240 | 3 | 10 | 200 | 3 | 7.5 | 25.3 | 1832 | 1 | E40610 V12 S15
SE304780 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 10 | 200 | 3 | 7.5 | 25.3 | 1832 | 1 | E40610 V12 S15
SE304780 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 10 | 200 | 3 | 7.5 | 25.3 | 1832 | 1 | E40610 V12 S15
SE304790 | C | CB | Square D | FAL32050 | 10 | 50 | 240 | 3 | 10 | 208 | 3 | 7.5 | 24.2 | 1832 | 1 | E40610 V12 S15
SE304790 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 10 | 208 | 3 | 7.5 | 24.2 | 1832 | 1 | E40610 V12 S15
SE304790 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 10 | 208 | 3 | 7.5 | 24.2 | 1832 | 1 | E40610 V12 S15
SE304800 | C | CB | Square D | FAL32040 | 10 | 40 | 240 | 3 | 10 | 240 | 3 | 7.5 | 22 | 1832 | 1 | E40610 V12 S15
SE304800 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 10 | 240 | 3 | 7.5 | 22 | 1832 | 1 | E40610 V12 S15
SE304800 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 10 | 240 | 3 | 7.5 | 22 | 1832 | 1 | E40610 V12 S15
SE304810 | C | CB | Square D | FAL34020 | 18 | 20 | 480 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1 | E40610 V12 S15
SE304810 |  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1 | E40610 V12 S15
SE304810 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1 | E40610 V12 S15
SE304820 | C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 1832 | 1 | E40610 V12 S15
SE304820 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 1832 | 1 | E40610 V12 S15
SE304820 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 1832 | 1 | E40610 V12 S15
SE304830 | C | CB | Square D | FAL32060 | 10 | 60 | 240 | 3 | 10 | 200 | 3 | 7.5 | 25.3 | 1832 | 1 | E40610 V12 S15
SE304830 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 10 | 200 | 3 | 7.5 | 25.3 | 1832 | 1 | E40610 V12 S15
SE304830 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 10 | 200 | 3 | 7.5 | 25.3 | 1832 | 1 | E40610 V12 S15
SE304840 | C | CB | Square D | FAL32060 | 10 | 60 | 240 | 3 | 10 | 208 | 3 | 7.5 | 24.2 | 1832 | 1 | E40610 V12 S15
SE304840 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 10 | 208 | 3 | 7.5 | 24.2 | 1832 | 1 | E40610 V12 S15
SE304840 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 10 | 208 | 3 | 7.5 | 24.2 | 1832 | 1 | E40610 V12 S15
SE304850 | C | CB | Square D | FAL32045 | 10 | 45 | 240 | 3 | 10 | 240 | 3 | 7.5 | 22 | 1832 | 1 | E40610 V12 S15
SE304850 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 10 | 240 | 3 | 7.5 | 22 | 1832 | 1 | E40610 V12 S15
SE304850 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 10 | 240 | 3 | 7.5 | 22 | 1832 | 1 | E40610 V12 S15
SE304860 | C | CB | Square D | FAL34025 | 18 | 25 | 480 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1 | E40610 V12 S15
SE304860 |  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1 | E40610 V12 S15
SE304860 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1 | E40610 V12 S15
SE304870 | C | CB | Square D | FAL36020 | 14 | 20 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 1832 | 1 | E40610 V12 S15
SE304870 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 1832 | 1 | E40610 V12 S15
SE304870 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 1832 | 1 | E40610 V12 S15
SE304880 | C | CB | Square D | FAL32060 | 10 | 60 | 240 | 3 | 10 | 200 | 3 | 10 | 32.2 | 1832 | 1 | E40610 V12 S15
SE304880 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 10 | 200 | 3 | 10 | 32.2 | 1832 | 1 | E40610 V12 S15
SE304880 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 10 | 200 | 3 | 10 | 32.2 | 1832 | 1 | E40610 V12 S15
SE304890 | C | CB | Square D | FAL32060 | 10 | 60 | 240 | 3 | 10 | 208 | 3 | 10 | 30.8 | 1832 | 1 | E40610 V12 S15
SE304890 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 10 | 208 | 3 | 10 | 30.8 | 1832 | 1 | E40610 V12 S15
SE304890 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 10 | 208 | 3 | 10 | 30.8 | 1832 | 1 | E40610 V12 S15
SE304900 | C | CB | Square D | FAL32050 | 10 | 50 | 240 | 3 | 10 | 240 | 3 | 10 | 28 | 1832 | 1 | E40610 V12 S15
SE304900 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 10 | 240 | 3 | 10 | 28 | 1832 | 1 | E40610 V12 S15
SE304900 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 10 | 240 | 3 | 10 | 28 | 1832 | 1 | E40610 V12 S15
SE304910 | C | CB | Square D | FAL34025 | 18 | 25 | 480 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1 | E40610 V12 S15
SE304910 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1 | E40610 V12 S15
SE304910 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1 | E40610 V12 S15
SE304920 | C | CB | Square D | FAL36020 | 14 | 20 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 1832 | 1 | E40610 V12 S15
SE304920 |  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 1832 | 1 | E40610 V12 S15
SE304920 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 1832 | 1 | E40610 V12 S15
SE304930 | C | CB | Square D | FAL32070 | 10 | 70 | 240 | 3 | 10 | 200 | 3 | 10 | 32.2 | 1832 | 1 | E40610 V12 S15
SE304930 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 10 | 200 | 3 | 10 | 32.2 | 1832 | 1 | E40610 V12 S15
SE304930 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 10 | 200 | 3 | 10 | 32.2 | 1832 | 1 | E40610 V12 S15
SE304940 | C | CB | Square D | FAL32070 | 10 | 70 | 240 | 3 | 10 | 208 | 3 | 10 | 30.8 | 1832 | 1 | E40610 V12 S15
SE304940 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 10 | 208 | 3 | 10 | 30.8 | 1832 | 1 | E40610 V12 S15
SE304940 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 10 | 208 | 3 | 10 | 30.8 | 1832 | 1 | E40610 V12 S15
SE304950 | C | CB | Square D | FAL32060 | 10 | 60 | 240 | 3 | 10 | 240 | 3 | 10 | 28 | 1832 | 1 | E40610 V12 S15
SE304950 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 10 | 240 | 3 | 10 | 28 | 1832 | 1 | E40610 V12 S15
SE304950 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 10 | 240 | 3 | 10 | 28 | 1832 | 1 | E40610 V12 S15
SE304960 | C | CB | Square D | FAL34030 | 18 | 30 | 480 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1 | E40610 V12 S15
SE304960 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1 | E40610 V12 S15
SE304960 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1 | E40610 V12 S15
SE304970 | C | CB | Square D | FAL36025 | 14 | 25 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 1832 | 1 | E40610 V12 S15
SE304970 |  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 1832 | 1 | E40610 V12 S15
SE304970 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 1832 | 1 | E40610 V12 S15
SE304980 | C | CB | Square D | FAL32090 | 10 | 90 | 240 | 3 | 10 | 200 | 3 | 15 | 48.3 | 2289 | 1 | E40610 V12 S15
SE304980 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 10 | 200 | 3 | 15 | 48.3 | 2289 | 1 | E40610 V12 S15
SE304980 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 10 | 200 | 3 | 15 | 48.3 | 2289 | 1 | E40610 V12 S15
SE304990 | C | CB | Square D | FAL32090 | 10 | 90 | 240 | 3 | 10 | 208 | 3 | 15 | 46.2 | 2289 | 1 | E40610 V12 S15
SE304990 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 10 | 208 | 3 | 15 | 46.2 | 2289 | 1 | E40610 V12 S15
SE304990 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 10 | 208 | 3 | 15 | 46.2 | 2289 | 1 | E40610 V12 S15
SE305000 | C | CB | Square D | FAL32080 | 10 | 80 | 240 | 3 | 10 | 240 | 3 | 15 | 42 | 2289 | 1 | E40610 V12 S15
SE305000 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 10 | 240 | 3 | 15 | 42 | 2289 | 1 | E40610 V12 S15
SE305000 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 10 | 240 | 3 | 15 | 42 | 2289 | 1 | E40610 V12 S15
SE305010 | C | CB | Square D | FAL34040 | 18 | 40 | 480 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1 | E40610 V12 S15
SE305010 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1 | E40610 V12 S15
SE305010 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1 | E40610 V12 S15
SE305020 | C | CB | Square D | FAL36030 | 14 | 30 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 1832 | 1 | E40610 V12 S15
SE305020 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 1832 | 1 | E40610 V12 S15
SE305020 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 1832 | 1 | E40610 V12 S15
SE305030 | C | CB | Square D | FAL32090 | 10 | 90 | 240 | 3 | 10 | 240 | 3 | 15 | 42 | 2289 | 1 | E40610 V12 S15
SE305030 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 10 | 240 | 3 | 15 | 42 | 2289 | 1 | E40610 V12 S15
SE305030 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 10 | 240 | 3 | 15 | 42 | 2289 | 1 | E40610 V12 S15
SE305040 | C | CB | Square D | FAL34045 | 18 | 45 | 480 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1 | E40610 V12 S15
SE305040 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1 | E40610 V12 S15
SE305040 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1 | E40610 V12 S15
SE305050 | C | CB | Square D | FAL36035 | 14 | 35 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 1832 | 1 | E40610 V12 S15
SE305050 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 1832 | 1 | E40610 V12 S15
SE305050 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 1832 | 1 | E40610 V12 S15
SE305060 | C | CB | Square D | FAL32100 | 10 | 100 | 240 | 3 | 10 | 200 | 3 | 20 | 62.1 | 2289 | 1 | E40610 V12 S15
SE305060 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 10 | 200 | 3 | 20 | 62.1 | 2289 | 1 | E40610 V12 S15
SE305060 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 10 | 200 | 3 | 20 | 62.1 | 2289 | 1 | E40610 V12 S15
SE305070 | C | CB | Square D | FAL32100 | 10 | 100 | 240 | 3 | 10 | 208 | 3 | 20 | 59.4 | 2289 | 1 | E40610 V12 S15
SE305070 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 10 | 208 | 3 | 20 | 59.4 | 2289 | 1 | E40610 V12 S15
SE305070 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 10 | 208 | 3 | 20 | 59.4 | 2289 | 1 | E40610 V12 S15
SE305080 | C | CB | Square D | FAL32090 | 10 | 90 | 240 | 3 | 10 | 240 | 3 | 20 | 54 | 2289 | 1 | E40610 V12 S15
SE305080 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 10 | 240 | 3 | 20 | 54 | 2289 | 1 | E40610 V12 S15
SE305080 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 10 | 240 | 3 | 20 | 54 | 2289 | 1 | E40610 V12 S15
SE305090 | C | CB | Square D | FAL34050 | 18 | 50 | 480 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1 | E40610 V12 S15
SE305090 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1 | E40610 V12 S15
SE305090 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1 | E40610 V12 S15
SE305100 | C | CB | Square D | FAL34060 | 18 | 60 | 480 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1 | E40610 V12 S15
SE305100 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1 | E40610 V12 S15
SE305100 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1 | E40610 V12 S15
SE305110 | C | CB | Square D | FAL36045 | 14 | 45 | 600 | 3 | 14 | 600 | 3 | 20 | 22 | 1832 | 1 | E40610 V12 S15
SE305110 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 14 | 600 | 3 | 20 | 22 | 1832 | 1 | E40610 V12 S15
SE305110 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 14 | 600 | 3 | 20 | 22 | 1832 | 1 | E40610 V12 S15
SE305120 | C | CB | Square D | FAL32100 | 10 | 100 | 240 | 3 | 10 | 240 | 3 | 25 | 68 | 2289 | 1 | E40610 V12 S15
SE305120 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 10 | 240 | 3 | 25 | 68 | 2289 | 1 | E40610 V12 S15
SE305120 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 10 | 240 | 3 | 25 | 68 | 2289 | 1 | E40610 V12 S15
SE305130 | C | CB | Square D | FAL34060 | 18 | 60 | 480 | 3 | 18 | 480 | 3 | 25 | 34 | 2289 | 1 | E40610 V12 S15
SE305130 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2289 | 1 | E40610 V12 S15
SE305130 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2289 | 1 | E40610 V12 S15
SE305140 | C | CB | Square D | FAL36050 | 14 | 50 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 1832 | 1 | E40610 V12 S15
SE305140 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 1832 | 1 | E40610 V12 S15
SE305140 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 1832 | 1 | E40610 V12 S15
SE305150 | C | CB | Square D | FAL34070 | 18 | 70 | 480 | 3 | 18 | 480 | 3 | 25 | 34 | 2289 | 1 | E40610 V12 S15
SE305150 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2289 | 1 | E40610 V12 S15
SE305150 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2289 | 1 | E40610 V12 S15
SE305160 | C | CB | Square D | FAL36060 | 14 | 60 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 1832 | 1 | E40610 V12 S15
SE305160 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 1832 | 1 | E40610 V12 S15
SE305160 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 1832 | 1 | E40610 V12 S15
SE305170 | C | CB | Square D | FAL34080 | 18 | 80 | 480 | 3 | 18 | 480 | 3 | 30 | 40 | 2289 | 1 | E40610 V12 S15
SE305170 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2289 | 1 | E40610 V12 S15
SE305170 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2289 | 1 | E40610 V12 S15
SE305180 | C | CB | Square D | FAL36060 | 14 | 60 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2289 | 1 | E40610 V12 S15
SE305180 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2289 | 1 | E40610 V12 S15
SE305180 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2289 | 1 | E40610 V12 S15
SE305190 | C | CB | Square D | FAL36070 | 14 | 70 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2289 | 1 | E40610 V12 S15
SE305190 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2289 | 1 | E40610 V12 S15
SE305190 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2289 | 1 | E40610 V12 S15
SE305200 | C | CB | Square D | FAL34090 | 18 | 90 | 480 | 3 | 18 | 480 | 3 | 40 | 52 | 2289 | 1 | E40610 V12 S15
SE305200 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 18 | 480 | 3 | 40 | 52 | 2289 | 1 | E40610 V12 S15
SE305200 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 18 | 480 | 3 | 40 | 52 | 2289 | 1 | E40610 V12 S15
SE305210 | C | CB | Square D | FAL36080 | 14 | 80 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2289 | 1 | E40610 V12 S15
SE305210 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2289 | 1 | E40610 V12 S15
SE305210 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2289 | 1 | E40610 V12 S15
SE305220 | C | CB | Square D | FAL36090 | 14 | 90 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2289 | 1 | E40610 V12 S15
SE305220 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2289 | 1 | E40610 V12 S15
SE305220 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2289 | 1 | E40610 V12 S15
SE305230 | C | CB | Square D | FAL34100 | 18 | 100 | 480 | 3 | 18 | 480 | 3 | 50 | 65 | 2289 | 1 | E40610 V12 S15
SE305230 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 18 | 480 | 3 | 50 | 65 | 2289 | 1 | E40610 V12 S15
SE305230 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 18 | 480 | 3 | 50 | 65 | 2289 | 1 | E40610 V12 S15
SE305240 | C | CB | Square D | FAL36090 | 14 | 90 | 600 | 3 | 14 | 600 | 3 | 50 | 52 | 2289 | 1 | E40610 V12 S15
SE305240 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 14 | 600 | 3 | 50 | 52 | 2289 | 1 | E40610 V12 S15
SE305240 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 14 | 600 | 3 | 50 | 52 | 2289 | 1 | E40610 V12 S15
SE305250 | C | CB | Square D | FAL36100 | 14 | 100 | 600 | 3 | 14 | 600 | 3 | 60 | 62 | 2289 | 1 | E40610 V12 S15
SE305250 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 14 | 600 | 3 | 60 | 62 | 2289 | 1 | E40610 V12 S15
SE305250 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 14 | 600 | 3 | 60 | 62 | 2289 | 1 | E40610 V12 S15
SE305260 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 200 | 3 | 0.5 | 2.5 | 1832 | 1 | E40610 V12 S16
SE305260 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 10 | 200 | 3 | 0.5 | 2.5 | 1832 | 1 | E40610 V12 S16
SE305260 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 10 | 200 | 3 | 0.5 | 2.5 | 1832 | 1 | E40610 V12 S16
SE305270 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 208 | 3 | 0.5 | 2.4 | 1832 | 1 | E40610 V12 S16
SE305270 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 10 | 208 | 3 | 0.5 | 2.4 | 1832 | 1 | E40610 V12 S16
SE305270 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 10 | 208 | 3 | 0.5 | 2.4 | 1832 | 1 | E40610 V12 S16
SE305280 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 240 | 3 | 0.5 | 2.2 | 1832 | 1 | E40610 V12 S16
SE305280 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 10 | 240 | 3 | 0.5 | 2.2 | 1832 | 1 | E40610 V12 S16
SE305280 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 10 | 240 | 3 | 0.5 | 2.2 | 1832 | 1 | E40610 V12 S16
SE305290 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 200 | 3 | 0.75 | 3.7 | 1832 | 1 | E40610 V12 S16
SE305290 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 10 | 200 | 3 | 0.75 | 3.7 | 1832 | 1 | E40610 V12 S16
SE305290 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 10 | 200 | 3 | 0.75 | 3.7 | 1832 | 1 | E40610 V12 S16
SE305300 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 208 | 3 | 0.75 | 3.5 | 1832 | 1 | E40610 V12 S16
SE305300 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 10 | 208 | 3 | 0.75 | 3.5 | 1832 | 1 | E40610 V12 S16
SE305300 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 10 | 208 | 3 | 0.75 | 3.5 | 1832 | 1 | E40610 V12 S16
SE305310 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 240 | 3 | 0.75 | 3.2 | 1832 | 1 | E40610 V12 S16
SE305310 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 10 | 240 | 3 | 0.75 | 3.2 | 1832 | 1 | E40610 V12 S16
SE305310 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 10 | 240 | 3 | 0.75 | 3.2 | 1832 | 1 | E40610 V12 S16
SE305320 | C | CB | Square D | FAL34015 | 18 | 15 | 480 | 3 | 18 | 480 | 3 | 0.75 | 1.6 | 1832 | 1 | E40610 V12 S16
SE305320 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 18 | 480 | 3 | 0.75 | 1.6 | 1832 | 1 | E40610 V12 S16
SE305320 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 18 | 480 | 3 | 0.75 | 1.6 | 1832 | 1 | E40610 V12 S16
SE305330 | C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 0.75 | 1.3 | 1832 | 1 | E40610 V12 S16
SE305330 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 14 | 600 | 3 | 0.75 | 1.3 | 1832 | 1 | E40610 V12 S16
SE305330 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 14 | 600 | 3 | 0.75 | 1.3 | 1832 | 1 | E40610 V12 S16
SE305340 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 200 | 3 | 1 | 4.8 | 1832 | 1 | E40610 V12 S16
SE305340 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 10 | 200 | 3 | 1 | 4.8 | 1832 | 1 | E40610 V12 S16
SE305340 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 10 | 200 | 3 | 1 | 4.8 | 1832 | 1 | E40610 V12 S16
SE305350 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 208 | 3 | 1 | 4.6 | 1832 | 1 | E40610 V12 S16
SE305350 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 10 | 208 | 3 | 1 | 4.6 | 1832 | 1 | E40610 V12 S16
SE305350 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 10 | 208 | 3 | 1 | 4.6 | 1832 | 1 | E40610 V12 S16
SE305360 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 240 | 3 | 1 | 4.2 | 1832 | 1 | E40610 V12 S16
SE305360 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 10 | 240 | 3 | 1 | 4.2 | 1832 | 1 | E40610 V12 S16
SE305360 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 10 | 240 | 3 | 1 | 4.2 | 1832 | 1 | E40610 V12 S16
SE305370 | C | CB | Square D | FAL34015 | 18 | 15 | 480 | 3 | 18 | 480 | 3 | 1 | 2.1 | 1832 | 1 | E40610 V12 S16
SE305370 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 18 | 480 | 3 | 1 | 2.1 | 1832 | 1 | E40610 V12 S16
SE305370 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 18 | 480 | 3 | 1 | 2.1 | 1832 | 1 | E40610 V12 S16
SE305380 | C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 1 | 1.7 | 1832 | 1 | E40610 V12 S16
SE305380 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 14 | 600 | 3 | 1 | 1.7 | 1832 | 1 | E40610 V12 S16
SE305380 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 14 | 600 | 3 | 1 | 1.7 | 1832 | 1 | E40610 V12 S16
SE305390 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 200 | 3 | 1.5 | 6.9 | 1832 | 1 | E40610 V12 S16
SE305390 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 10 | 200 | 3 | 1.5 | 6.9 | 1832 | 1 | E40610 V12 S16
SE305390 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 10 | 200 | 3 | 1.5 | 6.9 | 1832 | 1 | E40610 V12 S16
SE305400 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 208 | 3 | 1.5 | 6.6 | 1832 | 1 | E40610 V12 S16
SE305400 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 10 | 208 | 3 | 1.5 | 6.6 | 1832 | 1 | E40610 V12 S16
SE305400 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 10 | 208 | 3 | 1.5 | 6.6 | 1832 | 1 | E40610 V12 S16
SE305410 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 240 | 3 | 1.5 | 6 | 1832 | 1 | E40610 V12 S16
SE305410 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 10 | 240 | 3 | 1.5 | 6 | 1832 | 1 | E40610 V12 S16
SE305410 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 10 | 240 | 3 | 1.5 | 6 | 1832 | 1 | E40610 V12 S16
SE305420 | C | CB | Square D | FAL34015 | 18 | 15 | 480 | 3 | 18 | 480 | 3 | 1.5 | 3 | 1832 | 1 | E40610 V12 S16
SE305420 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 18 | 480 | 3 | 1.5 | 3 | 1832 | 1 | E40610 V12 S16
SE305420 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 18 | 480 | 3 | 1.5 | 3 | 1832 | 1 | E40610 V12 S16
SE305430 | C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 1.5 | 2.4 | 1832 | 1 | E40610 V12 S16
SE305430 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 14 | 600 | 3 | 1.5 | 2.4 | 1832 | 1 | E40610 V12 S16
SE305430 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 14 | 600 | 3 | 1.5 | 2.4 | 1832 | 1 | E40610 V12 S16
SE305440 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 200 | 3 | 2 | 7.82 | 1832 | 1 | E40610 V12 S16
SE305440 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 10 | 200 | 3 | 2 | 7.82 | 1832 | 1 | E40610 V12 S16
SE305440 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 10 | 200 | 3 | 2 | 7.82 | 1832 | 1 | E40610 V12 S16
SE305450 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 208 | 3 | 2 | 7.5 | 1832 | 1 | E40610 V12 S16
SE305450 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 10 | 208 | 3 | 2 | 7.5 | 1832 | 1 | E40610 V12 S16
SE305450 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 10 | 208 | 3 | 2 | 7.5 | 1832 | 1 | E40610 V12 S16
SE305460 | C | CB | Square D | FAL32020 | 10 | 20 | 240 | 3 | 10 | 200 | 3 | 2 | 7.82 | 1832 | 1 | E40610 V12 S16
SE305460 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 10 | 200 | 3 | 2 | 7.82 | 1832 | 1 | E40610 V12 S16
SE305460 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 10 | 200 | 3 | 2 | 7.82 | 1832 | 1 | E40610 V12 S16
SE305470 | C | CB | Square D | FAL32020 | 10 | 20 | 240 | 3 | 10 | 208 | 3 | 2 | 7.5 | 1832 | 1 | E40610 V12 S16
SE305470 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 10 | 208 | 3 | 2 | 7.5 | 1832 | 1 | E40610 V12 S16
SE305470 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 10 | 208 | 3 | 2 | 7.5 | 1832 | 1 | E40610 V12 S16
SE305480 | C | CB | Square D | FAL32015 | 10 | 15 | 240 | 3 | 10 | 240 | 3 | 2 | 6.8 | 1832 | 1 | E40610 V12 S16
SE305480 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 10 | 240 | 3 | 2 | 6.8 | 1832 | 1 | E40610 V12 S16
SE305480 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 10 | 240 | 3 | 2 | 6.8 | 1832 | 1 | E40610 V12 S16
SE305490 | C | CB | Square D | FAL34015 | 18 | 15 | 480 | 3 | 18 | 480 | 3 | 2 | 3.4 | 1832 | 1 | E40610 V12 S16
SE305490 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 18 | 480 | 3 | 2 | 3.4 | 1832 | 1 | E40610 V12 S16
SE305490 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 18 | 480 | 3 | 2 | 3.4 | 1832 | 1 | E40610 V12 S16
SE305500 | C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 2 | 2.7 | 1832 | 1 | E40610 V12 S16
SE305500 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 14 | 600 | 3 | 2 | 2.7 | 1832 | 1 | E40610 V12 S16
SE305500 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 14 | 600 | 3 | 2 | 2.7 | 1832 | 1 | E40610 V12 S16
SE305510 | C | CB | Square D | FAL32020 | 10 | 20 | 240 | 3 | 10 | 200 | 3 | 3 | 11 | 1832 | 1 | E40610 V12 S16
SE305510 |  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3 | 10 | 200 | 3 | 3 | 11 | 1832 | 1 | E40610 V12 S16
SE305510 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 10 | 200 | 3 | 3 | 11 | 1832 | 1 | E40610 V12 S16
SE305520 | C | CB | Square D | FAL32020 | 10 | 20 | 240 | 3 | 10 | 208 | 3 | 3 | 10.6 | 1832 | 1 | E40610 V12 S16
SE305520 |  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3 | 10 | 208 | 3 | 3 | 10.6 | 1832 | 1 | E40610 V12 S16
SE305520 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 10 | 208 | 3 | 3 | 10.6 | 1832 | 1 | E40610 V12 S16
SE305530 | C | CB | Square D | FAL32025 | 10 | 25 | 240 | 3 | 10 | 200 | 3 | 3 | 11 | 1832 | 1 | E40610 V12 S16
SE305530 |  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3 | 10 | 200 | 3 | 3 | 11 | 1832 | 1 | E40610 V12 S16
SE305530 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 10 | 200 | 3 | 3 | 11 | 1832 | 1 | E40610 V12 S16
SE305540 | C | CB | Square D | FAL32025 | 10 | 25 | 240 | 3 | 10 | 208 | 3 | 3 | 10.6 | 1832 | 1 | E40610 V12 S16
SE305540 |  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3 | 10 | 208 | 3 | 3 | 10.6 | 1832 | 1 | E40610 V12 S16
SE305540 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 10 | 208 | 3 | 3 | 10.6 | 1832 | 1 | E40610 V12 S16
SE305550 | C | CB | Square D | FAL32020 | 10 | 20 | 240 | 3 | 10 | 240 | 3 | 3 | 9.6 | 1832 | 1 | E40610 V12 S16
SE305550 |  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3 | 10 | 240 | 3 | 3 | 9.6 | 1832 | 1 | E40610 V12 S16
SE305550 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 10 | 240 | 3 | 3 | 9.6 | 1832 | 1 | E40610 V12 S16
SE305560 | C | CB | Square D | FAL34015 | 18 | 15 | 480 | 3 | 18 | 480 | 3 | 3 | 4.8 | 1832 | 1 | E40610 V12 S16
SE305560 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 18 | 480 | 3 | 3 | 4.8 | 1832 | 1 | E40610 V12 S16
SE305560 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 18 | 480 | 3 | 3 | 4.8 | 1832 | 1 | E40610 V12 S16
SE305570 | C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 3 | 3.9 | 1832 | 1 | E40610 V12 S16
SE305570 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 14 | 600 | 3 | 3 | 3.9 | 1832 | 1 | E40610 V12 S16
SE305570 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 14 | 600 | 3 | 3 | 3.9 | 1832 | 1 | E40610 V12 S16
SE305580 | C | CB | Square D | FAL32035 | 10 | 35 | 240 | 3 | 10 | 200 | 3 | 5 | 17.5 | 1832 | 1 | E40610 V12 S16
SE305580 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 10 | 200 | 3 | 5 | 17.5 | 1832 | 1 | E40610 V12 S16
SE305580 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 10 | 200 | 3 | 5 | 17.5 | 1832 | 1 | E40610 V12 S16
SE305590 | C | CB | Square D | FAL32035 | 10 | 35 | 240 | 3 | 10 | 208 | 3 | 5 | 16.7 | 1832 | 1 | E40610 V12 S16
SE305590 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 10 | 208 | 3 | 5 | 16.7 | 1832 | 1 | E40610 V12 S16
SE305590 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 10 | 208 | 3 | 5 | 16.7 | 1832 | 1 | E40610 V12 S16
SE305600 | C | CB | Square D | FAL32030 | 10 | 30 | 240 | 3 | 10 | 240 | 3 | 5 | 15.2 | 1832 | 1 | E40610 V12 S16
SE305600 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 10 | 240 | 3 | 5 | 15.2 | 1832 | 1 | E40610 V12 S16
SE305600 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 10 | 240 | 3 | 5 | 15.2 | 1832 | 1 | E40610 V12 S16
SE305610 | C | CB | Square D | FAL34015 | 18 | 15 | 480 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1 | E40610 V12 S16
SE305610 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1 | E40610 V12 S16
SE305610 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1 | E40610 V12 S16
SE305620 | C | CB | Square D | FAL32035 | 10 | 35 | 240 | 3 | 10 | 240 | 3 | 5 | 15.2 | 1832 | 1 | E40610 V12 S16
SE305620 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 10 | 240 | 3 | 5 | 15.2 | 1832 | 1 | E40610 V12 S16
SE305620 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 10 | 240 | 3 | 5 | 15.2 | 1832 | 1 | E40610 V12 S16
SE305630 | C | CB | Square D | FAL34020 | 18 | 20 | 480 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1 | E40610 V12 S16
SE305630 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1 | E40610 V12 S16
SE305630 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1 | E40610 V12 S16
SE305640 | C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 5 | 6.1 | 1832 | 1 | E40610 V12 S16
SE305640 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 14 | 600 | 3 | 5 | 6.1 | 1832 | 1 | E40610 V12 S16
SE305640 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 14 | 600 | 3 | 5 | 6.1 | 1832 | 1 | E40610 V12 S16
SE305650 | C | CB | Square D | FAL32050 | 10 | 50 | 240 | 3 | 10 | 200 | 3 | 7.5 | 25.3 | 1832 | 1 | E40610 V12 S16
SE305650 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 10 | 200 | 3 | 7.5 | 25.3 | 1832 | 1 | E40610 V12 S16
SE305650 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 10 | 200 | 3 | 7.5 | 25.3 | 1832 | 1 | E40610 V12 S16
SE305660 | C | CB | Square D | FAL32050 | 10 | 50 | 240 | 3 | 10 | 208 | 3 | 7.5 | 24.2 | 1832 | 1 | E40610 V12 S16
SE305660 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 10 | 208 | 3 | 7.5 | 24.2 | 1832 | 1 | E40610 V12 S16
SE305660 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 10 | 208 | 3 | 7.5 | 24.2 | 1832 | 1 | E40610 V12 S16
SE305670 | C | CB | Square D | FAL32040 | 10 | 40 | 240 | 3 | 10 | 240 | 3 | 7.5 | 22 | 1832 | 1 | E40610 V12 S16
SE305670 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 10 | 240 | 3 | 7.5 | 22 | 1832 | 1 | E40610 V12 S16
SE305670 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 10 | 240 | 3 | 7.5 | 22 | 1832 | 1 | E40610 V12 S16
SE305680 | C | CB | Square D | FAL34020 | 18 | 20 | 480 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1 | E40610 V12 S16
SE305680 |  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1 | E40610 V12 S16
SE305680 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1 | E40610 V12 S16
SE305690 | C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 1832 | 1 | E40610 V12 S16
SE305690 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 1832 | 1 | E40610 V12 S16
SE305690 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 1832 | 1 | E40610 V12 S16
SE305700 | C | CB | Square D | FAL32060 | 10 | 60 | 240 | 3 | 10 | 200 | 3 | 7.5 | 25.3 | 1832 | 1 | E40610 V12 S16
SE305700 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 10 | 200 | 3 | 7.5 | 25.3 | 1832 | 1 | E40610 V12 S16
SE305700 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 10 | 200 | 3 | 7.5 | 25.3 | 1832 | 1 | E40610 V12 S16
SE305710 | C | CB | Square D | FAL32060 | 10 | 60 | 240 | 3 | 10 | 208 | 3 | 7.5 | 24.2 | 1832 | 1 | E40610 V12 S16
SE305710 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 10 | 208 | 3 | 7.5 | 24.2 | 1832 | 1 | E40610 V12 S16
SE305710 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 10 | 208 | 3 | 7.5 | 24.2 | 1832 | 1 | E40610 V12 S16
SE305720 | C | CB | Square D | FAL32045 | 10 | 45 | 240 | 3 | 10 | 240 | 3 | 7.5 | 22 | 1832 | 1 | E40610 V12 S16
SE305720 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 10 | 240 | 3 | 7.5 | 22 | 1832 | 1 | E40610 V12 S16
SE305720 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 10 | 240 | 3 | 7.5 | 22 | 1832 | 1 | E40610 V12 S16
SE305730 | C | CB | Square D | FAL34025 | 18 | 25 | 480 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1 | E40610 V12 S16
SE305730 |  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1 | E40610 V12 S16
SE305730 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1 | E40610 V12 S16
SE305740 | C | CB | Square D | FAL36020 | 14 | 20 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 1832 | 1 | E40610 V12 S16
SE305740 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 1832 | 1 | E40610 V12 S16
SE305740 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 1832 | 1 | E40610 V12 S16
SE305750 | C | CB | Square D | FAL32060 | 10 | 60 | 240 | 3 | 10 | 200 | 3 | 10 | 32.2 | 1832 | 1 | E40610 V12 S16
SE305750 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 10 | 200 | 3 | 10 | 32.2 | 1832 | 1 | E40610 V12 S16
SE305750 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 10 | 200 | 3 | 10 | 32.2 | 1832 | 1 | E40610 V12 S16
SE305760 | C | CB | Square D | FAL32060 | 10 | 60 | 240 | 3 | 10 | 208 | 3 | 10 | 30.8 | 1832 | 1 | E40610 V12 S16
SE305760 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 10 | 208 | 3 | 10 | 30.8 | 1832 | 1 | E40610 V12 S16
SE305760 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 10 | 208 | 3 | 10 | 30.8 | 1832 | 1 | E40610 V12 S16
SE305770 | C | CB | Square D | FAL32050 | 10 | 50 | 240 | 3 | 10 | 240 | 3 | 10 | 28 | 1832 | 1 | E40610 V12 S16
SE305770 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 10 | 240 | 3 | 10 | 28 | 1832 | 1 | E40610 V12 S16
SE305770 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 10 | 240 | 3 | 10 | 28 | 1832 | 1 | E40610 V12 S16
SE305780 | C | CB | Square D | FAL34025 | 18 | 25 | 480 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1 | E40610 V12 S16
SE305780 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1 | E40610 V12 S16
SE305780 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1 | E40610 V12 S16
SE305790 | C | CB | Square D | FAL36020 | 14 | 20 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 1832 | 1 | E40610 V12 S16
SE305790 |  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 1832 | 1 | E40610 V12 S16
SE305790 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 1832 | 1 | E40610 V12 S16
SE305800 | C | CB | Square D | FAL32070 | 10 | 70 | 240 | 3 | 10 | 200 | 3 | 10 | 32.2 | 1832 | 1 | E40610 V12 S16
SE305800 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 10 | 200 | 3 | 10 | 32.2 | 1832 | 1 | E40610 V12 S16
SE305800 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 10 | 200 | 3 | 10 | 32.2 | 1832 | 1 | E40610 V12 S16
SE305810 | C | CB | Square D | FAL32070 | 10 | 70 | 240 | 3 | 10 | 208 | 3 | 10 | 30.8 | 1832 | 1 | E40610 V12 S16
SE305810 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 10 | 208 | 3 | 10 | 30.8 | 1832 | 1 | E40610 V12 S16
SE305810 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 10 | 208 | 3 | 10 | 30.8 | 1832 | 1 | E40610 V12 S16
SE305820 | C | CB | Square D | FAL32060 | 10 | 60 | 240 | 3 | 10 | 240 | 3 | 10 | 28 | 1832 | 1 | E40610 V12 S16
SE305820 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 10 | 240 | 3 | 10 | 28 | 1832 | 1 | E40610 V12 S16
SE305820 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 10 | 240 | 3 | 10 | 28 | 1832 | 1 | E40610 V12 S16
SE305830 | C | CB | Square D | FAL34030 | 18 | 30 | 480 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1 | E40610 V12 S16
SE305830 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1 | E40610 V12 S16
SE305830 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1 | E40610 V12 S16
SE305840 | C | CB | Square D | FAL36025 | 14 | 25 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 1832 | 1 | E40610 V12 S16
SE305840 |  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 1832 | 1 | E40610 V12 S16
SE305840 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 1832 | 1 | E40610 V12 S16
SE305850 | C | CB | Square D | FAL32090 | 10 | 90 | 240 | 3 | 10 | 200 | 3 | 15 | 48.3 | 2289 | 1 | E40610 V12 S16
SE305850 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 10 | 200 | 3 | 15 | 48.3 | 2289 | 1 | E40610 V12 S16
SE305850 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 10 | 200 | 3 | 15 | 48.3 | 2289 | 1 | E40610 V12 S16
SE305860 | C | CB | Square D | FAL32090 | 10 | 90 | 240 | 3 | 10 | 208 | 3 | 15 | 46.2 | 2289 | 1 | E40610 V12 S16
SE305860 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 10 | 208 | 3 | 15 | 46.2 | 2289 | 1 | E40610 V12 S16
SE305860 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 10 | 208 | 3 | 15 | 46.2 | 2289 | 1 | E40610 V12 S16
SE305870 | C | CB | Square D | FAL32080 | 10 | 80 | 240 | 3 | 10 | 240 | 3 | 15 | 42 | 2289 | 1 | E40610 V12 S16
SE305870 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 10 | 240 | 3 | 15 | 42 | 2289 | 1 | E40610 V12 S16
SE305870 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 10 | 240 | 3 | 15 | 42 | 2289 | 1 | E40610 V12 S16
SE305880 | C | CB | Square D | FAL34040 | 18 | 40 | 480 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1 | E40610 V12 S16
SE305880 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1 | E40610 V12 S16
SE305880 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1 | E40610 V12 S16
SE305890 | C | CB | Square D | FAL36030 | 14 | 30 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 1832 | 1 | E40610 V12 S16
SE305890 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 1832 | 1 | E40610 V12 S16
SE305890 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 1832 | 1 | E40610 V12 S16
SE305900 | C | CB | Square D | FAL32090 | 10 | 90 | 240 | 3 | 10 | 240 | 3 | 15 | 42 | 2289 | 1 | E40610 V12 S16
SE305900 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 10 | 240 | 3 | 15 | 42 | 2289 | 1 | E40610 V12 S16
SE305900 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 10 | 240 | 3 | 15 | 42 | 2289 | 1 | E40610 V12 S16
SE305910 | C | CB | Square D | FAL34045 | 18 | 45 | 480 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1 | E40610 V12 S16
SE305910 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1 | E40610 V12 S16
SE305910 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1 | E40610 V12 S16
SE305920 | C | CB | Square D | FAL36035 | 14 | 35 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 1832 | 1 | E40610 V12 S16
SE305920 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 1832 | 1 | E40610 V12 S16
SE305920 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 1832 | 1 | E40610 V12 S16
SE305930 | C | CB | Square D | FAL32100 | 10 | 100 | 240 | 3 | 10 | 200 | 3 | 20 | 62.1 | 2289 | 1 | E40610 V12 S16
SE305930 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 10 | 200 | 3 | 20 | 62.1 | 2289 | 1 | E40610 V12 S16
SE305930 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 10 | 200 | 3 | 20 | 62.1 | 2289 | 1 | E40610 V12 S16
SE305940 | C | CB | Square D | FAL32100 | 10 | 100 | 240 | 3 | 10 | 208 | 3 | 20 | 59.4 | 2289 | 1 | E40610 V12 S16
SE305940 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 10 | 208 | 3 | 20 | 59.4 | 2289 | 1 | E40610 V12 S16
SE305940 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 10 | 208 | 3 | 20 | 59.4 | 2289 | 1 | E40610 V12 S16
SE305950 | C | CB | Square D | FAL32090 | 10 | 90 | 240 | 3 | 10 | 240 | 3 | 20 | 54 | 2289 | 1 | E40610 V12 S16
SE305950 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 10 | 240 | 3 | 20 | 54 | 2289 | 1 | E40610 V12 S16
SE305950 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 10 | 240 | 3 | 20 | 54 | 2289 | 1 | E40610 V12 S16
SE305960 | C | CB | Square D | FAL34050 | 18 | 50 | 480 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1 | E40610 V12 S16
SE305960 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1 | E40610 V12 S16
SE305960 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1 | E40610 V12 S16
SE305970 | C | CB | Square D | FAL34060 | 18 | 60 | 480 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1 | E40610 V12 S16
SE305970 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1 | E40610 V12 S16
SE305970 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1 | E40610 V12 S16
SE305980 | C | CB | Square D | FAL36045 | 14 | 45 | 600 | 3 | 14 | 600 | 3 | 20 | 22 | 1832 | 1 | E40610 V12 S16
SE305980 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 14 | 600 | 3 | 20 | 22 | 1832 | 1 | E40610 V12 S16
SE305980 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 14 | 600 | 3 | 20 | 22 | 1832 | 1 | E40610 V12 S16
SE305990 | C | CB | Square D | FAL32100 | 10 | 100 | 240 | 3 | 10 | 240 | 3 | 25 | 68 | 3663 | 1 | E40610 V12 S16
SE305990 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 10 | 240 | 3 | 25 | 68 | 3663 | 1 | E40610 V12 S16
SE305990 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 10 | 240 | 3 | 25 | 68 | 3663 | 1 | E40610 V12 S16
SE306000 | C | CB | Square D | FAL34060 | 18 | 60 | 480 | 3 | 18 | 480 | 3 | 25 | 34 | 2289 | 1 | E40610 V12 S16
SE306000 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2289 | 1 | E40610 V12 S16
SE306000 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2289 | 1 | E40610 V12 S16
SE306010 | C | CB | Square D | FAL36050 | 14 | 50 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 1832 | 1 | E40610 V12 S16
SE306010 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 1832 | 1 | E40610 V12 S16
SE306010 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 1832 | 1 | E40610 V12 S16
SE306020 | C | CB | Square D | FAL34070 | 18 | 70 | 480 | 3 | 18 | 480 | 3 | 25 | 34 | 2289 | 1 | E40610 V12 S16
SE306020 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2289 | 1 | E40610 V12 S16
SE306020 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2289 | 1 | E40610 V12 S16
SE306030 | C | CB | Square D | FAL36060 | 14 | 60 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 1832 | 1 | E40610 V12 S16
SE306030 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 1832 | 1 | E40610 V12 S16
SE306030 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 1832 | 1 | E40610 V12 S16
SE306040 | C | CB | Square D | FAL34080 | 18 | 80 | 480 | 3 | 18 | 480 | 3 | 30 | 40 | 2289 | 1 | E40610 V12 S16
SE306040 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2289 | 1 | E40610 V12 S16
SE306040 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2289 | 1 | E40610 V12 S16
SE306050 | C | CB | Square D | FAL36060 | 14 | 60 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2289 | 1 | E40610 V12 S16
SE306050 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2289 | 1 | E40610 V12 S16
SE306050 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2289 | 1 | E40610 V12 S16
SE306060 | C | CB | Square D | FAL36070 | 14 | 70 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2289 | 1 | E40610 V12 S16
SE306060 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2289 | 1 | E40610 V12 S16
SE306060 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2289 | 1 | E40610 V12 S16
SE306070 | C | CB | Square D | FAL34090 | 18 | 90 | 480 | 3 | 18 | 480 | 3 | 40 | 52 | 2289 | 1 | E40610 V12 S16
SE306070 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 18 | 480 | 3 | 40 | 52 | 2289 | 1 | E40610 V12 S16
SE306070 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 18 | 480 | 3 | 40 | 52 | 2289 | 1 | E40610 V12 S16
SE306080 | C | CB | Square D | FAL36080 | 14 | 80 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2289 | 1 | E40610 V12 S16
SE306080 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2289 | 1 | E40610 V12 S16
SE306080 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2289 | 1 | E40610 V12 S16
SE306090 | C | CB | Square D | FAL36090 | 14 | 90 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2289 | 1 | E40610 V12 S16
SE306090 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2289 | 1 | E40610 V12 S16
SE306090 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2289 | 1 | E40610 V12 S16
SE306100 | C | CB | Square D | FAL34100 | 18 | 100 | 480 | 3 | 18 | 480 | 3 | 50 | 65 | 3663 | 1 | E40610 V12 S16
SE306100 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 18 | 480 | 3 | 50 | 65 | 3663 | 1 | E40610 V12 S16
SE306100 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 18 | 480 | 3 | 50 | 65 | 3663 | 1 | E40610 V12 S16
SE306110 | C | CB | Square D | FAL36090 | 14 | 90 | 600 | 3 | 14 | 600 | 3 | 50 | 52 | 2289 | 1 | E40610 V12 S16
SE306110 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 14 | 600 | 3 | 50 | 52 | 2289 | 1 | E40610 V12 S16
SE306110 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 14 | 600 | 3 | 50 | 52 | 2289 | 1 | E40610 V12 S16
SE306120 | C | CB | Square D | FAL36100 | 14 | 100 | 600 | 3 | 14 | 600 | 3 | 60 | 62 | 2289 | 1 | E40610 V12 S16
SE306120 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 14 | 600 | 3 | 60 | 62 | 2289 | 1 | E40610 V12 S16
SE306120 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 14 | 600 | 3 | 60 | 62 | 2289 | 1 | E40610 V12 S16