## Type C - FH TM
Issued: 2006-05-17
Last Revised: 2006-11-16
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in.) | Conditions of Acceptability | Combination UL File
SE306130 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 0.5 | 2.5 | 1832 | 1 | E40610 V12 S15
SE306130 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 65 | 200 | 3 | 0.5 | 2.5 | 1832 | 1 | E40610 V12 S15
SE306130 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 65 | 200 | 3 | 0.5 | 2.5 | 1832 | 1 | E40610 V12 S15
SE306140 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 0.5 | 2.4 | 1832 | 1 | E40610 V12 S15
SE306140 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 65 | 208 | 3 | 0.5 | 2.4 | 1832 | 1 | E40610 V12 S15
SE306140 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 65 | 208 | 3 | 0.5 | 2.4 | 1832 | 1 | E40610 V12 S15
SE306150 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 0.5 | 2.2 | 1832 | 1 | E40610 V12 S15
SE306150 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 65 | 240 | 3 | 0.5 | 2.2 | 1832 | 1 | E40610 V12 S15
SE306150 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 65 | 240 | 3 | 0.5 | 2.2 | 1832 | 1 | E40610 V12 S15
SE306160 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 0.75 | 3.7 | 1832 | 1 | E40610 V12 S15
SE306160 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 65 | 200 | 3 | 0.75 | 3.7 | 1832 | 1 | E40610 V12 S15
SE306160 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 65 | 200 | 3 | 0.75 | 3.7 | 1832 | 1 | E40610 V12 S15
SE306170 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 0.75 | 3.5 | 1832 | 1 | E40610 V12 S15
SE306170 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 65 | 208 | 3 | 0.75 | 3.5 | 1832 | 1 | E40610 V12 S15
SE306170 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 65 | 208 | 3 | 0.75 | 3.5 | 1832 | 1 | E40610 V12 S15
SE306180 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 0.75 | 3.2 | 1832 | 1 | E40610 V12 S15
SE306180 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 65 | 240 | 3 | 0.75 | 3.2 | 1832 | 1 | E40610 V12 S15
SE306180 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 65 | 240 | 3 | 0.75 | 3.2 | 1832 | 1 | E40610 V12 S15
SE306190 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 0.75 | 1.6 | 1832 | 1 | E40610 V12 S15
SE306190 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 25 | 480 | 3 | 0.75 | 1.6 | 1832 | 1 | E40610 V12 S15
SE306190 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 25 | 480 | 3 | 0.75 | 1.6 | 1832 | 1 | E40610 V12 S15
SE306200 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 0.75 | 1.3 | 1832 | 1 | E40610 V12 S15
SE306200 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 18 | 600 | 3 | 0.75 | 1.3 | 1832 | 1 | E40610 V12 S15
SE306200 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 18 | 600 | 3 | 0.75 | 1.3 | 1832 | 1 | E40610 V12 S15
SE306210 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 1 | 4.8 | 1832 | 1 | E40610 V12 S15
SE306210 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 65 | 200 | 3 | 1 | 4.8 | 1832 | 1 | E40610 V12 S15
SE306210 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 65 | 200 | 3 | 1 | 4.8 | 1832 | 1 | E40610 V12 S15
SE306220 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 1 | 4.6 | 1832 | 1 | E40610 V12 S15
SE306220 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 65 | 208 | 3 | 1 | 4.6 | 1832 | 1 | E40610 V12 S15
SE306220 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 65 | 208 | 3 | 1 | 4.6 | 1832 | 1 | E40610 V12 S15
SE306230 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 1 | 4.2 | 1832 | 1 | E40610 V12 S15
SE306230 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 65 | 240 | 3 | 1 | 4.2 | 1832 | 1 | E40610 V12 S15
SE306230 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 65 | 240 | 3 | 1 | 4.2 | 1832 | 1 | E40610 V12 S15
SE306240 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 1 | 2.1 | 1832 | 1 | E40610 V12 S15
SE306240 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 25 | 480 | 3 | 1 | 2.1 | 1832 | 1 | E40610 V12 S15
SE306240 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 25 | 480 | 3 | 1 | 2.1 | 1832 | 1 | E40610 V12 S15
SE306250 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 1 | 1.7 | 1832 | 1 | E40610 V12 S15
SE306250 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 18 | 600 | 3 | 1 | 1.7 | 1832 | 1 | E40610 V12 S15
SE306250 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 18 | 600 | 3 | 1 | 1.7 | 1832 | 1 | E40610 V12 S15
SE306260 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 1.5 | 6.9 | 1832 | 1 | E40610 V12 S15
SE306260 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 65 | 200 | 3 | 1.5 | 6.9 | 1832 | 1 | E40610 V12 S15
SE306260 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 65 | 200 | 3 | 1.5 | 6.9 | 1832 | 1 | E40610 V12 S15
SE306270 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 1.5 | 6.6 | 1832 | 1 | E40610 V12 S15
SE306270 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 65 | 208 | 3 | 1.5 | 6.6 | 1832 | 1 | E40610 V12 S15
SE306270 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 65 | 208 | 3 | 1.5 | 6.6 | 1832 | 1 | E40610 V12 S15
SE306280 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 1.5 | 6 | 1832 | 1 | E40610 V12 S15
SE306280 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 65 | 240 | 3 | 1.5 | 6 | 1832 | 1 | E40610 V12 S15
SE306280 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 65 | 240 | 3 | 1.5 | 6 | 1832 | 1 | E40610 V12 S15
SE306290 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 1.5 | 3 | 1832 | 1 | E40610 V12 S15
SE306290 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 25 | 480 | 3 | 1.5 | 3 | 1832 | 1 | E40610 V12 S15
SE306290 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 25 | 480 | 3 | 1.5 | 3 | 1832 | 1 | E40610 V12 S15
SE306300 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 1.5 | 2.4 | 1832 | 1 | E40610 V12 S15
SE306300 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 18 | 600 | 3 | 1.5 | 2.4 | 1832 | 1 | E40610 V12 S15
SE306300 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 18 | 600 | 3 | 1.5 | 2.4 | 1832 | 1 | E40610 V12 S15
SE306310 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 2 | 7.82 | 1832 | 1 | E40610 V12 S15
SE306310 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 65 | 200 | 3 | 2 | 7.82 | 1832 | 1 | E40610 V12 S15
SE306310 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 65 | 200 | 3 | 2 | 7.82 | 1832 | 1 | E40610 V12 S15
SE306320 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1 | E40610 V12 S15
SE306320 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1 | E40610 V12 S15
SE306320 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1 | E40610 V12 S15
SE306330 | C | CB | Square D | FHL36020 | 65 | 20 | 600 | 3 | 65 | 200 | 3 | 2 | 7.82 | 1832 | 1 | E40610 V12 S15
SE306330 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 65 | 200 | 3 | 2 | 7.82 | 1832 | 1 | E40610 V12 S15
SE306330 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 65 | 200 | 3 | 2 | 7.82 | 1832 | 1 | E40610 V12 S15
SE306340 | C | CB | Square D | FHL36020 | 65 | 20 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1 | E40610 V12 S15
SE306340 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1 | E40610 V12 S15
SE306340 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1 | E40610 V12 S15
SE306350 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 2 | 6.8 | 1832 | 1 | E40610 V12 S15
SE306350 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 65 | 240 | 3 | 2 | 6.8 | 1832 | 1 | E40610 V12 S15
SE306350 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 65 | 240 | 3 | 2 | 6.8 | 1832 | 1 | E40610 V12 S15
SE306360 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 2 | 3.4 | 1832 | 1 | E40610 V12 S15
SE306360 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 25 | 480 | 3 | 2 | 3.4 | 1832 | 1 | E40610 V12 S15
SE306360 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 25 | 480 | 3 | 2 | 3.4 | 1832 | 1 | E40610 V12 S15
SE306370 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 1832 | 1 | E40610 V12 S15
SE306370 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 1832 | 1 | E40610 V12 S15
SE306370 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 1832 | 1 | E40610 V12 S15
SE306380 | C | CB | Square D | FHL36020 | 65 | 20 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1 | E40610 V12 S15
SE306380 |  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1 | E40610 V12 S15
SE306380 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1 | E40610 V12 S15
SE306390 | C | CB | Square D | FHL36020 | 65 | 20 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1 | E40610 V12 S15
SE306390 |  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1 | E40610 V12 S15
SE306390 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1 | E40610 V12 S15
SE306400 | C | CB | Square D | FHL36025 | 65 | 25 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1 | E40610 V12 S15
SE306400 |  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1 | E40610 V12 S15
SE306400 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1 | E40610 V12 S15
SE306410 | C | CB | Square D | FHL36025 | 65 | 25 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1 | E40610 V12 S15
SE306410 |  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1 | E40610 V12 S15
SE306410 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1 | E40610 V12 S15
SE306420 | C | CB | Square D | FHL36020 | 65 | 20 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1 | E40610 V12 S15
SE306420 |  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1 | E40610 V12 S15
SE306420 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1 | E40610 V12 S15
SE306430 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 3 | 4.8 | 1832 | 1 | E40610 V12 S15
SE306430 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 25 | 480 | 3 | 3 | 4.8 | 1832 | 1 | E40610 V12 S15
SE306430 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 25 | 480 | 3 | 3 | 4.8 | 1832 | 1 | E40610 V12 S15
SE306440 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 3 | 3.9 | 1832 | 1 | E40610 V12 S15
SE306440 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 18 | 600 | 3 | 3 | 3.9 | 1832 | 1 | E40610 V12 S15
SE306440 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 18 | 600 | 3 | 3 | 3.9 | 1832 | 1 | E40610 V12 S15
SE306450 | C | CB | Square D | FHL36035 | 65 | 35 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1 | E40610 V12 S15
SE306450 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1 | E40610 V12 S15
SE306450 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1 | E40610 V12 S15
SE306460 | C | CB | Square D | FHL36035 | 65 | 35 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1 | E40610 V12 S15
SE306460 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1 | E40610 V12 S15
SE306460 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1 | E40610 V12 S15
SE306470 | C | CB | Square D | FHL36030 | 65 | 30 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1 | E40610 V12 S15
SE306470 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1 | E40610 V12 S15
SE306470 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1 | E40610 V12 S15
SE306480 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 5 | 7.6 | 1832 | 1 | E40610 V12 S15
SE306480 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 25 | 480 | 3 | 5 | 7.6 | 1832 | 1 | E40610 V12 S15
SE306480 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 25 | 480 | 3 | 5 | 7.6 | 1832 | 1 | E40610 V12 S15
SE306490 | C | CB | Square D | FHL36035 | 65 | 35 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1 | E40610 V12 S15
SE306490 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1 | E40610 V12 S15
SE306490 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1 | E40610 V12 S15
SE306500 | C | CB | Square D | FHL36020 | 25 | 20 | 600 | 3 | 25 | 480 | 3 | 5 | 7.6 | 1832 | 1 | E40610 V12 S15
SE306500 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 25 | 480 | 3 | 5 | 7.6 | 1832 | 1 | E40610 V12 S15
SE306500 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 25 | 480 | 3 | 5 | 7.6 | 1832 | 1 | E40610 V12 S15
SE306510 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 1832 | 1 | E40610 V12 S15
SE306510 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 1832 | 1 | E40610 V12 S15
SE306510 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 1832 | 1 | E40610 V12 S15
SE306520 | C | CB | Square D | FHL36050 | 65 | 50 | 600 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 1832 | 1 | E40610 V12 S15
SE306520 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 1832 | 1 | E40610 V12 S15
SE306520 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 1832 | 1 | E40610 V12 S15
SE306530 | C | CB | Square D | FHL36050 | 65 | 50 | 600 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 1832 | 1 | E40610 V12 S15
SE306530 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 1832 | 1 | E40610 V12 S15
SE306530 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 1832 | 1 | E40610 V12 S15
SE306540 | C | CB | Square D | FHL36040 | 65 | 40 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1 | E40610 V12 S15
SE306540 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1 | E40610 V12 S15
SE306540 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1 | E40610 V12 S15
SE306550 | C | CB | Square D | FHL36020 | 25 | 20 | 600 | 3 | 25 | 480 | 3 | 7.5 | 11 | 1832 | 1 | E40610 V12 S15
SE306550 |  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3 | 25 | 480 | 3 | 7.5 | 11 | 1832 | 1 | E40610 V12 S15
SE306550 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 25 | 480 | 3 | 7.5 | 11 | 1832 | 1 | E40610 V12 S15
SE306560 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1 | E40610 V12 S15
SE306560 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1 | E40610 V12 S15
SE306560 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1 | E40610 V12 S15
SE306570 | C | CB | Square D | FHL36060 | 65 | 60 | 600 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 1832 | 1 | E40610 V12 S15
SE306570 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 1832 | 1 | E40610 V12 S15
SE306570 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 1832 | 1 | E40610 V12 S15
SE306580 | C | CB | Square D | FHL36060 | 65 | 60 | 600 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 1832 | 1 | E40610 V12 S15
SE306580 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 1832 | 1 | E40610 V12 S15
SE306580 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 1832 | 1 | E40610 V12 S15
SE306590 | C | CB | Square D | FHL36045 | 65 | 45 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1 | E40610 V12 S15
SE306590 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1 | E40610 V12 S15
SE306590 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1 | E40610 V12 S15
SE306600 | C | CB | Square D | FHL36025 | 25 | 25 | 600 | 3 | 25 | 480 | 3 | 7.5 | 11 | 1832 | 1 | E40610 V12 S15
SE306600 |  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3 | 25 | 480 | 3 | 7.5 | 11 | 1832 | 1 | E40610 V12 S15
SE306600 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 25 | 480 | 3 | 7.5 | 11 | 1832 | 1 | E40610 V12 S15
SE306610 | C | CB | Square D | FHL36020 | 18 | 20 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1 | E40610 V12 S15
SE306610 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1 | E40610 V12 S15
SE306610 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1 | E40610 V12 S15
SE306620 | C | CB | Square D | FHL36060 | 65 | 60 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1 | E40610 V12 S15
SE306620 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1 | E40610 V12 S15
SE306620 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1 | E40610 V12 S15
SE306630 | C | CB | Square D | FHL36060 | 65 | 60 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1 | E40610 V12 S15
SE306630 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1 | E40610 V12 S15
SE306630 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1 | E40610 V12 S15
SE306640 | C | CB | Square D | FHL36050 | 65 | 50 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1 | E40610 V12 S15
SE306640 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1 | E40610 V12 S15
SE306640 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1 | E40610 V12 S15
SE306650 | C | CB | Square D | FHL36025 | 25 | 25 | 600 | 3 | 25 | 480 | 3 | 10 | 14 | 1832 | 1 | E40610 V12 S15
SE306650 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 25 | 480 | 3 | 10 | 14 | 1832 | 1 | E40610 V12 S15
SE306650 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 25 | 480 | 3 | 10 | 14 | 1832 | 1 | E40610 V12 S15
SE306660 | C | CB | Square D | FHL36020 | 18 | 20 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1 | E40610 V12 S15
SE306660 |  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1 | E40610 V12 S15
SE306660 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1 | E40610 V12 S15
SE306670 | C | CB | Square D | FHL36070 | 65 | 70 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1 | E40610 V12 S15
SE306670 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1 | E40610 V12 S15
SE306670 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1 | E40610 V12 S15
SE306680 | C | CB | Square D | FHL36070 | 65 | 70 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1 | E40610 V12 S15
SE306680 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1 | E40610 V12 S15
SE306680 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1 | E40610 V12 S15
SE306690 | C | CB | Square D | FHL36060 | 65 | 60 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1 | E40610 V12 S15
SE306690 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1 | E40610 V12 S15
SE306690 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1 | E40610 V12 S15
SE306700 | C | CB | Square D | FHL36030 | 25 | 30 | 600 | 3 | 25 | 480 | 3 | 10 | 14 | 1832 | 1 | E40610 V12 S15
SE306700 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 25 | 480 | 3 | 10 | 14 | 1832 | 1 | E40610 V12 S15
SE306700 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 25 | 480 | 3 | 10 | 14 | 1832 | 1 | E40610 V12 S15
SE306710 | C | CB | Square D | FHL36025 | 18 | 25 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1 | E40610 V12 S15
SE306710 |  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1 | E40610 V12 S15
SE306710 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1 | E40610 V12 S15
SE306720 | C | CB | Square D | FHL36090 | 65 | 90 | 600 | 3 | 65 | 200 | 3 | 15 | 48.3 | 2289 | 1 | E40610 V12 S15
SE306720 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 65 | 200 | 3 | 15 | 48.3 | 2289 | 1 | E40610 V12 S15
SE306720 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 65 | 200 | 3 | 15 | 48.3 | 2289 | 1 | E40610 V12 S15
SE306730 | C | CB | Square D | FHL36090 | 65 | 90 | 600 | 3 | 65 | 208 | 3 | 15 | 46.2 | 2289 | 1 | E40610 V12 S15
SE306730 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 65 | 208 | 3 | 15 | 46.2 | 2289 | 1 | E40610 V12 S15
SE306730 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 65 | 208 | 3 | 15 | 46.2 | 2289 | 1 | E40610 V12 S15
SE306740 | C | CB | Square D | FHL36080 | 65 | 80 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 2289 | 1 | E40610 V12 S15
SE306740 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 2289 | 1 | E40610 V12 S15
SE306740 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 2289 | 1 | E40610 V12 S15
SE306750 | C | CB | Square D | FHL36040 | 25 | 40 | 600 | 3 | 25 | 480 | 3 | 15 | 21 | 1832 | 1 | E40610 V12 S15
SE306750 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 480 | 3 | 15 | 21 | 1832 | 1 | E40610 V12 S15
SE306750 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 25 | 480 | 3 | 15 | 21 | 1832 | 1 | E40610 V12 S15
SE306760 | C | CB | Square D | FHL36030 | 18 | 30 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1 | E40610 V12 S15
SE306760 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1 | E40610 V12 S15
SE306760 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1 | E40610 V12 S15
SE306770 | C | CB | Square D | FHL36090 | 65 | 90 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 2289 | 1 | E40610 V12 S15
SE306770 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 2289 | 1 | E40610 V12 S15
SE306770 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 2289 | 1 | E40610 V12 S15
SE306780 | C | CB | Square D | FHL36045 | 25 | 45 | 600 | 3 | 25 | 480 | 3 | 15 | 21 | 1832 | 1 | E40610 V12 S15
SE306780 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 480 | 3 | 15 | 21 | 1832 | 1 | E40610 V12 S15
SE306780 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 25 | 480 | 3 | 15 | 21 | 1832 | 1 | E40610 V12 S15
SE306790 | C | CB | Square D | FHL36035 | 18 | 35 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1 | E40610 V12 S15
SE306790 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1 | E40610 V12 S15
SE306790 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1 | E40610 V12 S15
SE306800 | C | CB | Square D | FHL36100 | 65 | 100 | 600 | 3 | 65 | 200 | 3 | 20 | 62.1 | 2289 | 1 | E40610 V12 S15
SE306800 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 65 | 200 | 3 | 20 | 62.1 | 2289 | 1 | E40610 V12 S15
SE306800 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 65 | 200 | 3 | 20 | 62.1 | 2289 | 1 | E40610 V12 S15
SE306810 | C | CB | Square D | FHL36100 | 65 | 100 | 600 | 3 | 65 | 208 | 3 | 20 | 59.4 | 2289 | 1 | E40610 V12 S15
SE306810 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 65 | 208 | 3 | 20 | 59.4 | 2289 | 1 | E40610 V12 S15
SE306810 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 65 | 208 | 3 | 20 | 59.4 | 2289 | 1 | E40610 V12 S15
SE306820 | C | CB | Square D | FHL36090 | 65 | 90 | 600 | 3 | 65 | 240 | 3 | 20 | 54 | 2289 | 1 | E40610 V12 S15
SE306820 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 65 | 240 | 3 | 20 | 54 | 2289 | 1 | E40610 V12 S15
SE306820 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 65 | 240 | 3 | 20 | 54 | 2289 | 1 | E40610 V12 S15
SE306830 | C | CB | Square D | FHL36050 | 25 | 50 | 600 | 3 | 25 | 480 | 3 | 20 | 27 | 1832 | 1 | E40610 V12 S15
SE306830 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 25 | 480 | 3 | 20 | 27 | 1832 | 1 | E40610 V12 S15
SE306830 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 25 | 480 | 3 | 20 | 27 | 1832 | 1 | E40610 V12 S15
SE306840 | C | CB | Square D | FHL36060 | 25 | 60 | 600 | 3 | 25 | 480 | 3 | 20 | 27 | 1832 | 1 | E40610 V12 S15
SE306840 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 25 | 480 | 3 | 20 | 27 | 1832 | 1 | E40610 V12 S15
SE306840 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 25 | 480 | 3 | 20 | 27 | 1832 | 1 | E40610 V12 S15
SE306850 | C | CB | Square D | FHL36045 | 18 | 45 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1 | E40610 V12 S15
SE306850 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1 | E40610 V12 S15
SE306850 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1 | E40610 V12 S15
SE306860 | C | CB | Square D | FHL36100 | 65 | 100 | 600 | 3 | 65 | 240 | 3 | 25 | 68 | 2289 | 1 | E40610 V12 S15
SE306860 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 65 | 240 | 3 | 25 | 68 | 2289 | 1 | E40610 V12 S15
SE306860 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 65 | 240 | 3 | 25 | 68 | 2289 | 1 | E40610 V12 S15
SE306870 | C | CB | Square D | FHL36060 | 25 | 60 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 2289 | 1 | E40610 V12 S15
SE306870 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 2289 | 1 | E40610 V12 S15
SE306870 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 2289 | 1 | E40610 V12 S15
SE306880 | C | CB | Square D | FHL36050 | 18 | 50 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1 | E40610 V12 S15
SE306880 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1 | E40610 V12 S15
SE306880 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1 | E40610 V12 S15
SE306890 | C | CB | Square D | FHL36070 | 25 | 70 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 2289 | 1 | E40610 V12 S15
SE306890 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 2289 | 1 | E40610 V12 S15
SE306890 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 2289 | 1 | E40610 V12 S15
SE306900 | C | CB | Square D | FHL36060 | 18 | 60 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1 | E40610 V12 S15
SE306900 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1 | E40610 V12 S15
SE306900 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1 | E40610 V12 S15
SE306910 | C | CB | Square D | FHL36080 | 25 | 80 | 600 | 3 | 25 | 480 | 3 | 30 | 40 | 2289 | 1 | E40610 V12 S15
SE306910 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 25 | 480 | 3 | 30 | 40 | 2289 | 1 | E40610 V12 S15
SE306910 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 25 | 480 | 3 | 30 | 40 | 2289 | 1 | E40610 V12 S15
SE306920 | C | CB | Square D | FHL36060 | 18 | 60 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2289 | 1 | E40610 V12 S15
SE306920 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2289 | 1 | E40610 V12 S15
SE306920 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2289 | 1 | E40610 V12 S15
SE306930 | C | CB | Square D | FHL36070 | 18 | 70 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2289 | 1 | E40610 V12 S15
SE306930 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2289 | 1 | E40610 V12 S15
SE306930 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2289 | 1 | E40610 V12 S15
SE306940 | C | CB | Square D | FHL36090 | 25 | 90 | 600 | 3 | 25 | 480 | 3 | 40 | 52 | 2289 | 1 | E40610 V12 S15
SE306940 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 25 | 480 | 3 | 40 | 52 | 2289 | 1 | E40610 V12 S15
SE306940 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 25 | 480 | 3 | 40 | 52 | 2289 | 1 | E40610 V12 S15
SE306950 | C | CB | Square D | FHL36080 | 18 | 80 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2289 | 1 | E40610 V12 S15
SE306950 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2289 | 1 | E40610 V12 S15
SE306950 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2289 | 1 | E40610 V12 S15
SE306960 | C | CB | Square D | FHL36090 | 18 | 90 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2289 | 1 | E40610 V12 S15
SE306960 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2289 | 1 | E40610 V12 S15
SE306960 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2289 | 1 | E40610 V12 S15
SE306970 | C | CB | Square D | FHL36100 | 25 | 100 | 600 | 3 | 25 | 480 | 3 | 50 | 65 | 2289 | 1 | E40610 V12 S15
SE306970 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 25 | 480 | 3 | 50 | 65 | 2289 | 1 | E40610 V12 S15
SE306970 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 25 | 480 | 3 | 50 | 65 | 2289 | 1 | E40610 V12 S15
SE306980 | C | CB | Square D | FHL36090 | 18 | 90 | 600 | 3 | 18 | 600 | 3 | 50 | 52 | 2289 | 1 | E40610 V12 S15
SE306980 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 18 | 600 | 3 | 50 | 52 | 2289 | 1 | E40610 V12 S15
SE306980 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 18 | 600 | 3 | 50 | 52 | 2289 | 1 | E40610 V12 S15
SE306990 | C | CB | Square D | FHL36100 | 18 | 100 | 600 | 3 | 18 | 600 | 3 | 60 | 62 | 2289 | 1 | E40610 V12 S15
SE306990 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 18 | 600 | 3 | 60 | 62 | 2289 | 1 | E40610 V12 S15
SE306990 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 18 | 600 | 3 | 60 | 62 | 2289 | 1 | E40610 V12 S15
SE307000 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 0.5 | 2.5 | 1832 | 1 | E40610 V12 S16
SE307000 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 65 | 200 | 3 | 0.5 | 2.5 | 1832 | 1 | E40610 V12 S16
SE307000 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 65 | 200 | 3 | 0.5 | 2.5 | 1832 | 1 | E40610 V12 S16
SE307010 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 0.5 | 2.4 | 1832 | 1 | E40610 V12 S16
SE307010 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 65 | 208 | 3 | 0.5 | 2.4 | 1832 | 1 | E40610 V12 S16
SE307010 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 65 | 208 | 3 | 0.5 | 2.4 | 1832 | 1 | E40610 V12 S16
SE307020 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 0.5 | 2.2 | 1832 | 1 | E40610 V12 S16
SE307020 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 65 | 240 | 3 | 0.5 | 2.2 | 1832 | 1 | E40610 V12 S16
SE307020 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 65 | 240 | 3 | 0.5 | 2.2 | 1832 | 1 | E40610 V12 S16
SE307030 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 0.75 | 3.7 | 1832 | 1 | E40610 V12 S16
SE307030 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 65 | 200 | 3 | 0.75 | 3.7 | 1832 | 1 | E40610 V12 S16
SE307030 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 65 | 200 | 3 | 0.75 | 3.7 | 1832 | 1 | E40610 V12 S16
SE307040 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 0.75 | 3.5 | 1832 | 1 | E40610 V12 S16
SE307040 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 65 | 208 | 3 | 0.75 | 3.5 | 1832 | 1 | E40610 V12 S16
SE307040 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 65 | 208 | 3 | 0.75 | 3.5 | 1832 | 1 | E40610 V12 S16
SE307050 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 0.75 | 3.2 | 1832 | 1 | E40610 V12 S16
SE307050 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 65 | 240 | 3 | 0.75 | 3.2 | 1832 | 1 | E40610 V12 S16
SE307050 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 65 | 240 | 3 | 0.75 | 3.2 | 1832 | 1 | E40610 V12 S16
SE307060 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 0.75 | 1.6 | 1832 | 1 | E40610 V12 S16
SE307060 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 25 | 480 | 3 | 0.75 | 1.6 | 1832 | 1 | E40610 V12 S16
SE307060 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 25 | 480 | 3 | 0.75 | 1.6 | 1832 | 1 | E40610 V12 S16
SE307070 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 0.75 | 1.3 | 1832 | 1 | E40610 V12 S16
SE307070 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 18 | 600 | 3 | 0.75 | 1.3 | 1832 | 1 | E40610 V12 S16
SE307070 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 18 | 600 | 3 | 0.75 | 1.3 | 1832 | 1 | E40610 V12 S16
SE307080 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 1 | 4.8 | 1832 | 1 | E40610 V12 S16
SE307080 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 65 | 200 | 3 | 1 | 4.8 | 1832 | 1 | E40610 V12 S16
SE307080 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 65 | 200 | 3 | 1 | 4.8 | 1832 | 1 | E40610 V12 S16
SE307090 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 1 | 4.6 | 1832 | 1 | E40610 V12 S16
SE307090 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 65 | 208 | 3 | 1 | 4.6 | 1832 | 1 | E40610 V12 S16
SE307090 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 65 | 208 | 3 | 1 | 4.6 | 1832 | 1 | E40610 V12 S16
SE307100 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 1 | 4.2 | 1832 | 1 | E40610 V12 S16
SE307100 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 65 | 240 | 3 | 1 | 4.2 | 1832 | 1 | E40610 V12 S16
SE307100 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 65 | 240 | 3 | 1 | 4.2 | 1832 | 1 | E40610 V12 S16
SE307110 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 1 | 2.1 | 1832 | 1 | E40610 V12 S16
SE307110 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 25 | 480 | 3 | 1 | 2.1 | 1832 | 1 | E40610 V12 S16
SE307110 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 25 | 480 | 3 | 1 | 2.1 | 1832 | 1 | E40610 V12 S16
SE307120 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 1 | 1.7 | 1832 | 1 | E40610 V12 S16
SE307120 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 18 | 600 | 3 | 1 | 1.7 | 1832 | 1 | E40610 V12 S16
SE307120 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 18 | 600 | 3 | 1 | 1.7 | 1832 | 1 | E40610 V12 S16
SE307130 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 1.5 | 6.9 | 1832 | 1 | E40610 V12 S16
SE307130 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 65 | 200 | 3 | 1.5 | 6.9 | 1832 | 1 | E40610 V12 S16
SE307130 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 65 | 200 | 3 | 1.5 | 6.9 | 1832 | 1 | E40610 V12 S16
SE307140 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 1.5 | 6.6 | 1832 | 1 | E40610 V12 S16
SE307140 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 65 | 208 | 3 | 1.5 | 6.6 | 1832 | 1 | E40610 V12 S16
SE307140 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 65 | 208 | 3 | 1.5 | 6.6 | 1832 | 1 | E40610 V12 S16
SE307150 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 1.5 | 6 | 1832 | 1 | E40610 V12 S16
SE307150 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 65 | 240 | 3 | 1.5 | 6 | 1832 | 1 | E40610 V12 S16
SE307150 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 65 | 240 | 3 | 1.5 | 6 | 1832 | 1 | E40610 V12 S16
SE307160 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 1.5 | 3 | 1832 | 1 | E40610 V12 S16
SE307160 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 25 | 480 | 3 | 1.5 | 3 | 1832 | 1 | E40610 V12 S16
SE307160 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 25 | 480 | 3 | 1.5 | 3 | 1832 | 1 | E40610 V12 S16
SE307170 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 1.5 | 2.4 | 1832 | 1 | E40610 V12 S16
SE307170 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 18 | 600 | 3 | 1.5 | 2.4 | 1832 | 1 | E40610 V12 S16
SE307170 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 18 | 600 | 3 | 1.5 | 2.4 | 1832 | 1 | E40610 V12 S16
SE307180 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 2 | 7.82 | 1832 | 1 | E40610 V12 S16
SE307180 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 65 | 200 | 3 | 2 | 7.82 | 1832 | 1 | E40610 V12 S16
SE307180 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 65 | 200 | 3 | 2 | 7.82 | 1832 | 1 | E40610 V12 S16
SE307190 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1 | E40610 V12 S16
SE307190 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1 | E40610 V12 S16
SE307190 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1 | E40610 V12 S16
SE307200 | C | CB | Square D | FHL36020 | 65 | 20 | 600 | 3 | 65 | 200 | 3 | 2 | 7.82 | 1832 | 1 | E40610 V12 S16
SE307200 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 65 | 200 | 3 | 2 | 7.82 | 1832 | 1 | E40610 V12 S16
SE307200 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 65 | 200 | 3 | 2 | 7.82 | 1832 | 1 | E40610 V12 S16
SE307210 | C | CB | Square D | FHL36020 | 65 | 20 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1 | E40610 V12 S16
SE307210 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1 | E40610 V12 S16
SE307210 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1 | E40610 V12 S16
SE307220 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 2 | 6.8 | 1832 | 1 | E40610 V12 S16
SE307220 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 65 | 240 | 3 | 2 | 6.8 | 1832 | 1 | E40610 V12 S16
SE307220 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 65 | 240 | 3 | 2 | 6.8 | 1832 | 1 | E40610 V12 S16
SE307230 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 2 | 3.4 | 1832 | 1 | E40610 V12 S16
SE307230 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 25 | 480 | 3 | 2 | 3.4 | 1832 | 1 | E40610 V12 S16
SE307230 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 25 | 480 | 3 | 2 | 3.4 | 1832 | 1 | E40610 V12 S16
SE307240 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 1832 | 1 | E40610 V12 S16
SE307240 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 1832 | 1 | E40610 V12 S16
SE307240 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 1832 | 1 | E40610 V12 S16
SE307250 | C | CB | Square D | FHL36020 | 65 | 20 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1 | E40610 V12 S16
SE307250 |  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1 | E40610 V12 S16
SE307250 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1 | E40610 V12 S16
SE307260 | C | CB | Square D | FHL36020 | 65 | 20 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1 | E40610 V12 S16
SE307260 |  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1 | E40610 V12 S16
SE307260 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1 | E40610 V12 S16
SE307270 | C | CB | Square D | FHL36025 | 65 | 25 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1 | E40610 V12 S16
SE307270 |  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1 | E40610 V12 S16
SE307270 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1 | E40610 V12 S16
SE307280 | C | CB | Square D | FHL36025 | 65 | 25 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1 | E40610 V12 S16
SE307280 |  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1 | E40610 V12 S16
SE307280 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1 | E40610 V12 S16
SE307290 | C | CB | Square D | FHL36020 | 65 | 20 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1 | E40610 V12 S16
SE307290 |  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1 | E40610 V12 S16
SE307290 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1 | E40610 V12 S16
SE307300 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 3 | 4.8 | 1832 | 1 | E40610 V12 S16
SE307300 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 25 | 480 | 3 | 3 | 4.8 | 1832 | 1 | E40610 V12 S16
SE307300 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 25 | 480 | 3 | 3 | 4.8 | 1832 | 1 | E40610 V12 S16
SE307310 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 3 | 3.9 | 1832 | 1 | E40610 V12 S16
SE307310 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 18 | 600 | 3 | 3 | 3.9 | 1832 | 1 | E40610 V12 S16
SE307310 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 18 | 600 | 3 | 3 | 3.9 | 1832 | 1 | E40610 V12 S16
SE307320 | C | CB | Square D | FHL36035 | 65 | 35 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1 | E40610 V12 S16
SE307320 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1 | E40610 V12 S16
SE307320 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1 | E40610 V12 S16
SE307330 | C | CB | Square D | FHL36035 | 65 | 35 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1 | E40610 V12 S16
SE307330 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1 | E40610 V12 S16
SE307330 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1 | E40610 V12 S16
SE307340 | C | CB | Square D | FHL36030 | 65 | 30 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1 | E40610 V12 S16
SE307340 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1 | E40610 V12 S16
SE307340 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1 | E40610 V12 S16
SE307350 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 5 | 7.6 | 1832 | 1 | E40610 V12 S16
SE307350 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 25 | 480 | 3 | 5 | 7.6 | 1832 | 1 | E40610 V12 S16
SE307350 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 25 | 480 | 3 | 5 | 7.6 | 1832 | 1 | E40610 V12 S16
SE307360 | C | CB | Square D | FHL36035 | 65 | 35 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1 | E40610 V12 S16
SE307360 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1 | E40610 V12 S16
SE307360 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1 | E40610 V12 S16
SE307370 | C | CB | Square D | FHL36020 | 25 | 20 | 600 | 3 | 25 | 480 | 3 | 5 | 7.6 | 1832 | 1 | E40610 V12 S16
SE307370 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 25 | 480 | 3 | 5 | 7.6 | 1832 | 1 | E40610 V12 S16
SE307370 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 25 | 480 | 3 | 5 | 7.6 | 1832 | 1 | E40610 V12 S16
SE307380 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 1832 | 1 | E40610 V12 S16
SE307380 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 1832 | 1 | E40610 V12 S16
SE307380 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 1832 | 1 | E40610 V12 S16
SE307390 | C | CB | Square D | FHL36050 | 65 | 50 | 600 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 1832 | 1 | E40610 V12 S16
SE307390 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 1832 | 1 | E40610 V12 S16
SE307390 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 1832 | 1 | E40610 V12 S16
SE307400 | C | CB | Square D | FHL36050 | 65 | 50 | 600 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 1832 | 1 | E40610 V12 S16
SE307400 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 1832 | 1 | E40610 V12 S16
SE307400 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 1832 | 1 | E40610 V12 S16
SE307410 | C | CB | Square D | FHL36040 | 65 | 40 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1 | E40610 V12 S16
SE307410 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1 | E40610 V12 S16
SE307410 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1 | E40610 V12 S16
SE307420 | C | CB | Square D | FHL36020 | 25 | 20 | 600 | 3 | 25 | 480 | 3 | 7.5 | 11 | 1832 | 1 | E40610 V12 S16
SE307420 |  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3 | 25 | 480 | 3 | 7.5 | 11 | 1832 | 1 | E40610 V12 S16
SE307420 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 25 | 480 | 3 | 7.5 | 11 | 1832 | 1 | E40610 V12 S16
SE307430 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1 | E40610 V12 S16
SE307430 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1 | E40610 V12 S16
SE307430 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1 | E40610 V12 S16
SE307440 | C | CB | Square D | FHL36060 | 65 | 60 | 600 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 1832 | 1 | E40610 V12 S16
SE307440 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 1832 | 1 | E40610 V12 S16
SE307440 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 1832 | 1 | E40610 V12 S16
SE307450 | C | CB | Square D | FHL36060 | 65 | 60 | 600 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 1832 | 1 | E40610 V12 S16
SE307450 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 1832 | 1 | E40610 V12 S16
SE307450 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 1832 | 1 | E40610 V12 S16
SE307460 | C | CB | Square D | FHL36045 | 65 | 45 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1 | E40610 V12 S16
SE307460 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1 | E40610 V12 S16
SE307460 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1 | E40610 V12 S16
SE307470 | C | CB | Square D | FHL36025 | 25 | 25 | 600 | 3 | 25 | 480 | 3 | 7.5 | 11 | 1832 | 1 | E40610 V12 S16
SE307470 |  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3 | 25 | 480 | 3 | 7.5 | 11 | 1832 | 1 | E40610 V12 S16
SE307470 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 25 | 480 | 3 | 7.5 | 11 | 1832 | 1 | E40610 V12 S16
SE307480 | C | CB | Square D | FHL36020 | 18 | 20 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1 | E40610 V12 S16
SE307480 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1 | E40610 V12 S16
SE307480 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1 | E40610 V12 S16
SE307490 | C | CB | Square D | FHL36060 | 65 | 60 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1 | E40610 V12 S16
SE307490 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1 | E40610 V12 S16
SE307490 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1 | E40610 V12 S16
SE307500 | C | CB | Square D | FHL36060 | 65 | 60 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1 | E40610 V12 S16
SE307500 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1 | E40610 V12 S16
SE307500 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1 | E40610 V12 S16
SE307510 | C | CB | Square D | FHL36050 | 65 | 50 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1 | E40610 V12 S16
SE307510 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1 | E40610 V12 S16
SE307510 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1 | E40610 V12 S16
SE307520 | C | CB | Square D | FHL36025 | 25 | 25 | 600 | 3 | 25 | 480 | 3 | 10 | 14 | 1832 | 1 | E40610 V12 S16
SE307520 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 25 | 480 | 3 | 10 | 14 | 1832 | 1 | E40610 V12 S16
SE307520 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 25 | 480 | 3 | 10 | 14 | 1832 | 1 | E40610 V12 S16
SE307530 | C | CB | Square D | FHL36020 | 18 | 20 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1 | E40610 V12 S16
SE307530 |  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1 | E40610 V12 S16
SE307530 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1 | E40610 V12 S16
SE307540 | C | CB | Square D | FHL36070 | 65 | 70 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1 | E40610 V12 S16
SE307540 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1 | E40610 V12 S16
SE307540 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1 | E40610 V12 S16
SE307550 | C | CB | Square D | FHL36070 | 65 | 70 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1 | E40610 V12 S16
SE307550 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1 | E40610 V12 S16
SE307550 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1 | E40610 V12 S16
SE307560 | C | CB | Square D | FHL36060 | 65 | 60 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1 | E40610 V12 S16
SE307560 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1 | E40610 V12 S16
SE307560 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1 | E40610 V12 S16
SE307570 | C | CB | Square D | FHL36030 | 25 | 30 | 600 | 3 | 25 | 480 | 3 | 10 | 14 | 1832 | 1 | E40610 V12 S16
SE307570 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 25 | 480 | 3 | 10 | 14 | 1832 | 1 | E40610 V12 S16
SE307570 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 25 | 480 | 3 | 10 | 14 | 1832 | 1 | E40610 V12 S16
SE307580 | C | CB | Square D | FHL36025 | 18 | 25 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1 | E40610 V12 S16
SE307580 |  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1 | E40610 V12 S16
SE307580 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1 | E40610 V12 S16
SE307590 | C | CB | Square D | FHL36090 | 65 | 90 | 600 | 3 | 65 | 200 | 3 | 15 | 48.3 | 2289 | 1 | E40610 V12 S16
SE307590 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 65 | 200 | 3 | 15 | 48.3 | 2289 | 1 | E40610 V12 S16
SE307590 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 65 | 200 | 3 | 15 | 48.3 | 2289 | 1 | E40610 V12 S16
SE307600 | C | CB | Square D | FHL36090 | 65 | 90 | 600 | 3 | 65 | 208 | 3 | 15 | 46.2 | 2289 | 1 | E40610 V12 S16
SE307600 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 65 | 208 | 3 | 15 | 46.2 | 2289 | 1 | E40610 V12 S16
SE307600 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 65 | 208 | 3 | 15 | 46.2 | 2289 | 1 | E40610 V12 S16
SE307610 | C | CB | Square D | FHL36080 | 65 | 80 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 2289 | 1 | E40610 V12 S16
SE307610 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 2289 | 1 | E40610 V12 S16
SE307610 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 2289 | 1 | E40610 V12 S16
SE307620 | C | CB | Square D | FHL36040 | 25 | 40 | 600 | 3 | 25 | 480 | 3 | 15 | 21 | 1832 | 1 | E40610 V12 S16
SE307620 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 25 | 480 | 3 | 15 | 21 | 1832 | 1 | E40610 V12 S16
SE307620 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 25 | 480 | 3 | 15 | 21 | 1832 | 1 | E40610 V12 S16
SE307630 | C | CB | Square D | FHL36030 | 18 | 30 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1 | E40610 V12 S16
SE307630 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1 | E40610 V12 S16
SE307630 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1 | E40610 V12 S16
SE307640 | C | CB | Square D | FHL36090 | 65 | 90 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 2289 | 1 | E40610 V12 S16
SE307640 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 2289 | 1 | E40610 V12 S16
SE307640 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 2289 | 1 | E40610 V12 S16
SE307650 | C | CB | Square D | FHL36045 | 25 | 45 | 600 | 3 | 25 | 480 | 3 | 15 | 21 | 1832 | 1 | E40610 V12 S16
SE307650 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 25 | 480 | 3 | 15 | 21 | 1832 | 1 | E40610 V12 S16
SE307650 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 25 | 480 | 3 | 15 | 21 | 1832 | 1 | E40610 V12 S16
SE307660 | C | CB | Square D | FHL36035 | 18 | 35 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1 | E40610 V12 S16
SE307660 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1 | E40610 V12 S16
SE307660 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1 | E40610 V12 S16
SE307670 | C | CB | Square D | FHL36100 | 65 | 100 | 600 | 3 | 65 | 200 | 3 | 20 | 62.1 | 2289 | 1 | E40610 V12 S16
SE307670 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 65 | 200 | 3 | 20 | 62.1 | 2289 | 1 | E40610 V12 S16
SE307670 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 65 | 200 | 3 | 20 | 62.1 | 2289 | 1 | E40610 V12 S16
SE307680 | C | CB | Square D | FHL36100 | 65 | 100 | 600 | 3 | 65 | 208 | 3 | 20 | 59.4 | 2289 | 1 | E40610 V12 S16
SE307680 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 65 | 208 | 3 | 20 | 59.4 | 2289 | 1 | E40610 V12 S16
SE307680 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 65 | 208 | 3 | 20 | 59.4 | 2289 | 1 | E40610 V12 S16
SE307690 | C | CB | Square D | FHL36090 | 65 | 90 | 600 | 3 | 65 | 240 | 3 | 20 | 54 | 2289 | 1 | E40610 V12 S16
SE307690 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 65 | 240 | 3 | 20 | 54 | 2289 | 1 | E40610 V12 S16
SE307690 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 65 | 240 | 3 | 20 | 54 | 2289 | 1 | E40610 V12 S16
SE307700 | C | CB | Square D | FHL36050 | 25 | 50 | 600 | 3 | 25 | 480 | 3 | 20 | 27 | 1832 | 1 | E40610 V12 S16
SE307700 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 25 | 480 | 3 | 20 | 27 | 1832 | 1 | E40610 V12 S16
SE307700 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 25 | 480 | 3 | 20 | 27 | 1832 | 1 | E40610 V12 S16
SE307710 | C | CB | Square D | FHL36060 | 25 | 60 | 600 | 3 | 25 | 480 | 3 | 20 | 27 | 1832 | 1 | E40610 V12 S16
SE307710 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 25 | 480 | 3 | 20 | 27 | 1832 | 1 | E40610 V12 S16
SE307710 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 25 | 480 | 3 | 20 | 27 | 1832 | 1 | E40610 V12 S16
SE307720 | C | CB | Square D | FHL36045 | 18 | 45 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1 | E40610 V12 S16
SE307720 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1 | E40610 V12 S16
SE307720 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1 | E40610 V12 S16
SE307730 | C | CB | Square D | FHL36100 | 65 | 100 | 600 | 3 | 65 | 240 | 3 | 25 | 68 | 3663 | 1 | E40610 V12 S16
SE307730 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 65 | 240 | 3 | 25 | 68 | 3663 | 1 | E40610 V12 S16
SE307730 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 65 | 240 | 3 | 25 | 68 | 3663 | 1 | E40610 V12 S16
SE307740 | C | CB | Square D | FHL36060 | 25 | 60 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 2289 | 1 | E40610 V12 S16
SE307740 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 2289 | 1 | E40610 V12 S16
SE307740 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 2289 | 1 | E40610 V12 S16
SE307750 | C | CB | Square D | FHL36050 | 18 | 50 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1 | E40610 V12 S16
SE307750 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1 | E40610 V12 S16
SE307750 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1 | E40610 V12 S16
SE307760 | C | CB | Square D | FHL36070 | 25 | 70 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 2289 | 1 | E40610 V12 S16
SE307760 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 2289 | 1 | E40610 V12 S16
SE307760 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 2289 | 1 | E40610 V12 S16
SE307770 | C | CB | Square D | FHL36060 | 18 | 60 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1 | E40610 V12 S16
SE307770 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1 | E40610 V12 S16
SE307770 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1 | E40610 V12 S16
SE307780 | C | CB | Square D | FHL36080 | 25 | 80 | 600 | 3 | 25 | 480 | 3 | 30 | 40 | 2289 | 1 | E40610 V12 S16
SE307780 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 25 | 480 | 3 | 30 | 40 | 2289 | 1 | E40610 V12 S16
SE307780 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 25 | 480 | 3 | 30 | 40 | 2289 | 1 | E40610 V12 S16
SE307790 | C | CB | Square D | FHL36060 | 18 | 60 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2289 | 1 | E40610 V12 S16
SE307790 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2289 | 1 | E40610 V12 S16
SE307790 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2289 | 1 | E40610 V12 S16
SE307800 | C | CB | Square D | FHL36070 | 18 | 70 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2289 | 1 | E40610 V12 S16
SE307800 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2289 | 1 | E40610 V12 S16
SE307800 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2289 | 1 | E40610 V12 S16
SE307810 | C | CB | Square D | FHL36090 | 25 | 90 | 600 | 3 | 25 | 480 | 3 | 40 | 52 | 2289 | 1 | E40610 V12 S16
SE307810 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 25 | 480 | 3 | 40 | 52 | 2289 | 1 | E40610 V12 S16
SE307810 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 25 | 480 | 3 | 40 | 52 | 2289 | 1 | E40610 V12 S16
SE307820 | C | CB | Square D | FHL36080 | 18 | 80 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2289 | 1 | E40610 V12 S16
SE307820 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2289 | 1 | E40610 V12 S16
SE307820 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2289 | 1 | E40610 V12 S16
SE307830 | C | CB | Square D | FHL36090 | 18 | 90 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2289 | 1 | E40610 V12 S16
SE307830 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2289 | 1 | E40610 V12 S16
SE307830 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2289 | 1 | E40610 V12 S16
SE307840 | C | CB | Square D | FHL36100 | 25 | 100 | 600 | 3 | 25 | 480 | 3 | 50 | 65 | 3663 | 1 | E40610 V12 S16
SE307840 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 25 | 480 | 3 | 50 | 65 | 3663 | 1 | E40610 V12 S16
SE307840 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 25 | 480 | 3 | 50 | 65 | 3663 | 1 | E40610 V12 S16
SE307850 | C | CB | Square D | FHL36090 | 18 | 90 | 600 | 3 | 18 | 600 | 3 | 50 | 52 | 2289 | 1 | E40610 V12 S16
SE307850 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 18 | 600 | 3 | 50 | 52 | 2289 | 1 | E40610 V12 S16
SE307850 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 18 | 600 | 3 | 50 | 52 | 2289 | 1 | E40610 V12 S16
SE307860 | C | CB | Square D | FHL36100 | 18 | 100 | 600 | 3 | 18 | 600 | 3 | 60 | 62 | 2289 | 1 | E40610 V12 S16
SE307860 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 18 | 600 | 3 | 60 | 62 | 2289 | 1 | E40610 V12 S16
SE307860 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 18 | 600 | 3 | 60 | 62 | 2289 | 1 | E40610 V12 S16

## Type D - FH MG
Issued: 2006-05-17
Last Revised: 2006-11-16
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in.) | Conditions of Acceptability | Combination UL File
SE303130 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 5 | E40610 V12 S15
SE303130 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 5 | E40610 V12 S15
SE303130 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 5 | E40610 V12 S15
SE303140 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 5 | E40610 V12 S15
SE303140 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 5 | E40610 V12 S15
SE303140 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 5 | E40610 V12 S15
SE303150 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 5 | E40610 V12 S15
SE303150 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 5 | E40610 V12 S15
SE303150 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 5 | E40610 V12 S15
SE303160 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 5 | E40610 V12 S15
SE303160 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 5 | E40610 V12 S15
SE303160 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 5 | E40610 V12 S15
SE303170 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 5 | E40610 V12 S15
SE303170 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 5 | E40610 V12 S15
SE303170 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 5 | E40610 V12 S15
SE303180 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 5 | E40610 V12 S15
SE303180 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 5 | E40610 V12 S15
SE303180 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 5 | E40610 V12 S15
SE303190 | D | ICB | Square D | FHL3600311M | - | 3 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 5 | E40610 V12 S15
SE303190 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 5 | E40610 V12 S15
SE303190 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 5 | E40610 V12 S15
SE303200 | D | ICB | Square D | FHL3600311M | - | 3 | 600 | 3 | 50 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 5 | E40610 V12 S15
SE303200 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 50 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 5 | E40610 V12 S15
SE303200 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 50 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 5 | E40610 V12 S15
SE303210 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 5 | E40610 V12 S15
SE303210 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 5 | E40610 V12 S15
SE303210 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 5 | E40610 V12 S15
SE303220 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 5 | E40610 V12 S15
SE303220 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 5 | E40610 V12 S15
SE303220 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 5 | E40610 V12 S15
SE303230 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 5 | E40610 V12 S15
SE303230 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 5 | E40610 V12 S15
SE303230 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 5 | E40610 V12 S15
SE303240 | D | ICB | Square D | FHL3600311M | - | 3 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 5 | E40610 V12 S15
SE303240 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 5 | E40610 V12 S15
SE303240 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 5 | E40610 V12 S15
SE303250 | D | ICB | Square D | FHL3600311M | - | 3 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 1832 | 1, 5 | E40610 V12 S15
SE303250 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 1832 | 1, 5 | E40610 V12 S15
SE303250 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 1832 | 1, 5 | E40610 V12 S15
SE303260 | D | ICB | Square D | FHL3601513M | - | 15 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 5 | E40610 V12 S15
SE303260 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 5 | E40610 V12 S15
SE303260 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 5 | E40610 V12 S15
SE303270 | D | ICB | Square D | FHL3601513M | - | 15 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 5 | E40610 V12 S15
SE303270 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 5 | E40610 V12 S15
SE303270 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 5 | E40610 V12 S15
SE303280 | D | ICB | Square D | FHL3601513M | - | 15 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 5 | E40610 V12 S15
SE303280 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 5 | E40610 V12 S15
SE303280 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 5 | E40610 V12 S15
SE303290 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 5 | E40610 V12 S15
SE303290 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 5 | E40610 V12 S15
SE303290 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 5 | E40610 V12 S15
SE303300 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 5 | E40610 V12 S15
SE303300 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 5 | E40610 V12 S15
SE303300 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 5 | E40610 V12 S15
SE303310 | D | ICB | Square D | FHL3601513M | - | 15 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 5 | E40610 V12 S15
SE303310 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 5 | E40610 V12 S15
SE303310 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 5 | E40610 V12 S15
SE303320 | D | ICB | Square D | FHL3601513M | - | 15 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 5 | E40610 V12 S15
SE303320 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 5 | E40610 V12 S15
SE303320 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 5 | E40610 V12 S15
SE303330 | D | ICB | Square D | FHL3601513M | - | 15 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 5 | E40610 V12 S15
SE303330 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 5 | E40610 V12 S15
SE303330 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 5 | E40610 V12 S15
SE303340 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 5 | E40610 V12 S15
SE303340 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 5 | E40610 V12 S15
SE303340 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 5 | E40610 V12 S15
SE303350 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 1832 | 1, 5 | E40610 V12 S15
SE303350 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 1832 | 1, 5 | E40610 V12 S15
SE303350 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 1832 | 1, 5 | E40610 V12 S15
SE303360 | D | ICB | Square D | FHL3601513M | - | 15 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5 | E40610 V12 S15
SE303360 |  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5 | E40610 V12 S15
SE303360 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5 | E40610 V12 S15
SE303370 | D | ICB | Square D | FHL3601513M | - | 15 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5 | E40610 V12 S15
SE303370 |  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5 | E40610 V12 S15
SE303370 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5 | E40610 V12 S15
SE303380 | D | ICB | Square D | FHL3601513M | - | 15 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5 | E40610 V12 S15
SE303380 |  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5 | E40610 V12 S15
SE303380 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5 | E40610 V12 S15
SE303390 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 5 | E40610 V12 S15
SE303390 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 5 | E40610 V12 S15
SE303390 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 5 | E40610 V12 S15
SE303400 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 1832 | 1, 5 | E40610 V12 S15
SE303400 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 1832 | 1, 5 | E40610 V12 S15
SE303400 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 1832 | 1, 5 | E40610 V12 S15
SE303410 | D | ICB | Square D | FHL3605016M | - | 50 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5 | E40610 V12 S15
SE303410 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5 | E40610 V12 S15
SE303410 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5 | E40610 V12 S15
SE303420 | D | ICB | Square D | FHL3605016M | - | 50 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5 | E40610 V12 S15
SE303420 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5 | E40610 V12 S15
SE303420 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5 | E40610 V12 S15
SE303430 | D | ICB | Square D | FHL3603015M | - | 30 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5 | E40610 V12 S15
SE303430 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5 | E40610 V12 S15
SE303430 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5 | E40610 V12 S15
SE303440 | D | ICB | Square D | FHL3601513M | - | 15 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 5 | E40610 V12 S15
SE303440 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 5 | E40610 V12 S15
SE303440 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 5 | E40610 V12 S15
SE303450 | D | ICB | Square D | FHL3601513M | - | 15 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 1832 | 1, 5 | E40610 V12 S15
SE303450 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 1832 | 1, 5 | E40610 V12 S15
SE303450 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 1832 | 1, 5 | E40610 V12 S15
SE303460 | D | ICB | Square D | FHL3605016M | - | 50 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5 | E40610 V12 S15
SE303460 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5 | E40610 V12 S15
SE303460 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5 | E40610 V12 S15
SE303470 | D | ICB | Square D | FHL3605016M | - | 50 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5 | E40610 V12 S15
SE303470 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5 | E40610 V12 S15
SE303470 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5 | E40610 V12 S15
SE303480 | D | ICB | Square D | FHL3603015M | - | 30 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5 | E40610 V12 S15
SE303480 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5 | E40610 V12 S15
SE303480 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5 | E40610 V12 S15
SE303490 | D | ICB | Square D | FHL3601513M | - | 15 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5 | E40610 V12 S15
SE303490 |  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5 | E40610 V12 S15
SE303490 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5 | E40610 V12 S15
SE303500 | D | ICB | Square D | FHL3601513M | - | 15 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 5 | E40610 V12 S15
SE303500 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 5 | E40610 V12 S15
SE303500 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 5 | E40610 V12 S15
SE303510 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5 | E40610 V12 S15
SE303510 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5 | E40610 V12 S15
SE303510 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5 | E40610 V12 S15
SE303520 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5 | E40610 V12 S15
SE303520 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5 | E40610 V12 S15
SE303520 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5 | E40610 V12 S15
SE303530 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5 | E40610 V12 S15
SE303530 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5 | E40610 V12 S15
SE303530 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5 | E40610 V12 S15
SE303540 | D | ICB | Square D | FHL3603015M | - | 30 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 5 | E40610 V12 S15
SE303540 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 5 | E40610 V12 S15
SE303540 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 5 | E40610 V12 S15
SE303550 | D | ICB | Square D | FHL3603015M | - | 30 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1832 | 1, 5 | E40610 V12 S15
SE303550 |  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1832 | 1, 5 | E40610 V12 S15
SE303550 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1832 | 1, 5 | E40610 V12 S15
SE303560 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 5 | E40610 V12 S15
SE303560 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 5 | E40610 V12 S15
SE303560 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 5 | E40610 V12 S15
SE303570 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 5 | E40610 V12 S15
SE303570 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 5 | E40610 V12 S15
SE303570 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 5 | E40610 V12 S15
SE303580 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 5 | E40610 V12 S15
SE303580 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 5 | E40610 V12 S15
SE303580 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 5 | E40610 V12 S15
SE303590 | D | ICB | Square D | FHL3603015M | - | 30 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 5 | E40610 V12 S15
SE303590 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 5 | E40610 V12 S15
SE303590 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 5 | E40610 V12 S15
SE303600 | D | ICB | Square D | FHL3603015M | - | 30 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 5 | E40610 V12 S15
SE303600 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 5 | E40610 V12 S15
SE303600 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 5 | E40610 V12 S15
SE303610 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2289 | 1, 5 | E40610 V12 S15
SE303610 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2289 | 1, 5 | E40610 V12 S15
SE303610 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2289 | 1, 5 | E40610 V12 S15
SE303620 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 2289 | 1, 5 | E40610 V12 S15
SE303620 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 2289 | 1, 5 | E40610 V12 S15
SE303620 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 2289 | 1, 5 | E40610 V12 S15
SE303630 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 5 | E40610 V12 S15
SE303630 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 5 | E40610 V12 S15
SE303630 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 5 | E40610 V12 S15
SE303640 | D | ICB | Square D | FHL3605016M | - | 50 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 5 | E40610 V12 S15
SE303640 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 5 | E40610 V12 S15
SE303640 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 5 | E40610 V12 S15
SE303650 | D | ICB | Square D | FHL3603015M | - | 30 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 5 | E40610 V12 S15
SE303650 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 5 | E40610 V12 S15
SE303650 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 5 | E40610 V12 S15
SE303660 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2289 | 1, 5 | E40610 V12 S15
SE303660 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2289 | 1, 5 | E40610 V12 S15
SE303660 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2289 | 1, 5 | E40610 V12 S15
SE303670 | D | ICB | Square D | FHL3605016M | - | 50 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2289 | 1, 5 | E40610 V12 S15
SE303670 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2289 | 1, 5 | E40610 V12 S15
SE303670 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2289 | 1, 5 | E40610 V12 S15
SE303680 | D | ICB | Square D | FHL3605016M | - | 50 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 5 | E40610 V12 S15
SE303680 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 5 | E40610 V12 S15
SE303680 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 5 | E40610 V12 S15
SE303690 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2289 | 1, 5 | E40610 V12 S15
SE303690 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2289 | 1, 5 | E40610 V12 S15
SE303690 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2289 | 1, 5 | E40610 V12 S15
SE303700 | D | ICB | Square D | FHL3605016M | - | 50 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2289 | 1, 5 | E40610 V12 S15
SE303700 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2289 | 1, 5 | E40610 V12 S15
SE303700 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2289 | 1, 5 | E40610 V12 S15
SE303710 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2289 | 1, 5 | E40610 V12 S15
SE303710 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2289 | 1, 5 | E40610 V12 S15
SE303710 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2289 | 1, 5 | E40610 V12 S15
SE303720 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2289 | 1, 5 | E40610 V12 S15
SE303720 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2289 | 1, 5 | E40610 V12 S15
SE303720 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2289 | 1, 5 | E40610 V12 S15
SE303730 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 2289 | 1, 5 | E40610 V12 S15
SE303730 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 2289 | 1, 5 | E40610 V12 S15
SE303730 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 2289 | 1, 5 | E40610 V12 S15
SE303740 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2289 | 1, 5 | E40610 V12 S15
SE303740 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2289 | 1, 5 | E40610 V12 S15
SE303740 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2289 | 1, 5 | E40610 V12 S15
SE303750 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 2289 | 1, 5 | E40610 V12 S15
SE303750 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 2289 | 1, 5 | E40610 V12 S15
SE303750 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 2289 | 1, 5 | E40610 V12 S15
SE303760 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 5 | E40610 V12 S16
SE303760 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 5 | E40610 V12 S16
SE303760 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 5 | E40610 V12 S16
SE303770 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 5 | E40610 V12 S16
SE303770 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 5 | E40610 V12 S16
SE303770 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 5 | E40610 V12 S16
SE303780 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 5 | E40610 V12 S16
SE303780 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 5 | E40610 V12 S16
SE303780 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 5 | E40610 V12 S16
SE303790 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 5 | E40610 V12 S16
SE303790 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 5 | E40610 V12 S16
SE303790 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 5 | E40610 V12 S16
SE303800 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 5 | E40610 V12 S16
SE303800 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 5 | E40610 V12 S16
SE303800 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 5 | E40610 V12 S16
SE303810 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 5 | E40610 V12 S16
SE303810 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 5 | E40610 V12 S16
SE303810 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 5 | E40610 V12 S16
SE303820 | D | ICB | Square D | FHL3600311M | - | 3 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 5 | E40610 V12 S16
SE303820 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 5 | E40610 V12 S16
SE303820 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 5 | E40610 V12 S16
SE303830 | D | ICB | Square D | FHL3600311M | - | 3 | 600 | 3 | 50 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 5 | E40610 V12 S16
SE303830 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 50 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 5 | E40610 V12 S16
SE303830 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 50 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 5 | E40610 V12 S16
SE303840 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 5 | E40610 V12 S16
SE303840 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 5 | E40610 V12 S16
SE303840 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 5 | E40610 V12 S16
SE303850 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 5 | E40610 V12 S16
SE303850 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 5 | E40610 V12 S16
SE303850 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 5 | E40610 V12 S16
SE303860 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 5 | E40610 V12 S16
SE303860 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 5 | E40610 V12 S16
SE303860 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 5 | E40610 V12 S16
SE303870 | D | ICB | Square D | FHL3600311M | - | 3 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 5 | E40610 V12 S16
SE303870 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 5 | E40610 V12 S16
SE303870 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 5 | E40610 V12 S16
SE303880 | D | ICB | Square D | FHL3600311M | - | 3 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 1832 | 1, 5 | E40610 V12 S16
SE303880 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 1832 | 1, 5 | E40610 V12 S16
SE303880 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 1832 | 1, 5 | E40610 V12 S16
SE303890 | D | ICB | Square D | FHL3601513M | - | 15 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 5 | E40610 V12 S16
SE303890 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 5 | E40610 V12 S16
SE303890 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 5 | E40610 V12 S16
SE303900 | D | ICB | Square D | FHL3601513M | - | 15 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 5 | E40610 V12 S16
SE303900 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 5 | E40610 V12 S16
SE303900 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 5 | E40610 V12 S16
SE303910 | D | ICB | Square D | FHL3601513M | - | 15 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 5 | E40610 V12 S16
SE303910 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 5 | E40610 V12 S16
SE303910 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 5 | E40610 V12 S16
SE303920 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 5 | E40610 V12 S16
SE303920 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 5 | E40610 V12 S16
SE303920 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 5 | E40610 V12 S16
SE303930 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 5 | E40610 V12 S16
SE303930 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 5 | E40610 V12 S16
SE303930 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 5 | E40610 V12 S16
SE303940 | D | ICB | Square D | FHL3601513M | - | 15 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 5 | E40610 V12 S16
SE303940 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 5 | E40610 V12 S16
SE303940 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 5 | E40610 V12 S16
SE303950 | D | ICB | Square D | FHL3601513M | - | 15 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 5 | E40610 V12 S16
SE303950 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 5 | E40610 V12 S16
SE303950 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 5 | E40610 V12 S16
SE303960 | D | ICB | Square D | FHL3601513M | - | 15 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 5 | E40610 V12 S16
SE303960 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 5 | E40610 V12 S16
SE303960 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 5 | E40610 V12 S16
SE303970 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 5 | E40610 V12 S16
SE303970 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 5 | E40610 V12 S16
SE303970 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 5 | E40610 V12 S16
SE303980 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 1832 | 1, 5 | E40610 V12 S16
SE303980 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 1832 | 1, 5 | E40610 V12 S16
SE303980 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 1832 | 1, 5 | E40610 V12 S16
SE303990 | D | ICB | Square D | FHL3601513M | - | 15 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5 | E40610 V12 S16
SE303990 |  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5 | E40610 V12 S16
SE303990 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5 | E40610 V12 S16
SE304000 | D | ICB | Square D | FHL3601513M | - | 15 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5 | E40610 V12 S16
SE304000 |  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5 | E40610 V12 S16
SE304000 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5 | E40610 V12 S16
SE304010 | D | ICB | Square D | FHL3601513M | - | 15 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5 | E40610 V12 S16
SE304010 |  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5 | E40610 V12 S16
SE304010 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5 | E40610 V12 S16
SE304020 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 5 | E40610 V12 S16
SE304020 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 5 | E40610 V12 S16
SE304020 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 5 | E40610 V12 S16
SE304030 | D | ICB | Square D | FHL3600712M | - | 7 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 1832 | 1, 5 | E40610 V12 S16
SE304030 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 1832 | 1, 5 | E40610 V12 S16
SE304030 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 1832 | 1, 5 | E40610 V12 S16
SE304040 | D | ICB | Square D | FHL3605016M | - | 50 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5 | E40610 V12 S16
SE304040 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5 | E40610 V12 S16
SE304040 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5 | E40610 V12 S16
SE304050 | D | ICB | Square D | FHL3605016M | - | 50 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5 | E40610 V12 S16
SE304050 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5 | E40610 V12 S16
SE304050 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5 | E40610 V12 S16
SE304060 | D | ICB | Square D | FHL3603015M | - | 30 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5 | E40610 V12 S16
SE304060 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5 | E40610 V12 S16
SE304060 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5 | E40610 V12 S16
SE304070 | D | ICB | Square D | FHL3601513M | - | 15 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 5 | E40610 V12 S16
SE304070 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 5 | E40610 V12 S16
SE304070 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 5 | E40610 V12 S16
SE304080 | D | ICB | Square D | FHL3601513M | - | 15 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 1832 | 1, 5 | E40610 V12 S16
SE304080 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 1832 | 1, 5 | E40610 V12 S16
SE304080 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 1832 | 1, 5 | E40610 V12 S16
SE304090 | D | ICB | Square D | FHL3605016M | - | 50 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5 | E40610 V12 S16
SE304090 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5 | E40610 V12 S16
SE304090 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5 | E40610 V12 S16
SE304100 | D | ICB | Square D | FHL3605016M | - | 50 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5 | E40610 V12 S16
SE304100 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5 | E40610 V12 S16
SE304100 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5 | E40610 V12 S16
SE304110 | D | ICB | Square D | FHL3603015M | - | 30 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5 | E40610 V12 S16
SE304110 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5 | E40610 V12 S16
SE304110 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5 | E40610 V12 S16
SE304120 | D | ICB | Square D | FHL3601513M | - | 15 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5 | E40610 V12 S16
SE304120 |  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5 | E40610 V12 S16
SE304120 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5 | E40610 V12 S16
SE304130 | D | ICB | Square D | FHL3601513M | - | 15 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 5 | E40610 V12 S16
SE304130 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 5 | E40610 V12 S16
SE304130 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 5 | E40610 V12 S16
SE304140 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5 | E40610 V12 S16
SE304140 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5 | E40610 V12 S16
SE304140 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5 | E40610 V12 S16
SE304150 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5 | E40610 V12 S16
SE304150 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5 | E40610 V12 S16
SE304150 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5 | E40610 V12 S16
SE304160 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5 | E40610 V12 S16
SE304160 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5 | E40610 V12 S16
SE304160 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5 | E40610 V12 S16
SE304170 | D | ICB | Square D | FHL3603015M | - | 30 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 5 | E40610 V12 S16
SE304170 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 5 | E40610 V12 S16
SE304170 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 5 | E40610 V12 S16
SE304180 | D | ICB | Square D | FHL3603015M | - | 30 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1832 | 1, 5 | E40610 V12 S16
SE304180 |  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1832 | 1, 5 | E40610 V12 S16
SE304180 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1832 | 1, 5 | E40610 V12 S16
SE304190 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 5 | E40610 V12 S16
SE304190 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 5 | E40610 V12 S16
SE304190 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 5 | E40610 V12 S16
SE304200 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 5 | E40610 V12 S16
SE304200 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 5 | E40610 V12 S16
SE304200 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 5 | E40610 V12 S16
SE304210 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 5 | E40610 V12 S16
SE304210 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 5 | E40610 V12 S16
SE304210 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 5 | E40610 V12 S16
SE304220 | D | ICB | Square D | FHL3603015M | - | 30 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 5 | E40610 V12 S16
SE304220 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 5 | E40610 V12 S16
SE304220 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 5 | E40610 V12 S16
SE304230 | D | ICB | Square D | FHL3603015M | - | 30 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 5 | E40610 V12 S16
SE304230 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 5 | E40610 V12 S16
SE304230 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 5 | E40610 V12 S16
SE304240 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2289 | 1, 5 | E40610 V12 S16
SE304240 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2289 | 1, 5 | E40610 V12 S16
SE304240 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2289 | 1, 5 | E40610 V12 S16
SE304250 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 2289 | 1, 5 | E40610 V12 S16
SE304250 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 2289 | 1, 5 | E40610 V12 S16
SE304250 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 2289 | 1, 5 | E40610 V12 S16
SE304260 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 5 | E40610 V12 S16
SE304260 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 5 | E40610 V12 S16
SE304260 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 5 | E40610 V12 S16
SE304270 | D | ICB | Square D | FHL3605016M | - | 50 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 5 | E40610 V12 S16
SE304270 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 5 | E40610 V12 S16
SE304270 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 5 | E40610 V12 S16
SE304280 | D | ICB | Square D | FHL3603015M | - | 30 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 5 | E40610 V12 S16
SE304280 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 5 | E40610 V12 S16
SE304280 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 5 | E40610 V12 S16
SE304290 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 3663 | 1, 5 | E40610 V12 S16
SE304290 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 3663 | 1, 5 | E40610 V12 S16
SE304290 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 3663 | 1, 5 | E40610 V12 S16
SE304300 | D | ICB | Square D | FHL3605016M | - | 50 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2289 | 1, 5 | E40610 V12 S16
SE304300 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2289 | 1, 5 | E40610 V12 S16
SE304300 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2289 | 1, 5 | E40610 V12 S16
SE304310 | D | ICB | Square D | FHL3605016M | - | 50 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 5 | E40610 V12 S16
SE304310 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 5 | E40610 V12 S16
SE304310 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 5 | E40610 V12 S16
SE304320 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2289 | 1, 5 | E40610 V12 S16
SE304320 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2289 | 1, 5 | E40610 V12 S16
SE304320 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2289 | 1, 5 | E40610 V12 S16
SE304330 | D | ICB | Square D | FHL3605016M | - | 50 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2289 | 1, 5 | E40610 V12 S16
SE304330 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2289 | 1, 5 | E40610 V12 S16
SE304330 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2289 | 1, 5 | E40610 V12 S16
SE304340 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2289 | 1, 5 | E40610 V12 S16
SE304340 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2289 | 1, 5 | E40610 V12 S16
SE304340 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2289 | 1, 5 | E40610 V12 S16
SE304350 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2289 | 1, 5 | E40610 V12 S16
SE304350 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2289 | 1, 5 | E40610 V12 S16
SE304350 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2289 | 1, 5 | E40610 V12 S16
SE304360 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3663 | 1, 5 | E40610 V12 S16
SE304360 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3663 | 1, 5 | E40610 V12 S16
SE304360 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3663 | 1, 5 | E40610 V12 S16
SE304370 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2289 | 1, 5 | E40610 V12 S16
SE304370 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2289 | 1, 5 | E40610 V12 S16
SE304370 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2289 | 1, 5 | E40610 V12 S16
SE304380 | D | ICB | Square D | FHL3610018M | - | 100 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 2289 | 1, 5 | E40610 V12 S16
SE304380 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 2289 | 1, 5 | E40610 V12 S16
SE304380 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 2289 | 1, 5 | E40610 V12 S16