## K, L, & M-Frame
Issued: 2006-11-07
Last Revised: 2015-03-20
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE102011 | C | CB | Square D | KHL36110 | 65 | 110 | 600 | 3 | 65 | 200 | 3 | 25 | 78.2 | 2289 | 1 | E40610 V12 S15
|  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3
|  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3
SE102012 | C | CB | Square D | KHL36110 | 65 | 110 | 600 | 3 | 65 | 208 | 3 | 25 | 74.8 | 2289 | 1 | E40610 V12 S15
|  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3
|  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3
SE102013 | C | CB | Square D | KHL36110 | 65 | 110 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 2289 | 1 | E40610 V12 S15
|  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3
|  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3
SE102014 | C | CB | Square D | KHL36110 | 35 | 110 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 2289 | 1 | E40610 V12 S15
|  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3
|  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3
SE102015 | C | CB | Square D | KHL36110 | 25 | 110 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 2747 | 1, 7n | E40610 V12 S15
|  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3
|  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3
SE102016 | C | CB | Square D | KHL36125 | 65 | 125 | 600 | 3 | 65 | 200 | 3 | 30 | 92 | 2747 | 1, 7n | E40610 V12 S15
|  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3
|  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3
SE102017 | C | CB | Square D | KHL36125 | 65 | 125 | 600 | 3 | 65 | 208 | 3 | 30 | 88 | 2747 | 1, 7n | E40610 V12 S15
|  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3
|  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3
SE102018 | C | CB | Square D | KHL36150 | 65 | 150 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 2747 | 1, 7n | E40610 V12 S15
|  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3
|  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3
SE102019 | C | CB | Square D | KHL36125 | 35 | 125 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 2747 | 1, 7n | E40610 V12 S15
|  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3
|  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3
SE102020 | C | CB | Square D | KHL36150 | 25 | 150 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 7d | E40610 V12 S15
|  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3
|  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3
SE102021 | C | CB | Square D | KHL36175 | 65 | 175 | 600 | 3 | 65 | 200 | 3 | 40 | 120 | 3205 | 1, 7d | E40610 V12 S15
|  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3
|  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3
SE102022 | C | CB | Square D | KHL36175 | 65 | 175 | 600 | 3 | 65 | 208 | 3 | 40 | 114 | 3205 | 1, 7d | E40610 V12 S15
|  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3
|  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3
SE102023 | C | CB | Square D | KHL36200 | 65 | 200 | 600 | 3 | 65 | 240 | 3 | 50 | 130 | 3205 | 1, 7d | E40610 V12 S15
|  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3
|  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3
SE102024 | C | CB | Square D | KHL36200 | 35 | 200 | 600 | 3 | 35 | 480 | 3 | 100 | 124 | 3205 | 1, 7d | E40610 V12 S15
|  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3
|  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3
SE107005 | C | CB | Square D | KHL36200 | 25 | 200 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 5036 | 1, 7e | E40610 V12 S15
SE107005 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3
SE107005 |  | OLR | Telemecanique | LR9F5369 | 5 | 90 - 150 | 600 | 3
SE107005 |  | OLR | Telemecanique | LR9F5569 | 5 | 90 - 150 | 600 | 3
SE107006 | C | CB | Square D | KHL36200 | 65 | 200 | 600 | 3 | 65 | 200 | 3 | 50 | 150 | 5036 | 1, 7e | E40610 V12 S15
SE107006 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3
SE107006 |  | OLR | Telemecanique | LR9F5369 | 5 | 90 - 150 | 600 | 3
SE107006 |  | OLR | Telemecanique | LR9F5569 | 5 | 90 - 150 | 600 | 3
SE107007 | C | CB | Square D | KHL36200 | 65 | 200 | 600 | 3 | 65 | 208 | 3 | 50 | 143 | 5036 | 1, 7e | E40610 V12 S15
SE107007 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3
SE107007 |  | OLR | Telemecanique | LR9F5369 | 5 | 90 - 150 | 600 | 3
SE107007 |  | OLR | Telemecanique | LR9F5569 | 5 | 90 - 150 | 600 | 3
SE107008 | C | CB | Square D | KHL36225 | 65 | 225 | 600 | 3 | 65 | 240 | 3 | 60 | 154 | 5036 | 1, 7e | E40610 V12 S15
SE107008 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3
SE107008 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3
SE107008 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3
SE107009 | C | CB | Square D | KHL36225 | 35 | 225 | 600 | 3 | 35 | 480 | 3 | 125 | 156 | 5036 | 1, 7e | E40610 V12 S15
SE107009 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3
SE107009 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3
SE107009 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3
***
SE107010 | C | CB | Square D | LCL36300 | 100 | 300 | 600 | 3 | 100 | 200 | 3 | 60 | 177 | 6410 | 1, 7h | E04610 V12 S15
SE107010 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3
SE107010 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3
SE107010 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3
SE107011 | C | CB | Square D | LCL36300 | 100 | 300 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 6410 | 1, 7h | E04610 V12 S15
SE107011 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3
SE107011 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3
SE107011 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3
SE107012 | C | CB | Square D | LCL36300 | 100 | 300 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 6410 | 1, 7h | E04610 V12 S15
SE107012 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3
SE107012 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3
SE107012 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3
SE107013 | C | CB | Square D | LCL36300 | 65 | 300 | 600 | 3 | 65 | 480 | 3 | 150 | 180 | 6410 | 1, 7h | E04610 V12 S15
SE107013 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3
SE107013 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3
SE107013 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3
SE107014 | C | CB | Square D | LCL36300 | 35 | 300 | 600 | 3 | 35 | 600 | 3 | 150 | 144 | 6410 | 1, 7h | E04610 V12 S15
SE107014 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3
SE107014 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3
SE107014 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3
SE107015 | C | CB | Square D | LCL36300 | 100 | 300 | 600 | 3 | 100 | 200 | 3 | 60 | 177 | 6410 | 1, 7i | E04610 V12 S15
SE107015 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3
SE107015 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3
SE107015 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3
SE107016 | C | CB | Square D | LCL36300 | 100 | 300 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 6410 | 1, 7i | E04610 V12 S15
SE107016 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3
SE107016 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3
SE107016 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3
SE107017 | C | CB | Square D | LCL36350 | 100 | 350 | 600 | 3 | 100 | 200 | 3 | 75 | 221 | 6410 | 1, 7i | E04610 V12 S15
SE107017 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3
SE107017 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3
SE107017 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3
SE107018 | C | CB | Square D | LCL36350 | 100 | 350 | 600 | 3 | 100 | 208 | 3 | 75 | 211 | 6410 | 1, 7i | E04610 V12 S15
SE107018 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3
SE107018 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3
SE107018 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3
SE107019 | C | CB | Square D | LCL36300 | 100 | 300 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 6410 | 1, 7i | E04610 V12 S15
SE107019 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3
SE107019 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3
SE107019 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3
SE107020 | C | CB | Square D | LCL36400 | 100 | 400 | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 6410 | 1, 7i | E04610 V12 S15
SE107020 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3
SE107020 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3
SE107020 |  | OLR | Telemecanique | LR9F7575 | 5 | 200 - 330 | 600 | 3
SE107021 | C | CB | Square D | LCL36300 | 65 | 300 | 600 | 3 | 65 | 480 | 3 | 150 | 180 | 6410 | 1, 7i | E04610 V12 S15
SE107021 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3
SE107021 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3
SE107021 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3
SE107022 | C | CB | Square D | LCL36400 | 65 | 400 | 600 | 3 | 65 | 480 | 3 | 200 | 240 | 6410 | 1, 7i | E04610 V12 S15
SE107022 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3
SE107022 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3
SE107022 |  | OLR | Telemecanique | LR9F7575 | 5 | 200 - 330 | 600 | 3
SE107023 | C | CB | Square D | LCL36300 | 35 | 300 | 600 | 3 | 35 | 600 | 3 | 150 | 144 | 6410 | 1, 7i | E04610 V12 S15
SE107023 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3
SE107023 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3
SE107023 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3
SE107024 | C | CB | Square D | LCL36350 | 35 | 350 | 600 | 3 | 35 | 600 | 3 | 200 | 192 | 6410 | 1, 7i | E04610 V12 S15
SE107024 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3
SE107024 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3
SE107024 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3
SE107025 | C | CB | Square D | LCL36400 | 35 | 400 | 600 | 3 | 35 | 600 | 3 | 250 | 242 | 6410 | 1, 7i | E04610 V12 S15
SE107025 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3
SE107025 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3
SE107025 |  | OLR | Telemecanique | LR9F7575 | 5 | 200 - 330 | 600 | 3
SE107026 | C | CB | Square D | LCL36350 | 100 | 350 | 600 | 3 | 100 | 200 | 3 | 75 | 221 | 7325 | 1, 7f | E04610 V12 S15
SE107026 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3
SE107026 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3
SE107026 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3
SE107027 | C | CB | Square D | LCL36350 | 100 | 350 | 600 | 3 | 100 | 208 | 3 | 75 | 211 | 7325 | 1, 7f | E04610 V12 S15
SE107027 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3
SE107027 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3
SE107027 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3
SE107028 | C | CB | Square D | LCL36500 | 100 | 500 | 600 | 3 | 100 | 200 | 3 | 100 | 285 | 7325 | 1, 7f | E04610 V12 S15
SE107028 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3
SE107028 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3
SE107028 |  | OLR | Telemecanique | LR9F7575 | 5 | 200 - 330 | 600 | 3
SE107029 | C | CB | Square D | LCL36500 | 100 | 500 | 600 | 3 | 100 | 208 | 3 | 100 | 273 | 7325 | 1, 7f | E04610 V12 S15
SE107029 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3
SE107029 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3
SE107029 |  | OLR | Telemecanique | LR9F7575 | 5 | 200 - 330 | 600 | 3
SE107030 | C | CB | Square D | LCL36400 | 100 | 400 | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 7325 | 1, 7f | E04610 V12 S15
SE107030 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3
SE107030 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3
SE107030 |  | OLR | Telemecanique | LR9F7575 | 5 | 200 - 330 | 600 | 3
SE107031 | C | CB | Square D | LCL36600 | 100 | 600 | 600 | 3 | 100 | 240 | 3 | 125 | 312 | 7325 | 1, 7f | E04610 V12 S15
SE107031 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3
SE107031 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3
SE107031 |  | OLR | Telemecanique | LR9F7575 | 5 | 200 - 330 | 600 | 3
SE107032 | C | CB | Square D | LCL36300 | 65 | 300 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 7325 | 1, 7f | E04610 V12 S15
SE107032 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3
SE107032 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3
SE107032 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3
SE107033 | C | CB | Square D | LCL36300 | 35 | 300 | 600 | 3 | 35 | 600 | 3 | 125 | 125 | 7325 | 1, 7f | E04610 V12 S15
SE107033 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3
SE107033 |  | OLR | Telemecanique | LR9F5369 | 5 | 90 - 150 | 600 | 3
SE107033 |  | OLR | Telemecanique | LR9F5569 | 5 | 90 - 150 | 600 | 3
SE107034 | C | CB | Square D | LCL36400 | 65 | 400 | 600 | 3 | 65 | 480 | 3 | 200 | 240 | 7325 | 1, 7f | E04610 V12 S15
SE107034 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3
SE107034 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3
SE107034 |  | OLR | Telemecanique | LR9F7575 | 5 | 200 - 330 | 600 | 3
SE107035 | C | CB | Square D | LCL36600 | 65 | 600 | 600 | 3 | 65 | 480 | 3 | 250 | 302 | 7325 | 1, 7f | E04610 V12 S15
SE107035 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3
SE107035 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3
SE107035 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3
SE107036 | C | CB | Square D | LCL36400 | 35 | 400 | 600 | 3 | 35 | 600 | 3 | 250 | 242 | 7325 | 1, 7f | E04610 V12 S15
SE107036 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3
SE107036 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3
SE107036 |  | OLR | Telemecanique | LR9F7575 | 5 | 200 - 330 | 600 | 3
SE107037 | C | CB | Square D | LCL36500 | 35 | 500 | 600 | 3 | 35 | 600 | 3 | 300 | 289 | 7325 | 1, 7f | E04610 V12 S15
SE107037 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3
SE107037 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3
SE107037 |  | OLR | Telemecanique | LR9F7575 | 5 | 200 - 330 | 600 | 3
SE107038 | C | CB | Square D | LCL36500 | 100 | 500 | 600 | 3 | 100 | 200 | 3 | 100 | 285 | 7325 | 1, 7j | E04610 V12 S15
SE107038 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107038 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3
SE107038 |  | OLR | Telemecanique | LR9F7575 | 5 | 200 - 330 | 600 | 3
SE107039 | C | CB | Square D | LCL36500 | 100 | 500 | 600 | 3 | 100 | 208 | 3 | 100 | 273 | 7325 | 1, 7j | E04610 V12 S15
SE107039 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107039 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3
SE107039 |  | OLR | Telemecanique | LR9F7575 | 5 | 200 - 330 | 600 | 3
SE107040 | C | CB | Square D | LCL36600 | 100 | 600 | 600 | 3 | 100 | 240 | 3 | 125 | 312 | 7325 | 1, 7j | E04610 V12 S15
SE107040 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107040 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3
SE107040 |  | OLR | Telemecanique | LR9F7575 | 5 | 200 - 330 | 600 | 3
SE107041 | C | CB | Square D | LCL36600 | 65 | 600 | 600 | 3 | 65 | 480 | 3 | 250 | 302 | 7325 | 1, 7j | E04610 V12 S15
SE107041 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107041 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3
SE107041 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3
SE107042 | C | CB | Square D | LCL36500 | 35 | 500 | 600 | 3 | 35 | 600 | 3 | 300 | 289 | 7325 | 1, 7j | E04610 V12 S15
SE107042 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107042 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3
SE107042 |  | OLR | Telemecanique | LR9F7575 | 5 | 200 - 330 | 600 | 3
SE107043 | C | CB | Square D | MHL36800 | 65 | 800 | 600 | 3 | 65 | 200 | 3 | 125 | 359 | 15696 | 1, 7j | E04610 V12 S15
SE107043 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107043 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3
SE107043 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3
SE107044 | C | CB | Square D | MHL36800 | 65 | 800 | 600 | 3 | 65 | 208 | 3 | 125 | 343 | 15696 | 1, 7j | E04610 V12 S15
SE107044 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107044 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3
SE107044 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3
SE107045 | C | CB | Square D | MHL36900 | 65 | 900 | 600 | 3 | 65 | 200 | 3 | 150 | 414 | 15696 | 1, 7j | E04610 V12 S15
SE107045 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107045 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3
SE107045 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3
SE107046 | C | CB | Square D | MHL36900 | 65 | 900 | 600 | 3 | 65 | 208 | 3 | 150 | 396 | 15696 | 1, 7j | E04610 V12 S15
SE107046 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107046 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3
SE107046 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3
SE107047 | C | CB | Square D | MHL36800 | 65 | 800 | 600 | 3 | 65 | 240 | 3 | 150 | 360 | 15696 | 1, 7j | E04610 V12 S15
SE107047 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107047 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3
SE107047 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3
SE107048 | C | CB | Square D | MHL361000 | 65 | 1000 | 600 | 3 | 65 | 240 | 3 | 200 | 480 | 15696 | 1, 7j | E04610 V12 S15
SE107048 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107048 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3
SE107048 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3
SE107049 | C | CB | Square D | MHL36800 | 65 | 800 | 600 | 3 | 65 | 480 | 3 | 300 | 361 | 15696 | 1, 7j | E04610 V12 S15
SE107049 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107049 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3
SE107049 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3
SE107050 | C | CB | Square D | MHL36900 | 65 | 900 | 600 | 3 | 65 | 480 | 3 | 350 | 414 | 15696 | 1, 7j | E04610 V12 S15
SE107050 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107050 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3
SE107050 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3
SE107051 | C | CB | Square D | MHL36700 | 25 | 700 | 600 | 3 | 25 | 600 | 3 | 350 | 336 | 15696 | 1, 7j | E04610 V12 S15
SE107051 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107051 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3
SE107051 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3
SE107052 | C | CB | Square D | MHL361000 | 65 | 1000 | 600 | 3 | 65 | 480 | 3 | 400 | 477 | 15696 | 1, 7j | E04610 V12 S15
SE107052 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107052 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3
SE107052 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3
SE107053 | C | CB | Square D | MHL36800 | 25 | 800 | 600 | 3 | 25 | 600 | 3 | 400 | 382 | 15696 | 1, 7j | E04610 V12 S15
SE107053 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107053 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3
SE107053 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3
SE107054 | C | CB | Square D | MHL36900 | 25 | 900 | 600 | 3 | 25 | 600 | 3 | 450 | 412 | 15696 | 1, 7j | E04610 V12 S15
SE107054 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107054 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3
SE107054 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3
SE107055 | C | CB | Square D | MHL361000 | 25 | 1000 | 600 | 3 | 25 | 600 | 3 | 500 | 472 | 15696 | 1, 7j | E04610 V12 S15
SE107055 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107055 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3
SE107055 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3
SE107056 | D | CB | Square D | MAL3660042M | - | 600 | 600 | 3 | 42 | 200 | 3 | 125 | 359 | 15696 | 1, 7j | E04610 V12 S15
SE107056 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107056 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3
SE107056 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3
SE107057 | D | CB | Square D | MAL3660042M | - | 600 | 600 | 3 | 42 | 208 | 3 | 125 | 343 | 15696 | 1, 7j | E04610 V12 S15
SE107057 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107057 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3
SE107057 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3
SE107058 | D | CB | Square D | MAL3660042M | - | 600 | 600 | 3 | 42 | 200 | 3 | 150 | 414 | 15696 | 1, 7j | E04610 V12 S15
SE107058 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107058 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3
SE107058 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3
SE107059 | D | CB | Square D | MAL3660042M | - | 600 | 600 | 3 | 42 | 208 | 3 | 150 | 396 | 15696 | 1, 7j | E04610 V12 S15
SE107059 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107059 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3
SE107059 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3
SE107060 | D | CB | Square D | MAL3660042M | - | 600 | 600 | 3 | 42 | 240 | 3 | 150 | 360 | 15696 | 1, 7j | E04610 V12 S15
SE107060 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107060 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3
SE107060 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3
SE107061 | D | CB | Square D | MAL3680045M | - | 800 | 600 | 3 | 42 | 240 | 3 | 200 | 480 | 15696 | 1, 7j | E04610 V12 S15
SE107061 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107061 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3
SE107061 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3
SE107062 | D | CB | Square D | MAL3660044M | - | 600 | 600 | 3 | 30 | 480 | 3 | 300 | 361 | 15696 | 1, 7j | E04610 V12 S15
SE107062 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107062 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3
SE107062 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3
SE107063 | D | CB | Square D | MAL3660044M | - | 600 | 600 | 3 | 30 | 480 | 3 | 350 | 414 | 15696 | 1, 7j | E04610 V12 S15
SE107063 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107063 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3
SE107063 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3
SE107064 | D | CB | Square D | MAL3660042M | - | 600 | 600 | 3 | 22 | 600 | 3 | 350 | 336 | 15696 | 1, 7j | E04610 V12 S15
SE107064 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107064 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3
SE107064 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3
SE107065 | D | CB | Square D | MAL3680045M | - | 800 | 600 | 3 | 30 | 480 | 3 | 400 | 477 | 15696 | 1, 7j | E04610 V12 S15
SE107065 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107065 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3
SE107065 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3
SE107066 | D | CB | Square D | MAL3660044M | - | 600 | 600 | 3 | 22 | 600 | 3 | 400 | 382 | 15696 | 1, 7j | E04610 V12 S15
SE107066 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107066 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3
SE107066 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3
SE107067 | D | CB | Square D | MAL3660044M | - | 600 | 600 | 3 | 22 | 600 | 3 | 450 | 412 | 15696 | 1, 7j | E04610 V12 S15
SE107067 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107067 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3
SE107067 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3
SE107068 | D | CB | Square D | MAL3660044M | - | 600 | 600 | 3 | 22 | 600 | 3 | 500 | 472 | 15696 | 1, 7j | E04610 V12 S15
SE107068 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3
SE107068 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3
SE107068 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3
SE152622 | C | CB | Square D | KAL36110 | 42 | 110 | 600 | 3 | 42 | 200 | 3 | 25 | 78.2 | 2289 | 1, 7l | E40610 V12 S15
SE152622 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 42 | 200 | 3 | 25 | 78.2 | 2289 | 1, 7l | E40610 V12 S15
SE152622 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 42 | 200 | 3 | 25 | 78.2 | 2289 | 1, 7l | E40610 V12 S15
SE152623 | C | CB | Square D | KAL36110 | 42 | 110 | 600 | 3 | 42 | 208 | 3 | 25 | 74.8 | 2289 | 1, 7l | E40610 V12 S15
SE152623 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 42 | 208 | 3 | 25 | 74.8 | 2289 | 1, 7l | E40610 V12 S15
SE152623 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 42 | 208 | 3 | 25 | 74.8 | 2289 | 1, 7l | E40610 V12 S15
SE152624 | C | CB | Square D | KAL36110 | 42 | 110 | 600 | 3 | 42 | 240 | 3 | 30 | 80 | 2289 | 1, 7l | E40610 V12 S15
SE152624 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 42 | 240 | 3 | 30 | 80 | 2289 | 1, 7l | E40610 V12 S15
SE152624 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 42 | 240 | 3 | 30 | 80 | 2289 | 1, 7l | E40610 V12 S15
SE152625 | C | CB | Square D | KAL36110 | 25 | 110 | 600 | 3 | 25 | 480 | 3 | 60 | 77 | 2289 | 1, 7l | E40610 V12 S15
SE152624 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 25 | 480 | 3 | 60 | 77 | 2289 | 1, 7l | E40610 V12 S15
SE152625 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 25 | 480 | 3 | 60 | 77 | 2289 | 1, 7l | E40610 V12 S15
SE152626 | C | CB | Square D | KAL36110 | 22 | 110 | 600 | 3 | 22 | 600 | 3 | 75 | 77 | 2747 | 1, 7n | E40610 V12 S15
SE152626 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 22 | 600 | 3 | 75 | 77 | 2747 | 1, 7n | E40610 V12 S15
SE152626 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 22 | 600 | 3 | 75 | 77 | 2747 | 1, 7n | E40610 V12 S15
SE152627 | C | CB | Square D | KAL36125 | 42 | 125 | 600 | 3 | 42 | 200 | 3 | 30 | 92 | 2747 | 1, 7n | E40610 V12 S15
SE152627 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 42 | 200 | 3 | 30 | 92 | 2747 | 1, 7n | E40610 V12 S15
SE152627 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 42 | 200 | 3 | 30 | 92 | 2747 | 1, 7n | E40610 V12 S15
SE152628 | C | CB | Square D | KAL36125 | 42 | 125 | 600 | 3 | 42 | 208 | 3 | 30 | 88 | 2747 | 1, 7n | E40610 V12 S15
SE152628 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 42 | 208 | 3 | 30 | 88 | 2747 | 1, 7n | E40610 V12 S15
SE152628 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 42 | 208 | 3 | 30 | 88 | 2747 | 1, 7n | E40610 V12 S15
SE152629 | C | CB | Square D | KAL36150 | 42 | 150 | 600 | 3 | 42 | 240 | 3 | 40 | 104 | 2747 | 1, 7n | E40610 V12 S15
SE152629 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 42 | 240 | 3 | 40 | 104 | 2747 | 1, 7n | E40610 V12 S15
SE152629 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 42 | 240 | 3 | 40 | 104 | 2747 | 1, 7n | E40610 V12 S15
SE152630 | C | CB | Square D | KAL36125 | 25 | 125 | 600 | 3 | 25 | 480 | 3 | 75 | 96 | 2747 | 1, 7n | E40610 V12 S15
SE152630 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 25 | 480 | 3 | 75 | 96 | 2747 | 1, 7n | E40610 V12 S15
SE152630 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 25 | 480 | 3 | 75 | 96 | 2747 | 1, 7n | E40610 V12 S15
SE152631 | C | CB | Square D | KAL36150 | 22 | 150 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 3205 | 1, 7d | E40610 V12 S15
SE152631 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 3205 | 1, 7d | E40610 V12 S15
SE152631 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 3205 | 1, 7d | E40610 V12 S15
SE152632 | C | CB | Square D | KAL36175 | 42 | 175 | 600 | 3 | 42 | 200 | 3 | 40 | 120 | 3205 | 1, 7d | E40610 V12 S15
SE152632 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 42 | 200 | 3 | 40 | 120 | 3205 | 1, 7d | E40610 V12 S15
SE152632 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 42 | 200 | 3 | 40 | 120 | 3205 | 1, 7d | E40610 V12 S15
SE152633 | C | CB | Square D | KAL36175 | 42 | 175 | 600 | 3 | 42 | 208 | 3 | 40 | 114 | 3205 | 1, 7d | E40610 V12 S15
SE152633 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 42 | 208 | 3 | 40 | 114 | 3205 | 1, 7d | E40610 V12 S15
SE152633 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 42 | 208 | 3 | 40 | 114 | 3205 | 1, 7d | E40610 V12 S15
SE152634 | C | CB | Square D | KAL36200 | 42 | 200 | 600 | 3 | 42 | 240 | 3 | 50 | 130 | 3205 | 1, 7d | E40610 V12 S15
SE152634 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 42 | 240 | 3 | 50 | 130 | 3205 | 1, 7d | E40610 V12 S15
SE152634 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 42 | 240 | 3 | 50 | 130 | 3205 | 1, 7d | E40610 V12 S15
SE152635 | C | CB | Square D | KAL36200 | 25 | 200 | 600 | 3 | 25 | 480 | 3 | 100 | 124 | 3205 | 1, 7d | E40610 V12 S15
SE152635 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 25 | 480 | 3 | 100 | 124 | 3205 | 1, 7d | E40610 V12 S15
SE152635 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 25 | 480 | 3 | 100 | 124 | 3205 | 1, 7d | E40610 V12 S15
SE152636 | C | CB | Square D | KAL36200 | 22 | 200 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 5036 | 1, 7p | E40610 V12 S15
SE152636 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 5036 | 1, 7p | E40610 V12 S15
SE152636 |  | OLR | Telemecanique | LR9F5369 | 5 | 90 - 150 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 5036 | 1, 7p | E40610 V12 S15
SE152637 | C | CB | Square D | KAL36200 | 42 | 200 | 600 | 3 | 42 | 200 | 3 | 50 | 150 | 5036 | 1, 7p | E40610 V12 S15
SE152637 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 42 | 200 | 3 | 50 | 150 | 5036 | 1, 7p | E40610 V12 S15
SE152637 |  | OLR | Telemecanique | LR9F5369 | 5 | 90 - 150 | 600 | 3 | 42 | 200 | 3 | 50 | 150 | 5036 | 1, 7p | E40610 V12 S15
SE152638 | C | CB | Square D | KAL36200 | 42 | 200 | 600 | 3 | 42 | 208 | 3 | 50 | 143 | 5036 | 1, 7p | E40610 V12 S15
SE152638 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 42 | 208 | 3 | 50 | 143 | 5036 | 1, 7p | E40610 V12 S15
SE152638 |  | OLR | Telemecanique | LR9F5369 | 5 | 90 - 150 | 600 | 3 | 42 | 208 | 3 | 50 | 143 | 5036 | 1, 7p | E40610 V12 S15
SE152639 | C | CB | Square D | KAL36225 | 42 | 225 | 600 | 3 | 42 | 240 | 3 | 60 | 154 | 5036 | 1, 7p | E40610 V12 S15
SE152639 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 42 | 240 | 3 | 60 | 154 | 5036 | 1, 7p | E40610 V12 S15
SE152639 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 42 | 240 | 3 | 60 | 154 | 5036 | 1, 7p | E40610 V12 S15
SE152640 | C | CB | Square D | KAL36225 | 25 | 225 | 600 | 3 | 25 | 480 | 3 | 125 | 156 | 5036 | 1, 7p | E40610 V12 S15
SE152640 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 25 | 480 | 3 | 125 | 156 | 5036 | 1, 7p | E40610 V12 S15
SE152640 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 25 | 480 | 3 | 125 | 156 | 5036 | 1, 7p | E40610 V12 S15
SE152687 | C | CB | Square D | MAL36800 | 42 | 800 | 600 | 3 | 42 | 200 | 3 | 125 | 359 | 15696 | 1, 7j | E40610 V12 S15
SE152687 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 42 | 200 | 3 | 125 | 359 | 15696 | 1, 7j | E40610 V12 S15
SE152687 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 42 | 200 | 3 | 125 | 359 | 15696 | 1, 7j | E40610 V12 S15
SE152688 | C | CB | Square D | MAL36800 | 42 | 800 | 600 | 3 | 42 | 208 | 3 | 125 | 343 | 15696 | 1, 7j | E40610 V12 S15
SE152688 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 42 | 208 | 3 | 125 | 343 | 15696 | 1, 7j | E40610 V12 S15
SE152688 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 42 | 208 | 3 | 125 | 343 | 15696 | 1, 7j | E40610 V12 S15
SE152689 | C | CB | Square D | MAL36900 | 42 | 900 | 600 | 3 | 42 | 200 | 3 | 150 | 414 | 15696 | 1, 7j | E40610 V12 S15
SE152689 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 42 | 200 | 3 | 150 | 414 | 15696 | 1, 7j | E40610 V12 S15
SE152689 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 42 | 200 | 3 | 150 | 414 | 15696 | 1, 7j | E40610 V12 S15
SE152690 | C | CB | Square D | MAL36900 | 42 | 900 | 600 | 3 | 42 | 208 | 3 | 150 | 396 | 15696 | 1, 7j | E40610 V12 S15
SE152690 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 42 | 208 | 3 | 150 | 396 | 15696 | 1, 7j | E40610 V12 S15
SE152690 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 42 | 208 | 3 | 150 | 396 | 15696 | 1, 7j | E40610 V12 S15
SE152691 | C | CB | Square D | MAL36800 | 42 | 800 | 600 | 3 | 42 | 240 | 3 | 150 | 360 | 15696 | 1, 7j | E40610 V12 S15
SE152691 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 42 | 240 | 3 | 150 | 360 | 15696 | 1, 7j | E40610 V12 S15
SE152691 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 42 | 240 | 3 | 150 | 360 | 15696 | 1, 7j | E40610 V12 S15
SE152692 | C | CB | Square D | MAL361000 | 42 | 1000 | 600 | 3 | 42 | 240 | 3 | 200 | 480 | 15696 | 1, 7j | E40610 V12 S15
SE152692 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 42 | 240 | 3 | 200 | 480 | 15696 | 1, 7j | E40610 V12 S15
SE152692 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 42 | 240 | 3 | 200 | 480 | 15696 | 1, 7j | E40610 V12 S15
SE152693 | C | CB | Square D | MAL36800 | 30 | 800 | 600 | 3 | 30 | 480 | 3 | 300 | 361 | 15696 | 1, 7j | E40610 V12 S15
SE152693 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 30 | 480 | 3 | 300 | 361 | 15696 | 1, 7j | E40610 V12 S15
SE152693 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 30 | 480 | 3 | 300 | 361 | 15696 | 1, 7j | E40610 V12 S15
SE152694 | C | CB | Square D | MAL36900 | 30 | 900 | 600 | 3 | 30 | 480 | 3 | 350 | 414 | 15696 | 1, 7j | E40610 V12 S15
SE152694 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 30 | 480 | 3 | 350 | 414 | 15696 | 1, 7j | E40610 V12 S15
SE152694 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 30 | 480 | 3 | 350 | 414 | 15696 | 1, 7j | E40610 V12 S15
SE152695 | C | CB | Square D | MAL36700 | 22 | 700 | 600 | 3 | 22 | 600 | 3 | 350 | 336 | 15696 | 1, 7j | E40610 V12 S15
SE152695 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 22 | 600 | 3 | 350 | 336 | 15696 | 1, 7j | E40610 V12 S15
SE152695 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 22 | 600 | 3 | 350 | 336 | 15696 | 1, 7j | E40610 V12 S15
SE152696 | C | CB | Square D | MAL361000 | 30 | 1000 | 600 | 3 | 30 | 480 | 3 | 400 | 477 | 15696 | 1, 7j | E40610 V12 S15
SE152696 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 30 | 480 | 3 | 400 | 477 | 15696 | 1, 7j | E40610 V12 S15
SE152696 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 30 | 480 | 3 | 400 | 477 | 15696 | 1, 7j | E40610 V12 S15
SE152697 | C | CB | Square D | MAL36800 | 22 | 800 | 600 | 3 | 22 | 600 | 3 | 400 | 382 | 15696 | 1, 7j | E40610 V12 S15
SE152697 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 22 | 600 | 3 | 400 | 382 | 15696 | 1, 7j | E40610 V12 S15
SE152697 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 22 | 600 | 3 | 400 | 382 | 15696 | 1, 7j | E40610 V12 S15
SE152698 | C | CB | Square D | MAL36900 | 22 | 900 | 600 | 3 | 22 | 600 | 3 | 450 | 412 | 15696 | 1, 7j | E40610 V12 S15
SE152698 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 22 | 600 | 3 | 450 | 412 | 15696 | 1, 7j | E40610 V12 S15
SE152698 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 22 | 600 | 3 | 450 | 412 | 15696 | 1, 7j | E40610 V12 S15
SE152699 | C | CB | Square D | MAL361000 | 22 | 1000 | 600 | 3 | 22 | 600 | 3 | 500 | 472 | 15696 | 1, 7j | E40610 V12 S15
SE152699 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 22 | 600 | 3 | 500 | 472 | 15696 | 1, 7j | E40610 V12 S15
SE152699 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 22 | 600 | 3 | 500 | 472 | 15696 | 1, 7j | E40610 V12 S15
SE152700 | D | ICB | Square D | MHL3660042M | - | 600 | 600 | 3 | 65 | 200 | 3 | 125 | 359 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152700 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 65 | 200 | 3 | 125 | 359 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152700 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 65 | 200 | 3 | 125 | 359 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152701 | D | ICB | Square D | MHL3660042M | - | 600 | 600 | 3 | 65 | 208 | 3 | 125 | 343 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152701 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 65 | 208 | 3 | 125 | 343 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152701 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 65 | 208 | 3 | 125 | 343 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152702 | D | ICB | Square D | MHL3660042M | - | 600 | 600 | 3 | 65 | 200 | 3 | 150 | 414 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152702 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 65 | 200 | 3 | 150 | 414 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152702 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 65 | 200 | 3 | 150 | 414 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152703 | D | ICB | Square D | MHL3660042M | - | 600 | 600 | 3 | 65 | 208 | 3 | 150 | 396 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152703 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 65 | 208 | 3 | 150 | 396 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152703 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 65 | 208 | 3 | 150 | 396 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152704 | D | ICB | Square D | MHL3660042M | - | 600 | 600 | 3 | 65 | 240 | 3 | 150 | 360 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152704 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 65 | 240 | 3 | 150 | 360 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152704 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 65 | 240 | 3 | 150 | 360 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152705 | D | ICB | Square D | MHL3680045M | - | 800 | 600 | 3 | 65 | 240 | 3 | 200 | 480 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152705 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 65 | 240 | 3 | 200 | 480 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152705 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 65 | 240 | 3 | 200 | 480 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152706 | D | ICB | Square D | MHL3660044M | - | 600 | 600 | 3 | 65 | 480 | 3 | 300 | 361 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152706 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 65 | 480 | 3 | 300 | 361 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152706 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 65 | 480 | 3 | 300 | 361 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152707 | D | ICB | Square D | MHL3660044M | - | 600 | 600 | 3 | 65 | 480 | 3 | 350 | 414 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152707 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 65 | 480 | 3 | 350 | 414 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152707 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 65 | 480 | 3 | 350 | 414 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152708 | D | ICB | Square D | MHL3660042M | - | 600 | 600 | 3 | 22 | 600 | 3 | 350 | 336 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152708 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 22 | 600 | 3 | 350 | 336 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152708 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 22 | 600 | 3 | 350 | 336 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152709 | D | ICB | Square D | MHL3680045M | - | 800 | 600 | 3 | 65 | 480 | 3 | 400 | 477 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152709 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 65 | 480 | 3 | 400 | 477 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152709 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 65 | 480 | 3 | 400 | 477 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152710 | D | ICB | Square D | MHL3660044M | - | 600 | 600 | 3 | 22 | 600 | 3 | 400 | 382 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152710 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 22 | 600 | 3 | 400 | 382 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152710 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 22 | 600 | 3 | 400 | 382 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152711 | D | ICB | Square D | MHL3660044M | - | 600 | 600 | 3 | 22 | 600 | 3 | 450 | 412 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152711 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 22 | 600 | 3 | 450 | 412 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152711 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 22 | 600 | 3 | 450 | 412 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152712 | D | ICB | Square D | MHL3660042M | - | 600 | 600 | 3 | 22 | 600 | 3 | 500 | 472 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152712 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 22 | 600 | 3 | 500 | 472 | 15696 | 1, 5, 7j | E40610 V12 S15
SE152712 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 22 | 600 | 3 | 500 | 472 | 15696 | 1, 5, 7j | E40610 V12 S15
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = Use wire ties evenly spaced apart to secure conductors in place.
(7) = See Table 7 for minimum internal wiring between load side of short circuit protective device & line side of starter.
(8) = "@" refer to digest to complete contactor Catalog number for coil voltage and Form modifications.
(9) = Insulator to be provided underneath starter. (QMFZ2), Fastex, Type Formex GK-30, 1/32 inch minimum thickness by 4 inches x 5.7 inches.
Table 7 - Minimum Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation)
| Wire Code |  | Wire Size
| 7a |  | 12 AWG
| 7b |  | 8 AWG
| 7c |  | 2 AWG
| 7d |  | 1 AWG
| 7e |  | 250 MCM
| 7f |  | 300 MCM
| 7g |  | (2) 250 MCM
| 7h |  | 2/0 AWG
| 7i |  | 4/0 AWG
| 7j |  | (2) 4/0 AWG
| 7k |  | 10 AWG
| 7l |  | 6 AWG
| 7m |  | 4 AWG
| 7n |  | 3 AWG
| 7p |  | 1/0 AWG
| 7q |  | (2) 3/0 AWG
| 7r |  | (2) 2/0 AWG
| 7s |  | 3/0 AWG

## K,L,M-Frame-R
Issued: 2008-01-14
Last Revised: 2015-03-20
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE102250 | C | CB | Square D | MAL36600 | 42 | 600 | 600 | 3 | 42 | 208 | 3 | 125 | 343 | 19310 | 1, 7j | E40610 V12 S16
SE102250 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 42 | 208 | 3 | 125 | 343 | 19310 | 1, 7j | E40610 V12 S16
SE102250 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 42 | 208 | 3 | 125 | 343 | 19310 | 1, 7j | E40610 V12 S16
SE102250 |  | INTERLOCK | Telemecanique | LA9FF970 or LA9FF4F | NA | NA | NA | NA | 42 | 208 | 3 | 125 | 343 | 19310 | 1, 7j | E40610 V12 S16
SE102250 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 42 | 208 | 3 | 125 | 343 | 19310 | 1, 7j | E40610 V12 S16
SE102251 | C | CB | Square D | MAL36700 | 42 | 700 | 600 | 3 | 42 | 208 | 3 | 150 | 396 | 19310 | 1, 7j | E40610 V12 S16
SE102251 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 42 | 208 | 3 | 150 | 396 | 19310 | 1, 7j | E40610 V12 S16
SE102251 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 42 | 208 | 3 | 150 | 396 | 19310 | 1, 7j | E40610 V12 S16
SE102251 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 42 | 208 | 3 | 150 | 396 | 19310 | 1, 7j | E40610 V12 S16
SE102251 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 42 | 208 | 3 | 150 | 396 | 19310 | 1, 7j | E40610 V12 S16
SE102252 | C | CB | Square D | KHL36110 | 65 | 110 | 600 | 3 | 65 | 208 | 3 | 25 | 74.8 | 3662 | 1, 7L | E40610 V12 S16
SE102252 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 65 | 208 | 3 | 25 | 74.8 | 3662 | 1, 7L | E40610 V12 S16
SE102252 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 65 | 208 | 3 | 25 | 74.8 | 3662 | 1, 7L | E40610 V12 S16
SE102253 | C | CB | Square D | KHL36125 | 65 | 125 | 600 | 3 | 65 | 208 | 3 | 30 | 88 | 5036 | 1, 7n | E40610 V12 S16
SE102253 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 65 | 208 | 3 | 30 | 88 | 5036 | 1, 7n | E40610 V12 S16
SE102253 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 65 | 208 | 3 | 30 | 88 | 5036 | 1, 7n | E40610 V12 S16
SE102254 | C | CB | Square D | KHL36175 | 65 | 175 | 600 | 3 | 65 | 208 | 3 | 40 | 114 | 5036 | 1, 7d | E40610 V12 S16
SE102254 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 65 | 208 | 3 | 40 | 114 | 5036 | 1, 7d | E40610 V12 S16
SE102254 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 65 | 208 | 3 | 40 | 114 | 5036 | 1, 7d | E40610 V12 S16
SE102255 | C | CB | Square D | KHL36200 | 65 | 200 | 600 | 3 | 65 | 208 | 3 | 50 | 143 | 6409 | 1, 7p | E40610 V12 S16
SE102255 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 65 | 208 | 3 | 50 | 143 | 6409 | 1, 7p | E40610 V12 S16
SE102255 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 65 | 208 | 3 | 50 | 143 | 6409 | 1, 7p | E40610 V12 S16
SE102255 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 65 | 208 | 3 | 50 | 143 | 6409 | 1, 7p | E40610 V12 S16
SE102255 |  | OLR | Telemecanique | LR9F5369 | 5 | 90 - 150 | 600 | 3 | 65 | 208 | 3 | 50 | 143 | 6409 | 1, 7p | E40610 V12 S16
SE102256 | C | CB | Square D | LCL36300 | 100 | 300 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 9156 | 1, 7h | E40610 V12 S16
SE102256 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 9156 | 1, 7h | E40610 V12 S16
SE102256 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 9156 | 1, 7h | E40610 V12 S16
SE102256 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FH4H | NA | NA | NA | NA | 100 | 208 | 3 | 60 | 169 | 9156 | 1, 7h | E40610 V12 S16
SE102256 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 9156 | 1, 7h | E40610 V12 S16
SE102257 | C | CB | Square D | LCL36350 | 100 | 350 | 600 | 3 | 100 | 208 | 3 | 75 | 211 | 10987 | 1, 7i | E40610 V12 S16
SE102257 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 100 | 208 | 3 | 75 | 211 | 10987 | 1, 7i | E40610 V12 S16
SE102257 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 100 | 208 | 3 | 75 | 211 | 10987 | 1, 7i | E40610 V12 S16
SE102257 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FJ4J | NA | NA | NA | NA | 100 | 208 | 3 | 75 | 211 | 10987 | 1, 7i | E40610 V12 S16
SE102257 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 208 | 3 | 75 | 211 | 10987 | 1, 7i | E40610 V12 S16
SE102258 | C | CB | Square D | LCL36500 | 100 | 500 | 600 | 3 | 100 | 208 | 3 | 100 | 273 | 10987 | 1, 7f | E40610 V12 S16
SE102258 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 100 | 208 | 3 | 100 | 273 | 10987 | 1, 7f | E40610 V12 S16
SE102258 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 100 | 208 | 3 | 100 | 273 | 10987 | 1, 7f | E40610 V12 S16
SE102258 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FJ4J | NA | NA | NA | NA | 100 | 208 | 3 | 100 | 273 | 10987 | 1, 7f | E40610 V12 S16
SE102258 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3 | 100 | 208 | 3 | 100 | 273 | 10987 | 1, 7f | E40610 V12 S16
SE102259 | D | ICB | Square D | MAL3660042M | - | 600 | 600 | 3 | 42 | 208 | 3 | 125 | 343 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102259 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 42 | 208 | 3 | 125 | 343 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102259 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 42 | 208 | 3 | 125 | 343 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102259 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 42 | 208 | 3 | 125 | 343 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102259 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 42 | 208 | 3 | 125 | 343 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102260 | D | ICB | Square D | MAL3660042M | - | 600 | 600 | 3 | 42 | 208 | 3 | 150 | 396 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102260 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 42 | 208 | 3 | 150 | 396 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102260 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 42 | 208 | 3 | 150 | 396 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102260 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 42 | 208 | 3 | 150 | 396 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102260 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 42 | 208 | 3 | 150 | 396 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102265 | C | CB | Square D | KHL36110 | 65 | 110 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3662 | 1, 7L | E40610 V12 S16
SE102265 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3662 | 1, 7L | E40610 V12 S16
SE102265 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3662 | 1, 7L | E40610 V12 S16
SE102266 | D | ICB | Square D | KHL3625026M | - | 250 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3662 | 1, 5, 7L | E40610 V12 S16
SE102266 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3662 | 1, 5, 7L | E40610 V12 S16
SE102266 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3662 | 1, 5, 7L | E40610 V12 S16
SE102267 | C | CB | Square D | KHL36150 | 65 | 150 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 5036 | 1, 7n | E40610 V12 S16
SE102267 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 5036 | 1, 7n | E40610 V12 S16
SE102267 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 5036 | 1, 7n | E40610 V12 S16
SE102268 | C | CB | Square D | KHL36200 | 65 | 200 | 600 | 3 | 65 | 240 | 3 | 50 | 130 | 5036 | 1, 7d | E40610 V12 S16
SE102268 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 65 | 240 | 3 | 50 | 130 | 5036 | 1, 7d | E40610 V12 S16
SE102268 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 65 | 240 | 3 | 50 | 130 | 5036 | 1, 7d | E40610 V12 S16
SE102269 | D | ICB | Square D | KHP3625029M | - | 250 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 5036 | 1, 5, 7n | E40610 V12 S16
SE102269 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 5036 | 1, 5, 7n | E40610 V12 S16
SE102269 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 5036 | 1, 5, 7n | E40610 V12 S16
SE102270 | D | ICB | Square D | KHL3625031M | - | 250 | 600 | 3 | 65 | 240 | 3 | 50 | 130 | 5036 | 1, 5, 7d | E40610 V12 S16
SE102270 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 65 | 240 | 3 | 50 | 130 | 5036 | 1, 5, 7d | E40610 V12 S16
SE102270 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 65 | 240 | 3 | 50 | 130 | 5036 | 1, 5, 7d | E40610 V12 S16
SE102271 | C | CB | Square D | KHL36225 | 65 | 225 | 600 | 3 | 65 | 240 | 3 | 60 | 154 | 6409 | 1, 7p | E40610 V12 S16
SE102271 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 65 | 240 | 3 | 60 | 154 | 6409 | 1, 7p | E40610 V12 S16
SE102271 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 65 | 240 | 3 | 60 | 154 | 6409 | 1, 7p | E40610 V12 S16
SE102271 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 65 | 240 | 3 | 60 | 154 | 6409 | 1, 7p | E40610 V12 S16
SE102271 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 65 | 240 | 3 | 60 | 154 | 6409 | 1, 7p | E40610 V12 S16
SE102272 | C | CB | Square D | LCL36300 | 100 | 300 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 9156 | 1, 7h | E40610 V12 S16
SE102272 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 9156 | 1, 7h | E40610 V12 S16
SE102272 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 9156 | 1, 7h | E40610 V12 S16
SE102272 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 240 | 3 | 75 | 192 | 9156 | 1, 7h | E40610 V12 S16
SE102272 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 9156 | 1, 7h | E40610 V12 S16
SE102273 | C | CB | Square D | LCL36400 | 100 | 400 | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 10987 | 1, 7i | E40610 V12 S16
SE102273 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 10987 | 1, 7i | E40610 V12 S16
SE102273 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 10987 | 1, 7i | E40610 V12 S16
SE102273 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FJ4J | NA | NA | NA | NA | 100 | 240 | 3 | 100 | 248 | 10987 | 1, 7i | E40610 V12 S16
SE102273 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 10987 | 1, 7i | E40610 V12 S16
SE102274 | C | CB | Square D | LCL36600 | 100 | 600 | 600 | 3 | 100 | 240 | 3 | 125 | 312 | 10987 | 1, 7f | E40610 V12 S16
SE102274 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 100 | 240 | 3 | 125 | 312 | 10987 | 1, 7f | E40610 V12 S16
SE102274 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 100 | 240 | 3 | 125 | 312 | 10987 | 1, 7f | E40610 V12 S16
SE102274 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FJ4J | NA | NA | NA | NA | 100 | 240 | 3 | 125 | 312 | 10987 | 1, 7f | E40610 V12 S16
SE102274 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3 | 100 | 240 | 3 | 125 | 312 | 10987 | 1, 7f | E40610 V12 S16
SE102275 | C | CB | Square D | MAL36600 | 42 | 600 | 600 | 3 | 42 | 240 | 3 | 150 | 360 | 19310 | 1, 7j | E40610 V12 S16
SE102275 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 42 | 240 | 3 | 150 | 360 | 19310 | 1, 7j | E40610 V12 S16
SE102275 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 42 | 240 | 3 | 150 | 360 | 19310 | 1, 7j | E40610 V12 S16
SE102275 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 42 | 240 | 3 | 150 | 360 | 19310 | 1, 7j | E40610 V12 S16
SE102275 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 42 | 240 | 3 | 150 | 360 | 19310 | 1, 7j | E40610 V12 S16
SE102276 | C | CB | Square D | MAL36800 | 42 | 800 | 600 | 3 | 42 | 240 | 3 | 200 | 480 | 19310 | 1, 7j | E40610 V12 S16
SE102276 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 42 | 240 | 3 | 200 | 480 | 19310 | 1, 7j | E40610 V12 S16
SE102276 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 42 | 240 | 3 | 200 | 480 | 19310 | 1, 7j | E40610 V12 S16
SE102276 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 42 | 240 | 3 | 200 | 480 | 19310 | 1, 7j | E40610 V12 S16
SE102276 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 42 | 240 | 3 | 200 | 480 | 19310 | 1, 7j | E40610 V12 S16
SE102277 | D | ICB | Square D | MAL3660042M | - | 600 | 600 | 3 | 42 | 240 | 3 | 150 | 360 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102277 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 42 | 240 | 3 | 150 | 360 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102277 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 42 | 240 | 3 | 150 | 360 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102277 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 42 | 240 | 3 | 150 | 360 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102277 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 42 | 240 | 3 | 150 | 360 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102278 | D | ICB | Square D | MAL3680045M | - | 800 | 600 | 3 | 42 | 240 | 3 | 200 | 480 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102278 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 42 | 240 | 3 | 200 | 480 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102278 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 42 | 240 | 3 | 200 | 480 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102278 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 42 | 240 | 3 | 200 | 480 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102278 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 42 | 240 | 3 | 200 | 480 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102279 | C | CB | Square D | MAL36600 | 30 | 600 | 600 | 3 | 30 | 480 | 3 | 300 | 361 | 19310 | 1, 7j | E40610 V12 S16
SE102279 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 30 | 480 | 3 | 300 | 361 | 19310 | 1, 7j | E40610 V12 S16
SE102279 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 30 | 480 | 3 | 300 | 361 | 19310 | 1, 7j | E40610 V12 S16
SE102279 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 30 | 480 | 3 | 300 | 361 | 19310 | 1, 7j | E40610 V12 S16
SE102279 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 30 | 480 | 3 | 300 | 361 | 19310 | 1, 7j | E40610 V12 S16
SE102280 | C | CB | Square D | MAL36700 | 30 | 700 | 600 | 3 | 30 | 480 | 3 | 350 | 414 | 19310 | 1, 7j | E40610 V12 S16
SE102280 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 30 | 480 | 3 | 350 | 414 | 19310 | 1, 7j | E40610 V12 S16
SE102280 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 30 | 480 | 3 | 350 | 414 | 19310 | 1, 7j | E40610 V12 S16
SE102280 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 30 | 480 | 3 | 350 | 414 | 19310 | 1, 7j | E40610 V12 S16
SE102280 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 30 | 480 | 3 | 350 | 414 | 19310 | 1, 7j | E40610 V12 S16
SE102281 | C | CB | Square D | MAL36800 | 30 | 800 | 600 | 3 | 30 | 480 | 3 | 400 | 477 | 19310 | 1, 7j | E40610 V12 S16
SE102281 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 30 | 480 | 3 | 400 | 477 | 19310 | 1, 7j | E40610 V12 S16
SE102281 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 30 | 480 | 3 | 400 | 477 | 19310 | 1, 7j | E40610 V12 S16
SE102281 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 30 | 480 | 3 | 400 | 477 | 19310 | 1, 7j | E40610 V12 S16
SE102281 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 30 | 480 | 3 | 400 | 477 | 19310 | 1, 7j | E40610 V12 S16
SE102282 | C | CB | Square D | KHL36110 | 35 | 110 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 3662 | 1, 7L | E40610 V12 S16
SE102282 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 3662 | 1, 7L | E40610 V12 S16
SE102282 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 3662 | 1, 7L | E40610 V12 S16
SE102283 | C | CB | Square D | KHL36125 | 35 | 125 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 5036 | 1, 7n | E40610 V12 S16
SE102283 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 5036 | 1, 7n | E40610 V12 S16
SE102283 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 5036 | 1, 7n | E40610 V12 S16
SE102284 | C | CB | Square D | KHL36200 | 35 | 200 | 600 | 3 | 35 | 480 | 3 | 100 | 124 | 5036 | 1, 7d | E40610 V12 S16
SE102284 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 35 | 480 | 3 | 100 | 124 | 5036 | 1, 7d | E40610 V12 S16
SE102284 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 35 | 480 | 3 | 100 | 124 | 5036 | 1, 7d | E40610 V12 S16
SE102285 | C | CB | Square D | KHL36225 | 35 | 225 | 600 | 3 | 35 | 480 | 3 | 125 | 156 | 6409 | 1, 7p | E40610 V12 S16
SE102285 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 35 | 480 | 3 | 125 | 156 | 6409 | 1, 7p | E40610 V12 S16
SE102285 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 35 | 480 | 3 | 125 | 156 | 6409 | 1, 7p | E40610 V12 S16
SE102285 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 35 | 480 | 3 | 125 | 156 | 6409 | 1, 7p | E40610 V12 S16
SE102285 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 35 | 480 | 3 | 125 | 156 | 6409 | 1, 7p | E40610 V12 S16
SE102286 | C | CB | Square D | LCL36300 | 65 | 300 | 600 | 3 | 65 | 480 | 3 | 150 | 180 | 9156 | 1, 7h | E40610 V12 S16
SE102286 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3 | 65 | 480 | 3 | 150 | 180 | 9156 | 1, 7h | E40610 V12 S16
SE102286 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3 | 65 | 480 | 3 | 150 | 180 | 9156 | 1, 7h | E40610 V12 S16
SE102286 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FH4H | NA | NA | NA | NA | 65 | 480 | 3 | 150 | 180 | 9156 | 1, 7h | E40610 V12 S16
SE102286 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 65 | 480 | 3 | 150 | 180 | 9156 | 1, 7h | E40610 V12 S16
SE102287 | C | CB | Square D | LCL36400 | 65 | 400 | 600 | 3 | 65 | 480 | 3 | 200 | 240 | 10987 | 1, 7i | E40610 V12 S16
SE102287 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 65 | 480 | 3 | 200 | 240 | 10987 | 1, 7i | E40610 V12 S16
SE102287 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 65 | 480 | 3 | 200 | 240 | 10987 | 1, 7i | E40610 V12 S16
SE102287 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FJ4J | NA | NA | NA | NA | 65 | 480 | 3 | 200 | 240 | 10987 | 1, 7i | E40610 V12 S16
SE102287 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3 | 65 | 480 | 3 | 200 | 240 | 10987 | 1, 7i | E40610 V12 S16
SE102288 | C | CB | Square D | LCL36600 | 65 | 600 | 600 | 3 | 65 | 480 | 3 | 250 | 302 | 10987 | 1, 7f | E40610 V12 S16
SE102288 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 65 | 480 | 3 | 250 | 302 | 10987 | 1, 7f | E40610 V12 S16
SE102288 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 65 | 480 | 3 | 250 | 302 | 10987 | 1, 7f | E40610 V12 S16
SE102288 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FJ4J | NA | NA | NA | NA | 65 | 480 | 3 | 250 | 302 | 10987 | 1, 7f | E40610 V12 S16
SE102288 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 65 | 480 | 3 | 250 | 302 | 10987 | 1, 7f | E40610 V12 S16
SE102289 | D | ICB | Square D | MAL3660044M | - | 600 | 600 | 3 | 30 | 480 | 3 | 300 | 361 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102289 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 30 | 480 | 3 | 300 | 361 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102289 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 30 | 480 | 3 | 300 | 361 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102289 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 30 | 480 | 3 | 300 | 361 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102289 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 30 | 480 | 3 | 300 | 361 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102290 | D | ICB | Square D | MAL3660044M | - | 600 | 600 | 3 | 30 | 480 | 3 | 350 | 414 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102290 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 30 | 480 | 3 | 350 | 414 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102290 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 30 | 480 | 3 | 350 | 414 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102290 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 30 | 480 | 3 | 350 | 414 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102290 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 30 | 480 | 3 | 350 | 414 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102291 | D | ICB | Square D | MAL3680045M | - | 800 | 600 | 3 | 30 | 480 | 3 | 400 | 477 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102291 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 30 | 480 | 3 | 400 | 477 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102291 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 30 | 480 | 3 | 400 | 477 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102291 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 30 | 480 | 3 | 400 | 477 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102291 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 30 | 480 | 3 | 400 | 477 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102296 | C | CB | Square D | MAL36500 | 22 | 500 | 600 | 3 | 22 | 600 | 3 | 350 | 336 | 19310 | 1, 7j | E40610 V12 S16
SE102296 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 22 | 600 | 3 | 350 | 336 | 19310 | 1, 7j | E40610 V12 S16
SE102296 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 22 | 600 | 3 | 350 | 336 | 19310 | 1, 7j | E40610 V12 S16
SE102296 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 22 | 600 | 3 | 350 | 336 | 19310 | 1, 7j | E40610 V12 S16
SE102296 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 22 | 600 | 3 | 350 | 336 | 19310 | 1, 7j | E40610 V12 S16
SE102297 | C | CB | Square D | MAL36600 | 22 | 600 | 600 | 3 | 22 | 600 | 3 | 400 | 382 | 19310 | 1, 7j | E40610 V12 S16
SE102297 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 22 | 600 | 3 | 400 | 382 | 19310 | 1, 7j | E40610 V12 S16
SE102297 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 22 | 600 | 3 | 400 | 382 | 19310 | 1, 7j | E40610 V12 S16
SE102297 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 22 | 600 | 3 | 400 | 382 | 19310 | 1, 7j | E40610 V12 S16
SE102297 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 22 | 600 | 3 | 400 | 382 | 19310 | 1, 7j | E40610 V12 S16
SE102298 | C | CB | Square D | MAL36700 | 22 | 700 | 600 | 3 | 22 | 600 | 3 | 450 | 412 | 19310 | 1, 7j | E40610 V12 S16
SE102298 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 22 | 600 | 3 | 450 | 412 | 19310 | 1, 7j | E40610 V12 S16
SE102298 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 22 | 600 | 3 | 450 | 412 | 19310 | 1, 7j | E40610 V12 S16
SE102298 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 22 | 600 | 3 | 450 | 412 | 19310 | 1, 7j | E40610 V12 S16
SE102298 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 22 | 600 | 3 | 450 | 412 | 19310 | 1, 7j | E40610 V12 S16
SE102299 | C | CB | Square D | MAL36800 | 22 | 800 | 600 | 3 | 22 | 600 | 3 | 500 | 472 | 19310 | 1, 7j | E40610 V12 S16
SE102299 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 22 | 600 | 3 | 500 | 472 | 19310 | 1, 7j | E40610 V12 S16
SE102299 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 22 | 600 | 3 | 500 | 472 | 19310 | 1, 7j | E40610 V12 S16
SE102299 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 22 | 600 | 3 | 500 | 472 | 19310 | 1, 7j | E40610 V12 S16
SE102299 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 22 | 600 | 3 | 500 | 472 | 19310 | 1, 7j | E40610 V12 S16
SE102300 | C | CB | Square D | KHL36110 | 25 | 110 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 5036 | 1, 7n | E40610 V12 S16
SE102300 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 5036 | 1, 7n | E40610 V12 S16
SE102300 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 5036 | 1, 7n | E40610 V12 S16
SE102301 | C | CB | Square D | KHL36150 | 25 | 150 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 5036 | 1, 7d | E40610 V12 S16
SE102301 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 5036 | 1, 7d | E40610 V12 S16
SE102301 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 5036 | 1, 7d | E40610 V12 S16
SE102302 | C | CB | Square D | KHL36200 | 25 | 200 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 6409 | 1, 7p | E40610 V12 S16
|  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3
#REF! |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 6409 | 1, 7p | E40610 V12 S16
|  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA
SE102302 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 6409 | 1, 7p | E40610 V12 S16
SE102306 | D | ICB | Square D | MAL3660042M | - | 600 | 600 | 3 | 22 | 600 | 3 | 350 | 336 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102306 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 22 | 600 | 3 | 350 | 336 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102306 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 22 | 600 | 3 | 350 | 336 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102306 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 22 | 600 | 3 | 350 | 336 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102306 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 22 | 600 | 3 | 350 | 336 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102307 | D | ICB | Square D | MAL3660044M | - | 600 | 600 | 3 | 22 | 600 | 3 | 400 | 382 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102307 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 22 | 600 | 3 | 400 | 382 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102307 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 22 | 600 | 3 | 400 | 382 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102307 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 22 | 600 | 3 | 400 | 382 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102307 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 22 | 600 | 3 | 400 | 382 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102308 | D | ICB | Square D | MAL3660044M | - | 600 | 600 | 3 | 22 | 600 | 3 | 450 | 412 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102308 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 22 | 600 | 3 | 450 | 412 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102308 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 22 | 600 | 3 | 450 | 412 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102308 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 22 | 600 | 3 | 450 | 412 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102308 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 22 | 600 | 3 | 450 | 412 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102309 | D | ICB | Square D | MAL3660044M | - | 600 | 600 | 3 | 22 | 600 | 3 | 500 | 472 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102309 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 22 | 600 | 3 | 500 | 472 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102309 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 22 | 600 | 3 | 500 | 472 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102309 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 22 | 600 | 3 | 500 | 472 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102309 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 22 | 600 | 3 | 500 | 472 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102310 | C | CB | Square D | LCL36300 | 35 | 300 | 600 | 3 | 35 | 600 | 3 | 150 | 144 | 9156 | 1, 7h | E40610 V12 S16
SE102310 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3 | 35 | 600 | 3 | 150 | 144 | 9156 | 1, 7h | E40610 V12 S16
SE102310 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3 | 35 | 600 | 3 | 150 | 144 | 9156 | 1, 7h | E40610 V12 S16
SE102310 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FH4H | NA | NA | NA | NA | 35 | 600 | 3 | 150 | 144 | 9156 | 1, 7h | E40610 V12 S16
SE102310 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 35 | 600 | 3 | 150 | 144 | 9156 | 1, 7h | E40610 V12 S16
SE102311 | C | CB | Square D | LCL36350 | 35 | 350 | 600 | 3 | 35 | 600 | 3 | 200 | 192 | 10987 | 1, 7i | E40610 V12 S16
SE102311 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 35 | 600 | 3 | 200 | 192 | 10987 | 1, 7i | E40610 V12 S16
SE102311 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 35 | 600 | 3 | 200 | 192 | 10987 | 1, 7i | E40610 V12 S16
SE102311 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FJ4J | NA | NA | NA | NA | 35 | 600 | 3 | 200 | 192 | 10987 | 1, 7i | E40610 V12 S16
SE102311 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 35 | 600 | 3 | 200 | 192 | 10987 | 1, 7i | E40610 V12 S16
SE102312 | C | CB | Square D | LCL36400 | 35 | 400 | 600 | 3 | 35 | 600 | 3 | 250 | 242 | 10987 | 1, 7f | E40610 V12 S16
SE102312 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 35 | 600 | 3 | 250 | 242 | 10987 | 1, 7f | E40610 V12 S16
SE102312 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 35 | 600 | 3 | 250 | 242 | 10987 | 1, 7f | E40610 V12 S16
SE102312 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FJ4J | NA | NA | NA | NA | 35 | 600 | 3 | 250 | 242 | 10987 | 1, 7f | E40610 V12 S16
SE102312 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3 | 35 | 600 | 3 | 250 | 242 | 10987 | 1, 7f | E40610 V12 S16
SE102313 | C | CB | Square D | LCL36500 | 35 | 500 | 600 | 3 | 35 | 600 | 3 | 300 | 289 | 19310 | 1, 7j | E40610 V12 S16
SE102313 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 35 | 600 | 3 | 300 | 289 | 19310 | 1, 7j | E40610 V12 S16
SE102313 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 35 | 600 | 3 | 300 | 289 | 19310 | 1, 7j | E40610 V12 S16
SE102313 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 35 | 600 | 3 | 300 | 289 | 19310 | 1, 7j | E40610 V12 S16
SE102313 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3 | 35 | 600 | 3 | 300 | 289 | 19310 | 1, 7j | E40610 V12 S16
SE102314 | C | CB | Square D | LCL36600 | 35 | 600 | 600 | 3 | 35 | 600 | 3 | 350 | 336 | 19310 | 1, 7j | E40610 V12 S16
SE102314 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 35 | 600 | 3 | 350 | 336 | 19310 | 1, 7j | E40610 V12 S16
SE102314 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 35 | 600 | 3 | 350 | 336 | 19310 | 1, 7j | E40610 V12 S16
SE102314 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 35 | 600 | 3 | 350 | 336 | 19310 | 1, 7j | E40610 V12 S16
SE102314 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 35 | 600 | 3 | 350 | 336 | 19310 | 1, 7j | E40610 V12 S16
SE102315 | C | CB | Square D | LCL36600 | 35 | 600 | 600 | 3 | 35 | 600 | 3 | 400 | 382 | 19310 | 1, 7j | E40610 V12 S16
SE102315 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 35 | 600 | 3 | 400 | 382 | 19310 | 1, 7j | E40610 V12 S16
SE102315 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 35 | 600 | 3 | 400 | 382 | 19310 | 1, 7j | E40610 V12 S16
SE102315 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 35 | 600 | 3 | 400 | 382 | 19310 | 1, 7j | E40610 V12 S16
SE102315 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 35 | 600 | 3 | 400 | 382 | 19310 | 1, 7j | E40610 V12 S16
SE102316 | C | CB | Square D | LCL36600 | 35 | 600 | 600 | 3 | 35 | 600 | 3 | 450 | 412 | 19310 | 1, 7j | E40610 V12 S16
SE102316 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 35 | 600 | 3 | 450 | 412 | 19310 | 1, 7j | E40610 V12 S16
SE102316 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 35 | 600 | 3 | 450 | 412 | 19310 | 1, 7j | E40610 V12 S16
SE102316 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 35 | 600 | 3 | 450 | 412 | 19310 | 1, 7j | E40610 V12 S16
SE102316 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 35 | 600 | 3 | 450 | 412 | 19310 | 1, 7j | E40610 V12 S16
SE102317 | C | CB | Square D | LCL36600 | 35 | 600 | 600 | 3 | 35 | 600 | 3 | 500 | 472 | 19310 | 1, 7j | E40610 V12 S16
SE102317 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 35 | 600 | 3 | 500 | 472 | 19310 | 1, 7j | E40610 V12 S16
SE102317 |  | MC | Telemecanique | LC1F500 | 30 | 500 | 600 | 3 | 35 | 600 | 3 | 500 | 472 | 19310 | 1, 7j | E40610 V12 S16
SE102317 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 35 | 600 | 3 | 500 | 472 | 19310 | 1, 7j | E40610 V12 S16
SE102317 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 35 | 600 | 3 | 500 | 472 | 19310 | 1, 7j | E40610 V12 S16
SE102320 | C | CB | Square D | KAL36175 | 42 | 175 | 600 | 3 | 42 | 208 | 3 | 40 | 120 | 5036 | 1, 7d | E40610 V12 S16
SE102320 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 42 | 208 | 3 | 40 | 120 | 5036 | 1, 7d | E40610 V12 S16
SE102320 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 42 | 208 | 3 | 40 | 120 | 5036 | 1, 7d | E40610 V12 S16
SE102321 | C | CB | Square D | KAL36200 | 42 | 200 | 600 | 3 | 42 | 208 | 3 | 50 | 150 | 6409 | 1, 7p | E40610 V12 S16
SE102321 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 42 | 208 | 3 | 50 | 150 | 6409 | 1, 7p | E40610 V12 S16
SE102321 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 42 | 208 | 3 | 50 | 150 | 6409 | 1, 7p | E40610 V12 S16
SE102321 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 42 | 208 | 3 | 50 | 150 | 6409 | 1, 7p | E40610 V12 S16
SE102321 |  | OLR | Telemecanique | LR9F5369 | 5 | 90 - 150 | 600 | 3 | 42 | 208 | 3 | 50 | 150 | 6409 | 1, 7p | E40610 V12 S16
SE102328 | C | CB | Square D | MAL36600 | 42 | 600 | 600 | 3 | 42 | 208 | 3 | 125 | 359 | 19310 | 1, 7j | E40610 V12 S16
SE102328 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 42 | 208 | 3 | 125 | 359 | 19310 | 1, 7j | E40610 V12 S16
SE102328 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 42 | 208 | 3 | 125 | 359 | 19310 | 1, 7j | E40610 V12 S16
SE102328 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 42 | 208 | 3 | 125 | 359 | 19310 | 1, 7j | E40610 V12 S16
SE102328 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 42 | 208 | 3 | 125 | 359 | 19310 | 1, 7j | E40610 V12 S16
SE102329 | C | CB | Square D | MAL36700 | 42 | 700 | 600 | 3 | 42 | 208 | 3 | 150 | 414 | 19310 | 1, 7j | E40610 V12 S16
SE102329 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 42 | 208 | 3 | 150 | 414 | 19310 | 1, 7j | E40610 V12 S16
SE102329 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 42 | 208 | 3 | 150 | 414 | 19310 | 1, 7j | E40610 V12 S16
SE102329 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 42 | 208 | 3 | 150 | 414 | 19310 | 1, 7j | E40610 V12 S16
SE102329 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 42 | 208 | 3 | 150 | 414 | 19310 | 1, 7j | E40610 V12 S16
SE102334 | D | ICB | Square D | MHL3660042M | - | 600 | 600 | 3 | 65 | 208 | 3 | 150 | 414 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102334 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 65 | 208 | 3 | 150 | 414 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102334 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 65 | 208 | 3 | 150 | 414 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102334 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 65 | 208 | 3 | 150 | 414 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102334 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 65 | 208 | 3 | 150 | 414 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102335 | D | ICB | Square D | MHL3660042M | - | 600 | 600 | 3 | 65 | 208 | 3 | 125 | 359 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102335 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 65 | 208 | 3 | 125 | 359 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102335 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 65 | 208 | 3 | 125 | 359 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102335 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 65 | 208 | 3 | 125 | 359 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102335 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 65 | 208 | 3 | 125 | 359 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102336 | C | CB | Square D | KAL36110 | 42 | 110 | 600 | 3 | 42 | 240 | 3 | 30 | 80 | 3662 | 1, 7L | E40610 V12 S16
SE102336 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 42 | 240 | 3 | 30 | 80 | 3662 | 1, 7L | E40610 V12 S16
SE102336 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 42 | 240 | 3 | 30 | 80 | 3662 | 1, 7L | E40610 V12 S16
SE102337 | D | ICB | Square D | KAL3625026M | - | 250 | 600 | 3 | 42 | 240 | 3 | 30 | 80 | 3662 | 1, 5, 7L | E40610 V12 S16
SE102337 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 42 | 240 | 3 | 30 | 80 | 3662 | 1, 5, 7L | E40610 V12 S16
SE102337 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 42 | 240 | 3 | 30 | 80 | 3662 | 1, 5, 7L | E40610 V12 S16
SE102338 | C | CB | Square D | KAL36150 | 42 | 150 | 600 | 3 | 42 | 240 | 3 | 40 | 104 | 5036 | 1, 7n | E40610 V12 S16
SE102338 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 42 | 240 | 3 | 40 | 104 | 5036 | 1, 7n | E40610 V12 S16
SE102338 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 42 | 240 | 3 | 40 | 104 | 5036 | 1, 7n | E40610 V12 S16
SE102339 | C | CB | Square D | KAL36200 | 42 | 200 | 600 | 3 | 42 | 240 | 3 | 50 | 130 | 5036 | 1, 7d | E40610 V12 S16
SE102339 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 42 | 240 | 3 | 50 | 130 | 5036 | 1, 7d | E40610 V12 S16
SE102339 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 42 | 240 | 3 | 50 | 130 | 5036 | 1, 7d | E40610 V12 S16
SE102342 | C | CB | Square D | KAL36225 | 42 | 225 | 600 | 3 | 42 | 240 | 3 | 60 | 154 | 6409 | 1, 7p | E40610 V12 S16
SE102342 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 42 | 240 | 3 | 60 | 154 | 6409 | 1, 7p | E40610 V12 S16
SE102342 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 42 | 240 | 3 | 60 | 154 | 6409 | 1, 7p | E40610 V12 S16
SE102342 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 42 | 240 | 3 | 60 | 154 | 6409 | 1, 7p | E40610 V12 S16
SE102342 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 42 | 240 | 3 | 60 | 154 | 6409 | 1, 7p | E40610 V12 S16
SE102349 | C | CB | Square D | MAL36600 | 42 | 600 | 600 | 3 | 42 | 240 | 3 | 150 | 360 | 19310 | 1, 7j | E40610 V12 S16
SE102349 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 42 | 240 | 3 | 150 | 360 | 19310 | 1, 7j | E40610 V12 S16
SE102349 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 42 | 240 | 3 | 150 | 360 | 19310 | 1, 7j | E40610 V12 S16
SE102349 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 42 | 240 | 3 | 150 | 360 | 19310 | 1, 7j | E40610 V12 S16
SE102349 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 42 | 240 | 3 | 150 | 360 | 19310 | 1, 7j | E40610 V12 S16
SE102350 | C | CB | Square D | MAL36800 | 42 | 800 | 600 | 3 | 42 | 240 | 3 | 200 | 480 | 19310 | 1, 7j | E40610 V12 S16
SE102350 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 42 | 240 | 3 | 200 | 480 | 19310 | 1, 7j | E40610 V12 S16
SE102350 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 42 | 240 | 3 | 200 | 480 | 19310 | 1, 7j | E40610 V12 S16
SE102350 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 42 | 240 | 3 | 200 | 480 | 19310 | 1, 7j | E40610 V12 S16
SE102350 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 42 | 240 | 3 | 200 | 480 | 19310 | 1, 7j | E40610 V12 S16
SE102351 | D | ICB | Square D | MHL3660042M | - | 600 | 600 | 3 | 65 | 240 | 3 | 150 | 360 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102351 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 65 | 240 | 3 | 150 | 360 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102351 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 65 | 240 | 3 | 150 | 360 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102351 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 65 | 240 | 3 | 150 | 360 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102351 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 65 | 240 | 3 | 150 | 360 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102352 | D | ICB | Square D | MHL3680045M | - | 800 | 600 | 3 | 65 | 240 | 3 | 200 | 480 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102352 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 65 | 240 | 3 | 200 | 480 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102352 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 65 | 240 | 3 | 200 | 480 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102352 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 65 | 240 | 3 | 200 | 480 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102352 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 65 | 240 | 3 | 200 | 480 | 19310 | 1, 5, 7j | E40610 V12 S16
SE102353 | C | CB | Square D | KAL36110 | 25 | 110 | 600 | 3 | 25 | 480 | 3 | 60 | 77 | 3662 | 1, 7L | E40610 V12 S16
SE102353 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 25 | 480 | 3 | 60 | 77 | 3662 | 1, 7L | E40610 V12 S16
SE102353 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 25 | 480 | 3 | 60 | 77 | 3662 | 1, 7L | E40610 V12 S16
SE102354 | C | CB | Square D | KAL36125 | 25 | 125 | 600 | 3 | 25 | 480 | 3 | 75 | 96 | 5036 | 1, 7n | E40610 V12 S16
SE102354 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 25 | 480 | 3 | 75 | 96 | 5036 | 1, 7n | E40610 V12 S16
SE102354 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 25 | 480 | 3 | 75 | 96 | 5036 | 1, 7n | E40610 V12 S16
SE102355 | C | CB | Square D | KAL36200 | 25 | 200 | 600 | 3 | 25 | 480 | 3 | 100 | 124 | 5036 | 1, 7d | E40610 V12 S16
#REF! |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 25 | 480 | 3 | 100 | 124 | 5036 | 1, 7d | E40610 V12 S16
SE102355 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 25 | 480 | 3 | 100 | 124 | 5036 | 1, 7d | E40610 V12 S16
SE102356 | C | CB | Square D | KAL36225 | 25 | 225 | 600 | 3 | 25 | 480 | 3 | 125 | 156 | 6409 | 1, 7p | E40610 V12 S16
SE102356 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 25 | 480 | 3 | 125 | 156 | 6409 | 1, 7p | E40610 V12 S16
SE102356 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 25 | 480 | 3 | 125 | 156 | 6409 | 1, 7p | E40610 V12 S16
SE102356 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 25 | 480 | 3 | 125 | 156 | 6409 | 1, 7p | E40610 V12 S16
SE102356 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 25 | 480 | 3 | 125 | 156 | 6409 | 1, 7p | E40610 V12 S16
SE102363 | C | CB | Square D | MAL36600 | 30 | 600 | 600 | 3 | 30 | 480 | 3 | 300 | 361 | 19310 | 1, 7j | E40610 V12 S16
SE102363 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 30 | 480 | 3 | 300 | 361 | 19310 | 1, 7j | E40610 V12 S16
SE102363 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 30 | 480 | 3 | 300 | 361 | 19310 | 1, 7j | E40610 V12 S16
SE102363 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 30 | 480 | 3 | 300 | 361 | 19310 | 1, 7j | E40610 V12 S16
SE102363 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 30 | 480 | 3 | 300 | 361 | 19310 | 1, 7j | E40610 V12 S16
SE102364 | C | CB | Square D | MAL36700 | 30 | 700 | 600 | 3 | 30 | 480 | 3 | 350 | 414 | 19310 | 1, 7j | E40610 V12 S16
SE102364 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 30 | 480 | 3 | 350 | 414 | 19310 | 1, 7j | E40610 V12 S16
SE102364 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 30 | 480 | 3 | 350 | 414 | 19310 | 1, 7j | E40610 V12 S16
SE102364 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 30 | 480 | 3 | 350 | 414 | 19310 | 1, 7j | E40610 V12 S16
SE102364 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 30 | 480 | 3 | 350 | 414 | 19310 | 1, 7j | E40610 V12 S16
SE102365 | C | CB | Square D | MAL36800 | 30 | 800 | 600 | 3 | 30 | 480 | 3 | 400 | 477 | 19310 | 1, 7j | E40610 V12 S16
SE102365 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 30 | 480 | 3 | 400 | 477 | 19310 | 1, 7j | E40610 V12 S16
SE102365 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 30 | 480 | 3 | 400 | 477 | 19310 | 1, 7j | E40610 V12 S16
SE102365 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 30 | 480 | 3 | 400 | 477 | 19310 | 1, 7j | E40610 V12 S16
SE102365 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 30 | 480 | 3 | 400 | 477 | 19310 | 1, 7j | E40610 V12 S16
SE102370 | D | ICB | Square D | MHL3660044M | - | 600 | 600 | 3 | 65 | 480 | 3 | 300 | 361 | 19310 | 1, 7j | E40610 V12 S16
SE102370 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 65 | 480 | 3 | 300 | 361 | 19310 | 1, 7j | E40610 V12 S16
SE102370 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 65 | 480 | 3 | 300 | 361 | 19310 | 1, 7j | E40610 V12 S16
SE102370 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 65 | 480 | 3 | 300 | 361 | 19310 | 1, 7j | E40610 V12 S16
SE102370 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 65 | 480 | 3 | 300 | 361 | 19310 | 1, 7j | E40610 V12 S16
SE102371 | D | ICB | Square D | MHL3660044M | - | 600 | 600 | 3 | 65 | 480 | 3 | 350 | 414 | 19310 | 1, 7j | E40610 V12 S16
SE102371 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 65 | 480 | 3 | 350 | 414 | 19310 | 1, 7j | E40610 V12 S16
SE102371 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 65 | 480 | 3 | 350 | 414 | 19310 | 1, 7j | E40610 V12 S16
SE102371 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 65 | 480 | 3 | 350 | 414 | 19310 | 1, 7j | E40610 V12 S16
SE102371 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 65 | 480 | 3 | 350 | 414 | 19310 | 1, 7j | E40610 V12 S16
SE102372 | D | ICB | Square D | MHL3660045M | - | 600 | 600 | 3 | 65 | 480 | 3 | 400 | 477 | 19310 | 1, 7j | E40610 V12 S16
SE102372 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 65 | 480 | 3 | 400 | 477 | 19310 | 1, 7j | E40610 V12 S16
SE102372 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 65 | 480 | 3 | 400 | 477 | 19310 | 1, 7j | E40610 V12 S16
SE102372 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 65 | 480 | 3 | 400 | 477 | 19310 | 1, 7j | E40610 V12 S16
SE102372 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 65 | 480 | 3 | 400 | 477 | 19310 | 1, 7j | E40610 V12 S16
SE102373 | C | CB | Square D | KAL36110 | 22 | 110 | 600 | 3 | 22 | 600 | 3 | 75 | 77 | 3662 | 1, 7L | E40610 V12 S16
SE102373 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 22 | 600 | 3 | 75 | 77 | 3662 | 1, 7L | E40610 V12 S16
SE102373 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 22 | 600 | 3 | 75 | 77 | 3662 | 1, 7L | E40610 V12 S16
SE102374 | C | CB | Square D | KAL36150 | 22 | 150 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 5036 | 1, 7n | E40610 V12 S16
SE102374 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 5036 | 1, 7n | E40610 V12 S16
SE102374 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 5036 | 1, 7n | E40610 V12 S16
SE102375 | C | CB | Square D | KAL36200 | 22 | 200 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 5036 | 1, 7d | E40610 V12 S16
SE102375 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 5036 | 1, 7d | E40610 V12 S16
SE102375 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 5036 | 1, 7d | E40610 V12 S16
SE102375 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 22 | 600 | 3 | 125 | 125 | 5036 | 1, 7d | E40610 V12 S16
SE102375 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 5036 | 1, 7d | E40610 V12 S16
SE102392 | C | CB | Square D | MAL36500 | 22 | 500 | 600 | 3 | 22 | 600 | 3 | 350 | 336 | 19310 | 1, 7j | E40610 V12 S16
SE102392 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 22 | 600 | 3 | 350 | 336 | 19310 | 1, 7j | E40610 V12 S16
SE102392 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 22 | 600 | 3 | 350 | 336 | 19310 | 1, 7j | E40610 V12 S16
SE102392 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 22 | 600 | 3 | 350 | 336 | 19310 | 1, 7j | E40610 V12 S16
SE102392 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 22 | 600 | 3 | 350 | 336 | 19310 | 1, 7j | E40610 V12 S16
SE102393 | C | CB | Square D | MAL36600 | 22 | 600 | 600 | 3 | 22 | 600 | 3 | 400 | 382 | 19310 | 1, 7j | E40610 V12 S16
SE102393 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 22 | 600 | 3 | 400 | 382 | 19310 | 1, 7j | E40610 V12 S16
SE102393 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 22 | 600 | 3 | 400 | 382 | 19310 | 1, 7j | E40610 V12 S16
SE102393 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 22 | 600 | 3 | 400 | 382 | 19310 | 1, 7j | E40610 V12 S16
SE102393 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 22 | 600 | 3 | 400 | 382 | 19310 | 1, 7j | E40610 V12 S16
SE102394 | C | CB | Square D | MAL36700 | 22 | 700 | 600 | 3 | 22 | 600 | 3 | 450 | 412 | 19310 | 1, 7j | E40610 V12 S16
SE102394 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 22 | 600 | 3 | 450 | 412 | 19310 | 1, 7j | E40610 V12 S16
SE102394 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 22 | 600 | 3 | 450 | 412 | 19310 | 1, 7j | E40610 V12 S16
SE102394 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 22 | 600 | 3 | 450 | 412 | 19310 | 1, 7j | E40610 V12 S16
SE102394 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 22 | 600 | 3 | 450 | 412 | 19310 | 1, 7j | E40610 V12 S16
SE102395 | C | CB | Square D | MAL36800 | 22 | 800 | 600 | 3 | 22 | 600 | 3 | 500 | 472 | 19310 | 1, 7j | E40610 V12 S16
SE102395 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 22 | 600 | 3 | 500 | 472 | 19310 | 1, 7j | E40610 V12 S16
SE102395 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 22 | 600 | 3 | 500 | 472 | 19310 | 1, 7j | E40610 V12 S16
SE102395 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 22 | 600 | 3 | 500 | 472 | 19310 | 1, 7j | E40610 V12 S16
SE102395 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 22 | 600 | 3 | 500 | 472 | 19310 | 1, 7j | E40610 V12 S16
SE102399 | D | ICB | Square D | MHL3660042M | - | 600 | 600 | 3 | 22 | 600 | 3 | 350 | 336 | 19310 | 1, 7j | E40610 V12 S16
SE102399 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 22 | 600 | 3 | 350 | 336 | 19310 | 1, 7j | E40610 V12 S16
SE102399 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 22 | 600 | 3 | 350 | 336 | 19310 | 1, 7j | E40610 V12 S16
SE102399 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 22 | 600 | 3 | 350 | 336 | 19310 | 1, 7j | E40610 V12 S16
SE102399 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 22 | 600 | 3 | 350 | 336 | 19310 | 1, 7j | E40610 V12 S16
SE102400 | D | ICB | Square D | MHL3660044M | - | 600 | 600 | 3 | 22 | 600 | 3 | 400 | 382 | 19310 | 1, 7j | E40610 V12 S16
SE102400 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 22 | 600 | 3 | 400 | 382 | 19310 | 1, 7j | E40610 V12 S16
SE102400 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 22 | 600 | 3 | 400 | 382 | 19310 | 1, 7j | E40610 V12 S16
SE102400 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 22 | 600 | 3 | 400 | 382 | 19310 | 1, 7j | E40610 V12 S16
SE102400 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 22 | 600 | 3 | 400 | 382 | 19310 | 1, 7j | E40610 V12 S16
SE102401 | D | ICB | Square D | MHL3660044M | - | 600 | 600 | 3 | 22 | 600 | 3 | 450 | 412 | 19310 | 1, 7j | E40610 V12 S16
SE102401 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 22 | 600 | 3 | 450 | 412 | 19310 | 1, 7j | E40610 V12 S16
SE102401 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 22 | 600 | 3 | 450 | 412 | 19310 | 1, 7j | E40610 V12 S16
SE102401 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 22 | 600 | 3 | 450 | 412 | 19310 | 1, 7j | E40610 V12 S16
SE102401 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 22 | 600 | 3 | 450 | 412 | 19310 | 1, 7j | E40610 V12 S16
SE102402 | D | ICB | Square D | MHL3660044M | - | 600 | 600 | 3 | 22 | 600 | 3 | 500 | 472 | 19310 | 1, 7j | E40610 V12 S16
SE102402 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 22 | 600 | 3 | 500 | 472 | 19310 | 1, 7j | E40610 V12 S16
SE102402 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 22 | 600 | 3 | 500 | 472 | 19310 | 1, 7j | E40610 V12 S16
SE102402 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 22 | 600 | 3 | 500 | 472 | 19310 | 1, 7j | E40610 V12 S16
SE102402 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 22 | 600 | 3 | 500 | 472 | 19310 | 1, 7j | E40610 V12 S16
Conditions of Acceptability For Combination Motor Controllers:
Unless specified otherwise in the individual Recognitions, consideration is to be given to the following Conditions of Acceptability when these
components are employed as a combination motor controller in the end-use equipment: Specific Conditions of Use - Number refers to specific
condition number as defined below and number in parenthesis identifies specific information applicable to the combination motor controller.
C.O. A #:
|  | 1 | All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet
or cubic inches. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
|  | 2 | When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other
components shall not be installed in this area.
|  | 3 | When specified, the overload relay heater table shall be provided with the equipment.
|  | 4 | Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current &
connected to the terminals supplied with the individual components.
|  | 5 | The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination
Motor Controllers).
|  | 6 | Use wire ties evenly spaced apart to secure conductors in place.
|  | 7 | See Table 7 for minimum internal wiring between load side of short circuit protective device & line side of starter.
|  | 8 | "@" refer to Square D Digest to complete contactor Catalog number for coil voltage and Form modifications.
|  | 9 | Insulator to be provided underneath starter. (QMFZ2), Fastex, Type Formex GK-30, 1/32 inch minimum thickness by 4 inches x 5.7 inches.
Table 7 - Minimum Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
|  | Wire Code |  | Wire Size
|  | 7a |  | 12 AWG
|  | 7b |  | 8 AWG
|  | 7c |  | 2 AWG
|  | 7d |  | 1 AWG
|  | 7e |  | 250 MCM
|  | 7f |  | 300 MCM
|  | 7g |  | (2) 250 MCM
|  | 7h |  | 2/0 AWG
|  | 7i |  | 4/0 AWG
|  | 7j |  | (2) 4/0 AWG
|  | 7k |  | 10 AWG
|  | 7l |  | 6 AWG
|  | 7m |  | 4 AWG
|  | 7n |  | 3 AWG
|  | 7p |  | 1/0 AWG
|  | 7q |  | (2) 3/0 AWG
|  | 7r |  | (2) 2/0 AWG
|  | 7s |  | 3/0 AWG