## C.O.A.s
Conditions of Acceptability For Combination Motor Controllers:
Unless specified otherwise in the individual Recognitions, consideration is to be given to the following Conditions of Acceptability when these
components are employed as a combination motor controller in the end-use equipment: Specific Conditions of Use - Number refers to specific
condition number as defined below and number in parenthesis identifies specific information applicable to the combination motor controller.
C.O. A #:
1 | All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet
or cubic inches. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
2 | When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other
components shall not be installed in this area.
3 | When specified, the overload relay heater table shall be provided with the equipment.
4 | Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current &
connected to the terminals supplied with the individual components.
5 | The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination
Motor Controllers).
6 | Use wire ties evenly spaced apart to secure conductors in place.
7 | See Table 7 for minimum internal wiring between load side of short circuit protective device & line side of starter.
8 | "@" refer to Square D Digest to complete contactor Catalog number for coil voltage and Form modifications.
9 | Reserved for future use.
Table 7 - Minimum Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
Wire Code |  | Wire Size
7a |  | 12 AWG
7b |  | 8 AWG
7c |  | 2 AWG
7d |  | 1 AWG
7e |  | 250 MCM
7f |  | 300 MCM
7g |  | (2) 250 MCM
7h |  | 2/0 AWG
7i |  | 4/0 AWG
7j |  | (2) 4/0 AWG
7k |  | 10 AWG
7l |  | 6 AWG
7m |  | 4 AWG
7n |  | 3 AWG
7p |  | 1/0 AWG
7q |  | (2) 3/0 AWG
7r |  | (2) 2/0 AWG
7s |  | 3/0 AWG

## (D09-D40)&GS1
Issued: 2006-09-26
Last Revised: 2006-09-26
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in.) | Conditions of Acceptability | Combination UL File
SE502000 | A | FDS | Square D | GS1DDU3 | 50 | 30 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502000 |  | F | Any | Class CC | 200 | 30 | 600 | - | 100 | 200 | 3 | 2 | 7.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502000 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502000 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502000 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502000 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502000 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502000 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502000 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502000 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502000 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502000 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502000 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502000 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502000 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502000 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502000 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502000 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502001 | A | FDS | Square D | GS1DDU3 | 50 | 30 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502001 |  | F | Any | Class CC | 200 | 30 | 600 | - | 100 | 208 | 3 | 2 | 7.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502001 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502001 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502001 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502001 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502001 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502001 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502001 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502001 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502001 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502001 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502001 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502001 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502001 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502001 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502001 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502001 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502002 | A | FDS | Square D | GS1DDU3 | 50 | 30 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502002 |  | F | Any | Class CC | 200 | 25 | 600 | - | 100 | 240 | 3 | 2 | 6.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502002 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502002 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502002 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502002 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502002 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502002 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502002 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502002 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502002 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502002 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502002 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502002 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502002 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502002 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 818.12 | 1, 7k | E163364 V2 S1
SE502003 | A | FDS | Square D | GS1DDU3 | 50 | 30 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502003 |  | F | Any | Class CC | 200 | 30 | 600 | - | 100 | 480 | 3 | 5 | 7.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502003 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502003 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502003 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502003 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502003 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502003 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502003 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502003 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502003 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502003 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502003 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502003 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502003 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502003 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502003 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502003 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502004 | A | FDS | Square D | GS1DDU3 | 50 | 30 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 818.12 | 1, 7k | E163364 V2 S1
SE502004 |  | F | Any | Class CC | 200 | 30 | 600 | - | 100 | 600 | 3 | 7.5 | 9 | 818.12 | 1, 7k | E163364 V2 S1
SE502004 |  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 818.12 | 1, 7k | E163364 V2 S1
SE502004 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 818.12 | 1, 7k | E163364 V2 S1
SE502004 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 818.12 | 1, 7k | E163364 V2 S1
SE502004 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 818.12 | 1, 7k | E163364 V2 S1
SE502004 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 818.12 | 1, 7k | E163364 V2 S1
SE502004 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 818.12 | 1, 7k | E163364 V2 S1
SE502004 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 818.12 | 1, 7k | E163364 V2 S1
SE502004 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 818.12 | 1, 7k | E163364 V2 S1
SE502004 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 818.12 | 1, 7k | E163364 V2 S1
SE502004 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 818.12 | 1, 7k | E163364 V2 S1
SE502004 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 818.12 | 1, 7k | E163364 V2 S1
SE502004 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 818.12 | 1, 7k | E163364 V2 S1
SE502004 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 818.12 | 1, 7k | E163364 V2 S1
SE502004 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 818.12 | 1, 7k | E163364 V2 S1
SE502004 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 818.12 | 1, 7k | E163364 V2 S1
SE502004 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 818.12 | 1, 7k | E163364 V2 S1
SE502005 | A | FDS | Square D | GS1DDU3 | 50 | 30 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502005 |  | F | Any | Class CC | 200 | 30 | 600 | - | 100 | 200 | 3 | 2 | 7.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502005 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502005 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502005 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502005 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502005 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502005 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502005 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502005 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502005 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502005 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502005 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502005 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502005 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502005 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502005 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502005 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502006 | A | FDS | Square D | GS1DDU3 | 50 | 30 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1321.4 | 1, 7k | E163364 V2 S1
SE502006 |  | F | Any | Class CC | 200 | 30 | 600 | - | 100 | 208 | 3 | 2 | 7.5 | 1321.4 | 1, 7k | E163364 V2 S1
SE502006 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1321.4 | 1, 7k | E163364 V2 S1
SE502006 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1321.4 | 1, 7k | E163364 V2 S1
SE502006 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1321.4 | 1, 7k | E163364 V2 S1
SE502006 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1321.4 | 1, 7k | E163364 V2 S1
SE502006 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1321.4 | 1, 7k | E163364 V2 S1
SE502006 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1321.4 | 1, 7k | E163364 V2 S1
SE502006 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1321.4 | 1, 7k | E163364 V2 S1
SE502006 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1321.4 | 1, 7k | E163364 V2 S1
SE502006 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1321.4 | 1, 7k | E163364 V2 S1
SE502006 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1321.4 | 1, 7k | E163364 V2 S1
SE502006 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1321.4 | 1, 7k | E163364 V2 S1
SE502006 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1321.4 | 1, 7k | E163364 V2 S1
SE502006 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1321.4 | 1, 7k | E163364 V2 S1
SE502006 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1321.4 | 1, 7k | E163364 V2 S1
SE502006 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1321.4 | 1, 7k | E163364 V2 S1
SE502006 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1321.4 | 1, 7k | E163364 V2 S1
SE502007 | A | FDS | Square D | GS1DDU3 | 50 | 30 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502007 |  | F | Any | Class CC | 200 | 25 | 600 | - | 100 | 240 | 3 | 2 | 6.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502007 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502007 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502007 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502007 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502007 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502007 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502007 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502007 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502007 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502007 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502007 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502007 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502007 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502007 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1321.4 | 1, 7k | E163364 V2 S1
SE502008 | A | FDS | Square D | GS1DDU3 | 50 | 30 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502008 |  | F | Any | Class CC | 200 | 30 | 600 | - | 100 | 480 | 3 | 5 | 7.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502008 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502008 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502008 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502008 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502008 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502008 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502008 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502008 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502008 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502008 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502008 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502008 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502008 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502008 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502008 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502008 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502009 | A | FDS | Square D | GS1DDU3 | 50 | 30 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 1321.4 | 1, 7k | E163364 V2 S1
SE502009 |  | F | Any | Class CC | 200 | 30 | 600 | - | 100 | 600 | 3 | 7.5 | 9 | 1321.4 | 1, 7k | E163364 V2 S1
SE502009 |  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 1321.4 | 1, 7k | E163364 V2 S1
SE502009 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 1321.4 | 1, 7k | E163364 V2 S1
SE502009 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 1321.4 | 1, 7k | E163364 V2 S1
SE502009 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 1321.4 | 1, 7k | E163364 V2 S1
SE502009 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 1321.4 | 1, 7k | E163364 V2 S1
SE502009 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 1321.4 | 1, 7k | E163364 V2 S1
SE502009 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 1321.4 | 1, 7k | E163364 V2 S1
SE502009 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 1321.4 | 1, 7k | E163364 V2 S1
SE502009 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 1321.4 | 1, 7k | E163364 V2 S1
SE502009 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 1321.4 | 1, 7k | E163364 V2 S1
SE502009 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 1321.4 | 1, 7k | E163364 V2 S1
SE502009 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 1321.4 | 1, 7k | E163364 V2 S1
SE502009 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 1321.4 | 1, 7k | E163364 V2 S1
SE502009 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 1321.4 | 1, 7k | E163364 V2 S1
SE502009 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 1321.4 | 1, 7k | E163364 V2 S1
SE502009 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 600 | 3 | 7.5 | 9 | 1321.4 | 1, 7k | E163364 V2 S1
SE502010 | A | FDS | Square D | GS1DDU3 | 50 | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502010 |  | F | Any | Class CC | 200 | 30 | 600 | - | 100 | 200 | 3 | 3 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502010 |  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502010 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502010 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502010 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502010 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502010 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502010 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502010 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502010 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502010 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502010 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502010 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502010 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502010 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502010 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502010 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502010 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502010 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502011 | A | FDS | Square D | GS1DDU3 | 50 | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502011 |  | F | Any | Class CC | 200 | 30 | 600 | - | 100 | 208 | 3 | 3 | 10.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502011 |  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502011 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502011 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502011 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502011 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502011 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502011 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502011 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502011 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502011 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502011 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502011 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502011 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502011 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502011 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502011 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502011 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502011 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502012 | A | FDS | Square D | GS1DDU3 | 50 | 30 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502012 |  | F | Any | Class CC | 200 | 30 | 600 | - | 100 | 240 | 3 | 3 | 9.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502012 |  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502012 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502012 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502012 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502012 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502012 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502012 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502012 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502012 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502012 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502012 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502012 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502012 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502012 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502012 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502012 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502012 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502012 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 818.12 | 1, 7k | E163364 V2 S1
SE502013 | A | FDS | Square D | GS1DDU3 | 50 | 30 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502013 |  | F | Any | Class CC | 200 | 30 | 600 | - | 100 | 480 | 3 | 7.5 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502013 |  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502013 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502013 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502013 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502013 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502013 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502013 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502013 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502013 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502013 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502013 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502013 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502013 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502013 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502013 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502013 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502013 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502013 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502014 | A | FDS | Square D | GS1DDU3 | 50 | 30 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502014 |  | F | Any | Class CC | 200 | 30 | 600 | - | 100 | 600 | 3 | 10 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502014 |  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502014 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502014 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502014 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502014 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502014 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502014 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502014 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502014 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502014 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502014 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502014 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502014 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502014 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502014 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502014 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502014 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502014 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 818.12 | 1, 7k | E163364 V2 S1
SE502015 | A | FDS | Square D | GS1DDU3 | 50 | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502015 |  | F | Any | Class CC | 200 | 30 | 600 | - | 100 | 200 | 3 | 3 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502015 |  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502015 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502015 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502015 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502015 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502015 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502015 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502015 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502015 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502015 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502015 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502015 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502015 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502015 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502015 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502015 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502015 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502015 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502016 | A | FDS | Square D | GS1DDU3 | 50 | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502016 |  | F | Any | Class CC | 200 | 30 | 600 | - | 100 | 208 | 3 | 3 | 10.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502016 |  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502016 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502016 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502016 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502016 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502016 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502016 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502016 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502016 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502016 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502016 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502016 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502016 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502016 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502016 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502016 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502016 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502016 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502017 | A | FDS | Square D | GS1DDU3 | 50 | 30 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502017 |  | F | Any | Class CC | 200 | 30 | 600 | - | 100 | 240 | 3 | 3 | 9.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502017 |  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502017 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502017 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502017 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502017 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502017 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502017 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502017 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502017 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502017 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502017 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502017 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502017 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502017 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502017 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502017 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502017 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502017 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1321.4 | 1, 7k | E163364 V2 S1
SE502018 | A | FDS | Square D | GS1DDU3 | 50 | 30 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502018 |  | F | Any | Class CC | 200 | 30 | 600 | - | 100 | 480 | 3 | 7.5 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502018 |  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502018 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502018 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502018 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502018 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502018 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502018 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502018 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502018 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502018 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502018 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502018 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502018 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502018 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502018 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502018 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502018 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502018 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502019 | A | FDS | Square D | GS1DDU3 | 50 | 30 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502019 |  | F | Any | Class CC | 200 | 30 | 600 | - | 100 | 600 | 3 | 10 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502019 |  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502019 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502019 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502019 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502019 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502019 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502019 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502019 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502019 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502019 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502019 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502019 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502019 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502019 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502019 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502019 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502019 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502019 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 600 | 3 | 10 | 11 | 1321.4 | 1, 7k | E163364 V2 S1
SE502020 | A | FDS | Square D | GS1DU3 | 50 | 30 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502020 |  | F | Any | Class J | 200 | 30 | 600 | - | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502020 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502020 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502020 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502020 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502020 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502020 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502020 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502020 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502020 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502020 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502020 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502020 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502020 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502020 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502020 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502020 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502020 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502020 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502020 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502020 |  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE502021 | A | FDS | Square D | GS1DU3 | 50 | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE502021 |  | F | Any | Class J | 200 | 30 | 600 | - | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE502021 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE502021 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE502021 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE502021 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE502021 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE502021 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE502021 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE502021 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE502021 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE502021 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE502021 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE502021 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE502021 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE502021 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE502021 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE502021 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE502021 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE502021 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE502021 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE502021 |  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE502022 | A | FDS | Square D | GS1DU3 | 50 | 30 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 818.12 | 1, 7k | E163364 V2 S1
SE502022 |  | F | Any | Class J | 200 | 30 | 600 | - | 100 | 240 | 3 | 5 | 15.2 | 818.12 | 1, 7k | E163364 V2 S1
SE502022 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 818.12 | 1, 7k | E163364 V2 S1
SE502022 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 818.12 | 1, 7k | E163364 V2 S1
SE502022 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 818.12 | 1, 7k | E163364 V2 S1
SE502022 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 818.12 | 1, 7k | E163364 V2 S1
SE502022 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 818.12 | 1, 7k | E163364 V2 S1
SE502022 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 818.12 | 1, 7k | E163364 V2 S1
SE502022 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 818.12 | 1, 7k | E163364 V2 S1
SE502022 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 818.12 | 1, 7k | E163364 V2 S1
SE502022 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 818.12 | 1, 7k | E163364 V2 S1
SE502022 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 818.12 | 1, 7k | E163364 V2 S1
SE502022 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 818.12 | 1, 7k | E163364 V2 S1
SE502022 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 818.12 | 1, 7k | E163364 V2 S1
SE502022 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 818.12 | 1, 7k | E163364 V2 S1
SE502022 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 818.12 | 1, 7k | E163364 V2 S1
SE502022 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 818.12 | 1, 7k | E163364 V2 S1
SE502022 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 818.12 | 1, 7k | E163364 V2 S1
SE502022 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 818.12 | 1, 7k | E163364 V2 S1
SE502022 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 818.12 | 1, 7k | E163364 V2 S1
SE502022 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 818.12 | 1, 7k | E163364 V2 S1
SE502022 |  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 818.12 | 1, 7k | E163364 V2 S1
SE502023 | A | FDS | Square D | GS1DU3 | 50 | 30 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE502023 |  | F | Any | Class J | 200 | 30 | 600 | - | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE502023 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE502023 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE502023 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE502023 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE502023 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE502023 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE502023 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE502023 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE502023 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE502023 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE502023 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE502023 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE502023 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE502023 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE502023 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE502023 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE502023 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE502023 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE502023 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE502023 |  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE502024 | A | FDS | Square D | GS1DU3 | 50 | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE502024 |  | F | Any | Class J | 200 | 30 | 600 | - | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE502024 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE502024 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE502024 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE502024 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE502024 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE502024 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE502024 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE502024 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE502024 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE502024 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE502024 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE502024 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE502024 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE502024 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE502024 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE502024 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE502024 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE502024 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE502024 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE502024 |  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE502025 | A | FDS | Square D | GS1DU3 | 50 | 30 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1321 | 1, 7k | E163364 V2 S1
SE502025 |  | F | Any | Class J | 200 | 30 | 600 | - | 100 | 240 | 3 | 5 | 15.2 | 1321 | 1, 7k | E163364 V2 S1
SE502025 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1321 | 1, 7k | E163364 V2 S1
SE502025 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1321 | 1, 7k | E163364 V2 S1
SE502025 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1321 | 1, 7k | E163364 V2 S1
SE502025 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1321 | 1, 7k | E163364 V2 S1
SE502025 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1321 | 1, 7k | E163364 V2 S1
SE502025 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1321 | 1, 7k | E163364 V2 S1
SE502025 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1321 | 1, 7k | E163364 V2 S1
SE502025 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1321 | 1, 7k | E163364 V2 S1
SE502025 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1321 | 1, 7k | E163364 V2 S1
SE502025 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1321 | 1, 7k | E163364 V2 S1
SE502025 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1321 | 1, 7k | E163364 V2 S1
SE502025 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1321 | 1, 7k | E163364 V2 S1
SE502025 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1321 | 1, 7k | E163364 V2 S1
SE502025 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1321 | 1, 7k | E163364 V2 S1
SE502025 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1321 | 1, 7k | E163364 V2 S1
SE502025 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1321 | 1, 7k | E163364 V2 S1
SE502025 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1321 | 1, 7k | E163364 V2 S1
SE502025 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1321 | 1, 7k | E163364 V2 S1
SE502025 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1321 | 1, 7k | E163364 V2 S1
SE502025 |  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1321 | 1, 7k | E163364 V2 S1
SE502026 | A | FDS | Square D | GS1DU3 | 50 | 30 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 818.12 | 1, 7k | E163364 V2 S1
SE502026 |  | F | Any | Class J | 200 | 30 | 600 | - | 100 | 480 | 3 | 10 | 14 | 818.12 | 1, 7k | E163364 V2 S1
SE502026 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 818.12 | 1, 7k | E163364 V2 S1
SE502026 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 818.12 | 1, 7k | E163364 V2 S1
SE502026 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 818.12 | 1, 7k | E163364 V2 S1
SE502026 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 818.12 | 1, 7k | E163364 V2 S1
SE502026 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 818.12 | 1, 7k | E163364 V2 S1
SE502026 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 818.12 | 1, 7k | E163364 V2 S1
SE502026 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 818.12 | 1, 7k | E163364 V2 S1
SE502026 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 818.12 | 1, 7k | E163364 V2 S1
SE502026 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 818.12 | 1, 7k | E163364 V2 S1
SE502026 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 818.12 | 1, 7k | E163364 V2 S1
SE502026 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 818.12 | 1, 7k | E163364 V2 S1
SE502026 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 818.12 | 1, 7k | E163364 V2 S1
SE502026 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 818.12 | 1, 7k | E163364 V2 S1
SE502026 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 818.12 | 1, 7k | E163364 V2 S1
SE502026 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 818.12 | 1, 7k | E163364 V2 S1
SE502026 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 818.12 | 1, 7k | E163364 V2 S1
SE502026 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 818.12 | 1, 7k | E163364 V2 S1
SE502026 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 818.12 | 1, 7k | E163364 V2 S1
SE502026 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 818.12 | 1, 7k | E163364 V2 S1
SE502026 |  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 818.12 | 1, 7k | E163364 V2 S1
SE502027 | A | FDS | Square D | GS1DU3 | 50 | 30 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1321 | 1, 7k | E163364 V2 S1
SE502027 |  | F | Any | Class J | 200 | 30 | 600 | - | 100 | 480 | 3 | 10 | 14 | 1321 | 1, 7k | E163364 V2 S1
SE502027 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1321 | 1, 7k | E163364 V2 S1
SE502027 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1321 | 1, 7k | E163364 V2 S1
SE502027 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1321 | 1, 7k | E163364 V2 S1
SE502027 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1321 | 1, 7k | E163364 V2 S1
SE502027 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1321 | 1, 7k | E163364 V2 S1
SE502027 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1321 | 1, 7k | E163364 V2 S1
SE502027 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1321 | 1, 7k | E163364 V2 S1
SE502027 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1321 | 1, 7k | E163364 V2 S1
SE502027 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1321 | 1, 7k | E163364 V2 S1
SE502027 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1321 | 1, 7k | E163364 V2 S1
SE502027 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1321 | 1, 7k | E163364 V2 S1
SE502027 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1321 | 1, 7k | E163364 V2 S1
SE502027 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1321 | 1, 7k | E163364 V2 S1
SE502027 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1321 | 1, 7k | E163364 V2 S1
SE502027 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1321 | 1, 7k | E163364 V2 S1
SE502027 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1321 | 1, 7k | E163364 V2 S1
SE502027 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1321 | 1, 7k | E163364 V2 S1
SE502027 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1321 | 1, 7k | E163364 V2 S1
SE502027 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1321 | 1, 7k | E163364 V2 S1
SE502027 |  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1321 | 1, 7k | E163364 V2 S1
SE502028 | A | FDS | Square D | GS1DU3 | 50 | 30 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 818.12 | 1, 7k | E163364 V2 S1
SE502028 |  | F | Any | Class J | 200 | 30 | 600 | - | 100 | 600 | 3 | 15 | 17 | 818.12 | 1, 7k | E163364 V2 S1
SE502028 |  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 818.12 | 1, 7k | E163364 V2 S1
SE502028 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 818.12 | 1, 7k | E163364 V2 S1
SE502028 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 818.12 | 1, 7k | E163364 V2 S1
SE502028 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 818.12 | 1, 7k | E163364 V2 S1
SE502028 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 818.12 | 1, 7k | E163364 V2 S1
SE502028 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 818.12 | 1, 7k | E163364 V2 S1
SE502028 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 818.12 | 1, 7k | E163364 V2 S1
SE502028 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 818.12 | 1, 7k | E163364 V2 S1
SE502028 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 818.12 | 1, 7k | E163364 V2 S1
SE502028 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 818.12 | 1, 7k | E163364 V2 S1
SE502028 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 818.12 | 1, 7k | E163364 V2 S1
SE502028 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 818.12 | 1, 7k | E163364 V2 S1
SE502028 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 818.12 | 1, 7k | E163364 V2 S1
SE502028 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 818.12 | 1, 7k | E163364 V2 S1
SE502028 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 818.12 | 1, 7k | E163364 V2 S1
SE502028 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 818.12 | 1, 7k | E163364 V2 S1
SE502028 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 818.12 | 1, 7k | E163364 V2 S1
SE502028 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 818.12 | 1, 7k | E163364 V2 S1
SE502028 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 818.12 | 1, 7k | E163364 V2 S1
SE502028 |  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 818.12 | 1, 7k | E163364 V2 S1
SE502029 | A | FDS | Square D | GS1DU3 | 50 | 30 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 1321 | 1, 7k | E163364 V2 S1
SE502029 |  | F | Any | Class J | 200 | 30 | 600 | - | 100 | 600 | 3 | 15 | 17 | 1321 | 1, 7k | E163364 V2 S1
SE502029 |  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 1321 | 1, 7k | E163364 V2 S1
SE502029 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 1321 | 1, 7k | E163364 V2 S1
SE502029 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 1321 | 1, 7k | E163364 V2 S1
SE502029 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 1321 | 1, 7k | E163364 V2 S1
SE502029 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 1321 | 1, 7k | E163364 V2 S1
SE502029 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 1321 | 1, 7k | E163364 V2 S1
SE502029 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 1321 | 1, 7k | E163364 V2 S1
SE502029 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 1321 | 1, 7k | E163364 V2 S1
SE502029 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 1321 | 1, 7k | E163364 V2 S1
SE502029 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 1321 | 1, 7k | E163364 V2 S1
SE502029 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 1321 | 1, 7k | E163364 V2 S1
SE502029 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 1321 | 1, 7k | E163364 V2 S1
SE502029 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 1321 | 1, 7k | E163364 V2 S1
SE502029 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 1321 | 1, 7k | E163364 V2 S1
SE502029 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 1321 | 1, 7k | E163364 V2 S1
SE502029 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 1321 | 1, 7k | E163364 V2 S1
SE502029 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 1321 | 1, 7k | E163364 V2 S1
SE502029 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 1321 | 1, 7k | E163364 V2 S1
SE502029 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 1321 | 1, 7k | E163364 V2 S1
SE502029 |  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 1321 | 1, 7k | E163364 V2 S1
SE500230 | A | FDS | Square D | GS1DU3 | 50 | 30 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE500230 |  | F | Any | Class J | 200 | 30 | 600 | - | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE500230 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE500230 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE500230 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE500230 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE500230 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE500230 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE500230 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE500230 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE500230 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE500230 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE500230 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE500230 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE500230 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE500230 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE500230 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE500230 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE500230 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE500230 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE500230 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE500230 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE500230 |  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE500230 |  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 818.12 | 1, 7k | E163364 V2 S1
SE500231 | A | FDS | Square D | GS1DU3 | 50 | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE500231 |  | F | Any | Class J | 200 | 30 | 600 | - | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE500231 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE500231 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE500231 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE500231 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE500231 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE500231 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE500231 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE500231 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE500231 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE500231 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE500231 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE500231 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE500231 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE500231 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE500231 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE500231 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE500231 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE500231 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE500231 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE500231 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE500231 |  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 818.12 | 1, 7k | E163364 V2 S1
SE500232 | A | FDS | Square D | GS1DU3 | 50 | 30 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500232 |  | F | Any | Class J | 200 | 30 | 600 | - | 100 | 240 | 3 | 7.5 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500232 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500232 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500232 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500232 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500232 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500232 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500232 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500232 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500232 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500232 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500232 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500232 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500232 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500232 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500232 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500232 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500232 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500232 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500232 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500232 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500232 |  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500232 |  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500233 | A | FDS | Square D | GS1DU3 | 50 | 30 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 818.12 | 1, 7k | E163364 V2 S1
SE500233 |  | F | Any | Class J | 200 | 30 | 600 | - | 100 | 480 | 3 | 15 | 21 | 818.12 | 1, 7k | E163364 V2 S1
SE500233 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 818.12 | 1, 7k | E163364 V2 S1
SE500233 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 818.12 | 1, 7k | E163364 V2 S1
SE500233 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 818.12 | 1, 7k | E163364 V2 S1
SE500233 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 818.12 | 1, 7k | E163364 V2 S1
SE500233 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 818.12 | 1, 7k | E163364 V2 S1
SE500233 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 818.12 | 1, 7k | E163364 V2 S1
SE500233 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 818.12 | 1, 7k | E163364 V2 S1
SE500233 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 818.12 | 1, 7k | E163364 V2 S1
SE500233 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 818.12 | 1, 7k | E163364 V2 S1
SE500233 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 818.12 | 1, 7k | E163364 V2 S1
SE500233 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 818.12 | 1, 7k | E163364 V2 S1
SE500233 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 818.12 | 1, 7k | E163364 V2 S1
SE500233 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 818.12 | 1, 7k | E163364 V2 S1
SE500233 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 818.12 | 1, 7k | E163364 V2 S1
SE500233 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 818.12 | 1, 7k | E163364 V2 S1
SE500233 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 818.12 | 1, 7k | E163364 V2 S1
SE500233 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 818.12 | 1, 7k | E163364 V2 S1
SE500233 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 818.12 | 1, 7k | E163364 V2 S1
SE500233 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 818.12 | 1, 7k | E163364 V2 S1
SE500233 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 818.12 | 1, 7k | E163364 V2 S1
SE500233 |  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 818.12 | 1, 7k | E163364 V2 S1
SE500233 |  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 818.12 | 1, 7k | E163364 V2 S1
SE500234 | A | FDS | Square D | GS1DU3 | 50 | 30 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500234 |  | F | Any | Class J | 200 | 30 | 600 | - | 100 | 600 | 3 | 20 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500234 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500234 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500234 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500234 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500234 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500234 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500234 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500234 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500234 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500234 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500234 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500234 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500234 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500234 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500234 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500234 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500234 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500234 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500234 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500234 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500234 |  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500234 |  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 818.12 | 1, 7k | E163364 V2 S1
SE500235 | A | FDS | Square D | GS1DU3 | 50 | 30 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE500235 |  | F | Any | Class J | 200 | 30 | 600 | - | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE500235 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE500235 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE500235 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE500235 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE500235 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE500235 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE500235 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE500235 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE500235 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE500235 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE500235 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE500235 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE500235 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE500235 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE500235 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE500235 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE500235 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE500235 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE500235 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE500235 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE500235 |  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE500235 |  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1321 | 1, 7k | E163364 V2 S1
SE500236 | A | FDS | Square D | GS1DU3 | 50 | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE500236 |  | F | Any | Class J | 200 | 30 | 600 | - | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE500236 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE500236 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE500236 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE500236 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE500236 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE500236 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE500236 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE500236 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE500236 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE500236 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE500236 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE500236 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE500236 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE500236 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE500236 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE500236 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE500236 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE500236 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE500236 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE500236 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE500236 |  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1321 | 1, 7k | E163364 V2 S1
SE500237 | A | FDS | Square D | GS1DU3 | 50 | 30 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500237 |  | F | Any | Class J | 200 | 30 | 600 | - | 100 | 240 | 3 | 7.5 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500237 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500237 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500237 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500237 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500237 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500237 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500237 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500237 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500237 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500237 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500237 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500237 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500237 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500237 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500237 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500237 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500237 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500237 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500237 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500237 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500237 |  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500237 |  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500238 | A | FDS | Square D | GS1DU3 | 50 | 30 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1321 | 1, 7k | E163364 V2 S1
SE500238 |  | F | Any | Class J | 200 | 30 | 600 | - | 100 | 480 | 3 | 15 | 21 | 1321 | 1, 7k | E163364 V2 S1
SE500238 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1321 | 1, 7k | E163364 V2 S1
SE500238 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1321 | 1, 7k | E163364 V2 S1
SE500238 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1321 | 1, 7k | E163364 V2 S1
SE500238 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1321 | 1, 7k | E163364 V2 S1
SE500238 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1321 | 1, 7k | E163364 V2 S1
SE500238 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1321 | 1, 7k | E163364 V2 S1
SE500238 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1321 | 1, 7k | E163364 V2 S1
SE500238 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1321 | 1, 7k | E163364 V2 S1
SE500238 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1321 | 1, 7k | E163364 V2 S1
SE500238 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1321 | 1, 7k | E163364 V2 S1
SE500238 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1321 | 1, 7k | E163364 V2 S1
SE500238 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1321 | 1, 7k | E163364 V2 S1
SE500238 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1321 | 1, 7k | E163364 V2 S1
SE500238 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1321 | 1, 7k | E163364 V2 S1
SE500238 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1321 | 1, 7k | E163364 V2 S1
SE500238 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1321 | 1, 7k | E163364 V2 S1
SE500238 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1321 | 1, 7k | E163364 V2 S1
SE500238 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1321 | 1, 7k | E163364 V2 S1
SE500238 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1321 | 1, 7k | E163364 V2 S1
SE500238 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1321 | 1, 7k | E163364 V2 S1
SE500238 |  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1321 | 1, 7k | E163364 V2 S1
SE500238 |  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1321 | 1, 7k | E163364 V2 S1
SE500239 | A | FDS | Square D | GS1DU3 | 50 | 30 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500239 |  | F | Any | Class J | 200 | 30 | 600 | - | 100 | 600 | 3 | 20 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500239 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500239 |  | OLR | Telemecanique | LRD01 | 5 | 0.10 - 0.16 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500239 |  | OLR | Telemecanique | LRD02 | 5 | 0.16 - 0.25 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500239 |  | OLR | Telemecanique | LRD03 | 5 | 0.25 - 0.40 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500239 |  | OLR | Telemecanique | LRD04 | 5 | 0.40 - 0.63 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500239 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500239 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500239 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500239 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500239 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500239 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500239 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500239 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500239 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500239 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500239 |  | OLR | Telemecanique | LRD1508 | 5 | 2.5 - 4 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500239 |  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500239 |  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500239 |  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500239 |  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500239 |  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500239 |  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 1321 | 1, 7k | E163364 V2 S1
SE500240 | A | FDS | Square D | GS1GU3 | 200 | 60 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1321 | 1, 7b | E163364 V2 S1
SE500240 |  | F | Any | Class J | 200 | 60 | 600 | - | 100 | 200 | 3 | 7.5 | 25.3 | 1321 | 1, 7b | E163364 V2 S1
SE500240 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1321 | 1, 7b | E163364 V2 S1
SE500240 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1321 | 1, 7b | E163364 V2 S1
SE500240 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1321 | 1, 7b | E163364 V2 S1
SE500240 |  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1321 | 1, 7b | E163364 V2 S1
SE500240 |  | OLR | Telemecanique | LRD1530 | 5 | 23 - 28 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1321 | 1, 7b | E163364 V2 S1
SE500241 | A | FDS | Square D | GS1GU3 | 200 | 60 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1321 | 1, 7b | E163364 V2 S1
SE500241 |  | F | Any | Class J | 200 | 60 | 600 | - | 100 | 208 | 3 | 7.5 | 24.2 | 1321 | 1, 7b | E163364 V2 S1
SE500241 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1321 | 1, 7b | E163364 V2 S1
SE500241 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1321 | 1, 7b | E163364 V2 S1
SE500241 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1321 | 1, 7b | E163364 V2 S1
SE500241 |  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1321 | 1, 7b | E163364 V2 S1
SE500241 |  | OLR | Telemecanique | LRD1530 | 5 | 23 - 28 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1321 | 1, 7b | E163364 V2 S1
SE500242 | A | FDS | Square D | GS1GU3 | 200 | 60 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1321 | 1, 7b | E163364 V2 S1
SE500242 |  | F | Any | Class J | 200 | 60 | 600 | - | 100 | 240 | 3 | 10 | 28 | 1321 | 1, 7b | E163364 V2 S1
SE500242 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1321 | 1, 7b | E163364 V2 S1
SE500242 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1321 | 1, 7b | E163364 V2 S1
SE500242 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1321 | 1, 7b | E163364 V2 S1
SE500242 |  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1321 | 1, 7b | E163364 V2 S1
SE500242 |  | OLR | Telemecanique | LRD1530 | 5 | 23 - 28 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1321 | 1, 7b | E163364 V2 S1
SE500243 | A | FDS | Square D | GS1GU3 | 200 | 60 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1321 | 1, 7b | E163364 V2 S1
SE500243 |  | F | Any | Class J | 200 | 60 | 600 | - | 100 | 480 | 3 | 20 | 27 | 1321 | 1, 7b | E163364 V2 S1
SE500243 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1321 | 1, 7b | E163364 V2 S1
SE500243 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1321 | 1, 7b | E163364 V2 S1
SE500243 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1321 | 1, 7b | E163364 V2 S1
SE500243 |  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1321 | 1, 7b | E163364 V2 S1
SE500243 |  | OLR | Telemecanique | LRD1530 | 5 | 23 - 28 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1321 | 1, 7b | E163364 V2 S1
SE500244 | A | FDS | Square D | GS1GU3 | 200 | 60 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 1321 | 1, 7b | E163364 V2 S1
SE500244 |  | F | Any | Class J | 200 | 60 | 600 | - | 100 | 600 | 3 | 25 | 27 | 1321 | 1, 7b | E163364 V2 S1
SE500244 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 1321 | 1, 7b | E163364 V2 S1
SE500244 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 1321 | 1, 7b | E163364 V2 S1
SE500244 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 1321 | 1, 7b | E163364 V2 S1
SE500244 |  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 1321 | 1, 7b | E163364 V2 S1
SE500244 |  | OLR | Telemecanique | LRD1530 | 5 | 23 - 28 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 1321 | 1, 7b | E163364 V2 S1
SE500245 | A | FDS | Square D | GS1GU3 | 200 | 60 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1321 | 1, 7b | E163364 V2 S1
SE500245 |  | F | Any | Class J | 200 | 60 | 600 | - | 100 | 200 | 3 | 7.5 | 25.3 | 1321 | 1, 7b | E163364 V2 S1
SE500245 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1321 | 1, 7b | E163364 V2 S1
SE500245 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1321 | 1, 7b | E163364 V2 S1
SE500245 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1321 | 1, 7b | E163364 V2 S1
SE500245 |  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1321 | 1, 7b | E163364 V2 S1
SE500245 |  | OLR | Telemecanique | LRD1530 | 5 | 23 - 28 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1321 | 1, 7b | E163364 V2 S1
SE500246 | A | FDS | Square D | GS1GU3 | 200 | 60 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1321 | 1, 7b | E163364 V2 S1
SE500246 |  | F | Any | Class J | 200 | 60 | 600 | - | 100 | 208 | 3 | 7.5 | 24.2 | 1321 | 1, 7b | E163364 V2 S1
SE500246 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1321 | 1, 7b | E163364 V2 S1
SE500246 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1321 | 1, 7b | E163364 V2 S1
SE500246 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1321 | 1, 7b | E163364 V2 S1
SE500246 |  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1321 | 1, 7b | E163364 V2 S1
SE500246 |  | OLR | Telemecanique | LRD1530 | 5 | 23 - 28 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1321 | 1, 7b | E163364 V2 S1
SE500247 | A | FDS | Square D | GS1GU3 | 200 | 60 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1321 | 1, 7b | E163364 V2 S1
SE500247 |  | F | Any | Class J | 200 | 60 | 600 | - | 100 | 240 | 3 | 10 | 28 | 1321 | 1, 7b | E163364 V2 S1
SE500247 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1321 | 1, 7b | E163364 V2 S1
SE500247 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1321 | 1, 7b | E163364 V2 S1
SE500247 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1321 | 1, 7b | E163364 V2 S1
SE500247 |  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1321 | 1, 7b | E163364 V2 S1
SE500247 |  | OLR | Telemecanique | LRD1530 | 5 | 23 - 28 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1321 | 1, 7b | E163364 V2 S1
SE500248 | A | FDS | Square D | GS1GU3 | 200 | 60 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1321 | 1, 7b | E163364 V2 S1
SE500248 |  | F | Any | Class J | 200 | 60 | 600 | - | 100 | 480 | 3 | 20 | 27 | 1321 | 1, 7b | E163364 V2 S1
SE500248 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1321 | 1, 7b | E163364 V2 S1
SE500248 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1321 | 1, 7b | E163364 V2 S1
SE500248 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1321 | 1, 7b | E163364 V2 S1
SE500248 |  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1321 | 1, 7b | E163364 V2 S1
SE500248 |  | OLR | Telemecanique | LRD1530 | 5 | 23 - 28 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1321 | 1, 7b | E163364 V2 S1
SE500249 | A | FDS | Square D | GS1GU3 | 200 | 60 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 1321 | 1, 7b | E163364 V2 S1
SE500249 |  | F | Any | Class J | 200 | 60 | 600 | - | 100 | 600 | 3 | 25 | 27 | 1321 | 1, 7b | E163364 V2 S1
SE500249 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 1321 | 1, 7b | E163364 V2 S1
SE500249 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 1321 | 1, 7b | E163364 V2 S1
SE500249 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 1321 | 1, 7b | E163364 V2 S1
SE500249 |  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 1321 | 1, 7b | E163364 V2 S1
SE500249 |  | OLR | Telemecanique | LRD1530 | 5 | 23 - 28 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 1321 | 1, 7b | E163364 V2 S1
SE500250 | A | FDS | Square D | GS1GU3 | 200 | 60 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1321 | 1, 7b | E163364 V2 S1
SE500250 |  | F | Any | Class J | 200 | 60 | 600 | - | 100 | 200 | 3 | 10 | 32.2 | 1321 | 1, 7b | E163364 V2 S1
SE500250 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1321 | 1, 7b | E163364 V2 S1
SE500250 |  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1321 | 1, 7b | E163364 V2 S1
SE500250 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1321 | 1, 7b | E163364 V2 S1
SE500250 |  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1321 | 1, 7b | E163364 V2 S1
SE500250 |  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1321 | 1, 7b | E163364 V2 S1
SE500251 | A | FDS | Square D | GS1GU3 | 200 | 60 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1321 | 1, 7b | E163364 V2 S1
SE500251 |  | F | Any | Class J | 200 | 60 | 600 | - | 100 | 208 | 3 | 10 | 30.8 | 1321 | 1, 7b | E163364 V2 S1
SE500251 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1321 | 1, 7b | E163364 V2 S1
SE500251 |  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1321 | 1, 7b | E163364 V2 S1
SE500251 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1321 | 1, 7b | E163364 V2 S1
SE500251 |  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1321 | 1, 7b | E163364 V2 S1
SE500251 |  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1321 | 1, 7b | E163364 V2 S1
SE500252 | A | FDS | Square D | GS1GU3 | 200 | 60 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1321 | 1, 7b | E163364 V2 S1
SE500252 |  | F | Any | Class J | 200 | 60 | 600 | - | 100 | 240 | 3 | 10 | 28 | 1321 | 1, 7b | E163364 V2 S1
SE500252 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1321 | 1, 7b | E163364 V2 S1
SE500252 |  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1321 | 1, 7b | E163364 V2 S1
SE500252 |  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1321 | 1, 7b | E163364 V2 S1
SE500253 | A | FDS | Square D | GS1GU3 | 200 | 60 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 1321 | 1, 7b | E163364 V2 S1
SE500253 |  | F | Any | Class J | 200 | 60 | 600 | - | 100 | 480 | 3 | 30 | 40 | 1321 | 1, 7b | E163364 V2 S1
SE500253 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 1321 | 1, 7b | E163364 V2 S1
SE500253 |  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 1321 | 1, 7b | E163364 V2 S1
SE500253 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 1321 | 1, 7b | E163364 V2 S1
SE500253 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 1321 | 1, 7b | E163364 V2 S1
SE500253 |  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 1321 | 1, 7b | E163364 V2 S1
SE500253 |  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 1321 | 1, 7b | E163364 V2 S1
SE500253 |  | OLR | Telemecanique | LR2D3557 | 5 | 37 - 50 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 1321 | 1, 7b | E163364 V2 S1
SE500254 | A | FDS | Square D | GS1GU3 | 200 | 60 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 1321 | 1, 7b | E163364 V2 S1
SE500254 |  | F | Any | Class J | 200 | 60 | 600 | - | 100 | 600 | 3 | 30 | 32 | 1321 | 1, 7b | E163364 V2 S1
SE500254 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 1321 | 1, 7b | E163364 V2 S1
SE500254 |  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 1321 | 1, 7b | E163364 V2 S1
SE500254 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 1321 | 1, 7b | E163364 V2 S1
SE500254 |  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 1321 | 1, 7b | E163364 V2 S1
SE500254 |  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 1321 | 1, 7b | E163364 V2 S1
SE500255 | A | FDS | Square D | GS1GU3 | 200 | 60 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1321 | 1, 7b | E163364 V2 S1
SE500255 |  | F | Any | Class J | 200 | 60 | 600 | - | 100 | 200 | 3 | 10 | 32.2 | 1321 | 1, 7b | E163364 V2 S1
SE500255 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1321 | 1, 7b | E163364 V2 S1
SE500255 |  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1321 | 1, 7b | E163364 V2 S1
SE500255 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1321 | 1, 7b | E163364 V2 S1
SE500255 |  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1321 | 1, 7b | E163364 V2 S1
SE500255 |  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1321 | 1, 7b | E163364 V2 S1
SE500256 | A | FDS | Square D | GS1GU3 | 200 | 60 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1321 | 1, 7b | E163364 V2 S1
SE500256 |  | F | Any | Class J | 200 | 60 | 600 | - | 100 | 208 | 3 | 10 | 30.8 | 1321 | 1, 7b | E163364 V2 S1
SE500256 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1321 | 1, 7b | E163364 V2 S1
SE500256 |  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1321 | 1, 7b | E163364 V2 S1
SE500256 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1321 | 1, 7b | E163364 V2 S1
SE500256 |  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1321 | 1, 7b | E163364 V2 S1
SE500256 |  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1321 | 1, 7b | E163364 V2 S1
SE500257 | A | FDS | Square D | GS1GU3 | 200 | 60 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1321 | 1, 7b | E163364 V2 S1
SE500257 |  | F | Any | Class J | 200 | 60 | 600 | - | 100 | 240 | 3 | 10 | 28 | 1321 | 1, 7b | E163364 V2 S1
SE500257 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1321 | 1, 7b | E163364 V2 S1
SE500257 |  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1321 | 1, 7b | E163364 V2 S1
SE500257 |  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1321 | 1, 7b | E163364 V2 S1
SE500258 | A | FDS | Square D | GS1GU3 | 200 | 60 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 1321 | 1, 7b | E163364 V2 S1
SE500258 |  | F | Any | Class J | 200 | 60 | 600 | - | 100 | 480 | 3 | 30 | 40 | 1321 | 1, 7b | E163364 V2 S1
SE500258 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 1321 | 1, 7b | E163364 V2 S1
SE500258 |  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 1321 | 1, 7b | E163364 V2 S1
SE500258 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 1321 | 1, 7b | E163364 V2 S1
SE500258 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 1321 | 1, 7b | E163364 V2 S1
SE500258 |  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 1321 | 1, 7b | E163364 V2 S1
SE500258 |  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 1321 | 1, 7b | E163364 V2 S1
SE500258 |  | OLR | Telemecanique | LR2D3557 | 5 | 37 - 50 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 1321 | 1, 7b | E163364 V2 S1
SE500259 | A | FDS | Square D | GS1GU3 | 200 | 60 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 1321 | 1, 7b | E163364 V2 S1
SE500259 |  | F | Any | Class J | 200 | 60 | 600 | - | 100 | 600 | 3 | 30 | 32 | 1321 | 1, 7b | E163364 V2 S1
SE500259 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 1321 | 1, 7b | E163364 V2 S1
SE500259 |  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 1321 | 1, 7b | E163364 V2 S1
SE500259 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 1321 | 1, 7b | E163364 V2 S1
SE500259 |  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 1321 | 1, 7b | E163364 V2 S1
SE500259 |  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 1321 | 1, 7b | E163364 V2 S1

## D25 - D150_Fuse
Issued: 2007-03-19
Last Revised: 2007-03-19
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Min Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE500376 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500376 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500376 |  | F | Any | Class J Fuse | 200 | 20 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500376 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500376 |  | OLR | Telemecanique | LRD1516 | 5 | 9.0 - 13 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500377 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500377 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500377 |  | F | Any | Class J Fuse | 200 | 20 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500377 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500377 |  | OLR | Telemecanique | LRD1516 | 5 | 9.0 - 13 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500378 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500378 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500378 |  | F | Any | Class J Fuse | 200 | 30 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500378 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500378 |  | OLR | Telemecanique | LRD1521 | 5 | 12.0 - 18 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500379 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500379 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500379 |  | F | Any | Class J Fuse | 200 | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500379 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500379 |  | OLR | Telemecanique | LRD1521 | 5 | 12.0 - 18 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500380 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500380 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500380 |  | F | Any | Class J Fuse | 200 | 25 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500380 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500380 |  | OLR | Telemecanique | LRD1521 | 5 | 12.0 - 18 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500381 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500381 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500381 |  | F | Any | Class J Fuse | 200 | 45 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500381 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500381 |  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500382 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500382 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500382 |  | F | Any | Class J Fuse | 200 | 45 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500382 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500382 |  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500383 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500383 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500383 |  | F | Any | Class J Fuse | 200 | 40 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500383 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500383 |  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500384 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500384 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500384 |  | F | Any | Class J Fuse | 200 | 60 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500384 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500384 |  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500385 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500385 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500385 |  | F | Any | Class J Fuse | 200 | 50 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500385 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500385 |  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500386 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500386 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500386 |  | F | Any | Class J Fuse | 200 | 50 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500386 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500386 |  | OLR | Telemecanique | LRD1532 | 5 | 25 - 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500387 | A | DS | Square D | FHL36000M | 25 | 100 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500387 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500387 |  | F | Any | Class J Fuse | 200 | 25 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500387 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500387 |  | OLR | Telemecanique | LRD1521 | 5 | 12.0 - 18 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500388 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500388 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500388 |  | F | Any | Class J Fuse | 200 | 80 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500388 |  | MC | Telemecanique | LC1D50 | 10 | 50 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500388 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500389 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500389 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500389 |  | F | Any | Class J Fuse | 200 | 80 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500389 |  | MC | Telemecanique | LC1D50 | 10 | 50 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500389 |  | OLR | Telemecanique | LR2D3557 | 5 | 37 - 50 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500390 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500390 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500390 |  | F | Any | Class J Fuse | 200 | 70 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500390 |  | MC | Telemecanique | LC1D50 | 10 | 50 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500390 |  | OLR | Telemecanique | LR2D3557 | 5 | 37 - 50 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500391 | A | DS | Square D | FHL36000M | 25 | 100 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500391 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500391 |  | F | Any | Class J Fuse | 200 | 35 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500391 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500391 |  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500392 | A | DS | Square D | FHL36000M | 18 | 100 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500392 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500392 |  | F | Any | Class J Fuse | 200 | 30 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500392 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500392 |  | OLR | Telemecanique | LRD1521 | 5 | 12.0 - 18 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500393 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500393 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500393 |  | F | Any | Class J Fuse | 200 | 110 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500393 |  | MC | Telemecanique | LC1D65 | 10 | 65 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500393 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500394 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500394 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500394 |  | F | Any | Class J Fuse | 200 | 100 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500394 |  | MC | Telemecanique | LC1D65 | 10 | 65 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500394 |  | OLR | Telemecanique | LR2D3559 | 5 | 48 - 65 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500395 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500395 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500395 |  | F | Any | Class J Fuse | 200 | 90 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500395 |  | MC | Telemecanique | LC1D65 | 10 | 65 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500395 |  | OLR | Telemecanique | LR2D3559 | 5 | 48 - 65 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500396 | A | DS | Square D | FHL36000M | 25 | 100 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500396 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500396 |  | F | Any | Class J Fuse | 200 | 45 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500396 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500396 |  | OLR | Telemecanique | LRD1532 | 5 | 25 - 32 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500397 | A | DS | Square D | FHL36000M | 18 | 100 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500397 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500397 |  | F | Any | Class J Fuse | 200 | 40 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500397 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500397 |  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500398 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500398 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500398 |  | F | Any | Class J Fuse | 200 | 150 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500398 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500398 |  | OLR | Telemecanique | LR9D5567 | 5 | 60 -100 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500399 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500399 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500399 |  | F | Any | Class J Fuse | 200 | 125 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500399 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500399 |  | OLR | Telemecanique | LR9D5567 | 5 | 60 -100 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500400 | A | DS | Square D | FHL36000M | 65 | 100 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500400 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500400 |  | F | Any | Class J Fuse | 200 | 125 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500400 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500400 |  | OLR | Telemecanique | LR2D3563 | 5 | 63 - 80 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500401 | A | DS | Square D | FHL36000M | 25 | 100 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500401 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500401 |  | F | Any | Class J Fuse | 200 | 60 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500401 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500401 |  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500402 | A | DS | Square D | FHL36000M | 18 | 100 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500402 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500402 |  | F | Any | Class J Fuse | 200 | 45 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500402 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500402 |  | OLR | Telemecanique | LRD1532 | 5 | 25 - 32 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500403 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500403 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500403 |  | F | Any | Class J Fuse | 200 | 150 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500403 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500403 |  | OLR | Telemecanique | LR9D5567 | 5 | 60 - 100 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500404 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500404 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500404 |  | F | Any | Class J Fuse | 200 | 150 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500404 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500404 |  | OLR | Telemecanique | LR9D5567 | 5 | 60 -100 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500405 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500405 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500405 |  | F | Any | Class J Fuse | 200 | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500405 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500405 |  | OLR | Telemecanique | LR9D5567 | 5 | 60 -100 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500406 | A | DS | Square D | FHL36000M | 25 | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500406 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500406 |  | F | Any | Class J Fuse | 200 | 70 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500406 |  | MC | Telemecanique | LC1D50 | 10 | 50 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500406 |  | OLR | Telemecanique | LR2D3557 | 5 | 37 - 50 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500407 | A | DS | Square D | FHL36000M | 18 | 100 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500407 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500407 |  | F | Any | Class J Fuse | 200 | 60 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500407 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500407 |  | OLR | Telemecanique | LRD3555 | 5 | 30 - 40 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 4578 | 1, 6, 7(a) | E40610 V12 S20
SE500408 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500408 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500408 |  | F | Any | Class J Fuse | 200 | 200 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500408 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500408 |  | OLR | Telemecanique | LR9D5569 | 5 | 90 - 150 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500409 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500409 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500409 |  | F | Any | Class J Fuse | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500409 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500409 |  | OLR | Telemecanique | LR9D5569 | 5 | 90 - 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500410 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500410 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500410 |  | F | Any | Class J Fuse | 200 | 175 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500410 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500410 |  | OLR | Telemecanique | LR9D5569 | 5 | 90 - 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500411 | A | DS | Square D | FHL36000M | 25 | 100 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500411 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500411 |  | F | Any | Class J Fuse | 200 | 90 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500411 |  | MC | Telemecanique | LC1D65 | 10 | 65 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500411 |  | OLR | Telemecanique | LR2D3559 | 5 | 48 - 65 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500412 | A | DS | Square D | FHL36000M | 18 | 100 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500412 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500412 |  | F | Any | Class J Fuse | 200 | 70 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500412 |  | MC | Telemecanique | LC1D50 | 10 | 50 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500412 |  | OLR | Telemecanique | LRD3557 | 5 | 37 - 50 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 4578 | 1, 6, 7(k) | E40610 V12 S20
SE500413 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500413 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500413 |  | F | Any | Class J Fuse | 200 | 225 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500413 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500413 |  | OLR | Telemecanique | LR9D5569 | 5 | 90 - 150 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500414 | A | DS | Square D | FHL36000M | 25 | 100 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500414 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500414 |  | F | Any | Class J Fuse | 200 | 110 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500414 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500414 |  | OLR | Telemecanique | LR2D3561 | 5 | 55 - 70 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500415 | A | DS | Square D | FHL36000M | 18 | 100 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500415 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500415 |  | F | Any | Class J Fuse | 200 | 90 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500415 |  | MC | Telemecanique | LC1D65 | 10 | 65 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500415 |  | OLR | Telemecanique | LR2D3559 | 5 | 48 - 65 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500416 | A | DS | Square D | KHL36000M | 25 | 250 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500416 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500416 |  | F | Any | Class J Fuse | 200 | 125 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500416 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500416 |  | OLR | Telemecanique | LR9D5567 | 5 | 60 -100 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500417 | A | DS | Square D | FHL36000M | 18 | 100 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500417 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500417 |  | F | Any | Class J Fuse | 200 | 110 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500417 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500417 |  | OLR | Telemecanique | LR2D3561 | 5 | 55 - 70 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 4578 | 1, 6, 7(b) | E40610 V12 S20
SE500418 | A | DS | Square D | KHL36000M | 25 | 250 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500418 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500418 |  | F | Any | Class J Fuse | 200 | 175 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500418 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500418 |  | OLR | Telemecanique | LR9D5569 | 5 | 60 - 100 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500419 | A | DS | Square D | KHL36000M | 18 | 250 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500419 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500419 |  | F | Any | Class J Fuse | 200 | 125 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500419 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500419 |  | OLR | Telemecanique | LR9D5567 | 5 | 60 -100 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 4578 | 1, 6, 7(L) | E40610 V12 S20
SE500420 | A | DS | Square D | KHL36000M | 25 | 250 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500420 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500420 |  | F | Any | Class J Fuse | 200 | 225 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500420 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500420 |  | OLR | Telemecanique | LR9D5569 | 5 | 90 - 150 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500421 | A | DS | Square D | KHL36000M | 18 | 250 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500421 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500421 |  | F | Any | Class J Fuse | 200 | 175 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500421 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500421 |  | OLR | Telemecanique | LR9D5569 | 5 | 90 - 150 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 4578 | 1, 6, 7(m) | E40610 V12 S20
SE500422 | A | DS | Square D | KHL36000M | 18 | 250 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500422 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500422 |  | F | Any | Class J Fuse | 200 | 225 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500422 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE500422 |  | OLR | Telemecanique | LR9D5569 | 5 | 90 - 150 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 6409 | 1, 6, 7(n) | E40610 V12 S20
SE550090 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550090 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550090 |  | F | Any | Class J Fuse | 200 | 20 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550090 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550090 |  | OLR | Telemecanique | LRD1516 | 5 | 9.0 - 13 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550091 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550091 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550091 |  | F | Any | Class J Fuse | 200 | 20 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550091 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550091 |  | OLR | Telemecanique | LRD1516 | 5 | 9.0 - 13 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550092 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550092 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550092 |  | F | Any | Class J Fuse | 200 | 30 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550092 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550092 |  | OLR | Telemecanique | LRD1521 | 5 | 12.0 - 18 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550093 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550093 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550093 |  | F | Any | Class J Fuse | 200 | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550093 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550093 |  | OLR | Telemecanique | LRD1521 | 5 | 12.0 - 18 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550094 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550094 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550094 |  | F | Any | Class J Fuse | 200 | 25 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550094 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550094 |  | OLR | Telemecanique | LRD1521 | 5 | 12.0 - 18 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550095 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550095 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550095 |  | F | Any | Class J Fuse | 200 | 45 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550095 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550095 |  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550096 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550096 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550096 |  | F | Any | Class J Fuse | 200 | 45 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550096 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550096 |  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550097 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550097 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550097 |  | F | Any | Class J Fuse | 200 | 40 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550097 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550097 |  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550098 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2.649 | 1, 6, 7(k) | E40610 V12 S20
SE550098 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2.649 | 1, 6, 7(k) | E40610 V12 S20
SE550098 |  | F | Any | Class J Fuse | 200 | 60 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2.649 | 1, 6, 7(k) | E40610 V12 S20
SE550098 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2.649 | 1, 6, 7(k) | E40610 V12 S20
SE550098 |  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2.649 | 1, 6, 7(k) | E40610 V12 S20
SE550099 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550099 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550099 |  | F | Any | Class J Fuse | 200 | 50 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550099 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550099 |  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550100 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550100 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550100 |  | F | Any | Class J Fuse | 200 | 50 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550100 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550100 |  | OLR | Telemecanique | LRD1532 | 5 | 25 - 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550101 | A | DS | Square D | HGL36000S15 | 35 | 150 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550101 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550101 |  | F | Any | Class J Fuse | 200 | 25 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550101 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550101 |  | OLR | Telemecanique | LRD1521 | 5 | 12.0 - 18 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550102 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550102 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550102 |  | F | Any | Class J Fuse | 200 | 80 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550102 |  | MC | Telemecanique | LC1D50 | 10 | 50 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550102 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550103 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550103 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550103 |  | F | Any | Class J Fuse | 200 | 80 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550103 |  | MC | Telemecanique | LC1D50 | 10 | 50 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550103 |  | OLR | Telemecanique | LR2D3557 | 5 | 37 - 50 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550104 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2.649 | 1, 6, 7(k) | E40610 V12 S20
SE550104 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2.649 | 1, 6, 7(k) | E40610 V12 S20
SE550104 |  | F | Any | Class J Fuse | 200 | 70 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2.649 | 1, 6, 7(k) | E40610 V12 S20
SE550104 |  | MC | Telemecanique | LC1D50 | 10 | 50 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2.649 | 1, 6, 7(k) | E40610 V12 S20
SE550104 |  | OLR | Telemecanique | LR2D3557 | 5 | 37 - 50 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2.649 | 1, 6, 7(k) | E40610 V12 S20
SE550105 | A | DS | Square D | HGL36000S15 | 35 | 150 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550105 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550105 |  | F | Any | Class J Fuse | 200 | 35 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550105 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550105 |  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550106 | A | DS | Square D | HGL36000S15 | 18 | 150 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550106 |  | FH | Any | Listed Fuse Holder | 200 | 30 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550106 |  | F | Any | Class J Fuse | 200 | 30 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550106 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550106 |  | OLR | Telemecanique | LRD1521 | 5 | 12.0 - 18 | 600 | 3 | 100 | 600 | 3 | 15 | 17 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550107 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550107 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550107 |  | F | Any | Class J Fuse | 200 | 110 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550107 |  | MC | Telemecanique | LC1D65 | 10 | 65 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550107 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550108 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550108 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550108 |  | F | Any | Class J Fuse | 200 | 100 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550108 |  | MC | Telemecanique | LC1D65 | 10 | 65 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550108 |  | OLR | Telemecanique | LR2D3559 | 5 | 48 - 65 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550109 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550109 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550109 |  | F | Any | Class J Fuse | 200 | 90 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550109 |  | MC | Telemecanique | LC1D65 | 10 | 65 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550109 |  | OLR | Telemecanique | LR2D3559 | 5 | 48 - 65 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550110 | A | DS | Square D | HGL36000S15 | 35 | 150 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550110 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550110 |  | F | Any | Class J Fuse | 200 | 45 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550110 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550110 |  | OLR | Telemecanique | LRD1532 | 5 | 25 - 32 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550111 | A | DS | Square D | HGL36000S15 | 18 | 150 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550111 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550111 |  | F | Any | Class J Fuse | 200 | 40 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550111 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550111 |  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3 | 100 | 600 | 3 | 20 | 22 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550112 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2.649 | 1, 6, 7(L) | E40610 V12 S20
SE550112 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2.649 | 1, 6, 7(L) | E40610 V12 S20
SE550112 |  | F | Any | Class J Fuse | 200 | 150 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2.649 | 1, 6, 7(L) | E40610 V12 S20
SE550112 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2.649 | 1, 6, 7(L) | E40610 V12 S20
SE550112 |  | OLR | Telemecanique | LR9D5567 | 5 | 60 -100 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2.649 | 1, 6, 7(L) | E40610 V12 S20
SE550113 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2.649 | 1, 6, 7(L) | E40610 V12 S20
SE550113 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2.649 | 1, 6, 7(L) | E40610 V12 S20
SE550113 |  | F | Any | Class J Fuse | 200 | 125 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2.649 | 1, 6, 7(L) | E40610 V12 S20
SE550113 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2.649 | 1, 6, 7(L) | E40610 V12 S20
SE550113 |  | OLR | Telemecanique | LR9D5567 | 5 | 60 -100 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2.649 | 1, 6, 7(L) | E40610 V12 S20
SE550114 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550114 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550114 |  | F | Any | Class J Fuse | 200 | 125 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550114 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550114 |  | OLR | Telemecanique | LR2D3563 | 5 | 63 - 80 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550115 | A | DS | Square D | HGL36000S15 | 35 | 150 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550115 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550115 |  | F | Any | Class J Fuse | 200 | 60 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550115 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550115 |  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550116 | A | DS | Square D | HGL36000S15 | 18 | 150 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550116 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550116 |  | F | Any | Class J Fuse | 200 | 45 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550116 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550116 |  | OLR | Telemecanique | LRD1532 | 5 | 25 - 32 | 600 | 3 | 100 | 600 | 3 | 25 | 27 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550117 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 2.649 | 1, 6, 7(m) | E40610 V12 S20
SE550117 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 2.649 | 1, 6, 7(m) | E40610 V12 S20
SE550117 |  | F | Any | Class J Fuse | 200 | 150 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 2.649 | 1, 6, 7(m) | E40610 V12 S20
SE550117 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 2.649 | 1, 6, 7(m) | E40610 V12 S20
SE550117 |  | OLR | Telemecanique | LR9D5567 | 5 | 60 - 100 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 2.649 | 1, 6, 7(m) | E40610 V12 S20
SE550118 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 2.649 | 1, 6, 7(m) | E40610 V12 S20
SE550118 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 2.649 | 1, 6, 7(m) | E40610 V12 S20
SE550118 |  | F | Any | Class J Fuse | 200 | 150 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 2.649 | 1, 6, 7(m) | E40610 V12 S20
SE550118 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 2.649 | 1, 6, 7(m) | E40610 V12 S20
SE550118 |  | OLR | Telemecanique | LR9D5567 | 5 | 60 -100 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 2.649 | 1, 6, 7(m) | E40610 V12 S20
SE550119 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2.649 | 1, 6, 7(L) | E40610 V12 S20
SE550119 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2.649 | 1, 6, 7(L) | E40610 V12 S20
SE550119 |  | F | Any | Class J Fuse | 200 | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2.649 | 1, 6, 7(L) | E40610 V12 S20
SE550119 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2.649 | 1, 6, 7(L) | E40610 V12 S20
SE550119 |  | OLR | Telemecanique | LR9D5567 | 5 | 60 -100 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2.649 | 1, 6, 7(L) | E40610 V12 S20
SE550120 | A | DS | Square D | HGL36000S15 | 35 | 150 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2.649 | 1, 6, 7(k) | E40610 V12 S20
SE550120 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2.649 | 1, 6, 7(k) | E40610 V12 S20
SE550120 |  | F | Any | Class J Fuse | 200 | 70 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2.649 | 1, 6, 7(k) | E40610 V12 S20
SE550120 |  | MC | Telemecanique | LC1D50 | 10 | 50 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2.649 | 1, 6, 7(k) | E40610 V12 S20
SE550120 |  | OLR | Telemecanique | LR2D3557 | 5 | 37 - 50 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2.649 | 1, 6, 7(k) | E40610 V12 S20
SE550121 | A | DS | Square D | HGL36000S15 | 18 | 150 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550121 |  | FH | Any | Listed Fuse Holder | 200 | 60 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550121 |  | F | Any | Class J Fuse | 200 | 60 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550121 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550121 |  | OLR | Telemecanique | LRD3555 | 5 | 30 - 40 | 600 | 3 | 100 | 600 | 3 | 30 | 32 | 2.649 | 1, 6, 7(a) | E40610 V12 S20
SE550122 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3.709 | 1, 6, 7(n) | E40610 V12 S20
SE550122 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3.709 | 1, 6, 7(n) | E40610 V12 S20
SE550122 |  | F | Any | Class J Fuse | 200 | 200 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3.709 | 1, 6, 7(n) | E40610 V12 S20
SE550122 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3.709 | 1, 6, 7(n) | E40610 V12 S20
SE550122 |  | OLR | Telemecanique | LR9D5569 | 5 | 90 - 150 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3.709 | 1, 6, 7(n) | E40610 V12 S20
SE550123 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3.709 | 1, 6, 7(n) | E40610 V12 S20
SE550123 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3.709 | 1, 6, 7(n) | E40610 V12 S20
SE550123 |  | F | Any | Class J Fuse | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3.709 | 1, 6, 7(n) | E40610 V12 S20
SE550123 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3.709 | 1, 6, 7(n) | E40610 V12 S20
SE550123 |  | OLR | Telemecanique | LR9D5569 | 5 | 90 - 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3.709 | 1, 6, 7(n) | E40610 V12 S20
SE550124 | A | DS | Square D | HGL36000S15 | 65 | 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 2.649 | 1, 6, 7(m) | E40610 V12 S20
SE550124 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 2.649 | 1, 6, 7(m) | E40610 V12 S20
SE550124 |  | F | Any | Class J Fuse | 200 | 175 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 2.649 | 1, 6, 7(m) | E40610 V12 S20
SE550124 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 2.649 | 1, 6, 7(m) | E40610 V12 S20
SE550124 |  | OLR | Telemecanique | LR9D5569 | 5 | 90 - 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 2.649 | 1, 6, 7(m) | E40610 V12 S20
SE550125 | A | DS | Square D | HGL36000S15 | 35 | 150 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550125 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550125 |  | F | Any | Class J Fuse | 200 | 90 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550125 |  | MC | Telemecanique | LC1D65 | 10 | 65 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550125 |  | OLR | Telemecanique | LR2D3559 | 5 | 48 - 65 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550126 | A | DS | Square D | HGL36000S15 | 18 | 150 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 2.649 | 1, 6, 7(k) | E40610 V12 S20
SE550126 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 2.649 | 1, 6, 7(k) | E40610 V12 S20
SE550126 |  | F | Any | Class J Fuse | 200 | 70 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 2.649 | 1, 6, 7(k) | E40610 V12 S20
SE550126 |  | MC | Telemecanique | LC1D50 | 10 | 50 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 2.649 | 1, 6, 7(k) | E40610 V12 S20
SE550126 |  | OLR | Telemecanique | LRD3557 | 5 | 37 - 50 | 600 | 3 | 100 | 600 | 3 | 40 | 41 | 2.649 | 1, 6, 7(k) | E40610 V12 S20
SE550127 | A | DS | Square D | JGL36000S17 | 65 | 175 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3.709 | 1, 6, 7(n) | E40610 V12 S20
SE550127 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3.709 | 1, 6, 7(n) | E40610 V12 S20
SE550127 |  | F | Any | Class J Fuse | 200 | 225 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3.709 | 1, 6, 7(n) | E40610 V12 S20
SE550127 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3.709 | 1, 6, 7(n) | E40610 V12 S20
SE550127 |  | OLR | Telemecanique | LR9D5569 | 5 | 90 - 150 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3.709 | 1, 6, 7(n) | E40610 V12 S20
SE550128 | A | DS | Square D | HGL36000S15 | 35 | 150 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550128 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550128 |  | F | Any | Class J Fuse | 200 | 110 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550128 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550128 |  | OLR | Telemecanique | LR2D3561 | 5 | 55 - 70 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550129 | A | DS | Square D | HGL36000S15 | 18 | 150 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550129 |  | FH | Any | Listed Fuse Holder | 200 | 100 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550129 |  | F | Any | Class J Fuse | 200 | 90 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550129 |  | MC | Telemecanique | LC1D65 | 10 | 65 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550129 |  | OLR | Telemecanique | LR2D3559 | 5 | 48 - 65 | 600 | 3 | 100 | 600 | 3 | 50 | 52 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550130 | A | DS | Square D | HGL36000S15 | 35 | 150 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 2.649 | 1, 6, 7(L) | E40610 V12 S20
SE550130 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 2.649 | 1, 6, 7(L) | E40610 V12 S20
SE550130 |  | F | Any | Class J Fuse | 200 | 125 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 2.649 | 1, 6, 7(L) | E40610 V12 S20
SE550130 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 2.649 | 1, 6, 7(L) | E40610 V12 S20
SE550130 |  | OLR | Telemecanique | LR9D5567 | 5 | 60 -100 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 2.649 | 1, 6, 7(L) | E40610 V12 S20
SE550131 | A | DS | Square D | HGL36000S15 | 18 | 150 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550131 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550131 |  | F | Any | Class J Fuse | 200 | 110 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550131 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550131 |  | OLR | Telemecanique | LR2D3561 | 5 | 55 - 70 | 600 | 3 | 100 | 600 | 3 | 60 | 62 | 2.649 | 1, 6, 7(b) | E40610 V12 S20
SE550132 | A | DS | Square D | HGL36000S15 | 35 | 150 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 2.649 | 1, 6, 7(m) | E40610 V12 S20
SE550132 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 2.649 | 1, 6, 7(m) | E40610 V12 S20
SE550132 |  | F | Any | Class J Fuse | 200 | 175 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 2.649 | 1, 6, 7(m) | E40610 V12 S20
SE550132 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 2.649 | 1, 6, 7(m) | E40610 V12 S20
SE550132 |  | OLR | Telemecanique | LR9D5569 | 5 | 60 - 100 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 2.649 | 1, 6, 7(m) | E40610 V12 S20
SE550133 | A | DS | Square D | HGL36000S15 | 18 | 150 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 2.649 | 1, 6, 7(L) | E40610 V12 S20
SE550133 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 2.649 | 1, 6, 7(L) | E40610 V12 S20
SE550133 |  | F | Any | Class J Fuse | 200 | 125 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 2.649 | 1, 6, 7(L) | E40610 V12 S20
SE550133 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 2.649 | 1, 6, 7(L) | E40610 V12 S20
SE550133 |  | OLR | Telemecanique | LR9D5567 | 5 | 60 -100 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 2.649 | 1, 6, 7(L) | E40610 V12 S20
SE550134 | A | DS | Square D | JGL36000S17 | 35 | 175 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 3.709 | 1, 6, 7(n) | E40610 V12 S20
SE550134 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 3.709 | 1, 6, 7(n) | E40610 V12 S20
SE550134 |  | F | Any | Class J Fuse | 200 | 225 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 3.709 | 1, 6, 7(n) | E40610 V12 S20
SE550134 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 3.709 | 1, 6, 7(n) | E40610 V12 S20
SE550134 |  | OLR | Telemecanique | LR9D5569 | 5 | 90 - 150 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 3.709 | 1, 6, 7(n) | E40610 V12 S20
SE550135 | A | DS | Square D | HGL36000S15 | 18 | 150 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 2.649 | 1, 6, 7(m) | E40610 V12 S20
SE550135 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 2.649 | 1, 6, 7(m) | E40610 V12 S20
SE550135 |  | F | Any | Class J Fuse | 200 | 175 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 2.649 | 1, 6, 7(m) | E40610 V12 S20
SE550135 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 2.649 | 1, 6, 7(m) | E40610 V12 S20
SE550135 |  | OLR | Telemecanique | LR9D5569 | 5 | 90 - 150 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 2.649 | 1, 6, 7(m) | E40610 V12 S20
SE550136 | A | DS | Square D | JGL36000S17 | 18 | 175 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 3.709 | 1, 6, 7(n) | E40610 V12 S20
SE550136 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 3.709 | 1, 6, 7(n) | E40610 V12 S20
SE550136 |  | F | Any | Class J Fuse | 200 | 225 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 3.709 | 1, 6, 7(n) | E40610 V12 S20
SE550136 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 3.709 | 1, 6, 7(n) | E40610 V12 S20
SE550136 |  | OLR | Telemecanique | LR9D5569 | 5 | 90 - 150 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 3.709 | 1, 6, 7(n) | E40610 V12 S20

## F185 - F500_Fuse
Issued: 2007-03-19
Last Revised: 2008-04-08
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Min Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE502400 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 200 | 3 | 50 | 150 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502400 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 200 | 3 | 50 | 150 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502400 |  | F | Any | Class J Fuse | 200 | 225 | 600 | 3 | 100 | 200 | 3 | 50 | 150 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502400 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 200 | 3 | 50 | 150 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502400 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 200 | 3 | 50 | 150 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502400 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3 | 100 | 200 | 3 | 50 | 150 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502401 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502401 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502401 |  | F | Any | Class J Fuse | 200 | 225 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502401 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502401 |  | OLR | Telemecanique | LR9F5369 | 5 | 90 - 150 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502401 |  | OLR | Telemecanique | LR9F5569 | 5 | 90 - 150 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502402 | A | DS | Square D | LHL36000M | 65 | 400 | 600 | 3 | 100 | 200 | 3 | 60 | 177 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502402 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 200 | 3 | 60 | 177 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502402 |  | F | Any | Class J Fuse | 200 | 250 | 600 | 3 | 100 | 200 | 3 | 60 | 177 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502402 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3 | 100 | 200 | 3 | 60 | 177 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502402 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 200 | 3 | 60 | 177 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502402 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3 | 100 | 200 | 3 | 60 | 177 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502403 | A | DS | Square D | LHL36000M | 65 | 400 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502403 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502403 |  | F | Any | Class J Fuse | 200 | 250 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502403 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502403 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502403 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502404 | A | DS | Square D | KHL36000M | 65 | 250 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502404 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502404 |  | F | Any | Class J Fuse | 200 | 250 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502404 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502404 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502404 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502405 | A | DS | Square D | LHL36000M | 65 | 400 | 600 | 3 | 100 | 200 | 3 | 75 | 221 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502405 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 200 | 3 | 75 | 221 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502405 |  | F | Any | Class J Fuse | 200 | 350 | 600 | 3 | 100 | 200 | 3 | 75 | 221 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502405 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 100 | 200 | 3 | 75 | 221 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502405 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3 | 100 | 200 | 3 | 75 | 221 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502405 |  | OLR | Telemecanique | LR9F7575 | 5 | 200 - 330 | 600 | 3 | 100 | 200 | 3 | 75 | 221 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502406 | A | DS | Square D | LHL36000M | 65 | 400 | 600 | 3 | 100 | 208 | 3 | 75 | 211 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502406 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 208 | 3 | 75 | 211 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502406 |  | F | Any | Class J Fuse | 200 | 350 | 600 | 3 | 100 | 208 | 3 | 75 | 211 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502406 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 100 | 208 | 3 | 75 | 211 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502406 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 208 | 3 | 75 | 211 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502406 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3 | 100 | 208 | 3 | 75 | 211 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502407 | A | DS | Square D | LHL36000M | 65 | 400 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502407 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502407 |  | F | Any | Class J Fuse | 200 | 300 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502407 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502407 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502407 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502408 | A | DS | Square D | LHL36000M | 65 | 400 | 600 | 3 | 100 | 200 | 3 | 100 | 285 | 10987 | 1, 6, 7(f) | E40610 V12 S15
SE502408 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 200 | 3 | 100 | 285 | 10987 | 1, 6, 7(f) | E40610 V12 S15
SE502408 |  | F | Any | Class J Fuse | 200 | 450 | 600 | 3 | 100 | 200 | 3 | 100 | 285 | 10987 | 1, 6, 7(f) | E40610 V12 S15
SE502408 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 100 | 200 | 3 | 100 | 285 | 10987 | 1, 6, 7(f) | E40610 V12 S15
SE502408 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3 | 100 | 200 | 3 | 100 | 285 | 10987 | 1, 6, 7(f) | E40610 V12 S15
SE502408 |  | OLR | Telemecanique | LR9F7575 | 5 | 200 - 330 | 600 | 3 | 100 | 200 | 3 | 100 | 285 | 10987 | 1, 6, 7(f) | E40610 V12 S15
SE502409 | A | DS | Square D | LHL36000M | 65 | 400 | 600 | 3 | 100 | 208 | 3 | 100 | 273 | 10987 | 1, 6, 7(f) | E40610 V12 S15
SE502409 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 208 | 3 | 100 | 273 | 10987 | 1, 6, 7(f) | E40610 V12 S15
SE502409 |  | F | Any | Class J Fuse | 200 | 450 | 600 | 3 | 100 | 208 | 3 | 100 | 273 | 10987 | 1, 6, 7(f) | E40610 V12 S15
SE502409 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 100 | 208 | 3 | 100 | 273 | 10987 | 1, 6, 7(f) | E40610 V12 S15
SE502409 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3 | 100 | 208 | 3 | 100 | 273 | 10987 | 1, 6, 7(f) | E40610 V12 S15
SE502409 |  | OLR | Telemecanique | LR9F7575 | 5 | 200 - 330 | 600 | 3 | 100 | 208 | 3 | 100 | 273 | 10987 | 1, 6, 7(f) | E40610 V12 S15
SE502410 | A | DS | Square D | LHL36000M | 65 | 400 | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502410 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502410 |  | F | Any | Class J Fuse | 200 | 400 | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502410 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502410 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502410 |  | OLR | Telemecanique | LR9F7575 | 5 | 200 - 330 | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502411 | A | DS | Square D | MHL360006M | 65 | 600 | 600 | 3 | 100 | 200 | 3 | 125 | 359 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502411 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 200 | 3 | 125 | 359 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502411 |  | F | Any | Class J Fuse | 200 | 500 | 600 | 3 | 100 | 200 | 3 | 125 | 359 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502411 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 200 | 3 | 125 | 359 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502411 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 100 | 200 | 3 | 125 | 359 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502411 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3 | 100 | 200 | 3 | 125 | 359 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502412 | A | DS | Square D | MHL360006M | 65 | 600 | 600 | 3 | 100 | 208 | 3 | 125 | 343 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502412 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 208 | 3 | 125 | 343 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502412 |  | F | Any | Class J Fuse | 200 | 500 | 600 | 3 | 100 | 208 | 3 | 125 | 343 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502412 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 208 | 3 | 125 | 343 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502412 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 100 | 208 | 3 | 125 | 343 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502412 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3 | 100 | 208 | 3 | 125 | 343 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502413 | A | DS | Square D | LHL36000M | 65 | 400 | 600 | 3 | 100 | 240 | 3 | 125 | 312 | 10987 | 1, 6, 7(f) | E40610 V12 S15
SE502413 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 240 | 3 | 125 | 312 | 10987 | 1, 6, 7(f) | E40610 V12 S15
SE502413 |  | F | Any | Class J Fuse | 200 | 500 | 600 | 3 | 100 | 240 | 3 | 125 | 312 | 10987 | 1, 6, 7(f) | E40610 V12 S15
SE502413 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 100 | 240 | 3 | 125 | 312 | 10987 | 1, 6, 7(f) | E40610 V12 S15
SE502413 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3 | 100 | 240 | 3 | 125 | 312 | 10987 | 1, 6, 7(f) | E40610 V12 S15
SE502413 |  | OLR | Telemecanique | LR9F7575 | 5 | 200 - 330 | 600 | 3 | 100 | 240 | 3 | 125 | 312 | 10987 | 1, 6, 7(f) | E40610 V12 S15
SE502414 | A | DS | Square D | KHL36000M | 35 | 250 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502414 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502414 |  | F | Any | Class J Fuse | 200 | 250 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502414 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502414 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502414 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502415 | A | DS | Square D | KHL36000M | 25 | 250 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502415 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502415 |  | F | Any | Class J Fuse | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502415 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502415 |  | OLR | Telemecanique | LR9F5369 | 5 | 90 - 150 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502415 |  | OLR | Telemecanique | LR9F5569 | 5 | 90 - 150 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE502416 | A | DS | Square D | MHL360006M | 65 | 600 | 600 | 3 | 100 | 200 | 3 | 150 | 414 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502416 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 200 | 3 | 150 | 414 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502416 |  | F | Any | Class J Fuse | 200 | 600 | 600 | 3 | 100 | 200 | 3 | 150 | 414 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502416 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 200 | 3 | 150 | 414 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502416 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 100 | 200 | 3 | 150 | 414 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502416 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3 | 100 | 200 | 3 | 150 | 414 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502417 | A | DS | Square D | MHL360006M | 65 | 600 | 600 | 3 | 100 | 208 | 3 | 150 | 396 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502417 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 208 | 3 | 150 | 396 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502417 |  | F | Any | Class J Fuse | 200 | 600 | 600 | 3 | 100 | 208 | 3 | 150 | 396 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502417 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 208 | 3 | 150 | 396 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502417 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 100 | 208 | 3 | 150 | 396 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502417 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3 | 100 | 208 | 3 | 150 | 396 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502418 | A | DS | Square D | MHL360006M | 65 | 600 | 600 | 3 | 100 | 240 | 3 | 150 | 360 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502418 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 240 | 3 | 150 | 360 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502418 |  | F | Any | Class J Fuse | 200 | 550 | 600 | 3 | 100 | 240 | 3 | 150 | 360 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502418 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 240 | 3 | 150 | 360 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502418 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 100 | 240 | 3 | 150 | 360 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502418 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3 | 100 | 240 | 3 | 150 | 360 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502419 | A | DS | Square D | LHL36000M | 35 | 400 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502419 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502419 |  | F | Any | Class J Fuse | 200 | 300 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502419 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502419 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502419 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502420 | A | DS | Square D | LHL36000M | 25 | 400 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502420 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502420 |  | F | Any | Class J Fuse | 200 | 225 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502420 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502420 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502420 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE502421 | A | DS | Square D | MHL360006M | 65 | 600 | 600 | 3 | 100 | 240 | 3 | 200 | 480 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502421 |  | FH | Any | Listed Fuse Holder | 200 | 800 | 600 | 3 | 100 | 240 | 3 | 200 | 480 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502421 |  | F | Any | Class L Fuse | 200 | 700 | 600 | 3 | 100 | 240 | 3 | 200 | 480 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502421 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 240 | 3 | 200 | 480 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502421 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 100 | 240 | 3 | 200 | 480 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502421 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3 | 100 | 240 | 3 | 200 | 480 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502422 | A | DS | Square D | LHL36000M | 35 | 400 | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502422 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502422 |  | F | Any | Class J Fuse | 200 | 350 | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502422 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502422 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502422 |  | OLR | Telemecanique | LR9F7575 | 5 | 200 - 330 | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502423 | A | DS | Square D | LHL36000M | 25 | 400 | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502423 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502423 |  | F | Any | Class J Fuse | 200 | 300 | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502423 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502423 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502423 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502424 | A | DS | Square D | LHL36000M | 35 | 400 | 600 | 3 | 100 | 480 | 3 | 250 | 302 | 10987 | 1, 6, 7(f) | E40610 V12 S15
SE502424 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 480 | 3 | 250 | 302 | 10987 | 1, 6, 7(f) | E40610 V12 S15
SE502424 |  | F | Any | Class J Fuse | 200 | 450 | 600 | 3 | 100 | 480 | 3 | 250 | 302 | 10987 | 1, 6, 7(f) | E40610 V12 S15
SE502424 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 100 | 480 | 3 | 250 | 302 | 10987 | 1, 6, 7(f) | E40610 V12 S15
SE502424 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 100 | 480 | 3 | 250 | 302 | 10987 | 1, 6, 7(f) | E40610 V12 S15
SE502424 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3 | 100 | 480 | 3 | 250 | 302 | 10987 | 1, 6, 7(f) | E40610 V12 S15
SE502425 | A | DS | Square D | LHL36000M | 25 | 400 | 600 | 3 | 100 | 600 | 3 | 250 | 242 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502425 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 600 | 3 | 250 | 242 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502425 |  | F | Any | Class J Fuse | 200 | 400 | 600 | 3 | 100 | 600 | 3 | 250 | 242 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502425 |  | MC | Telemecanique | LC1F330 | 18 | 400 | 600 | 3 | 100 | 600 | 3 | 250 | 242 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502425 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3 | 100 | 600 | 3 | 250 | 242 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502425 |  | OLR | Telemecanique | LR9F7575 | 5 | 200 - 330 | 600 | 3 | 100 | 600 | 3 | 250 | 242 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE502426 | A | DS | Square D | MHL360006M | 65 | 400 | 600 | 3 | 100 | 480 | 3 | 300 | 361 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502426 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 480 | 3 | 300 | 361 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502426 |  | F | Any | Class J Fuse | 200 | 500 | 600 | 3 | 100 | 480 | 3 | 300 | 361 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502426 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 480 | 3 | 300 | 361 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502426 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 100 | 480 | 3 | 300 | 361 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502426 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3 | 100 | 480 | 3 | 300 | 361 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502427 | A | DS | Square D | MHL360006M | 25 | 400 | 600 | 3 | 100 | 600 | 3 | 300 | 289 | 43200 | 1, 6, 7(f) | E40610 V12 S15
SE502427 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 600 | 3 | 300 | 289 | 43200 | 1, 6, 7(f) | E40610 V12 S15
SE502427 |  | F | Any | Class J Fuse | 200 | 450 | 600 | 3 | 100 | 600 | 3 | 300 | 289 | 43200 | 1, 6, 7(f) | E40610 V12 S15
SE502427 |  | MC | Telemecanique | LC1F400 | 18 | 500 | 600 | 3 | 100 | 600 | 3 | 300 | 289 | 43200 | 1, 6, 7(f) | E40610 V12 S15
SE502427 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3 | 100 | 600 | 3 | 300 | 289 | 43200 | 1, 6, 7(f) | E40610 V12 S15
SE502427 |  | OLR | Telemecanique | LR9F7575 | 5 | 200 - 330 | 600 | 3 | 100 | 600 | 3 | 300 | 289 | 43200 | 1, 6, 7(f) | E40610 V12 S15
SE502428 | A | DS | Square D | MHL360006M | 65 | 600 | 600 | 3 | 100 | 480 | 3 | 350 | 414 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502428 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 480 | 3 | 350 | 414 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502428 |  | F | Any | Class J Fuse | 200 | 600 | 600 | 3 | 100 | 480 | 3 | 350 | 414 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502428 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 480 | 3 | 350 | 414 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502428 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 100 | 480 | 3 | 350 | 414 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502428 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3 | 100 | 480 | 3 | 350 | 414 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502429 | A | DS | Square D | MHL360006M | 25 | 600 | 600 | 3 | 100 | 600 | 3 | 350 | 336 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502429 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 600 | 3 | 350 | 336 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502429 |  | F | Any | Class J Fuse | 200 | 500 | 600 | 3 | 100 | 600 | 3 | 350 | 336 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502429 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 600 | 3 | 350 | 336 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502429 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 100 | 600 | 3 | 350 | 336 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502429 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3 | 100 | 600 | 3 | 350 | 336 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502430 | A | DS | Square D | MHL360006M | 65 | 600 | 600 | 3 | 100 | 480 | 3 | 400 | 477 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502430 |  | FH | Any | Listed Fuse Holder | 200 | 800 | 600 | 3 | 100 | 480 | 3 | 400 | 477 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502430 |  | F | Any | Class L Fuse | 200 | 700 | 600 | 3 | 100 | 480 | 3 | 400 | 477 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502430 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 480 | 3 | 400 | 477 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502430 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 100 | 480 | 3 | 400 | 477 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502430 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3 | 100 | 480 | 3 | 400 | 477 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502431 | A | DS | Square D | MHL360006M | 25 | 600 | 600 | 3 | 100 | 600 | 3 | 400 | 382 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502431 |  | FH | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 600 | 3 | 400 | 382 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502431 |  | F | Any | Class J Fuse | 200 | 600 | 600 | 3 | 100 | 600 | 3 | 400 | 382 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502431 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 600 | 3 | 400 | 382 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502431 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 100 | 600 | 3 | 400 | 382 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE502431 |  | OLR | Telemecanique | LR9F7579 | 5 | 300 - 500 | 600 | 3 | 100 | 600 | 3 | 400 | 382 | 43200 | 1, 6, 7(j) | E40610 V12 S15
SE551600 | A | DS | Square D | JGL36000S25 | 65 | 250 | 600 | 3 | 100 | 200 | 3 | 50 | 150 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551600 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 200 | 3 | 50 | 150 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551600 |  | F | Any | Class J Fuse | 200 | 225 | 600 | 3 | 100 | 200 | 3 | 50 | 150 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551600 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 200 | 3 | 50 | 150 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551600 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 200 | 3 | 50 | 150 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551600 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3 | 100 | 200 | 3 | 50 | 150 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551601 | A | DS | Square D | JGL36000S25 | 65 | 250 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551601 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551601 |  | F | Any | Class J Fuse | 200 | 225 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551601 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551601 |  | OLR | Telemecanique | LR9F5369 | 5 | 90 - 150 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551601 |  | OLR | Telemecanique | LR9F5569 | 5 | 90 - 150 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551602 | A | DS | Square D | JGL36000S25 | 65 | 250 | 600 | 3 | 100 | 200 | 3 | 60 | 177 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551602 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 200 | 3 | 60 | 177 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551602 |  | F | Any | Class J Fuse | 200 | 250 | 600 | 3 | 100 | 200 | 3 | 60 | 177 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551602 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3 | 100 | 200 | 3 | 60 | 177 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551602 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 200 | 3 | 60 | 177 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551602 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3 | 100 | 200 | 3 | 60 | 177 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551603 | A | DS | Square D | JGL36000S25 | 65 | 250 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551603 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551603 |  | F | Any | Class J Fuse | 200 | 250 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551603 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551603 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551603 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3 | 100 | 208 | 3 | 60 | 169 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551604 | A | DS | Square D | JGL36000S25 | 65 | 250 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551604 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551604 |  | F | Any | Class J Fuse | 200 | 250 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551604 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551604 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551604 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551605 | A | DS | Square D | JGL36000S25 | 65 | 250 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551605 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551605 |  | F | Any | Class J Fuse | 200 | 300 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551605 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551605 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551605 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551606 | A | DS | Square D | JGL36000S25 | 35 | 250 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551606 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551606 |  | F | Any | Class J Fuse | 200 | 250 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551606 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551606 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551606 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551607 | A | DS | Square D | JGL36000S17 | 18 | 175 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551607 |  | FH | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551607 |  | F | Any | Class J Fuse | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551607 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551607 |  | OLR | Telemecanique | LR9F5369 | 5 | 90 - 150 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551607 |  | OLR | Telemecanique | LR9F5569 | 5 | 90 - 150 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 7783 | 1, 6, 7(p) | E40610 V12 S15
SE551608 | A | DS | Square D | JGL36000S25 | 35 | 250 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551608 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551608 |  | F | Any | Class J Fuse | 200 | 300 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551608 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551608 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551608 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551609 | A | DS | Square D | JGL36000S25 | 18 | 250 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551609 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551609 |  | F | Any | Class J Fuse | 200 | 225 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551609 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551609 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551609 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 10987 | 1, 6, 7(h) | E40610 V12 S15
SE551610 | A | DS | Square D | JGL36000S25 | 18 | 250 | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE551610 |  | FH | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE551610 |  | F | Any | Class J Fuse | 200 | 300 | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE551610 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE551610 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 10987 | 1, 6, 7(i) | E40610 V12 S15
SE551610 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 10987 | 1, 6, 7(i) | E40610 V12 S15
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = Use wire ties evenly spaced apart to secure conductors in place.
(7) = See Table 7 for minimum internal wiring between load side of short circuit protective device & line side of starter.
(8) = "@" refer to digest to complete contactor Catalog number for coil voltage and Form modifications.
(9) = Insulator to be provided underneath starter. (QMFZ2), Fastex, Type Formex GK-30, 1/32 inch minimum thickness by 4 inches x 5.7 inches.
Table 7 - Minimum Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
| Wire Code |  | Wire Size
| 7a |  | 12 AWG
| 7b |  | 8 AWG
| 7c |  | 2 AWG
| 7d |  | 1 AWG
| 7e |  | 250 MCM
| 7f |  | 300 MCM
| 7g |  | (2) 250 MCM
| 7h |  | 2/0 AWG
| 7i |  | 4/0 AWG
| 7j |  | (2) 4/0 AWG
| 7k |  | 10 AWG
| 7L |  | 6 AWG
| 7m |  | 4 AWG
| 7n |  | 3 AWG
| 7p |  | 1/0 AWG
| 7q |  | (2) 3/0 AWG
| 7r |  | (2) 2/0 AWG
| 7s |  | 3/0 AWG

## F185 - F500_Reversing_Fuse
Issued: 2008-03-10
Last Revised: 2008-03-10
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE501000 | A | DS | Square D | MHL360006M | - | 600 | 600 | 3 | 100 | 208 | 3 | 125 | 359 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501000 |  | FB | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 208 | 3 | 125 | 359 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501000 |  | F | Any | Class J or R Time Delay Fuse | 200 | 500 | 600 | 3 | 100 | 208 | 3 | 125 | 359 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501000 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 208 | 3 | 125 | 359 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501000 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 208 | 3 | 125 | 359 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501000 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 100 | 208 | 3 | 125 | 359 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501000 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 100 | 208 | 3 | 125 | 359 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501001 | A | DS | Square D | LHL36000M | - | 400 | 600 | 3 | 100 | 208 | 3 | 50 | 150 | 10987 | 1, 5, 7p | E40610 V12 S16
SE501001 |  | FB | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 208 | 3 | 50 | 150 | 10987 | 1, 5, 7p | E40610 V12 S16
SE501001 |  | F | Any | Class J or R Time Delay Fuse | 200 | 225 | 600 | 3 | 100 | 208 | 3 | 50 | 150 | 10987 | 1, 5, 7p | E40610 V12 S16
SE501001 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 208 | 3 | 50 | 150 | 10987 | 1, 5, 7p | E40610 V12 S16
SE501001 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 208 | 3 | 50 | 150 | 10987 | 1, 5, 7p | E40610 V12 S16
SE501001 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 208 | 3 | 50 | 150 | 10987 | 1, 5, 7p | E40610 V12 S16
SE501001 |  | OLR | Telemecanique | LR9F5369 | 5 | 90 - 150 | 600 | 3 | 100 | 208 | 3 | 50 | 150 | 10987 | 1, 5, 7p | E40610 V12 S16
SE501002 | A | DS | Square D | LHL36000M | - | 400 | 600 | 3 | 100 | 208 | 3 | 60 | 177 | 15019 | 1, 5, 7h | E40610 V12 S16
SE501002 |  | FB | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 208 | 3 | 60 | 177 | 15019 | 1, 5, 7h | E40610 V12 S16
SE501002 |  | F | Any | Class J or R Time Delay Fuse | 200 | 250 | 600 | 3 | 100 | 208 | 3 | 60 | 177 | 15019 | 1, 5, 7h | E40610 V12 S16
SE501002 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3 | 100 | 208 | 3 | 60 | 177 | 15019 | 1, 5, 7h | E40610 V12 S16
SE501002 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3 | 100 | 208 | 3 | 60 | 177 | 15019 | 1, 5, 7h | E40610 V12 S16
SE501002 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FH4H | NA | NA | NA | NA | 100 | 208 | 3 | 60 | 177 | 15019 | 1, 5, 7h | E40610 V12 S16
SE501002 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 208 | 3 | 60 | 177 | 15019 | 1, 5, 7h | E40610 V12 S16
SE501003 | A | DS | Square D | LHL36000M | - | 400 | 600 | 3 | 100 | 208 | 3 | 75 | 221 | 15019 | 1, 5, 7i | E40610 V12 S16
SE501003 |  | FB | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 208 | 3 | 75 | 221 | 15019 | 1, 5, 7i | E40610 V12 S16
SE501003 |  | F | Any | Class J or R Time Delay Fuse | 200 | 350 | 600 | 3 | 100 | 208 | 3 | 75 | 221 | 15019 | 1, 5, 7i | E40610 V12 S16
SE501003 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 100 | 208 | 3 | 75 | 221 | 15019 | 1, 5, 7i | E40610 V12 S16
SE501003 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 100 | 208 | 3 | 75 | 221 | 15019 | 1, 5, 7i | E40610 V12 S16
SE501003 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FJ4J | NA | NA | NA | NA | 100 | 208 | 3 | 75 | 221 | 15019 | 1, 5, 7i | E40610 V12 S16
SE501003 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 208 | 3 | 75 | 221 | 15019 | 1, 5, 7i | E40610 V12 S16
SE501004 | A | DS | Square D | MHL360006M | - | 600 | 600 | 3 | 100 | 208 | 3 | 100 | 285 | 15019 | 1, 5, 7f | E40610 V12 S16
SE501004 |  | FB | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 208 | 3 | 100 | 285 | 15019 | 1, 5, 7f | E40610 V12 S16
SE501004 |  | F | Any | Class J or R Time Delay Fuse | 200 | 450 | 600 | 3 | 100 | 208 | 3 | 100 | 285 | 15019 | 1, 5, 7f | E40610 V12 S16
SE501004 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 100 | 208 | 3 | 100 | 285 | 15019 | 1, 5, 7f | E40610 V12 S16
SE501004 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 100 | 208 | 3 | 100 | 285 | 15019 | 1, 5, 7f | E40610 V12 S16
SE501004 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FJ4J | NA | NA | NA | NA | 100 | 208 | 3 | 100 | 285 | 15019 | 1, 5, 7f | E40610 V12 S16
SE501004 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3 | 100 | 208 | 3 | 100 | 285 | 15019 | 1, 5, 7f | E40610 V12 S16
SE501005 | A | DS | Square D | MHL360006M | - | 600 | 600 | 3 | 100 | 208 | 3 | 150 | 414 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501005 |  | FB | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 208 | 3 | 150 | 414 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501005 |  | F | Any | Class J or R Time Delay Fuse | 200 | 600 | 600 | 3 | 100 | 208 | 3 | 150 | 414 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501005 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 208 | 3 | 150 | 414 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501005 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 208 | 3 | 150 | 414 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501005 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 100 | 208 | 3 | 150 | 414 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501005 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 100 | 208 | 3 | 150 | 414 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501006 | A | DS | Square D | LHL36000M | - | 400 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 10987 | 1, 5, 7p | E40610 V12 S16
SE501006 |  | FB | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 10987 | 1, 5, 7p | E40610 V12 S16
SE501006 |  | F | Any | Class J or R Time Delay Fuse | 200 | 250 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 10987 | 1, 5, 7p | E40610 V12 S16
SE501006 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 10987 | 1, 5, 7p | E40610 V12 S16
SE501006 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 10987 | 1, 5, 7p | E40610 V12 S16
SE501006 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 240 | 3 | 60 | 154 | 10987 | 1, 5, 7p | E40610 V12 S16
SE501006 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 10987 | 1, 5, 7p | E40610 V12 S16
SE501007 | A | DS | Square D | LHL36000M | - | 400 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 15019 | 1, 5, 7h | E40610 V12 S16
SE501007 |  | FB | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 15019 | 1, 5, 7h | E40610 V12 S16
SE501007 |  | F | Any | Class J or R Time Delay Fuse | 200 | 300 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 15019 | 1, 5, 7h | E40610 V12 S16
SE501007 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 15019 | 1, 5, 7h | E40610 V12 S16
SE501007 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 15019 | 1, 5, 7h | E40610 V12 S16
SE501007 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FH4H | NA | NA | NA | NA | 100 | 240 | 3 | 75 | 192 | 15019 | 1, 5, 7h | E40610 V12 S16
SE501007 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 240 | 3 | 75 | 192 | 15019 | 1, 5, 7h | E40610 V12 S16
SE501008 | A | DS | Square D | LHL36000M | - | 400 | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 15019 | 1, 5, 7i | E40610 V12 S16
SE501008 |  | FB | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 15019 | 1, 5, 7i | E40610 V12 S16
SE501008 |  | F | Any | Class J or R Time Delay Fuse | 200 | 400 | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 15019 | 1, 5, 7i | E40610 V12 S16
SE501008 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 15019 | 1, 5, 7i | E40610 V12 S16
SE501008 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 15019 | 1, 5, 7i | E40610 V12 S16
SE501008 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FJ4J | NA | NA | NA | NA | 100 | 240 | 3 | 100 | 248 | 15019 | 1, 5, 7i | E40610 V12 S16
SE501008 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3 | 100 | 240 | 3 | 100 | 248 | 15019 | 1, 5, 7i | E40610 V12 S16
SE501009 | A | DS | Square D | MHL360006M | - | 600 | 600 | 3 | 100 | 240 | 3 | 125 | 312 | 15019 | 1, 5, 7f | E40610 V12 S16
SE501009 |  | FB | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 240 | 3 | 125 | 312 | 15019 | 1, 5, 7f | E40610 V12 S16
SE501009 |  | F | Any | Class J or R Time Delay Fuse | 200 | 500 | 600 | 3 | 100 | 240 | 3 | 125 | 312 | 15019 | 1, 5, 7f | E40610 V12 S16
SE501009 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 100 | 240 | 3 | 125 | 312 | 15019 | 1, 5, 7f | E40610 V12 S16
SE501009 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 100 | 240 | 3 | 125 | 312 | 15019 | 1, 5, 7f | E40610 V12 S16
SE501009 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FJ4J | NA | NA | NA | NA | 100 | 240 | 3 | 125 | 312 | 15019 | 1, 5, 7f | E40610 V12 S16
SE501009 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3 | 100 | 240 | 3 | 125 | 312 | 15019 | 1, 5, 7f | E40610 V12 S16
SE501010 | A | DS | Square D | MHL360006M | - | 600 | 600 | 3 | 100 | 240 | 3 | 150 | 360 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501010 |  | FB | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 240 | 3 | 150 | 360 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501010 |  | F | Any | Class J or R Time Delay Fuse | 200 | 550 | 600 | 3 | 100 | 240 | 3 | 150 | 360 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501010 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 240 | 3 | 150 | 360 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501010 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 240 | 3 | 150 | 360 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501010 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 100 | 240 | 3 | 150 | 360 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501010 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 100 | 240 | 3 | 150 | 360 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501011 | A | DS | Square D | MHL360008M | - | 800 | 600 | 3 | 100 | 240 | 3 | 200 | 480 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501011 |  | FB | Any | Listed Fuse Holder | 200 | 1200 | 600 | 3 | 100 | 240 | 3 | 200 | 480 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501011 |  | F | Any | Class J or R Time Delay Fuse | 200 | 700 | 600 | 3 | 100 | 240 | 3 | 200 | 480 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501011 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 240 | 3 | 200 | 480 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501011 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 240 | 3 | 200 | 480 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501011 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 100 | 240 | 3 | 200 | 480 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501011 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 100 | 240 | 3 | 200 | 480 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501012 | A | DS | Square D | MHL360006M | - | 600 | 600 | 3 | 100 | 480 | 3 | 300 | 361 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501012 |  | FB | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 480 | 3 | 300 | 361 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501012 |  | F | Any | Class J or R Time Delay Fuse | 200 | 500 | 600 | 3 | 100 | 480 | 3 | 300 | 361 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501012 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 480 | 3 | 300 | 361 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501012 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 480 | 3 | 300 | 361 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501012 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 100 | 480 | 3 | 300 | 361 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501012 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 100 | 480 | 3 | 300 | 361 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501013 | A | DS | Square D | MHL360006M | - | 600 | 600 | 3 | 100 | 480 | 3 | 350 | 414 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501013 |  | FB | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 480 | 3 | 350 | 414 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501013 |  | F | Any | Class J or R Time Delay Fuse | 200 | 600 | 600 | 3 | 100 | 480 | 3 | 350 | 414 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501013 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 480 | 3 | 350 | 414 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501013 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 480 | 3 | 350 | 414 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501013 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 100 | 480 | 3 | 350 | 414 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501013 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 100 | 480 | 3 | 350 | 414 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501014 | A | DS | Square D | MHL360008M | - | 800 | 600 | 3 | 100 | 480 | 3 | 400 | 477 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501014 |  | FB | Any | Listed Fuse Holder | 200 | 1200 | 600 | 3 | 100 | 480 | 3 | 400 | 477 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501014 |  | F | Any | Class J or R Time Delay Fuse | 200 | 700 | 600 | 3 | 100 | 480 | 3 | 400 | 477 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501014 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 480 | 3 | 400 | 477 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501014 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 480 | 3 | 400 | 477 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501014 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 100 | 480 | 3 | 400 | 477 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501014 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 100 | 480 | 3 | 400 | 477 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501015 | A | DS | Square D | LHL36000M | - | 400 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 10987 | 1, 5, 7p | E40610 V12 S16
SE501015 |  | FB | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 10987 | 1, 5, 7p | E40610 V12 S16
SE501015 |  | F | Any | Class J or R Time Delay Fuse | 200 | 250 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 10987 | 1, 5, 7p | E40610 V12 S16
SE501015 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 10987 | 1, 5, 7p | E40610 V12 S16
SE501015 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 10987 | 1, 5, 7p | E40610 V12 S16
SE501015 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 480 | 3 | 125 | 156 | 10987 | 1, 5, 7p | E40610 V12 S16
SE501015 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 10987 | 1, 5, 7p | E40610 V12 S16
SE501016 | A | DS | Square D | LHL36000M | - | 400 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 15019 | 1, 5, 7h | E40610 V12 S16
SE501016 |  | FB | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 15019 | 1, 5, 7h | E40610 V12 S16
SE501016 |  | F | Any | Class J or R Time Delay Fuse | 200 | 300 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 15019 | 1, 5, 7h | E40610 V12 S16
SE501016 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 15019 | 1, 5, 7h | E40610 V12 S16
SE501016 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 15019 | 1, 5, 7h | E40610 V12 S16
SE501016 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FH4H | NA | NA | NA | NA | 100 | 480 | 3 | 150 | 180 | 15019 | 1, 5, 7h | E40610 V12 S16
SE501016 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 480 | 3 | 150 | 180 | 15019 | 1, 5, 7h | E40610 V12 S16
SE501017 | A | DS | Square D | LHL36000M | - | 400 | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 15019 | 1, 5, 7i | E40610 V12 S16
SE501017 |  | FB | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 15019 | 1, 5, 7i | E40610 V12 S16
SE501017 |  | F | Any | Class J or R Time Delay Fuse | 200 | 350 | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 15019 | 1, 5, 7i | E40610 V12 S16
SE501017 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 15019 | 1, 5, 7i | E40610 V12 S16
SE501017 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 15019 | 1, 5, 7i | E40610 V12 S16
SE501017 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FJ4J | NA | NA | NA | NA | 100 | 480 | 3 | 200 | 240 | 15019 | 1, 5, 7i | E40610 V12 S16
SE501017 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3 | 100 | 480 | 3 | 200 | 240 | 15019 | 1, 5, 7i | E40610 V12 S16
SE501018 | A | DS | Square D | MHL360006M | - | 600 | 600 | 3 | 100 | 480 | 3 | 250 | 302 | 15019 | 1, 5, 7f | E40610 V12 S16
SE501018 |  | FB | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 480 | 3 | 250 | 302 | 15019 | 1, 5, 7f | E40610 V12 S16
SE501018 |  | F | Any | Class J or R Time Delay Fuse | 200 | 450 | 600 | 3 | 100 | 480 | 3 | 250 | 302 | 15019 | 1, 5, 7f | E40610 V12 S16
SE501018 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 100 | 480 | 3 | 250 | 302 | 15019 | 1, 5, 7f | E40610 V12 S16
SE501018 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 100 | 480 | 3 | 250 | 302 | 15019 | 1, 5, 7f | E40610 V12 S16
SE501018 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FJ4J | NA | NA | NA | NA | 100 | 480 | 3 | 250 | 302 | 15019 | 1, 5, 7f | E40610 V12 S16
SE501018 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 100 | 480 | 3 | 250 | 302 | 15019 | 1, 5, 7f | E40610 V12 S16
SE501019 | A | DS | Square D | MHL360006M | - | 600 | 600 | 3 | 100 | 600 | 3 | 350 | 336 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501019 |  | FB | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 600 | 3 | 350 | 336 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501019 |  | F | Any | Class J or R Time Delay Fuse | 200 | 500 | 600 | 3 | 100 | 600 | 3 | 350 | 336 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501019 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 600 | 3 | 350 | 336 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501019 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 600 | 3 | 350 | 336 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501019 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 100 | 600 | 3 | 350 | 336 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501019 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 100 | 600 | 3 | 350 | 336 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501020 | A | DS | Square D | MHL360006M | - | 600 | 600 | 3 | 100 | 600 | 3 | 400 | 382 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501020 |  | FB | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 600 | 3 | 400 | 382 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501020 |  | F | Any | Class J or R Time Delay Fuse | 200 | 600 | 600 | 3 | 100 | 600 | 3 | 400 | 382 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501020 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 600 | 3 | 400 | 382 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501020 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 600 | 3 | 400 | 382 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501020 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 100 | 600 | 3 | 400 | 382 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501020 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 100 | 600 | 3 | 400 | 382 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501021 | A | DS | Square D | MHL360006M | - | 600 | 600 | 3 | 100 | 600 | 3 | 450 | 412 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501021 |  | FB | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 600 | 3 | 450 | 412 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501021 |  | F | Any | Class J or R Time Delay Fuse | 200 | 600 | 600 | 3 | 100 | 600 | 3 | 450 | 412 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501021 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 600 | 3 | 450 | 412 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501021 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 600 | 3 | 450 | 412 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501021 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 100 | 600 | 3 | 450 | 412 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501021 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 100 | 600 | 3 | 450 | 412 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501022 | A | DS | Square D | LHL36000M | - | 400 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 15019 | 1, 5, 7p | E40610 V12 S16
SE501022 |  | FB | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 15019 | 1, 5, 7p | E40610 V12 S16
SE501022 |  | F | Any | Class J or R Time Delay Fuse | 200 | 225 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 15019 | 1, 5, 7p | E40610 V12 S16
SE501022 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 15019 | 1, 5, 7p | E40610 V12 S16
SE501022 |  | MC | Telemecanique | LC1F265 | 10 | 265 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 15019 | 1, 5, 7p | E40610 V12 S16
SE501022 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FH4H | NA | NA | NA | NA | 100 | 600 | 3 | 150 | 144 | 15019 | 1, 5, 7p | E40610 V12 S16
SE501022 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 600 | 3 | 150 | 144 | 15019 | 1, 5, 7p | E40610 V12 S16
SE501023 | A | DS | Square D | LHL36000M | - | 400 | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 15019 | 1, 5, 7h | E40610 V12 S16
SE501023 |  | FB | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 15019 | 1, 5, 7h | E40610 V12 S16
SE501023 |  | F | Any | Class J or R Time Delay Fuse | 200 | 300 | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 15019 | 1, 5, 7h | E40610 V12 S16
SE501023 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 15019 | 1, 5, 7h | E40610 V12 S16
SE501023 |  | MC | Telemecanique | LC1F330 | 18 | 330 | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 15019 | 1, 5, 7h | E40610 V12 S16
SE501023 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FJ4J | NA | NA | NA | NA | 100 | 600 | 3 | 200 | 192 | 15019 | 1, 5, 7h | E40610 V12 S16
SE501023 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 600 | 3 | 200 | 192 | 15019 | 1, 5, 7h | E40610 V12 S16
SE501024 | A | DS | Square D | LHL36000M | - | 400 | 600 | 3 | 100 | 600 | 3 | 250 | 242 | 15019 | 1, 5, 7i | E40610 V12 S16
SE501024 |  | FB | Any | Listed Fuse Holder | 200 | 400 | 600 | 3 | 100 | 600 | 3 | 250 | 242 | 15019 | 1, 5, 7i | E40610 V12 S16
SE501024 |  | F | Any | Class J or R Time Delay Fuse | 200 | 400 | 600 | 3 | 100 | 600 | 3 | 250 | 242 | 15019 | 1, 5, 7i | E40610 V12 S16
SE501024 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 100 | 600 | 3 | 250 | 242 | 15019 | 1, 5, 7i | E40610 V12 S16
SE501024 |  | MC | Telemecanique | LC1F400 | 18 | 400 | 600 | 3 | 100 | 600 | 3 | 250 | 242 | 15019 | 1, 5, 7i | E40610 V12 S16
SE501024 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FJ4J | NA | NA | NA | NA | 100 | 600 | 3 | 250 | 242 | 15019 | 1, 5, 7i | E40610 V12 S16
SE501024 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3 | 100 | 600 | 3 | 250 | 242 | 15019 | 1, 5, 7i | E40610 V12 S16
SE501025 | A | DS | Square D | MHL360006M | - | 600 | 600 | 3 | 100 | 600 | 3 | 300 | 289 | 24674 | 1, 5, 7f | E40610 V12 S16
SE501025 |  | FB | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 600 | 3 | 300 | 289 | 24674 | 1, 5, 7f | E40610 V12 S16
SE501025 |  | F | Any | Class J or R Time Delay Fuse | 200 | 450 | 600 | 3 | 100 | 600 | 3 | 300 | 289 | 24674 | 1, 5, 7f | E40610 V12 S16
SE501025 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 600 | 3 | 300 | 289 | 24674 | 1, 5, 7f | E40610 V12 S16
SE501025 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 600 | 3 | 300 | 289 | 24674 | 1, 5, 7f | E40610 V12 S16
SE501025 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 100 | 600 | 3 | 300 | 289 | 24674 | 1, 5, 7f | E40610 V12 S16
SE501025 |  | OLR | Telemecanique | LR9F7375 | 5 | 200 - 330 | 600 | 3 | 100 | 600 | 3 | 300 | 289 | 24674 | 1, 5, 7f | E40610 V12 S16
SE501026 | A | DS | Square D | KHL36000M | - | 250 | 600 | 3 | 100 | 208 | 3 | 25 | 78.2 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501026 |  | FB | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 25 | 78.2 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501026 |  | F | Any | Class J or R Time Delay Fuse | 200 | 125 | 600 | 3 | 100 | 208 | 3 | 25 | 78.2 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501026 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 208 | 3 | 25 | 78.2 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501026 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 208 | 3 | 25 | 78.2 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501026 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 208 | 3 | 25 | 78.2 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501026 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 100 | 208 | 3 | 25 | 78.2 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501027 | A | DS | Square D | KHL36000M | - | 250 | 600 | 3 | 100 | 208 | 3 | 30 | 92 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501027 |  | FB | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 30 | 92 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501027 |  | F | Any | Class J or R Time Delay Fuse | 200 | 150 | 600 | 3 | 100 | 208 | 3 | 30 | 92 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501027 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 208 | 3 | 30 | 92 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501027 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 208 | 3 | 30 | 92 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501027 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 208 | 3 | 30 | 92 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501027 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 100 | 208 | 3 | 30 | 92 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501028 | A | DS | Square D | KHL36000M | - | 250 | 600 | 3 | 100 | 208 | 3 | 40 | 120 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501028 |  | FB | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 40 | 120 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501028 |  | F | Any | Class J or R Time Delay Fuse | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 40 | 120 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501028 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 208 | 3 | 40 | 120 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501028 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 208 | 3 | 40 | 120 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501028 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 208 | 3 | 40 | 120 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501028 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 208 | 3 | 40 | 120 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501029 | A | DS | Square D | JLL36000S25 | - | 250 | 600 | 3 | 100 | 208 | 3 | 25 | 78.2 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501029 |  | FB | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 25 | 78.2 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501029 |  | F | Any | Class J or R Time Delay Fuse | 200 | 125 | 600 | 3 | 100 | 208 | 3 | 25 | 78.2 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501029 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 208 | 3 | 25 | 78.2 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501029 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 208 | 3 | 25 | 78.2 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501029 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 208 | 3 | 25 | 78.2 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501029 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 100 | 208 | 3 | 25 | 78.2 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501030 | A | DS | Square D | JLL36000S25 | - | 250 | 600 | 3 | 100 | 208 | 3 | 30 | 92 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501030 |  | FB | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 30 | 92 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501030 |  | F | Any | Class J or R Time Delay Fuse | 200 | 150 | 600 | 3 | 100 | 208 | 3 | 30 | 92 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501030 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 208 | 3 | 30 | 92 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501030 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 208 | 3 | 30 | 92 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501030 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 208 | 3 | 30 | 92 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501030 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 100 | 208 | 3 | 30 | 92 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501031 | A | DS | Square D | JLL36000S25 | - | 250 | 600 | 3 | 100 | 208 | 3 | 40 | 120 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501031 |  | FB | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 40 | 120 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501031 |  | F | Any | Class J or R Time Delay Fuse | 200 | 200 | 600 | 3 | 100 | 208 | 3 | 40 | 120 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501031 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 208 | 3 | 40 | 120 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501031 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 208 | 3 | 40 | 120 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501031 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 208 | 3 | 40 | 120 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501031 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 208 | 3 | 40 | 120 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501032 | A | DS | Square D | KHL36000M | - | 250 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501032 |  | FB | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501032 |  | F | Any | Class J or R Time Delay Fuse | 200 | 125 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501032 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501032 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501032 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 240 | 3 | 30 | 80 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501032 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501033 | A | DS | Square D | KHL36000M | - | 250 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501033 |  | FB | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501033 |  | F | Any | Class J or R Time Delay Fuse | 200 | 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501033 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501033 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501033 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 240 | 3 | 40 | 104 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501033 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501034 | A | DS | Square D | KHL36000M | - | 250 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501034 |  | FB | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501034 |  | F | Any | Class J or R Time Delay Fuse | 200 | 200 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501034 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501034 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501034 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 240 | 3 | 50 | 130 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501034 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501035 | A | DS | Square D | JLL36000S25 | - | 250 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501035 |  | FB | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501035 |  | F | Any | Class J or R Time Delay Fuse | 200 | 125 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501035 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501035 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501035 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 240 | 3 | 30 | 80 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501035 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501036 | A | DS | Square D | JLL36000S25 | - | 250 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501036 |  | FB | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501036 |  | F | Any | Class J or R Time Delay Fuse | 200 | 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501036 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501036 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501036 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 240 | 3 | 40 | 104 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501036 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501037 | A | DS | Square D | JLL36000S25 | - | 250 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501037 |  | FB | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501037 |  | F | Any | Class J or R Time Delay Fuse | 200 | 200 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501037 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501037 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501037 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 240 | 3 | 50 | 130 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501037 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501038 | A | DS | Square D | KHL36000M | - | 250 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501038 |  | FB | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501038 |  | F | Any | Class J or R Time Delay Fuse | 200 | 125 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501038 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501038 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501038 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 480 | 3 | 60 | 77 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501038 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501039 | A | DS | Square D | KHL36000M | - | 250 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501039 |  | FB | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501039 |  | F | Any | Class J or R Time Delay Fuse | 200 | 150 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501039 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501039 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501039 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 480 | 3 | 75 | 96 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501039 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501040 | A | DS | Square D | KHL36000M | - | 250 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501040 |  | FB | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501040 |  | F | Any | Class J or R Time Delay Fuse | 200 | 200 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501040 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501040 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501040 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 480 | 3 | 100 | 124 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501040 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501041 | A | DS | Square D | JLL36000S25 | - | 250 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501041 |  | FB | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501041 |  | F | Any | Class J or R Time Delay Fuse | 200 | 125 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501041 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501041 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501041 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 480 | 3 | 60 | 77 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501041 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501042 | A | DS | Square D | JLL36000S25 | - | 250 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501042 |  | FB | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501042 |  | F | Any | Class J or R Time Delay Fuse | 200 | 150 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501042 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501042 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501042 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 480 | 3 | 75 | 96 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501042 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501043 | A | DS | Square D | JLL36000S25 | - | 250 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501043 |  | FB | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501043 |  | F | Any | Class J or R Time Delay Fuse | 200 | 200 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501043 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501043 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501043 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 480 | 3 | 100 | 124 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501043 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501044 | A | DS | Square D | KHL36000M | - | 250 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501044 |  | FB | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501044 |  | F | Any | Class J or R Time Delay Fuse | 200 | 110 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501044 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501044 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501044 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 600 | 3 | 75 | 77 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501044 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501045 | A | DS | Square D | KHL36000M | - | 250 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501045 |  | FB | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501045 |  | F | Any | Class J or R Time Delay Fuse | 200 | 150 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501045 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501045 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501045 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 600 | 3 | 100 | 99 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501045 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501046 | A | DS | Square D | KHL36000M | - | 250 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501046 |  | FB | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501046 |  | F | Any | Class J or R Time Delay Fuse | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501046 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501046 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501046 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 600 | 3 | 125 | 125 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501046 |  | OLR | Telemecanique | LR9F5369 | 5 | 90 - 150 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501047 | A | DS | Square D | JLL36000S25 | - | 250 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501047 |  | FB | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501047 |  | F | Any | Class J or R Time Delay Fuse | 200 | 110 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501047 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501047 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501047 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 600 | 3 | 75 | 77 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501047 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 100 | 600 | 3 | 75 | 77 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501048 | A | DS | Square D | JLL36000S25 | - | 250 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501048 |  | FB | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501048 |  | F | Any | Class J or R Time Delay Fuse | 200 | 150 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501048 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501048 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501048 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 600 | 3 | 100 | 99 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501048 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 600 | 3 | 100 | 99 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501049 | A | DS | Square D | JLL36000S25 | - | 250 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501049 |  | FB | Any | Listed Fuse Holder | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501049 |  | F | Any | Class J or R Time Delay Fuse | 200 | 200 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501049 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501049 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501049 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 600 | 3 | 125 | 125 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501049 |  | OLR | Telemecanique | LR9F5369 | 5 | 90 - 150 | 600 | 3 | 100 | 600 | 3 | 125 | 125 | 8689 | 1, 5, 7p | E40610 V12 S16
SE501050 | A | DS | Square D | MHL360008M | - | 800 | 600 | 3 | 100 | 240 | 3 | 200 | 480 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501050 |  | FB | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 240 | 3 | 200 | 480 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501050 |  | F | Any | Class J or R Time Delay Fuse | 200 | 600 | 600 | 3 | 100 | 240 | 3 | 200 | 480 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501050 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 240 | 3 | 200 | 480 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501050 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 240 | 3 | 200 | 480 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501050 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 100 | 240 | 3 | 200 | 480 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501050 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 100 | 240 | 3 | 200 | 480 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501051 | A | DS | Square D | MHL360008M | - | 800 | 600 | 3 | 100 | 480 | 3 | 400 | 477 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501051 |  | FB | Any | Listed Fuse Holder | 200 | 600 | 600 | 3 | 100 | 480 | 3 | 400 | 477 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501051 |  | F | Any | Class J or R Time Delay Fuse | 200 | 600 | 600 | 3 | 100 | 480 | 3 | 400 | 477 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501051 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 480 | 3 | 400 | 477 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501051 |  | MC | Telemecanique | LC1F500 | 18 | 500 | 600 | 3 | 100 | 480 | 3 | 400 | 477 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501051 |  | INTERLOCK | Telemecanique | LA9FJ970 or LA9FK4K | NA | NA | NA | NA | 100 | 480 | 3 | 400 | 477 | 24674 | 1, 5, 7j | E40610 V12 S16
SE501051 |  | OLR | Telemecanique | LR9F7379 | 5 | 300 - 500 | 600 | 3 | 100 | 480 | 3 | 400 | 477 | 24674 | 1, 5, 7j | E40610 V12 S16