## Module C - Type D (IEC)
Last Revised: 2006-04-25
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu ft) | Conditions of Acceptability | Combination UL File | Other UL File References
SE301010 | D | ICB | Square D | GJL36007M02 | - | 7 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
SE301020 | D | ICB | Square D | GJL36007M02 | - | 7 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
SE301030 | D | ICB | Square D | GJL36007M02 | - | 7 | 600 | 3 | 65 | 480 | 3 | 3 | 4.8 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
SE301040 | D | ICB | Square D | GJL36007M02 | - | 7 | 600 | 3 | 25 | 600Y/347 | 3 | 5 | 6.1 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
SE301050 | D | ICB | Square D | GJL36015M03 | - | 15 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
SE301060 | D | ICB | Square D | GJL36015M03 | - | 15 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
SE301070 | D | ICB | Square D | GJL36015M03 | - | 15 | 600 | 3 | 65 | 480 | 3 | 5 | 7.6 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
SE301080 | D | ICB | Square D | GJL36015M03 | - | 15 | 600 | 3 | 25 | 600Y/347 | 3 | 7.5 | 9 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
SE301130 | D | ICB | Square D | GJL36007M02 | - | 7 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
SE301140 | D | ICB | Square D | GJL36007M02 | - | 7 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
SE301150 | D | ICB | Square D | GJL36007M02 | - | 7 | 600 | 3 | 65 | 480 | 3 | 3 | 4.8 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
SE301160 | D | ICB | Square D | GJL36007M02 | - | 7 | 600 | 3 | 25 | 600Y/347 | 3 | 5 | 6.1 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
SE301170 | D | ICB | Square D | GJL36015M03 | - | 15 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
SE301180 | D | ICB | Square D | GJL36015M03 | - | 15 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
SE301190 | D | ICB | Square D | GJL36015M03 | - | 15 | 600 | 3 | 65 | 480 | 3 | 5 | 7.6 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
SE301200 | D | ICB | Square D | GJL36015M03 | - | 15 | 600 | 3 | 25 | 600Y/347 | 3 | 7.5 | 9 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
SE301210 | D | ICB | Square D | GJL36015M03 | - | 15 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
SE301220 | D | ICB | Square D | GJL36015M03 | - | 15 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
SE301230 | D | ICB | Square D | GJL36015M03 | - | 15 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
SE301240 | D | ICB | Square D | GJL36015M03 | - | 15 | 600 | 3 | 25 | 600Y/347 | 3 | 10 | 11 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
SE301250 | D | ICB | Square D | GJL36015M03 | - | 15 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
SE301260 | D | ICB | Square D | GJL36015M03 | - | 15 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
SE301270 | D | ICB | Square D | GJL36015M03 | - | 15 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
SE301280 | D | ICB | Square D | GJL36015M03 | - | 15 | 600 | 3 | 25 | 600Y/347 | 3 | 10 | 11 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
SE301290 | D | ICB | Square D | GJL36030M04 | - | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
SE301300 | D | ICB | Square D | GJL36030M04 | - | 30 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
SE301310 | D | ICB | Square D | GJL36030M04 | - | 30 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
SE301320 | D | ICB | Square D | GJL36030M04 | - | 30 | 600 | 3 | 25 | 600Y/347 | 3 | 15 | 17 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
SE301330 | D | ICB | Square D | GJL36030M04 | - | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
SE301340 | D | ICB | Square D | GJL36030M04 | - | 30 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
SE301350 | D | ICB | Square D | GJL36030M04 | - | 30 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
SE301360 | D | ICB | Square D | GJL36030M04 | - | 30 | 600 | 3 | 25 | 600Y/347 | 3 | 15 | 17 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
SE301370 | D | ICB | Square D | GJL36030M04 | - | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
SE301380 | D | ICB | Square D | GJL36030M04 | - | 30 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
SE301390 | D | ICB | Square D | GJL36030M04 | - | 30 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
SE301400 | D | ICB | Square D | GJL36030M04 | - | 30 | 600 | 3 | 25 | 600Y/347 | 3 | 20 | 22 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
SE301410 | D | ICB | Square D | GJL36030M04 | - | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
SE301420 | D | ICB | Square D | GJL36030M04 | - | 30 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
SE301430 | D | ICB | Square D | GJL36030M04 | - | 30 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
SE301440 | D | ICB | Square D | GJL36030M04 | - | 30 | 600 | 3 | 25 | 600Y/347 | 3 | 20 | 22 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
SE301450 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 0.766 | 1(0.766), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3
|  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD1530 | 5 | 23 - 28 | 600 | 3
SE301460 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 0.766 | 1(0.766), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3
|  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD1530 | 5 | 23 - 28 | 600 | 3
|  | OLR | Telemecanique | LRD1532 | 5 | 25 - 32 | 600 | 3
SE301470 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 0.766 | 1(0.766), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3
|  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD1530 | 5 | 23 - 28 | 600 | 3
|  | OLR | Telemecanique | LRD1532 | 5 | 25 - 32 | 600 | 3
SE301480 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 25 | 600Y/347 | 3 | 25 | 27 | 0.766 | 1(0.766), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3
|  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD1530 | 5 | 23 - 28 | 600 | 3
|  | OLR | Telemecanique | LRD1532 | 5 | 25 - 32 | 600 | 3
SE301490 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 0.766 | 1(0.766), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3
|  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD1530 | 5 | 23 - 28 | 600 | 3
SE301500 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 0.766 | 1(0.766), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3
|  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD1530 | 5 | 23 - 28 | 600 | 3
|  | OLR | Telemecanique | LRD1532 | 5 | 25 - 32 | 600 | 3
SE301510 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 0.766 | 1(0.766), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3
|  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD1530 | 5 | 23 - 28 | 600 | 3
|  | OLR | Telemecanique | LRD1532 | 5 | 25 - 32 | 600 | 3
SE301520 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 25 | 600Y/347 | 3 | 25 | 27 | 0.766 | 1(0.766), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3
|  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD1530 | 5 | 23 - 28 | 600 | 3
|  | OLR | Telemecanique | LRD1532 | 5 | 25 - 32 | 600 | 3
SE301530 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 0.766 | 1(0.766), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3
|  | OLR | Telemecanique | LRD3322 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3
|  | OLR | Telemecanique | LR2D3522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3
SE301540 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 0.766 | 1(0.766), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3
|  | OLR | Telemecanique | LRD3322 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LR2D3522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3
SE301550 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 0.766 | 1(0.766), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3
|  | OLR | Telemecanique | LRD3322 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3
|  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3
|  | OLR | Telemecanique | LR2D3522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3
SE301560 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 25 | 600Y/347 | 3 | 30 | 32 | 0.766 | 1(0.766), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3
|  | OLR | Telemecanique | LRD3322 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3
|  | OLR | Telemecanique | LR2D3522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3
SE301570 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 0.766 | 1(0.766), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3
|  | OLR | Telemecanique | LRD3322 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3
|  | OLR | Telemecanique | LR2D3522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3
SE301580 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 0.766 | 1(0.766), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3
|  | OLR | Telemecanique | LRD3322 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LR2D3522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3
SE301590 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 0.766 | 1(0.766), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3
|  | OLR | Telemecanique | LRD3322 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3
|  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3
|  | OLR | Telemecanique | LR2D3522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3
SE301600 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 25 | 600Y/347 | 3 | 30 | 32 | 0.766 | 1(0.766), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3
|  | OLR | Telemecanique | LRD3322 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3
|  | OLR | Telemecanique | LR2D3522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3
SE301610 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 65 | 208 | 3 | 15 | 46.2 | 0.766 | 1(0.766), 5 | E169932 V1 S6
|  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3
|  | OLR | Telemecanique | LRD3322 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3
|  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3
|  | OLR | Telemecanique | LR2D3522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3
|  | OLR | Telemecanique | LR2D3557 | 5 | 37 - 50 | 600 | 3
SE301620 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 4.58 | 1(4.580), 5 | E169932 V1 S6
|  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3
|  | OLR | Telemecanique | LRD3322 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3
|  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3
|  | OLR | Telemecanique | LR2D3522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3
|  | OLR | Telemecanique | LR2D3557 | 5 | 37 - 50 | 600 | 3
SE301630 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 4.58 | 1(4.580), 5 | E169932 V1 S6
|  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3
|  | OLR | Telemecanique | LRD3322 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3
|  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3
|  | OLR | Telemecanique | LR2D3522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3
|  | OLR | Telemecanique | LR2D3557 | 5 | 37 - 50 | 600 | 3
SE301640 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 18 | 600Y/347 | 3 | 40 | 41 | 4.58 | 1(4.580), 5 | E169932 V1 S6
|  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3
|  | OLR | Telemecanique | LRD3322 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3
|  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3
|  | OLR | Telemecanique | LR2D3522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3
|  | OLR | Telemecanique | LR2D3557 | 5 | 37 - 50 | 600 | 3
SE301650 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 65 | 208 | 3 | 15 | 46.2 | 4.58 | 1(4.580), 5 | E169932 V1 S6
|  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3
|  | OLR | Telemecanique | LRD3322 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3
|  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3
|  | OLR | Telemecanique | LR2D3522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3
|  | OLR | Telemecanique | LR2D3557 | 5 | 37 - 50 | 600 | 3
SE301660 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 4.58 | 1(4.580), 5 | E169932 V1 S6
|  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3
|  | OLR | Telemecanique | LRD3322 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3
|  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3
|  | OLR | Telemecanique | LR2D3522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3
|  | OLR | Telemecanique | LR2D3557 | 5 | 37 - 50 | 600 | 3
SE301670 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 4.58 | 1(4.580), 5 | E169932 V1 S6
|  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3
|  | OLR | Telemecanique | LRD3322 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3
|  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3
|  | OLR | Telemecanique | LR2D3522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3
|  | OLR | Telemecanique | LR2D3557 | 5 | 37 - 50 | 600 | 3
SE301680 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 18 | 600Y/347 | 3 | 40 | 41 | 4.58 | 1(4.580), 5 | E169932 V1 S6
|  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3
|  | OLR | Telemecanique | LRD3322 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3
|  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3
|  | OLR | Telemecanique | LR2D3522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3
|  | OLR | Telemecanique | LR2D3557 | 5 | 37 - 50 | 600 | 3
SE301700 | D | ICB | Square D | GJL36007M02 | - | 7 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
SE301710 | D | ICB | Square D | GJL36015M03 | - | 15 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D09 | 5 | 9 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
SE301730 | D | ICB | Square D | GJL36007M02 | - | 7 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
SE301740 | D | ICB | Square D | GJL36015M03 | - | 15 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D09 | 5 | 9 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
SE301750 | D | ICB | Square D | GJL36015M03 | - | 15 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D12 | 5 | 12 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
SE301760 | D | ICB | Square D | GJL36015M03 | - | 15 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D12 | 5 | 12 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
SE301770 | D | ICB | Square D | GJL36030M04 | - | 30 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
SE301780 | D | ICB | Square D | GJL36030M04 | - | 30 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
SE301790 | D | ICB | Square D | GJL36030M04 | - | 30 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
SE301800 | D | ICB | Square D | GJL36030M04 | - | 30 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
SE301810 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 0.766 | 1(0.766), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3
|  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD1530 | 5 | 23 - 28 | 600 | 3
SE301820 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 0.766 | 1(0.766), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3
|  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1521 | 5 | 12 - 18 | 600 | 3
|  | OLR | Telemecanique | LRD1522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD1530 | 5 | 23 - 28 | 600 | 3
SE301830 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 0.766 | 1(0.766), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3
|  | OLR | Telemecanique | LRD3322 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3
|  | OLR | Telemecanique | LR2D3522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3
SE301840 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 0.766 | 1(0.766), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3
|  | OLR | Telemecanique | LRD3322 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3
|  | OLR | Telemecanique | LR2D3522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3
SE301850 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 65 | 200 | 3 | 15 | 48.3 | 0.766 | 1(0.766), 5 | E169932 V1 S6
|  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3
|  | OLR | Telemecanique | LRD3322 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3
|  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3
|  | OLR | Telemecanique | LR2D3522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3
|  | OLR | Telemecanique | LR2D3557 | 5 | 37 - 50 | 600 | 3
SE301860 | D | ICB | Square D | GJL36050M05 | - | 50 | 600 | 3 | 65 | 200 | 3 | 15 | 48.3 | 4.58 | 1(4.580), 5 | E169932 V1 S6
|  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3
|  | OLR | Telemecanique | LRD3322 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LRD3353 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3
|  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3
|  | OLR | Telemecanique | LR2D3522 | 5 | 17 - 25 | 600 | 3
|  | OLR | Telemecanique | LR2D3553 | 5 | 23 - 32 | 600 | 3
|  | OLR | Telemecanique | LR2D3555 | 5 | 30 - 40 | 600 | 3
|  | OLR | Telemecanique | LR2D3557 | 5 | 37 - 50 | 600 | 3
SE300970 | D | ICB | Square D | GJL36015M03 | - | 15 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
SE300980 | D | ICB | Square D | GJL36015M03 | - | 15 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
SE300990 | D | ICB | Square D | GJL36015M03 | - | 15 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
SE301000 | D | ICB | Square D | GJL36015M03 | - | 15 | 600 | 3 | 25 | 600Y/347 | 3 | 10 | 11 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC1D18 | 5 | 18 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
SE301090 | D | ICB | Square D | GJL36015M03 | - | 15 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
SE301100 | D | ICB | Square D | GJL36015M03 | - | 15 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
SE301110 | D | ICB | Square D | GJL36015M03 | - | 15 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3
SE301120 | D | ICB | Square D | GJL36015M03 | - | 15 | 600 | 3 | 25 | 600Y/347 | 3 | 10 | 11 | 0.474 | 1(0.474), 5 | E163364 V2 S1
|  | MC | Telemecanique | LC2D18 | 5 | 18 | 600 | 3
|  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3
|  | OLR | Telemecanique | LRD1510 | 5 | 4 - 6 | 600 | 3
|  | OLR | Telemecanique | LRD1512 | 5 | 5.5 - 8 | 600 | 3
|  | OLR | Telemecanique | LRD1514 | 5 | 7 - 10 | 600 | 3
|  | OLR | Telemecanique | LRD1516 | 5 | 9 - 13 | 600 | 3