## Size 1
Issued: 2006-11-20
Last Revised: 2015-03-20
|  |  |  | "@" refer to Digest to complete | [8 empty] | Use Square D Digest for selection of Melting Alloy and Bi-Metal Overloads only
starter Catalog number for coil
voltage codes and Form modifications
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Min Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE100066 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 22 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100066 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 22 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100067 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 22 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100067 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 22 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100068 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 22 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100068 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 22 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100069 | C | CB | Square D | FAL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100069 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100070 | C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100070 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100071 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 22 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100071 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 22 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100072 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 22 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100072 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 22 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100073 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 22 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100073 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 22 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100074 | C | CB | Square D | FAL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100074 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100075 | C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100075 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100076 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 22 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100076 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 22 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100077 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 22 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100077 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 22 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100078 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 22 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100078 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 22 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100079 | C | CB | Square D | FAL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100079 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100080 | C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100080 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100081 | C | CB | Square D | FAL36020 | 25 | 20 | 600 | 3 | 22 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100081 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 22 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100082 | C | CB | Square D | FAL36020 | 25 | 20 | 600 | 3 | 22 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100082 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 22 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100083 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 22 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100083 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 22 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100084 | C | CB | Square D | FAL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100084 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100085 | C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100085 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100086 | C | CB | Square D | FAL36020 | 25 | 20 | 600 | 3 | 22 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100086 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 22 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100087 | C | CB | Square D | FAL36020 | 25 | 20 | 600 | 3 | 22 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100087 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 22 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100088 | C | CB | Square D | FAL36020 | 25 | 20 | 600 | 3 | 22 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100088 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 22 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100089 | C | CB | Square D | FAL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100089 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100090 | C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100090 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100091 | C | CB | Square D | FAL36030 | 25 | 30 | 600 | 3 | 22 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100091 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 22 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100092 | C | CB | Square D | FAL36030 | 25 | 30 | 600 | 3 | 22 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100092 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 22 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100093 | C | CB | Square D | FAL36025 | 25 | 25 | 600 | 3 | 22 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100093 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 22 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100094 | C | CB | Square D | FAL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100094 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100095 | C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100095 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100096 | C | CB | Square D | FAL36045 | 25 | 45 | 600 | 3 | 22 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100096 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 22 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100097 | C | CB | Square D | FAL36045 | 25 | 45 | 600 | 3 | 22 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100097 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 22 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100098 | C | CB | Square D | FAL36040 | 25 | 40 | 600 | 3 | 22 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100098 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 22 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100099 | C | CB | Square D | FAL36020 | 18 | 20 | 600 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100099 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100100 | C | CB | Square D | FAL36020 | 14 | 20 | 600 | 3 | 14 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100100 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100101 | C | CB | Square D | FAL36050 | 25 | 50 | 600 | 3 | 22 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100101 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 22 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100102 | C | CB | Square D | FAL36030 | 18 | 30 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100102 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100103 | C | CB | Square D | FAL36025 | 14 | 25 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100103 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100104 | C | CB | Square D | FAL36035 | 18 | 35 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100104 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100105 | C | CB | Square D | FAL36030 | 14 | 30 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100105 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100106 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 22 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100106 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 22 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100107 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 22 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100107 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 22 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100108 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 22 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100108 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 22 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100109 | C | CB | Square D | FAL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100109 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100110 | C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100110 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100111 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 22 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100111 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 22 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100112 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 22 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100112 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 22 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100113 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 22 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100113 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 22 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100114 | C | CB | Square D | FAL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100114 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100115 | C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100115 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100116 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 22 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100116 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 22 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100117 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 22 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100117 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 22 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100118 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 22 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100118 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 22 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100119 | C | CB | Square D | FAL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100119 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100120 | C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100120 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100121 | C | CB | Square D | FAL36020 | 25 | 20 | 600 | 3 | 22 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100121 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 22 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100122 | C | CB | Square D | FAL36020 | 25 | 20 | 600 | 3 | 22 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100122 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 22 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100123 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 22 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100123 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 22 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100124 | C | CB | Square D | FAL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100124 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100125 | C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100125 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100126 | C | CB | Square D | FAL36020 | 25 | 20 | 600 | 3 | 22 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100126 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 22 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100127 | C | CB | Square D | FAL36020 | 25 | 20 | 600 | 3 | 22 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100127 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 22 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100128 | C | CB | Square D | FAL36020 | 25 | 20 | 600 | 3 | 22 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100128 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 22 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100129 | C | CB | Square D | FAL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100129 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100130 | C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100130 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100131 | C | CB | Square D | FAL36030 | 25 | 30 | 600 | 3 | 22 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100131 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 22 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100132 | C | CB | Square D | FAL36030 | 25 | 30 | 600 | 3 | 22 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100132 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 22 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100133 | C | CB | Square D | FAL36025 | 25 | 25 | 600 | 3 | 22 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100133 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 22 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100134 | C | CB | Square D | FAL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100134 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100135 | C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100135 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100136 | C | CB | Square D | FAL36045 | 25 | 45 | 600 | 3 | 22 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100136 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 22 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100137 | C | CB | Square D | FAL36045 | 25 | 45 | 600 | 3 | 22 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100137 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 22 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100138 | C | CB | Square D | FAL36040 | 25 | 40 | 600 | 3 | 22 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100138 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 22 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100139 | C | CB | Square D | FAL36020 | 18 | 20 | 600 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100139 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100140 | C | CB | Square D | FAL36020 | 14 | 20 | 600 | 3 | 14 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100140 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100141 | C | CB | Square D | FAL36050 | 25 | 50 | 600 | 3 | 22 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100141 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 22 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100142 | C | CB | Square D | FAL36030 | 18 | 30 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100142 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100143 | C | CB | Square D | FAL36025 | 14 | 25 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100143 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100144 | C | CB | Square D | FAL36035 | 18 | 35 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100144 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100145 | C | CB | Square D | FAL36030 | 14 | 30 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100145 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 7a, 8 | E40610 V12 S1
SE100212 | C | CB | Square D | FAL36030 | 25 | 30 | 600 | 3 | 25 | 200 | 3 | 3 | 11 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100212 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 25 | 200 | 3 | 3 | 11 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100213 | C | CB | Square D | FAL36030 | 25 | 30 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100213 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100214 | C | CB | Square D | FAL36025 | 25 | 25 | 600 | 3 | 25 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100214 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 25 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100215 | C | CB | Square D | FAL36045 | 25 | 45 | 600 | 3 | 25 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100215 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 25 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100216 | C | CB | Square D | FAL36045 | 25 | 45 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100216 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100217 | C | CB | Square D | FAL36040 | 25 | 40 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100217 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100218 | C | CB | Square D | FAL36050 | 25 | 50 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100218 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100219 | C | CB | Square D | FAL36030 | 18 | 30 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100219 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100220 | C | CB | Square D | FAL36035 | 18 | 35 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100220 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100221 | C | CB | Square D | FAL36030 | 25 | 30 | 600 | 3 | 25 | 200 | 3 | 3 | 11 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100221 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 25 | 200 | 3 | 3 | 11 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100222 | C | CB | Square D | FAL36030 | 25 | 30 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100222 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100223 | C | CB | Square D | FAL36025 | 25 | 25 | 600 | 3 | 25 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100223 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 25 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100224 | C | CB | Square D | FAL36045 | 25 | 45 | 600 | 3 | 25 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100224 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 25 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100225 | C | CB | Square D | FAL36045 | 25 | 45 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100225 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100226 | C | CB | Square D | FAL36040 | 25 | 40 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100226 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100227 | C | CB | Square D | FAL36050 | 25 | 50 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100227 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100228 | C | CB | Square D | FAL36030 | 18 | 30 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100228 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100229 | C | CB | Square D | FAL36035 | 18 | 35 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100229 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100230 | C | CB | Square D | FAL36030 | 25 | 30 | 600 | 3 | 25 | 200 | 3 | 3 | 11 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100230 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 25 | 200 | 3 | 3 | 11 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100231 | C | CB | Square D | FAL36030 | 25 | 30 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100231 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100232 | C | CB | Square D | FAL36025 | 25 | 25 | 600 | 3 | 25 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100232 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 25 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100233 | C | CB | Square D | FAL36045 | 25 | 45 | 600 | 3 | 25 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100233 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 25 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100234 | C | CB | Square D | FAL36045 | 25 | 45 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100234 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100235 | C | CB | Square D | FAL36040 | 25 | 40 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100235 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100236 | C | CB | Square D | FAL36050 | 25 | 50 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100236 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100237 | C | CB | Square D | FAL36030 | 18 | 30 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100237 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100238 | C | CB | Square D | FAL36035 | 18 | 35 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100238 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100239 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 25 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100239 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 25 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100240 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 25 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100240 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 25 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100241 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 25 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100241 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 25 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100242 | C | CB | Square D | FAL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100242 |  | STR | Square D | 8536SCO3@B20 | 5 | 0.5 - 2.3 | 600 | 3 | 18 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100243 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 25 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100243 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 25 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100244 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 25 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100244 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 25 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100245 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 25 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100245 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 25 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100246 | C | CB | Square D | FAL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100246 |  | STR | Square D | 8536SCO3@B20 | 5 | 0.5 - 2.3 | 600 | 3 | 18 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100247 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 25 | 200 | 3 | 1 | 4.8 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100247 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 25 | 200 | 3 | 1 | 4.8 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100248 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 25 | 208 | 3 | 1 | 4.6 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100248 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 25 | 208 | 3 | 1 | 4.6 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100249 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 25 | 240 | 3 | 1 | 4.2 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100249 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 25 | 240 | 3 | 1 | 4.2 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100250 | C | CB | Square D | FAL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 1 | 2.1 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100250 |  | STR | Square D | 8536SCO3@B20 | 5 | 0.5 - 2.3 | 600 | 3 | 18 | 480 | 3 | 1 | 2.1 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100251 | C | CB | Square D | FAL36020 | 25 | 20 | 600 | 3 | 25 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100251 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100252 | C | CB | Square D | FAL36020 | 25 | 20 | 600 | 3 | 25 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100252 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100253 | C | CB | Square D | FAL36015 | 25 | 15 | 600 | 3 | 25 | 240 | 3 | 1.5 | 6 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100253 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 240 | 3 | 1.5 | 6 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100254 | C | CB | Square D | FAL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 1.5 | 3 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100254 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 18 | 480 | 3 | 1.5 | 3 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100255 | C | CB | Square D | FAL36020 | 25 | 20 | 600 | 3 | 25 | 200 | 3 | 2 | 7.8 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100255 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 200 | 3 | 2 | 7.8 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100256 | C | CB | Square D | FAL36020 | 25 | 20 | 600 | 3 | 25 | 208 | 3 | 2 | 7.5 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100256 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 208 | 3 | 2 | 7.5 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100257 | C | CB | Square D | FAL36020 | 25 | 20 | 600 | 3 | 25 | 240 | 3 | 2 | 6.8 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100257 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 240 | 3 | 2 | 6.8 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100258 | C | CB | Square D | FAL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 2 | 3.4 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100258 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 18 | 480 | 3 | 2 | 3.4 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100259 | C | CB | Square D | FAL36030 | 25 | 30 | 600 | 3 | 25 | 200 | 3 | 3 | 11 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100259 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 200 | 3 | 3 | 11 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100260 | C | CB | Square D | FAL36030 | 25 | 30 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100260 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100261 | C | CB | Square D | FAL36025 | 25 | 25 | 600 | 3 | 25 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100261 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100262 | C | CB | Square D | FAL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 3 | 4.8 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100262 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 18 | 480 | 3 | 3 | 4.8 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100263 | C | CB | Square D | FAL36045 | 25 | 45 | 600 | 3 | 25 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100263 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100264 | C | CB | Square D | FAL36040 | 25 | 40 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100264 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100265 | C | CB | Square D | FAL36040 | 25 | 40 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100265 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100266 | C | CB | Square D | FAL36020 | 18 | 20 | 600 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100266 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100267 | C | CB | Square D | FAL36050 | 25 | 50 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100267 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100268 | C | CB | Square D | FAL36030 | 18 | 30 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100268 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100269 | C | CB | Square D | FAL36035 | 18 | 35 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100269 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 7a, 8 | E40610 V12 S1
SE100354 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100354 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100355 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100355 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100356 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100356 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100357 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100357 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100358 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100358 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100359 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100359 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100360 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100360 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100361 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100361 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100362 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100362 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100363 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100363 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100364 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100364 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100365 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100365 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100366 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100366 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100367 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100367 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100368 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100368 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100369 | C | CB | Square D | FHL36020 | 65 | 20 | 600 | 3 | 65 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100369 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100370 | C | CB | Square D | FHL36020 | 65 | 20 | 600 | 3 | 65 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100370 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100371 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100371 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100372 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100372 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100373 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100373 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100374 | C | CB | Square D | FHL36020 | 65 | 20 | 600 | 3 | 65 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100374 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100375 | C | CB | Square D | FHL36020 | 65 | 20 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100375 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100376 | C | CB | Square D | FHL36020 | 65 | 20 | 600 | 3 | 65 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100376 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100377 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100377 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100378 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100378 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100379 | C | CB | Square D | FHL36030 | 65 | 30 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100379 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100380 | C | CB | Square D | FHL36030 | 65 | 30 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100380 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100381 | C | CB | Square D | FHL36025 | 65 | 25 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100381 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100382 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100382 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100383 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100383 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100384 | C | CB | Square D | FHL36045 | 65 | 45 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100384 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100385 | C | CB | Square D | FHL36045 | 65 | 45 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100385 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100386 | C | CB | Square D | FHL36040 | 65 | 40 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100386 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100387 | C | CB | Square D | FHL36020 | 25 | 20 | 600 | 3 | 25 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100387 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100388 | C | CB | Square D | FHL36020 | 18 | 20 | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100388 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100389 | C | CB | Square D | FHL36050 | 65 | 50 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100389 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100390 | C | CB | Square D | FHL36030 | 25 | 30 | 600 | 3 | 25 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100390 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100391 | C | CB | Square D | FHL36025 | 18 | 25 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100391 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100392 | C | CB | Square D | FHL36035 | 25 | 35 | 600 | 3 | 25 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100392 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100393 | C | CB | Square D | FHL36030 | 18 | 30 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100393 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100394 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100394 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100395 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100395 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100396 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100396 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100397 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100397 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100398 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100398 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100399 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100399 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100400 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100400 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100401 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100401 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100402 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100402 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100403 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100403 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100404 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100404 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100405 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100405 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100406 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100406 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100407 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100407 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100408 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100408 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100409 | C | CB | Square D | FHL36020 | 65 | 20 | 600 | 3 | 65 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100409 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100410 | C | CB | Square D | FHL36020 | 65 | 20 | 600 | 3 | 65 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100410 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100411 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100411 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100412 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100412 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100413 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100413 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100414 | C | CB | Square D | FHL36020 | 65 | 20 | 600 | 3 | 65 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100414 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100415 | C | CB | Square D | FHL36020 | 65 | 20 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100415 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100416 | C | CB | Square D | FHL36020 | 65 | 20 | 600 | 3 | 65 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100416 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100417 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100417 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100418 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100418 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100419 | C | CB | Square D | FHL36030 | 65 | 30 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100419 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100420 | C | CB | Square D | FHL36030 | 65 | 30 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100420 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100421 | C | CB | Square D | FHL36025 | 65 | 25 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100421 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100422 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100422 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100423 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100423 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100424 | C | CB | Square D | FHL36045 | 65 | 45 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100424 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100425 | C | CB | Square D | FHL36045 | 65 | 45 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100425 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100426 | C | CB | Square D | FHL36040 | 65 | 40 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100426 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100427 | C | CB | Square D | FHL36020 | 25 | 20 | 600 | 3 | 25 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100427 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100428 | C | CB | Square D | FHL36020 | 18 | 20 | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100428 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100429 | C | CB | Square D | FHL36050 | 65 | 50 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100429 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100430 | C | CB | Square D | FHL36030 | 25 | 30 | 600 | 3 | 25 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100430 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100431 | C | CB | Square D | FHL36025 | 18 | 25 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100431 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100432 | C | CB | Square D | FHL36035 | 25 | 35 | 600 | 3 | 25 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100432 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100433 | C | CB | Square D | FHL36030 | 18 | 30 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100433 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE100515 | C | CB | Square D | FHL36030 | 65 | 30 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100515 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100516 | C | CB | Square D | FHL36030 | 65 | 30 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100516 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100517 | C | CB | Square D | FHL36025 | 65 | 25 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100517 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100518 | C | CB | Square D | FHL36045 | 65 | 45 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100518 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100519 | C | CB | Square D | FHL36045 | 65 | 45 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100519 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100520 | C | CB | Square D | FHL36040 | 65 | 40 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100520 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100521 | C | CB | Square D | FHL36050 | 65 | 50 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100521 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100522 | C | CB | Square D | FHL36030 | 25 | 30 | 600 | 3 | 25 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100522 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 25 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100523 | C | CB | Square D | FHL36025 | 18 | 25 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100523 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100524 | C | CB | Square D | FHL36035 | 25 | 35 | 600 | 3 | 25 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100524 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 25 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100525 | C | CB | Square D | FHL36030 | 18 | 30 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100525 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100526 | C | CB | Square D | FHL36030 | 65 | 30 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100526 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100527 | C | CB | Square D | FHL36030 | 65 | 30 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100527 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100528 | C | CB | Square D | FHL36025 | 65 | 25 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100528 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100529 | C | CB | Square D | FHL36045 | 65 | 45 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100529 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100530 | C | CB | Square D | FHL36045 | 65 | 45 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100530 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100531 | C | CB | Square D | FHL36040 | 65 | 40 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100531 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100532 | C | CB | Square D | FHL36050 | 65 | 50 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100532 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100533 | C | CB | Square D | FHL36030 | 25 | 30 | 600 | 3 | 25 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100533 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 25 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100534 | C | CB | Square D | FHL36025 | 18 | 25 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100534 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100535 | C | CB | Square D | FHL36035 | 25 | 35 | 600 | 3 | 25 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100535 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 25 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100536 | C | CB | Square D | FHL36030 | 18 | 30 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100536 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100537 | C | CB | Square D | FHL36030 | 65 | 30 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100537 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100538 | C | CB | Square D | FHL36030 | 65 | 30 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100538 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100539 | C | CB | Square D | FHL36025 | 65 | 25 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100539 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100540 | C | CB | Square D | FHL36045 | 65 | 45 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100540 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100541 | C | CB | Square D | FHL36045 | 65 | 45 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100541 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100542 | C | CB | Square D | FHL36040 | 65 | 40 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100542 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100543 | C | CB | Square D | FHL36050 | 65 | 50 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100543 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100544 | C | CB | Square D | FHL36030 | 25 | 30 | 600 | 3 | 25 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100544 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 25 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100545 | C | CB | Square D | FHL36025 | 18 | 25 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100545 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100546 | C | CB | Square D | FHL36035 | 25 | 35 | 600 | 3 | 25 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100546 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 25 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100547 | C | CB | Square D | FHL36030 | 18 | 30 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100547 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100548 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100548 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 65 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100549 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100549 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 65 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100550 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100550 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 65 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100551 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100551 |  | STR | Square D | 8536SCO3@B20 | 5 | 0.5 - 2.3 | 600 | 3 | 25 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100552 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100552 |  | STR | Square D | 8536SCO3@B24 | 5 | 0.5 - 2.3 | 600 | 3 | 18 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100553 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100553 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 65 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100554 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100554 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 65 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100555 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100555 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 65 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100556 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100556 |  | STR | Square D | 8536SCO3@B20 | 5 | 0.5 - 2.3 | 600 | 3 | 25 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100557 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100557 |  | STR | Square D | 8536SCO3@B24 | 5 | 0.5 - 2.3 | 600 | 3 | 18 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100558 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 1 | 4.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100558 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 65 | 200 | 3 | 1 | 4.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100559 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 1 | 4.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100559 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 65 | 208 | 3 | 1 | 4.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100560 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 1 | 4.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100560 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 65 | 240 | 3 | 1 | 4.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100561 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 1 | 2.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100561 |  | STR | Square D | 8536SCO3@B20 | 5 | 0.5 - 2.3 | 600 | 3 | 25 | 480 | 3 | 1 | 2.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100562 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 1 | 1.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100562 |  | STR | Square D | 8536SCO3@B24 | 5 | 0.5 - 2.3 | 600 | 3 | 18 | 600 | 3 | 1 | 1.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100563 | C | CB | Square D | FHL36020 | 65 | 20 | 600 | 3 | 65 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100563 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100564 | C | CB | Square D | FHL36020 | 65 | 20 | 600 | 3 | 65 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100564 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100565 | C | CB | Square D | FHL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 1.5 | 6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100565 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 240 | 3 | 1.5 | 6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100566 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 1.5 | 3 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100566 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 25 | 480 | 3 | 1.5 | 3 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100567 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100567 |  | STR | Square D | 8536SCO3@B34 | 5 | 2 - 9 | 600 | 3 | 18 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100568 | C | CB | Square D | FHL36020 | 65 | 20 | 600 | 3 | 65 | 200 | 3 | 2 | 7.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100568 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 200 | 3 | 2 | 7.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100569 | C | CB | Square D | FHL36020 | 65 | 20 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100569 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100570 | C | CB | Square D | FHL36020 | 65 | 20 | 600 | 3 | 65 | 240 | 3 | 2 | 6.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100570 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 240 | 3 | 2 | 6.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100571 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 2 | 3.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100571 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 25 | 480 | 3 | 2 | 3.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100572 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100572 |  | STR | Square D | 8536SCO3@B34 | 5 | 2 - 9 | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100573 | C | CB | Square D | FHL36030 | 65 | 30 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100573 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100574 | C | CB | Square D | FHL36030 | 65 | 30 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100574 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100575 | C | CB | Square D | FHL36025 | 65 | 25 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100575 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100576 | C | CB | Square D | FHL36015 | 25 | 15 | 600 | 3 | 25 | 480 | 3 | 3 | 4.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100576 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 25 | 480 | 3 | 3 | 4.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100577 | C | CB | Square D | FHL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 3 | 3.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100577 |  | STR | Square D | 8536SCO3@B34 | 5 | 2 - 9 | 600 | 3 | 18 | 600 | 3 | 3 | 3.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100578 | C | CB | Square D | FHL36045 | 65 | 45 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100578 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100579 | C | CB | Square D | FHL36040 | 65 | 40 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100579 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100580 | C | CB | Square D | FHL36040 | 65 | 40 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100580 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100581 | C | CB | Square D | FHL36020 | 25 | 20 | 600 | 3 | 25 | 480 | 3 | 5 | 7.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100581 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 480 | 3 | 5 | 7.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100582 | C | CB | Square D | FHL36020 | 18 | 20 | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100582 |  | STR | Square D | 8536SCO3@B34 | 5 | 2 - 9 | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100583 | C | CB | Square D | FHL36050 | 65 | 50 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100583 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100584 | C | CB | Square D | FHL36030 | 25 | 30 | 600 | 3 | 25 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100584 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100585 | C | CB | Square D | FHL36025 | 18 | 25 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100585 |  | STR | Square D | 8536SCO3@B44 | 5 | 6 - 27 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100586 | C | CB | Square D | FHL36035 | 25 | 35 | 600 | 3 | 25 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100586 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100587 | C | CB | Square D | FHL36030 | 18 | 30 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE100587 |  | STR | Square D | 8536SCO3@B44 | 5 | 6 - 27 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = Use wire ties evenly spaced apart to secure conductors in place.
(7) = See Table 7 for minimum internal wiring between load side of short circuit protective device & line side of starter.
(8) = "@" refer to digest to complete contactor Catalog number for coil voltage and Form modifications.
(9) = Insulator to be provided underneath starter. (QMFZ2), Fastex, Type Formex GK-30, 1/32 inch minimum thickness by 4 inches x 5.7 inches.
Table 7 - Minimum Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
|  | Wire Code |  | Wire Size
|  | 7a |  | 12 AWG
|  | 7b |  | 8 AWG
|  | 7c |  | 2 AWG
|  | 7d |  | 1 AWG
|  | 7e |  | 250 MCM
|  | 7f |  | 300 MCM
|  | 7g |  | (2) 250 MCM

## Size 2
Issued: 2006-12-06
Last Revised: 2015-03-20
|  |  |  | "@" refer to Digest to complete | [8 empty] | Use Square D Digest for selection of Melting Alloy and Bi-Metal Overloads only
starter Catalog number for coil
voltage codes and Form modifications
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Min Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE100650 | C | CB | Square D | FAL36080 | 25 | 80 | 600 | 3 | 22 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100650 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 22 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100651 | C | CB | Square D | FAL36080 | 25 | 80 | 600 | 3 | 22 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100651 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 22 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100652 | C | CB | Square D | FAL36070 | 25 | 70 | 600 | 3 | 22 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100652 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 22 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100653 | C | CB | Square D | FAL36100 | 25 | 100 | 600 | 3 | 22 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100653 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 22 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100654 | C | CB | Square D | FAL36050 | 18 | 50 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100654 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100655 | C | CB | Square D | FAL36045 | 14 | 45 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100655 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100656 | C | CB | Square D | FAL36070 | 18 | 70 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100656 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100657 | C | CB | Square D | FAL36060 | 14 | 60 | 600 | 3 | 14 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100657 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 14 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100658 | C | CB | Square D | FAL36090 | 18 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100658 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100659 | C | CB | Square D | FAL36070 | 14 | 70 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100659 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100660 | C | CB | Square D | FAL36080 | 25 | 80 | 600 | 3 | 22 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100660 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 22 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100661 | C | CB | Square D | FAL36080 | 25 | 80 | 600 | 3 | 22 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100661 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 22 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100662 | C | CB | Square D | FAL36070 | 25 | 70 | 600 | 3 | 22 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100662 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 22 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100663 | C | CB | Square D | FAL36100 | 25 | 100 | 600 | 3 | 22 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100663 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 22 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100664 | C | CB | Square D | FAL36050 | 18 | 50 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100664 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100665 | C | CB | Square D | FAL36045 | 14 | 45 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100665 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100666 | C | CB | Square D | FAL36070 | 18 | 70 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100666 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100667 | C | CB | Square D | FAL36060 | 14 | 60 | 600 | 3 | 14 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100667 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 14 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100668 | C | CB | Square D | FAL36090 | 18 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100668 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100669 | C | CB | Square D | FAL36070 | 14 | 70 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100669 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 7b, 8, 9 | E40610 V12 S1
SE100698 | C | CB | Square D | FAL36080 | 25 | 80 | 600 | 3 | 25 | 200 | 3 | 10 | 32.2 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100698 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 25 | 200 | 3 | 10 | 32.2 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100699 | C | CB | Square D | FAL36080 | 25 | 80 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100699 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100700 | C | CB | Square D | FAL36070 | 25 | 70 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100700 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100701 | C | CB | Square D | FAL36100 | 25 | 100 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100701 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100702 | C | CB | Square D | FAL36050 | 18 | 50 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100702 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100703 | C | CB | Square D | FAL36070 | 18 | 70 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100703 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100704 | C | CB | Square D | FAL36090 | 18 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100704 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100705 | C | CB | Square D | FAL36080 | 25 | 80 | 600 | 3 | 25 | 200 | 3 | 10 | 32.2 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100705 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 25 | 200 | 3 | 10 | 32.2 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100706 | C | CB | Square D | FAL36080 | 25 | 80 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100706 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100707 | C | CB | Square D | FAL36070 | 25 | 70 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100707 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100708 | C | CB | Square D | FAL36100 | 25 | 100 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100708 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100709 | C | CB | Square D | FAL36050 | 18 | 50 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100709 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100710 | C | CB | Square D | FAL36070 | 18 | 70 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100710 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100711 | C | CB | Square D | FAL36090 | 18 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100711 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100712 | C | CB | Square D | FAL36080 | 25 | 80 | 600 | 3 | 25 | 200 | 3 | 10 | 32.2 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100712 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 25 | 200 | 3 | 10 | 32.2 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100713 | C | CB | Square D | FAL36080 | 25 | 80 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100713 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100714 | C | CB | Square D | FAL36070 | 25 | 70 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100714 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100715 | C | CB | Square D | FAL36100 | 25 | 100 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100715 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100716 | C | CB | Square D | FAL36050 | 18 | 50 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100716 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100717 | C | CB | Square D | FAL36070 | 18 | 70 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100717 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100718 | C | CB | Square D | FAL36090 | 18 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100718 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100719 | C | CB | Square D | FAL36080 | 25 | 80 | 600 | 3 | 25 | 200 | 3 | 10 | 32.2 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100719 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 25 | 200 | 3 | 10 | 32.2 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100720 | C | CB | Square D | FAL36080 | 25 | 80 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100720 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100721 | C | CB | Square D | FAL36070 | 25 | 70 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100721 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100722 | C | CB | Square D | FAL36100 | 25 | 100 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100722 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100723 | C | CB | Square D | FAL36050 | 18 | 50 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100723 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100724 | C | CB | Square D | FAL36070 | 18 | 70 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100724 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100725 | C | CB | Square D | FAL36090 | 18 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100725 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 1832 | 1, 7b, 8, 9 | E40610 V12 S1
SE100746 | C | CB | Square D | FHL36080 | 65 | 80 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100746 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100747 | C | CB | Square D | FHL36080 | 65 | 80 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100747 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100748 | C | CB | Square D | FHL36070 | 65 | 70 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100748 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100749 | C | CB | Square D | FHL36100 | 65 | 100 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100749 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100750 | C | CB | Square D | FHL36050 | 25 | 50 | 600 | 3 | 25 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100750 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 25 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100751 | C | CB | Square D | FHL36045 | 18 | 45 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100751 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100752 | C | CB | Square D | FHL36070 | 25 | 70 | 600 | 3 | 25 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100752 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 25 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100753 | C | CB | Square D | FHL36060 | 18 | 60 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100753 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100754 | C | CB | Square D | FHL36090 | 25 | 90 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100754 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100755 | C | CB | Square D | FHL36070 | 18 | 70 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100755 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100756 | C | CB | Square D | FHL36080 | 65 | 80 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100756 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100757 | C | CB | Square D | FHL36080 | 65 | 80 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100757 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100758 | C | CB | Square D | FHL36070 | 65 | 70 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100758 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100759 | C | CB | Square D | FHL36100 | 65 | 100 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100759 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100760 | C | CB | Square D | FHL36050 | 25 | 50 | 600 | 3 | 25 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100760 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 25 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100761 | C | CB | Square D | FHL36045 | 18 | 45 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100761 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100762 | C | CB | Square D | FHL36070 | 25 | 70 | 600 | 3 | 25 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100762 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 25 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100763 | C | CB | Square D | FHL36060 | 18 | 60 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100763 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100764 | C | CB | Square D | FHL36090 | 25 | 90 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100764 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100765 | C | CB | Square D | FHL36070 | 18 | 70 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100765 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE100806 | C | CB | Square D | FHL36080 | 65 | 80 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100806 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100807 | C | CB | Square D | FHL36080 | 65 | 80 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100807 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100808 | C | CB | Square D | FHL36070 | 65 | 70 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100808 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100809 | C | CB | Square D | FHL36100 | 65 | 100 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100809 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100810 | C | CB | Square D | FHL36050 | 25 | 50 | 600 | 3 | 25 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100810 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 25 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100811 | C | CB | Square D | FHL36045 | 18 | 45 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100811 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100812 | C | CB | Square D | FHL36070 | 25 | 70 | 600 | 3 | 25 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100812 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 25 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100813 | C | CB | Square D | FHL36060 | 18 | 60 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100813 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100814 | C | CB | Square D | FHL36090 | 25 | 90 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100814 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100815 | C | CB | Square D | FHL36070 | 18 | 70 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100815 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100816 | C | CB | Square D | FHL36080 | 65 | 80 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100816 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100817 | C | CB | Square D | FHL36080 | 65 | 80 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100817 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100818 | C | CB | Square D | FHL36070 | 65 | 70 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100818 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100819 | C | CB | Square D | FHL36100 | 65 | 100 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100819 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100820 | C | CB | Square D | FHL36050 | 25 | 50 | 600 | 3 | 25 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100820 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 25 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100821 | C | CB | Square D | FHL36045 | 18 | 45 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100821 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100822 | C | CB | Square D | FHL36070 | 25 | 70 | 600 | 3 | 25 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100822 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 25 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100823 | C | CB | Square D | FHL36060 | 18 | 60 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100823 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100824 | C | CB | Square D | FHL36090 | 25 | 90 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100824 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100825 | C | CB | Square D | FHL36070 | 18 | 70 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100825 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100826 | C | CB | Square D | FHL36080 | 65 | 80 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100826 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100827 | C | CB | Square D | FHL36080 | 65 | 80 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100827 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100828 | C | CB | Square D | FHL36070 | 65 | 70 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100828 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100829 | C | CB | Square D | FHL36100 | 65 | 100 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100829 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100830 | C | CB | Square D | FHL36050 | 25 | 50 | 600 | 3 | 25 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100830 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 25 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100831 | C | CB | Square D | FHL36045 | 18 | 45 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100831 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100832 | C | CB | Square D | FHL36070 | 25 | 70 | 600 | 3 | 25 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100832 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 25 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100833 | C | CB | Square D | FHL36060 | 18 | 60 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100833 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100834 | C | CB | Square D | FHL36090 | 25 | 90 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100834 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100835 | C | CB | Square D | FHL36070 | 18 | 70 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100835 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100836 | C | CB | Square D | FHL36080 | 65 | 80 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100836 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100837 | C | CB | Square D | FHL36080 | 65 | 80 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100837 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100838 | C | CB | Square D | FHL36070 | 65 | 70 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100838 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100839 | C | CB | Square D | FHL36100 | 65 | 100 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100839 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100840 | C | CB | Square D | FHL36050 | 25 | 50 | 600 | 3 | 25 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100840 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 25 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100841 | C | CB | Square D | FHL36045 | 18 | 45 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100841 |  | STR | Square D | 8536SDO1@B54 | 5 | 10 - 45 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100842 | C | CB | Square D | FHL36070 | 25 | 70 | 600 | 3 | 25 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100842 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 25 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100843 | C | CB | Square D | FHL36060 | 18 | 60 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100843 |  | STR | Square D | 8536SDO1@B54 | 5 | 10 - 45 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100844 | C | CB | Square D | FHL36090 | 25 | 90 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100844 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100845 | C | CB | Square D | FHL36070 | 18 | 70 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE100845 |  | STR | Square D | 8536SDO1@B54 | 5 | 10 - 45 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = Use wire ties evenly spaced apart to secure conductors in place.
(7) = See Table 7 for minimum internal wiring between load side of short circuit protective device & line side of starter.
(8) = "@" refer to digest to complete contactor Catalog number for coil voltage and Form modifications.
(9) = Insulator to be provided underneath starter. (QMFZ2), Fastex, Type Formex GK-30, 1/32 inch minimum thickness by 4 inches x 5.7 inches.
Table 7 - Minimum Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
|  | Wire Code |  | Wire Size
|  | 7a |  | 12 AWG
|  | 7b |  | 8 AWG
|  | 7c |  | 2 AWG
|  | 7d |  | 1 AWG
|  | 7e |  | 250 MCM
|  | 7f |  | 300 MCM
|  | 7g |  | (2) 250 MCM

## Size 3
Issued: 2006-12-06
Last Revised: 2015-03-20
|  |  |  | "@" refer to Digest to complete | [8 empty] | Use Square D Digest for selection of Melting Alloy and Bi-Metal Overloads only
starter Catalog number for coil
voltage codes and Form modifications
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Min Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE100924 | C | CB | Square D | FAL36090 | 18 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE100924 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE100925 | C | CB | Square D | FAL36070 | 14 | 70 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE100925 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE100926 | C | CB | Square D | FAL36100 | 18 | 100 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE100926 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE100927 | C | CB | Square D | FAL36080 | 14 | 80 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE100927 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE100928 | C | CB | Square D | FAL36100 | 14 | 100 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE100928 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE100929 | C | CB | Square D | FAL36090 | 18 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE100929 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE100930 | C | CB | Square D | FAL36070 | 14 | 70 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE100930 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE100931 | C | CB | Square D | FAL36100 | 18 | 100 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE100931 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE100932 | C | CB | Square D | FAL36080 | 14 | 80 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE100932 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE100933 | C | CB | Square D | FAL36100 | 14 | 100 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE100933 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE100966 | C | CB | Square D | FAL36090 | 18 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE100966 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE100967 | C | CB | Square D | FAL36100 | 18 | 100 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE100967 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE100968 | C | CB | Square D | FAL36090 | 18 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE100968 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE100969 | C | CB | Square D | FAL36100 | 18 | 100 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE100969 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE100970 | C | CB | Square D | FAL36090 | 18 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE100970 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE100971 | C | CB | Square D | FAL36100 | 18 | 100 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE100971 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE100972 | C | CB | Square D | FAL36090 | 18 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE100972 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE100973 | C | CB | Square D | FAL36100 | 18 | 100 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE100973 |  | STR | Square D | 8536SEO1@B60 | 5 | 20 - 90 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE100998 | C | CB | Square D | FHL36090 | 25 | 90 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE100998 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE100999 | C | CB | Square D | FHL36070 | 18 | 70 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE100999 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE101000 | C | CB | Square D | FHL36100 | 25 | 100 | 600 | 3 | 25 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE101000 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 25 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE101001 | C | CB | Square D | FHL36080 | 18 | 80 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE101001 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE101002 | C | CB | Square D | FHL36100 | 18 | 100 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE101002 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE101003 | C | CB | Square D | FHL36090 | 25 | 90 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE101003 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE101004 | C | CB | Square D | FHL36070 | 18 | 70 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE101004 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE101005 | C | CB | Square D | FHL36100 | 25 | 100 | 600 | 3 | 25 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE101005 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 25 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE101006 | C | CB | Square D | FHL36080 | 18 | 80 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE101006 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE101007 | C | CB | Square D | FHL36100 | 18 | 100 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE101007 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE101056 | C | CB | Square D | FHL36090 | 25 | 90 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101056 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101057 | C | CB | Square D | FHL36070 | 18 | 70 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101057 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101058 | C | CB | Square D | FHL36100 | 25 | 100 | 600 | 3 | 25 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101058 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 25 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101059 | C | CB | Square D | FHL36080 | 18 | 80 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101059 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101060 | C | CB | Square D | FHL36100 | 18 | 100 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101060 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101061 | C | CB | Square D | FHL36090 | 25 | 90 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101061 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101062 | C | CB | Square D | FHL36070 | 18 | 70 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101062 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101063 | C | CB | Square D | FHL36100 | 25 | 100 | 600 | 3 | 25 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101063 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 25 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101064 | C | CB | Square D | FHL36080 | 18 | 80 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101064 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101065 | C | CB | Square D | FHL36100 | 18 | 100 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101065 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101066 | C | CB | Square D | FHL36090 | 25 | 90 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101066 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101067 | C | CB | Square D | FHL36070 | 18 | 70 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101067 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101068 | C | CB | Square D | FHL36100 | 25 | 100 | 600 | 3 | 25 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101068 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 25 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101069 | C | CB | Square D | FHL36080 | 18 | 80 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101069 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101070 | C | CB | Square D | FHL36100 | 18 | 100 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101070 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101071 | C | CB | Square D | FHL36090 | 25 | 90 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101071 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 25 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101072 | C | CB | Square D | FHL36070 | 18 | 70 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101072 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101073 | C | CB | Square D | FHL36100 | 25 | 100 | 600 | 3 | 25 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101073 |  | STR | Square D | 8536SEO1@B60 | 5 | 20 - 90 | 600 | 3 | 25 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101074 | C | CB | Square D | FHL36080 | 18 | 80 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101074 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101075 | C | CB | Square D | FHL36100 | 18 | 100 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE101075 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = Use wire ties evenly spaced apart to secure conductors in place.
(7) = See Table 7 for minimum internal wiring between load side of short circuit protective device & line side of starter.
(8) = "@" refer to digest to complete contactor Catalog number for coil voltage and Form modifications.
(9) = Insulator to be provided underneath starter. (QMFZ2), Fastex, Type Formex GK-30, 1/32 inch minimum thickness by 4 inches x 5.7 inches.
Table 7 - Minimum Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
|  | Wire Code |  | Wire Size
|  | 7a |  | 12 AWG
|  | 7b |  | 8 AWG
|  | 7c |  | 2 AWG
|  | 7d |  | 1 AWG
|  | 7e |  | 250 MCM
|  | 7f |  | 300 MCM
|  | 7g |  | (2) 250 MCM

## Size 4
Issued: 2007-02-01
Last Revised: 2015-03-20
|  |  |  | "@" refer to Digest to complete | [8 empty] | Use Square D Digest for selection of Melting Alloy and Bi-Metal Overloads only
starter Catalog number for coil
voltage codes and Form modifications
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Min Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE101128 | C | CB | Square D | KAL36100 | 25 | 100 | 600 | 3 | 25 | 480 | 3 | 30 | 40 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101128 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 25 | 480 | 3 | 30 | 40 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101129 | C | CB | Square D | KAL36080 | 22 | 80 | 600 | 3 | 22 | 600 | 3 | 30 | 32 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101129 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 22 | 600 | 3 | 30 | 32 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101130 | C | CB | Square D | KAL36150 | 25 | 150 | 600 | 3 | 25 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101130 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 25 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101131 | C | CB | Square D | KAL36100 | 22 | 100 | 600 | 3 | 22 | 600 | 3 | 40 | 41 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101131 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 22 | 600 | 3 | 40 | 41 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101132 | C | CB | Square D | KAL36150 | 22 | 150 | 600 | 3 | 22 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101132 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 22 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101133 | C | CB | Square D | KAL36150 | 22 | 150 | 600 | 3 | 22 | 600 | 3 | 60 | 62 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101133 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 22 | 600 | 3 | 60 | 62 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101134 | C | CB | Square D | KAL36100 | 25 | 100 | 600 | 3 | 25 | 480 | 3 | 30 | 40 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101134 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 25 | 480 | 3 | 30 | 40 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101135 | C | CB | Square D | KAL36080 | 22 | 80 | 600 | 3 | 22 | 600 | 3 | 30 | 32 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101135 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 22 | 600 | 3 | 30 | 32 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101136 | C | CB | Square D | KAL36150 | 25 | 150 | 600 | 3 | 25 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101136 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 25 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101137 | C | CB | Square D | KAL36100 | 22 | 100 | 600 | 3 | 22 | 600 | 3 | 40 | 41 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101137 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 22 | 600 | 3 | 40 | 41 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101138 | C | CB | Square D | KAL36150 | 22 | 150 | 600 | 3 | 22 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101138 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 22 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101139 | C | CB | Square D | KAL36150 | 22 | 150 | 600 | 3 | 22 | 600 | 3 | 60 | 62 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101139 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 22 | 600 | 3 | 60 | 62 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101172 | C | CB | Square D | KAL36150 | 25 | 150 | 600 | 3 | 25 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101172 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 25 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101173 | C | CB | Square D | KAL36150 | 22 | 150 | 600 | 3 | 22 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101173 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 22 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101174 | C | CB | Square D | KAL36150 | 22 | 150 | 600 | 3 | 22 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101174 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 22 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101175 | C | CB | Square D | KAL36150 | 25 | 150 | 600 | 3 | 25 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101175 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 25 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101176 | C | CB | Square D | KAL36150 | 22 | 150 | 600 | 3 | 22 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101176 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 22 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101177 | C | CB | Square D | KAL36150 | 22 | 150 | 600 | 3 | 22 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101177 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 22 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101178 | C | CB | Square D | KAL36150 | 25 | 150 | 600 | 3 | 25 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101178 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 25 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101179 | C | CB | Square D | KAL36150 | 22 | 150 | 600 | 3 | 22 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101179 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 22 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101180 | C | CB | Square D | KAL36150 | 22 | 150 | 600 | 3 | 22 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101180 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 22 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101181 | C | CB | Square D | KAL36150 | 25 | 150 | 600 | 3 | 25 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101181 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 25 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101182 | C | CB | Square D | KAL36150 | 22 | 150 | 600 | 3 | 22 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101182 |  | STR | Square D | 8536SFO1@B74 | 10 | 60 - 135 | 600 | 3 | 22 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101183 | C | CB | Square D | KAL36150 | 22 | 150 | 600 | 3 | 22 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101183 |  | STR | Square D | 8536SFO1@B74 | 10 | 60 - 135 | 600 | 3 | 22 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101222 | C | CB | Square D | KHL36080 | 25 | 80 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101222 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101225 | C | CB | Square D | KHL36100 | 25 | 100 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101225 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101227 | C | CB | Square D | KHL36150 | 25 | 150 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101227 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101229 | C | CB | Square D | KHL36150 | 25 | 150 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101229 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101231 | C | CB | Square D | KHL36200 | 25 | 200 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101231 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101232 | C | CB | Square D | KHL36250 | 25 | 250 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101232 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101235 | C | CB | Square D | KHL36080 | 25 | 80 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101235 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101238 | C | CB | Square D | KHL36100 | 25 | 100 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101238 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101240 | C | CB | Square D | KHL36150 | 25 | 150 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101240 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101242 | C | CB | Square D | KHL36150 | 25 | 150 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101242 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101244 | C | CB | Square D | KHL36200 | 25 | 200 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101244 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101245 | C | CB | Square D | KHL36250 | 25 | 250 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101245 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE101308 | C | CB | Square D | KHL36250 | 65 | 250 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101308 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101309 | C | CB | Square D | KHL36250 | 65 | 250 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101309 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101310 | C | CB | Square D | KHL36150 | 35 | 150 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101310 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101311 | C | CB | Square D | KHL36175 | 35 | 175 | 600 | 3 | 35 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101311 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 35 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101312 | C | CB | Square D | KHL36150 | 25 | 150 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101312 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101313 | C | CB | Square D | KHL36200 | 35 | 200 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101313 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101314 | C | CB | Square D | KHL36150 | 25 | 150 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101314 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101315 | C | CB | Square D | KHL36250 | 35 | 250 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101315 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101316 | C | CB | Square D | KHL36200 | 25 | 200 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101316 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101317 | C | CB | Square D | KHL36250 | 25 | 250 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101317 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101318 | C | CB | Square D | KHL36250 | 65 | 250 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101318 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101319 | C | CB | Square D | KHL36250 | 65 | 250 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101319 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101320 | C | CB | Square D | KHL36150 | 35 | 150 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101320 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101321 | C | CB | Square D | KHL36175 | 35 | 175 | 600 | 3 | 35 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101321 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 35 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101322 | C | CB | Square D | KHL36150 | 25 | 150 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101322 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101323 | C | CB | Square D | KHL36200 | 35 | 200 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101323 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101324 | C | CB | Square D | KHL36150 | 25 | 150 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101324 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101325 | C | CB | Square D | KHL36250 | 35 | 250 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101325 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101326 | C | CB | Square D | KHL36200 | 25 | 200 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101326 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101327 | C | CB | Square D | KHL36250 | 25 | 250 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101327 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101328 | C | CB | Square D | KHL36250 | 65 | 250 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101328 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101329 | C | CB | Square D | KHL36250 | 65 | 250 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101329 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101330 | C | CB | Square D | KHL36150 | 35 | 150 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101330 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101331 | C | CB | Square D | KHL36175 | 35 | 175 | 600 | 3 | 35 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101331 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 35 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101332 | C | CB | Square D | KHL36150 | 25 | 150 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101332 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101333 | C | CB | Square D | KHL36200 | 35 | 200 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101333 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101334 | C | CB | Square D | KHL36150 | 25 | 150 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101334 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101335 | C | CB | Square D | KHL36250 | 35 | 250 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101335 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101336 | C | CB | Square D | KHL36200 | 25 | 200 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101336 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101337 | C | CB | Square D | KHL36250 | 25 | 250 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101337 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101338 | C | CB | Square D | KHL36250 | 65 | 250 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101338 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101339 | C | CB | Square D | KHL36250 | 65 | 250 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101339 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101340 | C | CB | Square D | KHL36175 | 35 | 175 | 600 | 3 | 35 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101340 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 35 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101341 | C | CB | Square D | KHL36200 | 35 | 200 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101341 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101342 | C | CB | Square D | KHL36150 | 25 | 150 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101342 |  | STR | Square D | 8536SFO1@B74 | 10 | 60 - 135 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101343 | C | CB | Square D | KHL36250 | 35 | 250 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101343 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101344 | C | CB | Square D | KHL36200 | 25 | 200 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101344 |  | STR | Square D | 8536SFO1@B74 | 10 | 60 - 135 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101345 | C | CB | Square D | KHL36250 | 25 | 250 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE101345 |  | STR | Square D | 8536SFO1@B74 | 10 | 60 - 135 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 7d, 8 | E40610 V12 S1
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = Use wire ties evenly spaced apart to secure conductors in place.
(7) = See Table 7 for minimum internal wiring between load side of short circuit protective device & line side of starter.
(8) = "@" refer to digest to complete contactor Catalog number for coil voltage and Form modifications.
(9) = Insulator to be provided underneath starter. (QMFZ2), Fastex, Type Formex GK-30, 1/32 inch minimum thickness by 4 inches x 5.7 inches.
Table 7 - Minimum Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
|  | Wire Code |  | Wire Size
|  | 7a |  | 12 AWG
|  | 7b |  | 8 AWG
|  | 7c |  | 2 AWG
|  | 7d |  | 1 AWG
|  | 7e |  | 250 MCM
|  | 7f |  | 300 MCM
|  | 7g |  | (2) 250 MCM

## Size 5
Issued: 2008-04-08
Last Revised: 2015-03-20
|  |  |  | "@" refer to Digest to complete | [8 empty] | Use Square D Digest for selection of Melting Alloy and Bi-Metal Overloads only
contactor Catalog number for coil
voltage codes and Form modifications
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Min Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE101388 | D | ICB | Square D | LAL3640035M | - | 400 | 600 | 3 | 42 | 200 | 3 | 75 | 221 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101388 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 42 | 200 | 3 | 75 | 221 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101389 | D | ICB | Square D | LAL3640035M | - | 400 | 600 | 3 | 42 | 208 | 3 | 75 | 211 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101389 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 42 | 208 | 3 | 75 | 211 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101390 | D | ICB | Square D | LAL3640033M | - | 400 | 600 | 3 | 42 | 240 | 3 | 75 | 192 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101390 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 42 | 240 | 3 | 75 | 192 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101391 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 42 | 240 | 3 | 100 | 248 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101391 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 42 | 240 | 3 | 100 | 248 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101392 | D | ICB | Square D | LAL3640030M | - | 400 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101392 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101393 | D | ICB | Square D | LAL3640028M | - | 400 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101393 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101394 | D | ICB | Square D | LAL3640032M | - | 400 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101394 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101395 | D | ICB | Square D | LAL3640030M | - | 400 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101395 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101396 | D | ICB | Square D | LAL3640033M | - | 400 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101396 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101397 | D | ICB | Square D | LAL3640032M | - | 400 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101397 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101398 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101398 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101399 | D | ICB | Square D | LAL3640033M | - | 400 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101399 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101400 | D | ICB | Square D | LAL3640035M | - | 400 | 600 | 3 | 42 | 200 | 3 | 75 | 221 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101400 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 42 | 200 | 3 | 75 | 221 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101401 | D | ICB | Square D | LAL3640035M | - | 400 | 600 | 3 | 42 | 208 | 3 | 75 | 211 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101401 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 42 | 208 | 3 | 75 | 211 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101402 | D | ICB | Square D | LAL3640033M | - | 400 | 600 | 3 | 42 | 240 | 3 | 75 | 192 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101402 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 42 | 240 | 3 | 75 | 192 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101403 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 42 | 240 | 3 | 100 | 248 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101403 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 42 | 240 | 3 | 100 | 248 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101404 | D | ICB | Square D | LAL3640030M | - | 400 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101404 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101405 | D | ICB | Square D | LAL3640028M | - | 400 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101405 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101406 | D | ICB | Square D | LAL3640032M | - | 400 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101406 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101407 | D | ICB | Square D | LAL3640030M | - | 400 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101407 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101408 | D | ICB | Square D | LAL3640033M | - | 400 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101408 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101409 | D | ICB | Square D | LAL3640032M | - | 400 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101409 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101410 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101410 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101411 | D | ICB | Square D | LAL3640033M | - | 400 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101411 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101412 | D | ICB | Square D | LAL3640035M | - | 400 | 600 | 3 | 42 | 200 | 3 | 75 | 221 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101412 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 42 | 200 | 3 | 75 | 221 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101413 | D | ICB | Square D | LAL3640035M | - | 400 | 600 | 3 | 42 | 208 | 3 | 75 | 211 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101413 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 42 | 208 | 3 | 75 | 211 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101414 | D | ICB | Square D | LAL3640033M | - | 400 | 600 | 3 | 42 | 240 | 3 | 75 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101414 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 42 | 240 | 3 | 75 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101415 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 42 | 240 | 3 | 100 | 248 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101415 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 42 | 240 | 3 | 100 | 248 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101416 | D | ICB | Square D | LAL3640030M | - | 400 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101416 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101417 | D | ICB | Square D | LAL3640028M | - | 400 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101417 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101418 | D | ICB | Square D | LAL3640032M | - | 400 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101418 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101419 | D | ICB | Square D | LAL3640030M | - | 400 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101419 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101420 | D | ICB | Square D | LAL3640033M | - | 400 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101420 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101421 | D | ICB | Square D | LAL3640032M | - | 400 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101421 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101422 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101422 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101423 | D | ICB | Square D | LAL3640033M | - | 400 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101423 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101424 | D | ICB | Square D | LAL3640035M | - | 400 | 600 | 3 | 42 | 200 | 3 | 75 | 221 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101424 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 42 | 200 | 3 | 75 | 221 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101425 | D | ICB | Square D | LAL3640035M | - | 400 | 600 | 3 | 42 | 208 | 3 | 75 | 211 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101425 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 42 | 208 | 3 | 75 | 211 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101426 | D | ICB | Square D | LAL3640033M | - | 400 | 600 | 3 | 42 | 240 | 3 | 75 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101426 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 42 | 240 | 3 | 75 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101427 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 42 | 240 | 3 | 100 | 248 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101427 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 42 | 240 | 3 | 100 | 248 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101428 | D | ICB | Square D | LAL3640030M | - | 400 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101428 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101429 | D | ICB | Square D | LAL3640028M | - | 400 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101429 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101430 | D | ICB | Square D | LAL3640032M | - | 400 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101430 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101431 | D | ICB | Square D | LAL3640030M | - | 400 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101431 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101432 | D | ICB | Square D | LAL3640033M | - | 400 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101432 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101433 | D | ICB | Square D | LAL3640032M | - | 400 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101433 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101434 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101434 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101435 | D | ICB | Square D | LAL3640033M | - | 400 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101435 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101436 | D | ICB | Square D | LAL3640035M | - | 400 | 600 | 3 | 42 | 200 | 3 | 75 | 221 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101436 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 42 | 200 | 3 | 75 | 221 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101437 | D | ICB | Square D | LAL3640035M | - | 400 | 600 | 3 | 42 | 208 | 3 | 75 | 211 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101437 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 42 | 208 | 3 | 75 | 211 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101438 | D | ICB | Square D | LAL3640033M | - | 400 | 600 | 3 | 42 | 240 | 3 | 75 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101438 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 42 | 240 | 3 | 75 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101439 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 42 | 240 | 3 | 100 | 248 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101439 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 42 | 240 | 3 | 100 | 248 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101440 | D | ICB | Square D | LAL3640030M | - | 400 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101440 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101441 | D | ICB | Square D | LAL3640028M | - | 400 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101441 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101442 | D | ICB | Square D | LAL3640032M | - | 400 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101442 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101443 | D | ICB | Square D | LAL3640030M | - | 400 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101443 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101444 | D | ICB | Square D | LAL3640033M | - | 400 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101444 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101445 | D | ICB | Square D | LAL3640032M | - | 400 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101445 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101446 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101446 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101447 | D | ICB | Square D | LAL3640033M | - | 400 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101447 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101448 | D | ICB | Square D | LAL3640035M | - | 400 | 600 | 3 | 42 | 200 | 3 | 75 | 221 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101448 |  | STR | Square D | 8536SGO1@B80 | 10 | 120 - 270 | 600 | 3 | 42 | 200 | 3 | 75 | 221 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101449 | D | ICB | Square D | LAL3640035M | - | 400 | 600 | 3 | 42 | 208 | 3 | 75 | 211 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101449 |  | STR | Square D | 8536SGO1@B80 | 10 | 120 - 270 | 600 | 3 | 42 | 208 | 3 | 75 | 211 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101450 | D | ICB | Square D | LAL3640033M | - | 400 | 600 | 3 | 42 | 240 | 3 | 75 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101450 |  | STR | Square D | 8536SGO1@B80 | 10 | 120 - 270 | 600 | 3 | 42 | 240 | 3 | 75 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101451 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 42 | 240 | 3 | 100 | 248 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101451 |  | STR | Square D | 8536SGO1@B80 | 10 | 120 - 270 | 600 | 3 | 42 | 240 | 3 | 100 | 248 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101452 | D | ICB | Square D | LAL3640030M | - | 400 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101452 |  | STR | Square D | 8536SGO1@B80 | 10 | 120 - 270 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101453 | D | ICB | Square D | LAL3640032M | - | 400 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101453 |  | STR | Square D | 8536SGO1@B80 | 10 | 120 - 270 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101454 | D | ICB | Square D | LAL3640030M | - | 400 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101454 |  | STR | Square D | 8536SGO1@B84 | 10 | 120 - 270 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101455 | D | ICB | Square D | LAL3640033M | - | 400 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101455 |  | STR | Square D | 8536SGO1@B80 | 10 | 120 - 270 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101456 | D | ICB | Square D | LAL3640032M | - | 400 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101456 |  | STR | Square D | 8536SGO1@B84 | 10 | 120 - 270 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101457 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101457 |  | STR | Square D | 8536SGO1@B80 | 10 | 120 - 270 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101458 | D | ICB | Square D | LAL3640033M | - | 400 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101458 |  | STR | Square D | 8536SGO1@B84 | 10 | 120 - 270 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101501 | D | ICB | Square D | LHL3640035M | - | 400 | 600 | 3 | 65 | 200 | 3 | 75 | 221 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101501 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 65 | 200 | 3 | 75 | 221 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101502 | D | ICB | Square D | LHL3640035M | - | 400 | 600 | 3 | 65 | 208 | 3 | 75 | 211 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101502 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 65 | 208 | 3 | 75 | 211 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101503 | D | ICB | Square D | LHL3640033M | - | 400 | 600 | 3 | 65 | 240 | 3 | 75 | 192 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101503 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 65 | 240 | 3 | 75 | 192 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101504 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 65 | 240 | 3 | 100 | 248 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101504 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 65 | 240 | 3 | 100 | 248 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101505 | D | ICB | Square D | LHL3640030M | - | 400 | 600 | 3 | 35 | 480 | 3 | 100 | 124 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101505 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 35 | 480 | 3 | 100 | 124 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101506 | D | ICB | Square D | LHL3640028M | - | 400 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101506 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101507 | D | ICB | Square D | LHL3640032M | - | 400 | 600 | 3 | 35 | 480 | 3 | 125 | 156 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101507 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 35 | 480 | 3 | 125 | 156 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101508 | D | ICB | Square D | LHL3640030M | - | 400 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101508 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101509 | D | ICB | Square D | LHL3640033M | - | 400 | 600 | 3 | 35 | 480 | 3 | 150 | 180 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101509 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 35 | 480 | 3 | 150 | 180 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101510 | D | ICB | Square D | LHL3640032M | - | 400 | 600 | 3 | 25 | 600 | 3 | 150 | 144 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101510 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 25 | 600 | 3 | 150 | 144 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101511 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 35 | 480 | 3 | 200 | 240 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101511 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 35 | 480 | 3 | 200 | 240 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101512 | D | ICB | Square D | LHL3640033M | - | 400 | 600 | 3 | 25 | 600 | 3 | 200 | 192 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101512 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 25 | 600 | 3 | 200 | 192 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101513 | D | ICB | Square D | LHL3640035M | - | 400 | 600 | 3 | 65 | 200 | 3 | 75 | 221 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101513 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 65 | 200 | 3 | 75 | 221 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101514 | D | ICB | Square D | LHL3640035M | - | 400 | 600 | 3 | 65 | 208 | 3 | 75 | 211 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101514 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 65 | 208 | 3 | 75 | 211 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101515 | D | ICB | Square D | LHL3640033M | - | 400 | 600 | 3 | 65 | 240 | 3 | 75 | 192 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101515 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 65 | 240 | 3 | 75 | 192 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101516 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 65 | 240 | 3 | 100 | 248 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101516 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 65 | 240 | 3 | 100 | 248 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101517 | D | ICB | Square D | LHL3640030M | - | 400 | 600 | 3 | 35 | 480 | 3 | 100 | 124 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101517 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 35 | 480 | 3 | 100 | 124 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101518 | D | ICB | Square D | LHL3640028M | - | 400 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101518 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101519 | D | ICB | Square D | LHL3640032M | - | 400 | 600 | 3 | 35 | 480 | 3 | 125 | 156 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101519 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 35 | 480 | 3 | 125 | 156 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101520 | D | ICB | Square D | LHL3640030M | - | 400 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101520 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101521 | D | ICB | Square D | LHL3640033M | - | 400 | 600 | 3 | 35 | 480 | 3 | 150 | 180 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101521 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 35 | 480 | 3 | 150 | 180 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101522 | D | ICB | Square D | LHL3640032M | - | 400 | 600 | 3 | 25 | 600 | 3 | 150 | 144 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101522 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 25 | 600 | 3 | 150 | 144 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101523 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 35 | 480 | 3 | 200 | 240 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101523 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 35 | 480 | 3 | 200 | 240 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101524 | D | ICB | Square D | LHL3640033M | - | 400 | 600 | 3 | 25 | 600 | 3 | 200 | 192 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101524 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 25 | 600 | 3 | 200 | 192 | 7325 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101525 | D | ICB | Square D | LHL3640035M | - | 400 | 600 | 3 | 42 | 200 | 3 | 75 | 221 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101525 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 42 | 200 | 3 | 75 | 221 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101526 | D | ICB | Square D | LHL3640035M | - | 400 | 600 | 3 | 42 | 208 | 3 | 75 | 211 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101526 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 42 | 208 | 3 | 75 | 211 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101527 | D | ICB | Square D | LHL3640033M | - | 400 | 600 | 3 | 42 | 240 | 3 | 75 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101527 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 42 | 240 | 3 | 75 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101528 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 42 | 240 | 3 | 100 | 248 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101528 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 42 | 240 | 3 | 100 | 248 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101529 | D | ICB | Square D | LHL3640030M | - | 400 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101529 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101530 | D | ICB | Square D | LHL3640028M | - | 400 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101530 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101531 | D | ICB | Square D | LHL3640032M | - | 400 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101531 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101532 | D | ICB | Square D | LHL3640030M | - | 400 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101532 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101533 | D | ICB | Square D | LHL3640033M | - | 400 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101533 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101534 | D | ICB | Square D | LHL3640032M | - | 400 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101534 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101535 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101535 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101536 | D | ICB | Square D | LHL3640033M | - | 400 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101536 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101537 | D | ICB | Square D | LHL3640035M | - | 400 | 600 | 3 | 42 | 200 | 3 | 75 | 221 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101537 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 42 | 200 | 3 | 75 | 221 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101538 | D | ICB | Square D | LHL3640035M | - | 400 | 600 | 3 | 42 | 208 | 3 | 75 | 211 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101538 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 42 | 208 | 3 | 75 | 211 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101539 | D | ICB | Square D | LHL3640033M | - | 400 | 600 | 3 | 42 | 240 | 3 | 75 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101539 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 42 | 240 | 3 | 75 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101540 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 42 | 240 | 3 | 100 | 248 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101540 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 42 | 240 | 3 | 100 | 248 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101541 | D | ICB | Square D | LHL3640030M | - | 400 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101541 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101542 | D | ICB | Square D | LHL3640028M | - | 400 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101542 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101543 | D | ICB | Square D | LHL3640032M | - | 400 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101543 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101544 | D | ICB | Square D | LHL3640030M | - | 400 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101544 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101545 | D | ICB | Square D | LHL3640033M | - | 400 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101545 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101546 | D | ICB | Square D | LHL3640032M | - | 400 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101546 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101547 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101547 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101548 | D | ICB | Square D | LHL3640033M | - | 400 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101548 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101549 | D | ICB | Square D | LHL3640035M | - | 400 | 600 | 3 | 42 | 200 | 3 | 75 | 221 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101549 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 42 | 200 | 3 | 75 | 221 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101550 | D | ICB | Square D | LHL3640035M | - | 400 | 600 | 3 | 42 | 208 | 3 | 75 | 211 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101550 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 42 | 208 | 3 | 75 | 211 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101551 | D | ICB | Square D | LHL3640033M | - | 400 | 600 | 3 | 42 | 240 | 3 | 75 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101551 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 42 | 240 | 3 | 75 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101552 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 42 | 240 | 3 | 100 | 248 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101552 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 42 | 240 | 3 | 100 | 248 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101553 | D | ICB | Square D | LHL3640030M | - | 400 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101553 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101554 | D | ICB | Square D | LHL3640028M | - | 400 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101554 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101555 | D | ICB | Square D | LHL3640032M | - | 400 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101555 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101556 | D | ICB | Square D | LHL3640030M | - | 400 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101556 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101557 | D | ICB | Square D | LHL3640033M | - | 400 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101557 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101558 | D | ICB | Square D | LHL3640032M | - | 400 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101558 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101559 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101559 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101560 | D | ICB | Square D | LHL3640033M | - | 400 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101560 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101561 | D | ICB | Square D | LHL3640035M | - | 400 | 600 | 3 | 42 | 200 | 3 | 75 | 221 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101561 |  | STR | Square D | 8536SGO1@B80 | 10 | 120 - 270 | 600 | 3 | 42 | 200 | 3 | 75 | 221 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101562 | D | ICB | Square D | LHL3640035M | - | 400 | 600 | 3 | 42 | 208 | 3 | 75 | 211 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101562 |  | STR | Square D | 8536SGO1@B80 | 10 | 120 - 270 | 600 | 3 | 42 | 208 | 3 | 75 | 211 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101563 | D | ICB | Square D | LHL3640033M | - | 400 | 600 | 3 | 42 | 240 | 3 | 75 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101563 |  | STR | Square D | 8536SGO1@B80 | 10 | 120 - 270 | 600 | 3 | 42 | 240 | 3 | 75 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101564 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 42 | 240 | 3 | 100 | 248 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101564 |  | STR | Square D | 8536SGO1@B80 | 10 | 120 - 270 | 600 | 3 | 42 | 240 | 3 | 100 | 248 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101565 | D | ICB | Square D | LHL3640030M | - | 400 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101565 |  | STR | Square D | 8536SGO1@B80 | 10 | 120 - 270 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101566 | D | ICB | Square D | LHL3640032M | - | 400 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101566 |  | STR | Square D | 8536SGO1@B80 | 10 | 120 - 270 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101567 | D | ICB | Square D | LHL3640030M | - | 400 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101567 |  | STR | Square D | 8536SGO1@B84 | 10 | 120 - 270 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101568 | D | ICB | Square D | LHL3640033M | - | 400 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101568 |  | STR | Square D | 8536SGO1@B80 | 10 | 120 - 270 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101569 | D | ICB | Square D | LHL3640032M | - | 400 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101569 |  | STR | Square D | 8536SGO1@B84 | 10 | 120 - 270 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101570 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101570 |  | STR | Square D | 8536SGO1@B80 | 10 | 120 - 270 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101571 | D | ICB | Square D | LHL3640033M | - | 400 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101571 |  | STR | Square D | 8536SGO1@B84 | 10 | 120 - 270 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 7325 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101596 | C | CB | Square D | LAL36250 | 30 | 250 | 600 | 3 | 30 | 480 | 3 | 75 | 96 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101596 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 30 | 480 | 3 | 75 | 96 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101597 | C | CB | Square D | LAL36200 | 22 | 200 | 600 | 3 | 22 | 600 | 3 | 75 | 77 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101597 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 22 | 600 | 3 | 75 | 77 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101598 | C | CB | Square D | LAL36300 | 30 | 300 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101598 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101599 | C | CB | Square D | LAL36250 | 22 | 250 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101599 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101600 | C | CB | Square D | LAL36400 | 30 | 400 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101600 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101601 | C | CB | Square D | LAL36300 | 22 | 300 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101601 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101602 | C | CB | Square D | LAL36400 | 22 | 400 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101602 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101603 | C | CB | Square D | LAL36250 | 30 | 250 | 600 | 3 | 30 | 480 | 3 | 75 | 96 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101603 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 30 | 480 | 3 | 75 | 96 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101604 | C | CB | Square D | LAL36200 | 22 | 200 | 600 | 3 | 22 | 600 | 3 | 75 | 77 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101604 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 22 | 600 | 3 | 75 | 77 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101605 | C | CB | Square D | LAL36300 | 30 | 300 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101605 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101606 | C | CB | Square D | LAL36250 | 22 | 250 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101606 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101607 | C | CB | Square D | LAL36400 | 30 | 400 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101607 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101608 | C | CB | Square D | LAL36300 | 22 | 300 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101608 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101609 | C | CB | Square D | LAL36400 | 22 | 400 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101609 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101610 | C | CB | Square D | LAL36250 | 30 | 250 | 600 | 3 | 30 | 480 | 3 | 75 | 96 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101610 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 75 | 96 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101611 | C | CB | Square D | LAL36300 | 30 | 300 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101611 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101612 | C | CB | Square D | LAL36250 | 22 | 250 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101612 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101613 | C | CB | Square D | LAL36400 | 30 | 400 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101613 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101614 | C | CB | Square D | LAL36300 | 22 | 300 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101614 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101615 | C | CB | Square D | LAL36400 | 22 | 400 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101615 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101616 | C | CB | Square D | LAL36250 | 30 | 250 | 600 | 3 | 30 | 480 | 3 | 75 | 96 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101616 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 75 | 96 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101617 | C | CB | Square D | LAL36300 | 30 | 300 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101617 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101618 | C | CB | Square D | LAL36250 | 22 | 250 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101618 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101619 | C | CB | Square D | LAL36400 | 30 | 400 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101619 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101620 | C | CB | Square D | LAL36300 | 22 | 300 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101620 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101621 | C | CB | Square D | LAL36400 | 22 | 400 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101621 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101622 | C | CB | Square D | LAL36250 | 30 | 250 | 600 | 3 | 30 | 480 | 3 | 75 | 96 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101622 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 75 | 96 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101623 | C | CB | Square D | LAL36300 | 30 | 300 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101623 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101624 | C | CB | Square D | LAL36250 | 22 | 250 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101624 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101625 | C | CB | Square D | LAL36400 | 30 | 400 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101625 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101626 | C | CB | Square D | LAL36300 | 22 | 300 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101626 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101627 | C | CB | Square D | LAL36400 | 22 | 400 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101627 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101628 | C | CB | Square D | LAL36300 | 30 | 300 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101628 |  | STR | Square D | 8536SGO1@B80 | 10 | 120 - 270 | 600 | 3 | 30 | 480 | 3 | 100 | 124 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101629 | C | CB | Square D | LAL36400 | 30 | 400 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101629 |  | STR | Square D | 8536SGO1@B80 | 10 | 120 - 270 | 600 | 3 | 30 | 480 | 3 | 125 | 156 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101630 | C | CB | Square D | LAL36300 | 22 | 300 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101630 |  | STR | Square D | 8536SGO1@B84 | 10 | 120 - 270 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101631 | C | CB | Square D | LAL36400 | 22 | 400 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101631 |  | STR | Square D | 8536SGO1@B84 | 10 | 120 - 270 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101632 | C | CB | Square D | LHL36250 | 35 | 250 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101632 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101633 | C | CB | Square D | LHL36200 | 25 | 200 | 600 | 3 | 22 | 600 | 3 | 75 | 77 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101633 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 22 | 600 | 3 | 75 | 77 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101634 | C | CB | Square D | LHL36300 | 35 | 300 | 600 | 3 | 35 | 480 | 3 | 100 | 124 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101634 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 35 | 480 | 3 | 100 | 124 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101635 | C | CB | Square D | LHL36250 | 25 | 250 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101635 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101636 | C | CB | Square D | LHL36400 | 35 | 400 | 600 | 3 | 35 | 480 | 3 | 125 | 156 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101636 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 35 | 480 | 3 | 125 | 156 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101637 | C | CB | Square D | LHL36300 | 25 | 300 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101637 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101638 | C | CB | Square D | LHL36400 | 25 | 400 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101638 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101639 | C | CB | Square D | LHL36250 | 35 | 250 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101639 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101640 | C | CB | Square D | LHL36200 | 25 | 200 | 600 | 3 | 22 | 600 | 3 | 75 | 77 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101640 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 22 | 600 | 3 | 75 | 77 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101641 | C | CB | Square D | LHL36300 | 35 | 300 | 600 | 3 | 35 | 480 | 3 | 100 | 124 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101641 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 35 | 480 | 3 | 100 | 124 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101642 | C | CB | Square D | LHL36250 | 25 | 250 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101642 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 22 | 600 | 3 | 100 | 99 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101643 | C | CB | Square D | LHL36400 | 35 | 400 | 600 | 3 | 35 | 480 | 3 | 125 | 156 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101643 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 35 | 480 | 3 | 125 | 156 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101644 | C | CB | Square D | LHL36300 | 25 | 300 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101644 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 22 | 600 | 3 | 125 | 125 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101645 | C | CB | Square D | LHL36400 | 25 | 400 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101645 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101646 | C | CB | Square D | LHL36250 | 35 | 250 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101646 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101647 | C | CB | Square D | LHL36300 | 35 | 300 | 600 | 3 | 35 | 480 | 3 | 100 | 124 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101647 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 35 | 480 | 3 | 100 | 124 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101648 | C | CB | Square D | LHL36250 | 25 | 250 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101648 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101649 | C | CB | Square D | LHL36400 | 35 | 400 | 600 | 3 | 35 | 480 | 3 | 125 | 156 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101649 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 35 | 480 | 3 | 125 | 156 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101650 | C | CB | Square D | LHL36300 | 25 | 300 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101650 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101651 | C | CB | Square D | LHL36400 | 25 | 400 | 600 | 3 | 25 | 600 | 3 | 150 | 144 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101651 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 25 | 600 | 3 | 150 | 144 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101652 | C | CB | Square D | LHL36250 | 35 | 250 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101652 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101653 | C | CB | Square D | LHL36300 | 35 | 300 | 600 | 3 | 35 | 480 | 3 | 100 | 124 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101653 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 35 | 480 | 3 | 100 | 124 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101654 | C | CB | Square D | LHL36250 | 25 | 250 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101654 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101655 | C | CB | Square D | LHL36400 | 35 | 400 | 600 | 3 | 35 | 480 | 3 | 125 | 156 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101655 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 35 | 480 | 3 | 125 | 156 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101656 | C | CB | Square D | LHL36300 | 25 | 300 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101656 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101657 | C | CB | Square D | LHL36400 | 25 | 400 | 600 | 3 | 25 | 600 | 3 | 150 | 144 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101657 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 25 | 600 | 3 | 150 | 144 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101658 | C | CB | Square D | LHL36250 | 35 | 250 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101658 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101659 | C | CB | Square D | LHL36300 | 35 | 300 | 600 | 3 | 35 | 480 | 3 | 100 | 124 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101659 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 35 | 480 | 3 | 100 | 124 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101660 | C | CB | Square D | LHL36250 | 25 | 250 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101660 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101661 | C | CB | Square D | LHL36400 | 35 | 400 | 600 | 3 | 35 | 480 | 3 | 125 | 156 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101661 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 35 | 480 | 3 | 125 | 156 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101662 | C | CB | Square D | LHL36300 | 25 | 300 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101662 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101663 | C | CB | Square D | LHL36400 | 25 | 400 | 600 | 3 | 25 | 600 | 3 | 150 | 144 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101663 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 25 | 600 | 3 | 150 | 144 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101664 | C | CB | Square D | LHL36300 | 35 | 300 | 600 | 3 | 35 | 480 | 3 | 100 | 124 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101664 |  | STR | Square D | 8536SGO1@B80 | 10 | 120 - 270 | 600 | 3 | 35 | 480 | 3 | 100 | 124 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101665 | C | CB | Square D | LHL36400 | 35 | 400 | 600 | 3 | 35 | 480 | 3 | 125 | 156 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101665 |  | STR | Square D | 8536SGO1@B80 | 10 | 120 - 270 | 600 | 3 | 35 | 480 | 3 | 125 | 156 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101666 | C | CB | Square D | LHL36300 | 25 | 300 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101666 |  | STR | Square D | 8536SGO1@B84 | 10 | 120 - 270 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101667 | C | CB | Square D | LHL36400 | 25 | 400 | 600 | 3 | 25 | 600 | 3 | 150 | 144 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
SE101667 |  | STR | Square D | 8536SGO1@B84 | 10 | 120 - 270 | 600 | 3 | 25 | 600 | 3 | 150 | 144 | 7325 | 1, 6, 7e, 8 | E40610 V12 S1
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = Use wire ties evenly spaced apart to secure conductors in place.
(7) = See Table 7 for minimum internal wiring between load side of short circuit protective device & line side of starter.
(8) = "@" refer to digest to complete contactor Catalog number for coil voltage and Form modifications.
(9) = Insulator to be provided underneath starter. (QMFZ2), Fastex, Type Formex GK-30, 1/32 inch minimum thickness by 4 inches x 5.7 inches.
Table 7 - Minimum Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
|  | Wire Code |  | Wire Size
|  | 7a |  | 12 AWG
|  | 7b |  | 8 AWG
|  | 7c |  | 2 AWG
|  | 7d |  | 1 AWG
|  | 7e |  | 250 MCM
|  | 7f |  | 300 MCM
|  | 7g |  | (2) 250 MCM

## Size 6
Issued: 2008-04-08
Last Revised: 2015-03-20
|  |  |  | "@" refer to Digest to complete | [8 empty] | Use Square D Digest for selection of Melting Alloy and Bi-Metal Overloads only
contactor Catalog number for coil
voltage codes and Form modifications
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Min Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE101668 | D | ICB | Square D | LAL3640033M | - | 400 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101668 |  | STR | Square D | 8536SHO2@ | 18 | 540 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101669 | D | ICB | Square D | LAL3640033M | - | 400 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101669 |  | STR | Square D | 8536SHO2@ | 18 | 540 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101670 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101670 |  | STR | Square D | 8536SHO2@ | 18 | 540 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101671 | D | ICB | Square D | LAL3640035M | - | 400 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101671 |  | STR | Square D | 8536SHO2@ | 18 | 540 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101672 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 250 | 302 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101672 |  | STR | Square D | 8536SHO2@ | 18 | 540 | 600 | 3 | 30 | 480 | 3 | 250 | 302 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101673 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101673 |  | STR | Square D | 8536SHO2@ | 18 | 540 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101674 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 22 | 600 | 3 | 300 | 289 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101674 |  | STR | Square D | 8536SHO2@ | 18 | 540 | 600 | 3 | 22 | 600 | 3 | 300 | 289 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101675 | D | ICB | Square D | LAL3640033M | - | 400 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101675 |  | STR | Square D | 8536SHO2@B | 18 | 540 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101676 | D | ICB | Square D | LAL3640032M | - | 400 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101676 |  | STR | Square D | 8536SHO2@B | 18 | 540 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101677 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101677 |  | STR | Square D | 8536SHO2@B | 18 | 540 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101678 | D | ICB | Square D | LAL3640035M | - | 400 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101678 |  | STR | Square D | 8536SHO2@B | 18 | 540 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101679 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 250 | 302 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101679 |  | STR | Square D | 8536SHO2@B | 18 | 540 | 600 | 3 | 30 | 480 | 3 | 250 | 302 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101680 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101680 |  | STR | Square D | 8536SHO2@B | 18 | 540 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101681 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 22 | 600 | 3 | 300 | 289 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101681 |  | STR | Square D | 8536SHO2@B | 18 | 540 | 600 | 3 | 22 | 600 | 3 | 300 | 289 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101682 | D | ICB | Square D | LAL3640033M | - | 400 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101682 |  | STR | Square D | 8536SHO2@H10 | 18 | 180 - 540 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101683 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101683 |  | STR | Square D | 8536SHO2@H10 | 18 | 180 - 540 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101684 | D | ICB | Square D | LAL3640035M | - | 400 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101684 |  | STR | Square D | 8536SHO2@H10 | 18 | 180 - 540 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101685 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 250 | 302 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101685 |  | STR | Square D | 8536SHO2@H10 | 18 | 180 - 540 | 600 | 3 | 30 | 480 | 3 | 250 | 302 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101686 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101686 |  | STR | Square D | 8536SHO2@H10 | 18 | 180 - 540 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101687 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 22 | 600 | 3 | 300 | 289 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101687 |  | STR | Square D | 8536SHO2@H10 | 18 | 180 - 540 | 600 | 3 | 22 | 600 | 3 | 300 | 289 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101688 | D | ICB | Square D | LAL3640033M | - | 400 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101688 |  | STR | Square D | 8536SHO2@H20 | 18 | 180 - 540 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101689 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101689 |  | STR | Square D | 8536SHO2@H20 | 18 | 180 - 540 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101690 | D | ICB | Square D | LAL3640035M | - | 400 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101690 |  | STR | Square D | 8536SHO2@H20 | 18 | 180 - 540 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101691 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 250 | 302 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101691 |  | STR | Square D | 8536SHO2@H20 | 18 | 180 - 540 | 600 | 3 | 30 | 480 | 3 | 250 | 302 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101692 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101692 |  | STR | Square D | 8536SHO2@H20 | 18 | 180 - 540 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101693 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 22 | 600 | 3 | 300 | 289 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101693 |  | STR | Square D | 8536SHO2@H20 | 18 | 180 - 540 | 600 | 3 | 22 | 600 | 3 | 300 | 289 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101694 | D | ICB | Square D | LAL3640033M | - | 400 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101694 |  | STR | Square D | 8536SHO2@H30 | 18 | 180 - 540 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101695 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101695 |  | STR | Square D | 8536SHO2@H30 | 18 | 180 - 540 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101696 | D | ICB | Square D | LAL3640035M | - | 400 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101696 |  | STR | Square D | 8536SHO2@H30 | 18 | 180 - 540 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101697 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 250 | 302 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101697 |  | STR | Square D | 8536SHO2@H30 | 18 | 180 - 540 | 600 | 3 | 30 | 480 | 3 | 250 | 302 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101698 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101698 |  | STR | Square D | 8536SHO2@H30 | 18 | 180 - 540 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101699 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 22 | 600 | 3 | 300 | 289 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101699 |  | STR | Square D | 8536SHO2@H30 | 18 | 180 - 540 | 600 | 3 | 22 | 600 | 3 | 300 | 289 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101700 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101700 |  | STR | Square D | 8536SHO2@B90 | 18 | 240 - 540 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101701 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 250 | 302 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101701 |  | STR | Square D | 8536SHO2@B90 | 18 | 240 - 540 | 600 | 3 | 30 | 480 | 3 | 250 | 302 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101702 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101702 |  | STR | Square D | 8536SHO2@B94 | 18 | 240 - 540 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101703 | D | ICB | Square D | LAL3640036M | - | 400 | 600 | 3 | 22 | 600 | 3 | 300 | 289 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101703 |  | STR | Square D | 8536SHO2@B94 | 18 | 240 - 540 | 600 | 3 | 22 | 600 | 3 | 300 | 289 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101704 | D | ICB | Square D | LHL3640033M | - | 400 | 600 | 3 | 35 | 480 | 3 | 150 | 180 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101704 |  | STR | Square D | 8536SHO2@ | 18 | 540 | 600 | 3 | 35 | 480 | 3 | 150 | 180 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101705 | D | ICB | Square D | LHL3640033M | - | 400 | 600 | 3 | 25 | 600 | 3 | 150 | 144 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101705 |  | STR | Square D | 8536SHO2@ | 18 | 540 | 600 | 3 | 25 | 600 | 3 | 150 | 144 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101706 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 35 | 480 | 3 | 200 | 240 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101706 |  | STR | Square D | 8536SHO2@ | 18 | 540 | 600 | 3 | 35 | 480 | 3 | 200 | 240 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101707 | D | ICB | Square D | LHL3640035M | - | 400 | 600 | 3 | 25 | 600 | 3 | 200 | 192 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101707 |  | STR | Square D | 8536SHO2@ | 18 | 540 | 600 | 3 | 25 | 600 | 3 | 200 | 192 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101708 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 35 | 480 | 3 | 250 | 302 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101708 |  | STR | Square D | 8536SHO2@ | 18 | 540 | 600 | 3 | 35 | 480 | 3 | 250 | 302 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101709 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 25 | 600 | 3 | 250 | 242 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101709 |  | STR | Square D | 8536SHO2@ | 18 | 540 | 600 | 3 | 25 | 600 | 3 | 250 | 242 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101710 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 25 | 600 | 3 | 300 | 289 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101710 |  | STR | Square D | 8536SHO2@ | 18 | 540 | 600 | 3 | 25 | 600 | 3 | 300 | 289 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101711 | D | ICB | Square D | LHL3640033M | - | 400 | 600 | 3 | 35 | 480 | 3 | 150 | 180 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101711 |  | STR | Square D | 8536SHO2@B | 18 | 540 | 600 | 3 | 35 | 480 | 3 | 150 | 180 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101712 | D | ICB | Square D | LHL3640032M | - | 400 | 600 | 3 | 25 | 600 | 3 | 150 | 144 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101712 |  | STR | Square D | 8536SHO2@B | 18 | 540 | 600 | 3 | 25 | 600 | 3 | 150 | 144 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101713 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 35 | 480 | 3 | 200 | 240 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101713 |  | STR | Square D | 8536SHO2@B | 18 | 540 | 600 | 3 | 35 | 480 | 3 | 200 | 240 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101714 | D | ICB | Square D | LHL3640035M | - | 400 | 600 | 3 | 25 | 600 | 3 | 200 | 192 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101714 |  | STR | Square D | 8536SHO2@B | 18 | 540 | 600 | 3 | 25 | 600 | 3 | 200 | 192 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101715 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 35 | 480 | 3 | 250 | 302 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101715 |  | STR | Square D | 8536SHO2@B | 18 | 540 | 600 | 3 | 35 | 480 | 3 | 250 | 302 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101716 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 25 | 600 | 3 | 250 | 242 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101716 |  | STR | Square D | 8536SHO2@B | 18 | 540 | 600 | 3 | 25 | 600 | 3 | 250 | 242 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101717 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 25 | 600 | 3 | 300 | 289 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101717 |  | STR | Square D | 8536SHO2@B | 18 | 540 | 600 | 3 | 25 | 600 | 3 | 300 | 289 | 19310 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE101718 | D | ICB | Square D | LHL3640033M | - | 400 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101718 |  | STR | Square D | 8536SHO2@H10 | 18 | 180 - 540 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101719 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101719 |  | STR | Square D | 8536SHO2@H10 | 18 | 180 - 540 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101720 | D | ICB | Square D | LHL3640035M | - | 400 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101720 |  | STR | Square D | 8536SHO2@H10 | 18 | 180 - 540 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101721 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 250 | 302 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101721 |  | STR | Square D | 8536SHO2@H10 | 18 | 180 - 540 | 600 | 3 | 30 | 480 | 3 | 250 | 302 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101722 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101722 |  | STR | Square D | 8536SHO2@H10 | 18 | 180 - 540 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101723 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 22 | 600 | 3 | 300 | 289 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101723 |  | STR | Square D | 8536SHO2@H10 | 18 | 180 - 540 | 600 | 3 | 22 | 600 | 3 | 300 | 289 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101724 | D | ICB | Square D | LHL3640033M | - | 400 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101724 |  | STR | Square D | 8536SHO2@H20 | 18 | 180 - 540 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101725 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101725 |  | STR | Square D | 8536SHO2@H20 | 18 | 180 - 540 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101726 | D | ICB | Square D | LHL3640035M | - | 400 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101726 |  | STR | Square D | 8536SHO2@H20 | 18 | 180 - 540 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101727 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 250 | 302 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101727 |  | STR | Square D | 8536SHO2@H20 | 18 | 180 - 540 | 600 | 3 | 30 | 480 | 3 | 250 | 302 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101728 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101728 |  | STR | Square D | 8536SHO2@H20 | 18 | 180 - 540 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101729 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 22 | 600 | 3 | 300 | 289 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101729 |  | STR | Square D | 8536SHO2@H20 | 18 | 180 - 540 | 600 | 3 | 22 | 600 | 3 | 300 | 289 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101730 | D | ICB | Square D | LHL3640033M | - | 400 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101730 |  | STR | Square D | 8536SHO2@H30 | 18 | 180 - 540 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101731 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101731 |  | STR | Square D | 8536SHO2@H30 | 18 | 180 - 540 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101732 | D | ICB | Square D | LHL3640035M | - | 400 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101732 |  | STR | Square D | 8536SHO2@H30 | 18 | 180 - 540 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101733 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 250 | 302 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101733 |  | STR | Square D | 8536SHO2@H30 | 18 | 180 - 540 | 600 | 3 | 30 | 480 | 3 | 250 | 302 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101734 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101734 |  | STR | Square D | 8536SHO2@H30 | 18 | 180 - 540 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101735 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 22 | 600 | 3 | 300 | 289 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101735 |  | STR | Square D | 8536SHO2@H30 | 18 | 180 - 540 | 600 | 3 | 22 | 600 | 3 | 300 | 289 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101736 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101736 |  | STR | Square D | 8536SHO2@B90 | 18 | 240 - 540 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101737 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 30 | 480 | 3 | 250 | 302 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101737 |  | STR | Square D | 8536SHO2@B90 | 18 | 240 - 540 | 600 | 3 | 30 | 480 | 3 | 250 | 302 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101738 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101738 |  | STR | Square D | 8536SHO2@B94 | 18 | 240 - 540 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101739 | D | ICB | Square D | LHL3640036M | - | 400 | 600 | 3 | 22 | 600 | 3 | 300 | 289 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101739 |  | STR | Square D | 8536SHO2@B94 | 18 | 240 - 540 | 600 | 3 | 22 | 600 | 3 | 300 | 289 | 19310 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE101944 | C | CB | Square D | MAL36450 | 30 | 450 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101944 |  | STR | Square D | 8536SHO2@ | 18 | 540 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101945 | C | CB | Square D | MAL36400 | 22 | 400 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101945 |  | STR | Square D | 8536SHO2@ | 18 | 540 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101946 | C | CB | Square D | MAL36600 | 30 | 600 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101946 |  | STR | Square D | 8536SHO2@ | 18 | 540 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101947 | C | CB | Square D | MAL36500 | 22 | 500 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101947 |  | STR | Square D | 8536SHO2@ | 18 | 540 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101948 | C | CB | Square D | MAL36600 | 22 | 600 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101948 |  | STR | Square D | 8536SHO2@ | 18 | 540 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101949 | C | CB | Square D | MAL36450 | 30 | 450 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101949 |  | STR | Square D | 8536SHO2@B | 18 | 540 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101950 | C | CB | Square D | MAL36400 | 22 | 400 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101950 |  | STR | Square D | 8536SHO2@B | 18 | 540 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101951 | C | CB | Square D | MAL36600 | 30 | 600 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101951 |  | STR | Square D | 8536SHO2@B | 18 | 540 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101952 | C | CB | Square D | MAL36500 | 22 | 500 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101952 |  | STR | Square D | 8536SHO2@B | 18 | 540 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101953 | C | CB | Square D | MAL36600 | 22 | 600 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101953 |  | STR | Square D | 8536SHO2@B | 18 | 540 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101954 | C | CB | Square D | MAL36450 | 30 | 450 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 7g, 8 | E40610 V12 S1
SE101954 |  | STR | Square D | 8536SHO2@H10 | 18 | 180 - 540 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 7g, 8 | E40610 V12 S1
SE101955 | C | CB | Square D | MAL36600 | 30 | 600 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 7g, 8 | E40610 V12 S1
SE101955 |  | STR | Square D | 8536SHO2@H10 | 18 | 180 - 540 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 7g, 8 | E40610 V12 S1
SE101956 | C | CB | Square D | MAL36500 | 22 | 500 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 7g, 8 | E40610 V12 S1
SE101956 |  | STR | Square D | 8536SHO2@H10 | 18 | 180 - 540 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 7g, 8 | E40610 V12 S1
SE101957 | C | CB | Square D | MAL36600 | 22 | 600 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 7g, 8 | E40610 V12 S1
SE101957 |  | STR | Square D | 8536SHO2@H10 | 18 | 180 - 540 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 7g, 8 | E40610 V12 S1
SE101958 | C | CB | Square D | MAL36450 | 30 | 450 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 7g, 8 | E40610 V12 S1
SE101958 |  | STR | Square D | 8536SHO2@H20 | 18 | 180 - 540 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 7g, 8 | E40610 V12 S1
SE101959 | C | CB | Square D | MAL36600 | 30 | 600 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 7g, 8 | E40610 V12 S1
SE101959 |  | STR | Square D | 8536SHO2@H20 | 18 | 180 - 540 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 7g, 8 | E40610 V12 S1
SE101960 | C | CB | Square D | MAL36500 | 22 | 500 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 7g, 8 | E40610 V12 S1
SE101960 |  | STR | Square D | 8536SHO2@H20 | 18 | 180 - 540 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 7g, 8 | E40610 V12 S1
SE101961 | C | CB | Square D | MAL36600 | 22 | 600 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 7g, 8 | E40610 V12 S1
SE101961 |  | STR | Square D | 8536SHO2@H20 | 18 | 180 - 540 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 7g, 8 | E40610 V12 S1
SE101962 | C | CB | Square D | MAL36450 | 30 | 450 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 7g, 8 | E40610 V12 S1
SE101962 |  | STR | Square D | 8536SHO2@H30 | 18 | 180 - 540 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 7g, 8 | E40610 V12 S1
SE101963 | C | CB | Square D | MAL36600 | 30 | 600 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 7g, 8 | E40610 V12 S1
SE101963 |  | STR | Square D | 8536SHO2@H30 | 18 | 180 - 540 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 7g, 8 | E40610 V12 S1
SE101964 | C | CB | Square D | MAL36500 | 22 | 500 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 7g, 8 | E40610 V12 S1
SE101964 |  | STR | Square D | 8536SHO2@H30 | 18 | 180 - 540 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 7g, 8 | E40610 V12 S1
SE101965 | C | CB | Square D | MAL36600 | 22 | 600 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 7g, 8 | E40610 V12 S1
SE101965 |  | STR | Square D | 8536SHO2@H30 | 18 | 180 - 540 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 7g, 8 | E40610 V12 S1
SE101966 | C | CB | Square D | MAL36600 | 30 | 600 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 7g, 8 | E40610 V12 S1
SE101966 |  | STR | Square D | 8536SHO2@B90 | 18 | 240 - 540 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 7g, 8 | E40610 V12 S1
SE101967 | C | CB | Square D | MAL36600 | 22 | 600 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 7g, 8 | E40610 V12 S1
SE101967 |  | STR | Square D | 8536SHO2@B94 | 18 | 240 - 540 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 7g, 8 | E40610 V12 S1
SE101968 | C | CB | Square D | MHL36450 | 65 | 450 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101968 |  | STR | Square D | 8536SHO2@ | 18 | 540 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101969 | C | CB | Square D | MHL36400 | 25 | 400 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101969 |  | STR | Square D | 8536SHO2@ | 18 | 540 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101970 | C | CB | Square D | MHL36600 | 65 | 600 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101970 |  | STR | Square D | 8536SHO2@ | 18 | 540 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101971 | C | CB | Square D | MHL36500 | 25 | 500 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101971 |  | STR | Square D | 8536SHO2@ | 18 | 540 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101972 | C | CB | Square D | MHL36600 | 25 | 600 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101972 |  | STR | Square D | 8536SHO2@ | 18 | 540 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101973 | C | CB | Square D | MHL36450 | 65 | 450 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101973 |  | STR | Square D | 8536SHO2@B | 18 | 540 | 600 | 3 | 30 | 480 | 3 | 150 | 180 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101974 | C | CB | Square D | MHL36400 | 25 | 400 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101974 |  | STR | Square D | 8536SHO2@B | 18 | 540 | 600 | 3 | 22 | 600 | 3 | 150 | 144 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101975 | C | CB | Square D | MHL36600 | 65 | 600 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101975 |  | STR | Square D | 8536SHO2@B | 18 | 540 | 600 | 3 | 30 | 480 | 3 | 200 | 240 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101976 | C | CB | Square D | MHL36500 | 25 | 500 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101976 |  | STR | Square D | 8536SHO2@B | 18 | 540 | 600 | 3 | 22 | 600 | 3 | 200 | 192 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101977 | C | CB | Square D | MHL36600 | 25 | 600 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
SE101977 |  | STR | Square D | 8536SHO2@B | 18 | 540 | 600 | 3 | 22 | 600 | 3 | 250 | 242 | 19310 | 1, 3, 7g, 8 | E40610 V12 S1
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = Use wire ties evenly spaced apart to secure conductors in place.
(7) = See Table 7 for minimum internal wiring between load side of short circuit protective device & line side of starter.
(8) = "@" refer to digest to complete contactor Catalog number for coil voltage and Form modifications.
(9) = Insulator to be provided underneath starter. (QMFZ2), Fastex, Type Formex GK-30, 1/32 inch minimum thickness by 4 inches x 5.7 inches.
Table 7 - Minimum Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
|  | Wire Code |  | Wire Size
|  | 7a |  | 12 AWG
|  | 7b |  | 8 AWG
|  | 7c |  | 2 AWG
|  | 7d |  | 1 AWG
|  | 7e |  | 250 MCM
|  | 7f |  | 300 MCM
|  | 7g |  | (2) 250 MCM