## Size1
Issued: 2007-01-23
Last Revised: 2007-01-23
|  |  |  | "@" refer to Digest to complete | [8 empty] | Use Square D Digest for selection of Melting Alloy and Bi-Metal Overloads only
starter Catalog number for coil
voltage codes and Form modifications
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE150000 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150000 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150001 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150001 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150002 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150002 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150003 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150003 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150004 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150004 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150005 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150005 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150006 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150006 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150007 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150007 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150008 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150008 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150009 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150009 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150010 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150010 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150011 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150011 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150012 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150012 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150013 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150013 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150014 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150014 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150015 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150015 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150016 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150016 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150017 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150017 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150018 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150018 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150019 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150019 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150020 | C | CB | Square D | HDL36020 | 25 | 20 | 600 | 3 | 25 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150020 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150021 | C | CB | Square D | HDL36020 | 25 | 20 | 600 | 3 | 25 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150021 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150022 | C | CB | Square D | HDL36020 | 25 | 20 | 600 | 3 | 25 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150022 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150023 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150023 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150024 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150024 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150025 | C | CB | Square D | HDL36030 | 25 | 30 | 600 | 3 | 25 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150025 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150026 | C | CB | Square D | HDL36030 | 25 | 30 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150026 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150027 | C | CB | Square D | HDL36025 | 25 | 25 | 600 | 3 | 25 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150027 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150028 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150028 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150029 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150029 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150030 | C | CB | Square D | HDL36045 | 25 | 45 | 600 | 3 | 25 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150030 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150031 | C | CB | Square D | HDL36050 | 25 | 50 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150031 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150032 | C | CB | Square D | HDL36040 | 25 | 40 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150032 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150033 | C | CB | Square D | HDL36020 | 18 | 20 | 600 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150033 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150034 | C | CB | Square D | HDL36020 | 14 | 20 | 600 | 3 | 14 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150034 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150035 | C | CB | Square D | HDL36060 | 25 | 60 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150035 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150036 | C | CB | Square D | HDL36030 | 18 | 30 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150036 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150037 | C | CB | Square D | HDL36025 | 14 | 25 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150037 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150038 | C | CB | Square D | HDL36040 | 18 | 40 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150038 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150039 | C | CB | Square D | HDL36030 | 14 | 30 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150039 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150040 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150040 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150041 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150041 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150042 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150042 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150043 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150043 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150044 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150044 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150045 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150045 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150046 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150046 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150047 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150047 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150048 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150048 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150049 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150049 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150050 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150050 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150051 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150051 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150052 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150052 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150053 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150053 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150054 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150054 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150055 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150055 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150056 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150056 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150057 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150057 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150058 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150058 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150059 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150059 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150060 | C | CB | Square D | HDL36020 | 25 | 20 | 600 | 3 | 25 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150060 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150061 | C | CB | Square D | HDL36020 | 25 | 20 | 600 | 3 | 25 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150061 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150062 | C | CB | Square D | HDL36020 | 25 | 20 | 600 | 3 | 25 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150062 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150063 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150063 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150064 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150064 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150065 | C | CB | Square D | HDL36030 | 25 | 30 | 600 | 3 | 25 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150065 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150066 | C | CB | Square D | HDL36030 | 25 | 30 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150066 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150067 | C | CB | Square D | HDL36025 | 25 | 25 | 600 | 3 | 25 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150067 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150068 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150068 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150069 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150069 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150070 | C | CB | Square D | HDL36045 | 25 | 45 | 600 | 3 | 25 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150070 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150071 | C | CB | Square D | HDL36050 | 25 | 50 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150071 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150072 | C | CB | Square D | HDL36040 | 25 | 40 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150072 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150073 | C | CB | Square D | HDL36020 | 18 | 20 | 600 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150073 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150074 | C | CB | Square D | HDL36020 | 14 | 20 | 600 | 3 | 14 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150074 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150075 | C | CB | Square D | HDL36060 | 25 | 60 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150075 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150076 | C | CB | Square D | HDL36030 | 18 | 30 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150076 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150077 | C | CB | Square D | HDL36025 | 14 | 25 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150077 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150078 | C | CB | Square D | HDL36040 | 18 | 40 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150078 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150079 | C | CB | Square D | HDL36030 | 14 | 30 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150079 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150080 | C | CB | Square D | HDL36030 | 25 | 30 | 600 | 3 | 25 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150080 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 25 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150081 | C | CB | Square D | HDL36030 | 25 | 30 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150081 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150082 | C | CB | Square D | HDL36025 | 25 | 25 | 600 | 3 | 25 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150082 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 25 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150083 | C | CB | Square D | HDL36045 | 25 | 45 | 600 | 3 | 25 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150083 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 25 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150084 | C | CB | Square D | HDL36050 | 25 | 50 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150084 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150085 | C | CB | Square D | HDL36040 | 25 | 40 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150085 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150086 | C | CB | Square D | HDL36060 | 25 | 60 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150086 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150087 | C | CB | Square D | HDL36030 | 18 | 30 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150087 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150088 | C | CB | Square D | HDL36025 | 14 | 25 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150088 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150089 | C | CB | Square D | HDL36040 | 18 | 40 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150089 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150090 | C | CB | Square D | HDL36030 | 14 | 30 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150090 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150091 | C | CB | Square D | HDL36030 | 25 | 30 | 600 | 3 | 25 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150091 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 25 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150092 | C | CB | Square D | HDL36030 | 25 | 30 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150092 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150093 | C | CB | Square D | HDL36025 | 25 | 25 | 600 | 3 | 25 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150093 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 25 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150094 | C | CB | Square D | HDL36045 | 25 | 45 | 600 | 3 | 25 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150094 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 25 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150095 | C | CB | Square D | HDL36050 | 25 | 50 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150095 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150096 | C | CB | Square D | HDL36040 | 25 | 40 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150096 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150097 | C | CB | Square D | HDL36060 | 25 | 60 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150097 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150098 | C | CB | Square D | HDL36030 | 18 | 30 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150098 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150099 | C | CB | Square D | HDL36025 | 14 | 25 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150099 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150100 | C | CB | Square D | HDL36040 | 18 | 40 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150100 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150101 | C | CB | Square D | HDL36030 | 14 | 30 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150101 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150102 | C | CB | Square D | HDL36030 | 25 | 30 | 600 | 3 | 25 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150102 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 25 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150103 | C | CB | Square D | HDL36030 | 25 | 30 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150103 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150104 | C | CB | Square D | HDL36025 | 25 | 25 | 600 | 3 | 25 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150104 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 25 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150105 | C | CB | Square D | HDL36045 | 25 | 45 | 600 | 3 | 25 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150105 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 25 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150106 | C | CB | Square D | HDL36050 | 25 | 50 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150106 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150107 | C | CB | Square D | HDL36040 | 25 | 40 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150107 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150108 | C | CB | Square D | HDL36060 | 25 | 60 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150108 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150109 | C | CB | Square D | HDL36030 | 18 | 30 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150109 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150110 | C | CB | Square D | HDL36025 | 14 | 25 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150110 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150111 | C | CB | Square D | HDL36040 | 18 | 40 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150111 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150112 | C | CB | Square D | HDL36030 | 14 | 30 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150112 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150113 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150113 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 25 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150114 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150114 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 25 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150115 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150115 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 25 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150116 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150116 |  | STR | Square D | 8536SCO3@B20 | 5 | 0.5 - 2.3 | 600 | 3 | 18 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150117 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150117 |  | STR | Square D | 8536SCO3@B24 | 5 | 0.5 - 2.3 | 600 | 3 | 14 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150118 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150118 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 25 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150119 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150119 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 25 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150120 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150120 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 25 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150121 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150121 |  | STR | Square D | 8536SCO3@B20 | 5 | 0.5 - 2.3 | 600 | 3 | 18 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150122 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150122 |  | STR | Square D | 8536SCO3@B24 | 5 | 0.5 - 2.3 | 600 | 3 | 14 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150123 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 200 | 3 | 1 | 4.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150123 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 25 | 200 | 3 | 1 | 4.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150124 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 208 | 3 | 1 | 4.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150124 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 25 | 208 | 3 | 1 | 4.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150125 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 240 | 3 | 1 | 4.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150125 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 25 | 240 | 3 | 1 | 4.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150126 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 1 | 2.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150126 |  | STR | Square D | 8536SCO3@B20 | 5 | 0.5 - 2.3 | 600 | 3 | 18 | 480 | 3 | 1 | 2.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150127 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 1 | 1.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150127 |  | STR | Square D | 8536SCO3@B24 | 5 | 0.5 - 2.3 | 600 | 3 | 14 | 600 | 3 | 1 | 1.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150128 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150128 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150129 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150129 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150130 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 240 | 3 | 1.5 | 6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150130 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 240 | 3 | 1.5 | 6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150131 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 1.5 | 3 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150131 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 18 | 480 | 3 | 1.5 | 3 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150132 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150132 |  | STR | Square D | 8536SCO3@B34 | 5 | 2 - 9 | 600 | 3 | 14 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150133 | C | CB | Square D | HDL36020 | 25 | 20 | 600 | 3 | 25 | 200 | 3 | 2 | 7.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150133 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 200 | 3 | 2 | 7.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150134 | C | CB | Square D | HDL36020 | 25 | 20 | 600 | 3 | 25 | 208 | 3 | 2 | 7.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150134 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 208 | 3 | 2 | 7.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150135 | C | CB | Square D | HDL36020 | 25 | 20 | 600 | 3 | 25 | 240 | 3 | 2 | 6.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150135 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 240 | 3 | 2 | 6.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150136 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 2 | 3.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150136 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 18 | 480 | 3 | 2 | 3.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150137 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 2 | 2.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150137 |  | STR | Square D | 8536SCO3@B34 | 5 | 2 - 9 | 600 | 3 | 14 | 600 | 3 | 2 | 2.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150138 | C | CB | Square D | HDL36030 | 25 | 30 | 600 | 3 | 25 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150138 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150139 | C | CB | Square D | HDL36030 | 25 | 30 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150139 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150140 | C | CB | Square D | HDL36025 | 25 | 25 | 600 | 3 | 25 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150140 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150141 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 3 | 4.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150141 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 18 | 480 | 3 | 3 | 4.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150142 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 3 | 3.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150142 |  | STR | Square D | 8536SCO3@B34 | 5 | 2 - 9 | 600 | 3 | 14 | 600 | 3 | 3 | 3.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150143 | C | CB | Square D | HDL36045 | 25 | 45 | 600 | 3 | 25 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150143 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150144 | C | CB | Square D | HDL36040 | 25 | 40 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150144 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150145 | C | CB | Square D | HDL36040 | 25 | 40 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150145 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150146 | C | CB | Square D | HDL36020 | 18 | 20 | 600 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150146 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150147 | C | CB | Square D | HDL36020 | 14 | 20 | 600 | 3 | 14 | 600 | 3 | 5 | 6.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150147 |  | STR | Square D | 8536SCO3@B34 | 5 | 2 - 9 | 600 | 3 | 14 | 600 | 3 | 5 | 6.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150148 | C | CB | Square D | HDL36060 | 25 | 60 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150148 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150149 | C | CB | Square D | HDL36030 | 18 | 30 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150149 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150150 | C | CB | Square D | HDL36025 | 14 | 25 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150150 |  | STR | Square D | 8536SCO3@B44 | 5 | 6 - 27 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150151 | C | CB | Square D | HDL36040 | 18 | 40 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150151 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150152 | C | CB | Square D | HDL36030 | 14 | 30 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150152 |  | STR | Square D | 8536SCO3@B44 | 5 | 6 - 27 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150153 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150153 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150154 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150154 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150155 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150155 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150156 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150156 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 35 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150157 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150157 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150158 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150158 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150159 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150159 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150160 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150160 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150161 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150161 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 35 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150162 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150162 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150163 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150163 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150164 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150164 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150165 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150165 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150166 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150166 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 35 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150167 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150167 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150168 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150168 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150169 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150169 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150170 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150170 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150171 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150171 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 35 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150172 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150172 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150173 | C | CB | Square D | HGL36020 | 65 | 20 | 600 | 3 | 65 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150173 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150174 | C | CB | Square D | HGL36020 | 65 | 20 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150174 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150175 | C | CB | Square D | HGL36020 | 65 | 20 | 600 | 3 | 65 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150175 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150176 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150176 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 35 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150177 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150177 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150178 | C | CB | Square D | HGL36030 | 65 | 30 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150178 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150179 | C | CB | Square D | HGL36030 | 65 | 30 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150179 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150180 | C | CB | Square D | HGL36025 | 65 | 25 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150180 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150181 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150181 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 35 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150182 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150182 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150183 | C | CB | Square D | HGL36045 | 65 | 45 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150183 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150184 | C | CB | Square D | HGL36050 | 65 | 50 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150184 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150185 | C | CB | Square D | HGL36040 | 65 | 40 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150185 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150186 | C | CB | Square D | HGL36020 | 35 | 20 | 600 | 3 | 35 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150186 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 35 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150187 | C | CB | Square D | HGL36020 | 18 | 20 | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150187 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150188 | C | CB | Square D | HGL36060 | 65 | 60 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150188 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150189 | C | CB | Square D | HGL36030 | 35 | 30 | 600 | 3 | 35 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150189 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 35 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150190 | C | CB | Square D | HGL36025 | 18 | 25 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150190 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150191 | C | CB | Square D | HGL36040 | 35 | 40 | 600 | 3 | 35 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150191 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 35 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150192 | C | CB | Square D | HGL36030 | 18 | 30 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150192 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150193 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150193 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150194 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150194 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150195 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150195 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150196 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150196 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 35 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150197 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150197 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150198 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150198 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150199 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150199 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150200 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150200 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150201 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150201 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 35 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150202 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150202 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150203 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150203 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150204 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150204 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150205 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150205 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150206 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150206 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 35 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150207 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150207 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150208 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150208 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150209 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150209 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150210 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150210 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150211 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150211 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 35 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150212 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150212 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150213 | C | CB | Square D | HGL36020 | 65 | 20 | 600 | 3 | 65 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150213 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150214 | C | CB | Square D | HGL36020 | 65 | 20 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150214 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150215 | C | CB | Square D | HGL36020 | 65 | 20 | 600 | 3 | 65 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150215 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150216 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150216 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 35 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150217 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150217 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150218 | C | CB | Square D | HGL36030 | 65 | 30 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150218 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150219 | C | CB | Square D | HGL36030 | 65 | 30 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150219 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150220 | C | CB | Square D | HGL36025 | 65 | 25 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150220 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150221 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150221 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 35 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150222 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150222 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150223 | C | CB | Square D | HGL36045 | 65 | 45 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150223 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150224 | C | CB | Square D | HGL36050 | 65 | 50 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150224 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150225 | C | CB | Square D | HGL36040 | 65 | 40 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150225 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150226 | C | CB | Square D | HGL36020 | 35 | 20 | 600 | 3 | 35 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150226 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 35 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150227 | C | CB | Square D | HGL36020 | 18 | 20 | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150227 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150228 | C | CB | Square D | HGL36060 | 65 | 60 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150228 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150229 | C | CB | Square D | HGL36030 | 35 | 30 | 600 | 3 | 35 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150229 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 35 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150230 | C | CB | Square D | HGL36025 | 18 | 25 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150230 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150231 | C | CB | Square D | HGL36040 | 35 | 40 | 600 | 3 | 35 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150231 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 35 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150232 | C | CB | Square D | HGL36030 | 18 | 30 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150232 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150233 | C | CB | Square D | HGL36030 | 65 | 30 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150233 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150234 | C | CB | Square D | HGL36030 | 65 | 30 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150234 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150235 | C | CB | Square D | HGL36025 | 65 | 25 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150235 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150236 | C | CB | Square D | HGL36045 | 65 | 45 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150236 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150237 | C | CB | Square D | HGL36050 | 65 | 50 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150237 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150238 | C | CB | Square D | HGL36040 | 65 | 40 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150238 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150239 | C | CB | Square D | HGL36060 | 65 | 60 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150239 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150240 | C | CB | Square D | HGL36030 | 35 | 30 | 600 | 3 | 35 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150240 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 35 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150241 | C | CB | Square D | HGL36025 | 18 | 25 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150241 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150242 | C | CB | Square D | HGL36040 | 35 | 40 | 600 | 3 | 35 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150242 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 35 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150243 | C | CB | Square D | HGL36030 | 18 | 30 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150243 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150244 | C | CB | Square D | HGL36030 | 65 | 30 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150244 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150245 | C | CB | Square D | HGL36030 | 65 | 30 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150245 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150246 | C | CB | Square D | HGL36025 | 65 | 25 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150246 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150247 | C | CB | Square D | HGL36045 | 65 | 45 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150247 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150248 | C | CB | Square D | HGL36050 | 65 | 50 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150248 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150249 | C | CB | Square D | HGL36040 | 65 | 40 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150249 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150250 | C | CB | Square D | HGL36060 | 65 | 60 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150250 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150251 | C | CB | Square D | HGL36030 | 35 | 30 | 600 | 3 | 35 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150251 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 35 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150252 | C | CB | Square D | HGL36025 | 18 | 25 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150252 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150253 | C | CB | Square D | HGL36040 | 35 | 40 | 600 | 3 | 35 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150253 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 35 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150254 | C | CB | Square D | HGL36030 | 18 | 30 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150254 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150255 | C | CB | Square D | HGL36030 | 65 | 30 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150255 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150256 | C | CB | Square D | HGL36030 | 65 | 30 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150256 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150257 | C | CB | Square D | HGL36025 | 65 | 25 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150257 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150258 | C | CB | Square D | HGL36045 | 65 | 45 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150258 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150259 | C | CB | Square D | HGL36050 | 65 | 50 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150259 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150260 | C | CB | Square D | HGL36040 | 65 | 40 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150260 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150261 | C | CB | Square D | HGL36060 | 65 | 60 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150261 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150262 | C | CB | Square D | HGL36030 | 35 | 30 | 600 | 3 | 35 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150262 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 35 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150263 | C | CB | Square D | HGL36025 | 18 | 25 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150263 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150264 | C | CB | Square D | HGL36040 | 35 | 40 | 600 | 3 | 35 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150264 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 35 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150265 | C | CB | Square D | HGL36030 | 18 | 30 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150265 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150266 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150266 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 65 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150267 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150267 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 65 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150268 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150268 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 65 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150269 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150269 |  | STR | Square D | 8536SCO3@B20 | 5 | 0.5 - 2.3 | 600 | 3 | 35 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150270 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150270 |  | STR | Square D | 8536SCO3@B24 | 5 | 0.5 - 2.3 | 600 | 3 | 18 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150271 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150271 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 65 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150272 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150272 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 65 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150273 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150273 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 65 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150274 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150274 |  | STR | Square D | 8536SCO3@B20 | 5 | 0.5 - 2.3 | 600 | 3 | 35 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150275 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150275 |  | STR | Square D | 8536SCO3@B24 | 5 | 0.5 - 2.3 | 600 | 3 | 18 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150276 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 1 | 4.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150276 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 65 | 200 | 3 | 1 | 4.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150277 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 1 | 4.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150277 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 65 | 208 | 3 | 1 | 4.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150278 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 1 | 4.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150278 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 65 | 240 | 3 | 1 | 4.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150279 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 1 | 2.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150279 |  | STR | Square D | 8536SCO3@B20 | 5 | 0.5 - 2.3 | 600 | 3 | 35 | 480 | 3 | 1 | 2.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150280 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 1 | 1.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150280 |  | STR | Square D | 8536SCO3@B24 | 5 | 0.5 - 2.3 | 600 | 3 | 18 | 600 | 3 | 1 | 1.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150281 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150281 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150282 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150282 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150283 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 1.5 | 6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150283 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 240 | 3 | 1.5 | 6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150284 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 1.5 | 3 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150284 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 35 | 480 | 3 | 1.5 | 3 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150285 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150285 |  | STR | Square D | 8536SCO3@B34 | 5 | 2 - 9 | 600 | 3 | 18 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150286 | C | CB | Square D | HGL36020 | 65 | 20 | 600 | 3 | 65 | 200 | 3 | 2 | 7.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150286 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 200 | 3 | 2 | 7.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150287 | C | CB | Square D | HGL36020 | 65 | 20 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150287 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150288 | C | CB | Square D | HGL36020 | 65 | 20 | 600 | 3 | 65 | 240 | 3 | 2 | 6.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150288 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 240 | 3 | 2 | 6.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150289 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 2 | 3.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150289 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 35 | 480 | 3 | 2 | 3.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150290 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150290 |  | STR | Square D | 8536SCO3@B34 | 5 | 2 - 9 | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150291 | C | CB | Square D | HGL36030 | 65 | 30 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150291 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150292 | C | CB | Square D | HGL36030 | 65 | 30 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150292 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150293 | C | CB | Square D | HGL36025 | 65 | 25 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150293 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150294 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 3 | 4.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150294 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 35 | 480 | 3 | 3 | 4.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150295 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 3 | 3.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150295 |  | STR | Square D | 8536SCO3@B34 | 5 | 2 - 9 | 600 | 3 | 18 | 600 | 3 | 3 | 3.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150296 | C | CB | Square D | HGL36045 | 65 | 45 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150296 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150297 | C | CB | Square D | HGL36040 | 65 | 40 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150297 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150298 | C | CB | Square D | HGL36040 | 65 | 40 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150298 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150299 | C | CB | Square D | HGL36020 | 35 | 20 | 600 | 3 | 35 | 480 | 3 | 5 | 7.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150299 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 35 | 480 | 3 | 5 | 7.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150300 | C | CB | Square D | HGL36020 | 18 | 20 | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150300 |  | STR | Square D | 8536SCO3@B34 | 5 | 2 - 9 | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150301 | C | CB | Square D | HGL36060 | 65 | 60 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150301 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150302 | C | CB | Square D | HGL36030 | 35 | 30 | 600 | 3 | 35 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150302 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 35 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150303 | C | CB | Square D | HGL36025 | 18 | 25 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150303 |  | STR | Square D | 8536SCO3@B44 | 5 | 6 - 27 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150304 | C | CB | Square D | HGL36040 | 35 | 40 | 600 | 3 | 35 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150304 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 35 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150305 | C | CB | Square D | HGL36030 | 18 | 30 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150305 |  | STR | Square D | 8536SCO3@B44 | 5 | 6 - 27 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150306 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150306 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150307 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150307 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150308 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150308 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150309 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150309 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150310 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150310 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150311 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150311 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150312 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150312 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150313 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150313 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150314 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150314 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150315 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150315 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150316 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150316 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150317 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150317 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150318 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150318 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150319 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150319 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150320 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150320 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150321 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150321 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150322 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150322 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150323 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150323 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150324 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150324 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150325 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150325 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150326 | C | CB | Square D | HJL36020 | 100 | 20 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150326 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150327 | C | CB | Square D | HJL36020 | 100 | 20 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150327 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150328 | C | CB | Square D | HJL36020 | 100 | 20 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150328 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150329 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150329 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150330 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150330 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150331 | C | CB | Square D | HJL36030 | 100 | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150331 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150332 | C | CB | Square D | HJL36030 | 100 | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150332 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150333 | C | CB | Square D | HJL36025 | 100 | 25 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150333 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150334 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150334 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150335 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150335 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150336 | C | CB | Square D | HJL36045 | 100 | 45 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150336 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150337 | C | CB | Square D | HJL36050 | 100 | 50 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150337 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150338 | C | CB | Square D | HJL36040 | 100 | 40 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150338 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150339 | C | CB | Square D | HJL36020 | 65 | 20 | 600 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150339 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150340 | C | CB | Square D | HJL36020 | 25 | 20 | 600 | 3 | 25 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150340 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150341 | C | CB | Square D | HJL36060 | 100 | 60 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150341 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150342 | C | CB | Square D | HJL36030 | 65 | 30 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150342 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150343 | C | CB | Square D | HJL36025 | 25 | 25 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150343 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150344 | C | CB | Square D | HJL36040 | 65 | 40 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150344 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150345 | C | CB | Square D | HJL36030 | 25 | 30 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150345 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150346 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150346 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150347 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150347 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150348 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150348 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150349 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150349 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150350 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150350 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150351 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150351 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150352 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150352 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150353 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150353 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150354 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150354 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150355 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150355 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150356 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150356 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150357 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150357 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150358 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150358 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150359 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150359 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150360 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150360 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150361 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150361 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150362 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150362 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150363 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150363 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150364 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150364 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150365 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150365 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150366 | C | CB | Square D | HJL36020 | 100 | 20 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150366 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150367 | C | CB | Square D | HJL36020 | 100 | 20 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150367 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150368 | C | CB | Square D | HJL36020 | 100 | 20 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150368 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150369 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150369 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150370 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150370 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150371 | C | CB | Square D | HJL36030 | 100 | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150371 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150372 | C | CB | Square D | HJL36030 | 100 | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150372 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150373 | C | CB | Square D | HJL36025 | 100 | 25 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150373 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150374 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150374 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150375 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150375 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150376 | C | CB | Square D | HJL36045 | 100 | 45 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150376 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150377 | C | CB | Square D | HJL36050 | 100 | 50 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150377 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150378 | C | CB | Square D | HJL36040 | 100 | 40 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150378 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150379 | C | CB | Square D | HJL36020 | 65 | 20 | 600 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150379 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150380 | C | CB | Square D | HJL36020 | 25 | 20 | 600 | 3 | 25 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150380 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150381 | C | CB | Square D | HJL36060 | 100 | 60 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150381 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150382 | C | CB | Square D | HJL36030 | 65 | 30 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150382 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150383 | C | CB | Square D | HJL36025 | 25 | 25 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150383 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150384 | C | CB | Square D | HJL36040 | 65 | 40 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150384 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150385 | C | CB | Square D | HJL36030 | 25 | 30 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150385 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150386 | C | CB | Square D | HJL36030 | 100 | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150386 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150387 | C | CB | Square D | HJL36030 | 100 | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150387 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150388 | C | CB | Square D | HJL36025 | 100 | 25 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150388 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150389 | C | CB | Square D | HJL36045 | 100 | 45 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150389 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150390 | C | CB | Square D | HJL36050 | 100 | 50 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150390 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150391 | C | CB | Square D | HJL36040 | 100 | 40 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150391 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150392 | C | CB | Square D | HJL36060 | 100 | 60 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150392 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150393 | C | CB | Square D | HJL36030 | 65 | 30 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150393 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150394 | C | CB | Square D | HJL36025 | 25 | 25 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150394 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150395 | C | CB | Square D | HJL36040 | 65 | 40 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150395 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150396 | C | CB | Square D | HJL36030 | 25 | 30 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150396 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150397 | C | CB | Square D | HJL36030 | 100 | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150397 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150398 | C | CB | Square D | HJL36030 | 100 | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150398 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150399 | C | CB | Square D | HJL36025 | 100 | 25 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150399 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150400 | C | CB | Square D | HJL36045 | 100 | 45 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150400 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150401 | C | CB | Square D | HJL36050 | 100 | 50 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150401 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150402 | C | CB | Square D | HJL36040 | 100 | 40 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150402 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150403 | C | CB | Square D | HJL36060 | 100 | 60 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150403 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150404 | C | CB | Square D | HJL36030 | 65 | 30 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150404 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150405 | C | CB | Square D | HJL36025 | 25 | 25 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150405 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150406 | C | CB | Square D | HJL36040 | 65 | 40 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150406 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150407 | C | CB | Square D | HJL36030 | 25 | 30 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150407 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150408 | C | CB | Square D | HJL36030 | 100 | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150408 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150409 | C | CB | Square D | HJL36030 | 100 | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150409 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150410 | C | CB | Square D | HJL36025 | 100 | 25 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150410 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150411 | C | CB | Square D | HJL36045 | 100 | 45 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150411 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150412 | C | CB | Square D | HJL36050 | 100 | 50 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150412 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150413 | C | CB | Square D | HJL36040 | 100 | 40 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150413 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150414 | C | CB | Square D | HJL36060 | 100 | 60 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150414 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150415 | C | CB | Square D | HJL36030 | 65 | 30 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150415 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150416 | C | CB | Square D | HJL36025 | 25 | 25 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150416 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150417 | C | CB | Square D | HJL36040 | 65 | 40 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150417 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150418 | C | CB | Square D | HJL36030 | 25 | 30 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150418 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150419 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150419 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150420 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150420 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150421 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150421 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150422 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150422 |  | STR | Square D | 8536SCO3@B20 | 5 | 0.5 - 2.3 | 600 | 3 | 65 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150423 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150423 |  | STR | Square D | 8536SCO3@B24 | 5 | 0.5 - 2.3 | 600 | 3 | 25 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150424 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150424 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150425 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150425 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150426 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150426 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150427 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150427 |  | STR | Square D | 8536SCO3@B20 | 5 | 0.5 - 2.3 | 600 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150428 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150428 |  | STR | Square D | 8536SCO3@B24 | 5 | 0.5 - 2.3 | 600 | 3 | 25 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150429 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150429 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150430 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150430 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150431 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150431 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150432 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150432 |  | STR | Square D | 8536SCO3@B20 | 5 | 0.5 - 2.3 | 600 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150433 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 1 | 1.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150433 |  | STR | Square D | 8536SCO3@B24 | 5 | 0.5 - 2.3 | 600 | 3 | 25 | 600 | 3 | 1 | 1.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150434 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150434 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150435 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150435 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150436 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150436 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150437 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150437 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150438 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150438 |  | STR | Square D | 8536SCO3@B34 | 5 | 2 - 9 | 600 | 3 | 25 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150439 | C | CB | Square D | HJL36020 | 100 | 20 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150439 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150440 | C | CB | Square D | HJL36020 | 100 | 20 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150440 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150441 | C | CB | Square D | HJL36020 | 100 | 20 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150441 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150442 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150442 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150443 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 2 | 2.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150443 |  | STR | Square D | 8536SCO3@B34 | 5 | 2 - 9 | 600 | 3 | 25 | 600 | 3 | 2 | 2.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150444 | C | CB | Square D | HJL36030 | 100 | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150444 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150445 | C | CB | Square D | HJL36030 | 100 | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150445 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150446 | C | CB | Square D | HJL36025 | 100 | 25 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150446 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150447 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150447 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150448 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 3 | 3.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150448 |  | STR | Square D | 8536SCO3@B34 | 5 | 2 - 9 | 600 | 3 | 25 | 600 | 3 | 3 | 3.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150449 | C | CB | Square D | HJL36045 | 100 | 45 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150449 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150450 | C | CB | Square D | HJL36040 | 100 | 40 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150450 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150451 | C | CB | Square D | HJL36040 | 100 | 40 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150451 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150452 | C | CB | Square D | HJL36020 | 65 | 20 | 600 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150452 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150453 | C | CB | Square D | HJL36020 | 25 | 20 | 600 | 3 | 25 | 600 | 3 | 5 | 6.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150453 |  | STR | Square D | 8536SCO3@B34 | 5 | 2 - 9 | 600 | 3 | 25 | 600 | 3 | 5 | 6.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150454 | C | CB | Square D | HJL36060 | 100 | 60 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150454 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150455 | C | CB | Square D | HJL36030 | 65 | 30 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150455 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150456 | C | CB | Square D | HJL36025 | 25 | 25 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150456 |  | STR | Square D | 8536SCO3@B44 | 5 | 6 - 27 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150457 | C | CB | Square D | HJL36040 | 65 | 40 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150457 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150458 | C | CB | Square D | HJL36030 | 25 | 30 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150458 |  | STR | Square D | 8536SCO3@B44 | 5 | 6 - 27 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150459 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150459 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150460 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150460 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150461 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150461 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150462 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150462 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150463 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150463 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150464 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150464 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150465 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150465 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150466 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150466 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150467 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150467 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150468 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150468 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150469 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150469 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150470 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150470 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150471 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150471 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150472 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150472 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150473 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150473 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150474 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150474 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150475 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150475 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150476 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150476 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150477 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150477 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150478 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150478 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150479 | C | CB | Square D | HLL36020 | 100 | 20 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150479 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150480 | C | CB | Square D | HLL36020 | 100 | 20 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150480 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150481 | C | CB | Square D | HLL36020 | 100 | 20 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150481 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150482 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150482 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150483 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150483 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150484 | C | CB | Square D | HLL36030 | 100 | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150484 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150485 | C | CB | Square D | HLL36030 | 100 | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150485 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150486 | C | CB | Square D | HLL36025 | 100 | 25 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150486 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150487 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150487 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150488 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150488 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150489 | C | CB | Square D | HLL36045 | 100 | 45 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150489 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150490 | C | CB | Square D | HLL36050 | 100 | 50 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150490 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150491 | C | CB | Square D | HLL36040 | 100 | 40 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150491 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150492 | C | CB | Square D | HLL36020 | 100 | 20 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150492 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150493 | C | CB | Square D | HLL36020 | 50 | 20 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150493 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150494 | C | CB | Square D | HLL36060 | 100 | 60 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150494 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150495 | C | CB | Square D | HLL36030 | 100 | 30 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150495 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150496 | C | CB | Square D | HLL36025 | 50 | 25 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150496 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150497 | C | CB | Square D | HLL36040 | 100 | 40 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150497 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150498 | C | CB | Square D | HLL36030 | 50 | 30 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150498 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150499 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150499 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150500 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150500 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150501 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150501 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150502 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150502 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150503 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150503 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150504 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150504 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150505 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150505 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150506 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150506 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150507 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150507 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150508 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150508 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150509 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150509 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150510 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150510 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150511 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150511 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150512 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150512 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150513 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150513 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150514 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150514 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150515 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150515 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150516 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150516 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150517 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150517 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150518 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150518 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150519 | C | CB | Square D | HLL36020 | 100 | 20 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150519 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150520 | C | CB | Square D | HLL36020 | 100 | 20 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150520 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150521 | C | CB | Square D | HLL36020 | 100 | 20 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150521 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150522 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150522 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150523 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150523 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150524 | C | CB | Square D | HLL36030 | 100 | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150524 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150525 | C | CB | Square D | HLL36030 | 100 | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150525 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150526 | C | CB | Square D | HLL36025 | 100 | 25 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150526 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150527 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150527 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150528 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150528 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150529 | C | CB | Square D | HLL36045 | 100 | 45 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150529 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150530 | C | CB | Square D | HLL36050 | 100 | 50 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150530 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150531 | C | CB | Square D | HLL36040 | 100 | 40 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150531 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150532 | C | CB | Square D | HLL36020 | 100 | 20 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150532 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150533 | C | CB | Square D | HLL36020 | 50 | 20 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150533 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150534 | C | CB | Square D | HLL36060 | 100 | 60 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150534 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150535 | C | CB | Square D | HLL36030 | 100 | 30 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150535 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150536 | C | CB | Square D | HLL36025 | 50 | 25 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150536 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150537 | C | CB | Square D | HLL36040 | 100 | 40 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150537 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150538 | C | CB | Square D | HLL36030 | 50 | 30 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150538 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE150539 | C | CB | Square D | HLL36030 | 100 | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150539 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150540 | C | CB | Square D | HLL36030 | 100 | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150540 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150541 | C | CB | Square D | HLL36025 | 100 | 25 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150541 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150542 | C | CB | Square D | HLL36045 | 100 | 45 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150542 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150543 | C | CB | Square D | HLL36050 | 100 | 50 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150543 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150544 | C | CB | Square D | HLL36040 | 100 | 40 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150544 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150545 | C | CB | Square D | HLL36060 | 100 | 60 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150545 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150546 | C | CB | Square D | HLL36030 | 100 | 30 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150546 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150547 | C | CB | Square D | HLL36025 | 50 | 25 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150547 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150548 | C | CB | Square D | HLL36040 | 100 | 40 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150548 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150549 | C | CB | Square D | HLL36030 | 50 | 30 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150549 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150550 | C | CB | Square D | HLL36030 | 100 | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150550 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150551 | C | CB | Square D | HLL36030 | 100 | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150551 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150552 | C | CB | Square D | HLL36025 | 100 | 25 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150552 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150553 | C | CB | Square D | HLL36045 | 100 | 45 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150553 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150554 | C | CB | Square D | HLL36050 | 100 | 50 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150554 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150555 | C | CB | Square D | HLL36040 | 100 | 40 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150555 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150556 | C | CB | Square D | HLL36060 | 100 | 60 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150556 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150557 | C | CB | Square D | HLL36030 | 100 | 30 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150557 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150558 | C | CB | Square D | HLL36025 | 50 | 25 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150558 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150559 | C | CB | Square D | HLL36040 | 100 | 40 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150559 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150560 | C | CB | Square D | HLL36030 | 50 | 30 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150560 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150561 | C | CB | Square D | HLL36030 | 100 | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150561 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150562 | C | CB | Square D | HLL36030 | 100 | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150562 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150563 | C | CB | Square D | HLL36025 | 100 | 25 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150563 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150564 | C | CB | Square D | HLL36045 | 100 | 45 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150564 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150565 | C | CB | Square D | HLL36050 | 100 | 50 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150565 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150566 | C | CB | Square D | HLL36040 | 100 | 40 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150566 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150567 | C | CB | Square D | HLL36060 | 100 | 60 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150567 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150568 | C | CB | Square D | HLL36030 | 100 | 30 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150568 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150569 | C | CB | Square D | HLL36025 | 50 | 25 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150569 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150570 | C | CB | Square D | HLL36040 | 100 | 40 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150570 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150571 | C | CB | Square D | HLL36030 | 50 | 30 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150571 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150572 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150572 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150573 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150573 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150574 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150574 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150575 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150575 |  | STR | Square D | 8536SCO3@B20 | 5 | 0.5 - 2.3 | 600 | 3 | 100 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150576 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150576 |  | STR | Square D | 8536SCO3@B24 | 5 | 0.5 - 2.3 | 600 | 3 | 50 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150577 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150577 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150578 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150578 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150579 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150579 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150580 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150580 |  | STR | Square D | 8536SCO3@B20 | 5 | 0.5 - 2.3 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150581 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150581 |  | STR | Square D | 8536SCO3@B24 | 5 | 0.5 - 2.3 | 600 | 3 | 50 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150582 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150582 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150583 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150583 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150584 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150584 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150585 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150585 |  | STR | Square D | 8536SCO3@B20 | 5 | 0.5 - 2.3 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150586 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150586 |  | STR | Square D | 8536SCO3@B24 | 5 | 0.5 - 2.3 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150587 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150587 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150588 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150588 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150589 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150589 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150590 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150590 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150591 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150591 |  | STR | Square D | 8536SCO3@B34 | 5 | 2 - 9 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150592 | C | CB | Square D | HLL36020 | 100 | 20 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150592 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150593 | C | CB | Square D | HLL36020 | 100 | 20 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150593 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150594 | C | CB | Square D | HLL36020 | 100 | 20 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150594 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150595 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150595 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150596 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150596 |  | STR | Square D | 8536SCO3@B34 | 5 | 2 - 9 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150597 | C | CB | Square D | HLL36030 | 100 | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150597 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150598 | C | CB | Square D | HLL36030 | 100 | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150598 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150599 | C | CB | Square D | HLL36025 | 100 | 25 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150599 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150600 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150600 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150601 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150601 |  | STR | Square D | 8536SCO3@B34 | 5 | 2 - 9 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150602 | C | CB | Square D | HLL36045 | 100 | 45 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150602 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150603 | C | CB | Square D | HLL36050 | 100 | 50 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150603 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150604 | C | CB | Square D | HLL36040 | 100 | 40 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150604 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150605 | C | CB | Square D | HLL36020 | 100 | 20 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150605 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150606 | C | CB | Square D | HLL36020 | 50 | 20 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150606 |  | STR | Square D | 8536SCO3@B34 | 5 | 2 - 9 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150607 | C | CB | Square D | HLL36060 | 100 | 60 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150607 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150608 | C | CB | Square D | HLL36030 | 100 | 30 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150608 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150609 | C | CB | Square D | HLL36025 | 50 | 25 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150609 |  | STR | Square D | 8536SCO3@B44 | 5 | 6 - 27 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150610 | C | CB | Square D | HLL36040 | 100 | 40 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150610 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150611 | C | CB | Square D | HLL36030 | 50 | 30 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150611 |  | STR | Square D | 8536SCO3@B44 | 5 | 6 - 27 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE150612 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150612 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150613 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150613 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150614 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150614 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150615 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150615 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150616 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150616 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150617 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150617 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150618 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150618 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150619 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150619 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150620 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150620 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150621 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150621 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150622 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150622 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150623 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150623 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150624 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150624 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150625 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150625 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150626 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150626 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150627 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150627 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150628 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150628 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150629 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150629 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150630 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150630 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150631 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150631 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150632 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150632 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150633 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150633 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150634 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150634 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150635 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150635 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150636 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150636 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150637 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150637 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150638 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150638 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150639 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150639 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150640 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150640 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150641 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150641 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150642 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150642 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150643 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150643 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150644 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150644 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150645 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150645 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150646 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150646 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150647 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150647 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150648 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150648 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150649 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150649 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150650 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150650 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150651 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150651 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150652 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150652 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150653 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150653 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150654 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150654 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150655 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150655 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150656 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150656 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150657 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150657 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150658 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150658 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150659 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150659 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150660 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150660 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150661 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150661 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150662 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150662 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150663 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150663 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150664 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150664 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150665 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150665 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150666 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150666 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150667 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150667 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150668 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150668 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150669 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150669 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150670 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150670 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150671 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150671 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150672 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150672 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150673 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150673 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150674 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150674 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150675 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150675 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150676 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150676 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150677 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150677 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150678 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150678 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150679 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150679 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150680 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150680 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150681 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150681 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150682 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150682 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150683 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150683 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150684 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150684 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150685 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150685 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150686 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150686 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150687 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150687 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150688 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150688 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150689 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150689 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150690 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150690 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150691 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150691 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150692 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150692 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150693 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150693 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150694 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150694 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150695 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150695 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150696 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150696 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150697 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150697 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150698 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150698 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150699 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150699 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150700 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150700 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150701 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150701 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150702 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150702 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150703 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150703 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150704 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150704 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150705 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150705 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150706 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150706 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150707 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150707 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150708 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150708 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150709 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150709 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150710 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150710 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150711 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150711 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150712 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150712 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150713 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150713 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150714 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150714 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150715 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150715 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150716 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150716 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150717 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150717 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150718 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150718 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150719 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150719 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150720 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150720 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150721 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150721 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150722 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150722 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150723 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150723 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150724 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150724 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150725 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150725 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150726 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150726 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150727 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150727 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150728 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150728 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150729 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150729 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150730 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150730 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150731 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150731 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150732 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150732 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150733 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150733 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150734 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150734 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150735 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150735 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150736 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150736 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150737 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150737 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150738 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150738 |  | STR | Square D | 8536SCO3@B20 | 5 | 0.5 - 2.3 | 600 | 3 | 65 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150739 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150739 |  | STR | Square D | 8536SCO3@B24 | 5 | 0.5 - 2.3 | 600 | 3 | 25 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150740 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150740 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150741 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150741 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150742 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150742 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150743 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150743 |  | STR | Square D | 8536SCO3@B20 | 5 | 0.5 - 2.3 | 600 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150744 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150744 |  | STR | Square D | 8536SCO3@B24 | 5 | 0.5 - 2.3 | 600 | 3 | 25 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150745 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150745 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150746 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150746 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150747 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150747 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150748 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150748 |  | STR | Square D | 8536SCO3@B20 | 5 | 0.5 - 2.3 | 600 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150749 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 1 | 1.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150749 |  | STR | Square D | 8536SCO3@B24 | 5 | 0.5 - 2.3 | 600 | 3 | 25 | 600 | 3 | 1 | 1.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150750 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150750 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150751 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150751 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150752 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150752 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150753 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150753 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150754 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150754 |  | STR | Square D | 8536SCO3@B34 | 5 | 2 - 9 | 600 | 3 | 25 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150755 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150755 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150756 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150756 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150757 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150757 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150758 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150758 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150759 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 2 | 2.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150759 |  | STR | Square D | 8536SCO3@B34 | 5 | 2 - 9 | 600 | 3 | 25 | 600 | 3 | 2 | 2.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150760 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150760 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150761 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150761 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150762 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150762 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150763 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150763 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150764 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 3 | 3.9 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150764 |  | STR | Square D | 8536SCO3@B34 | 5 | 2 - 9 | 600 | 3 | 25 | 600 | 3 | 3 | 3.9 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150765 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150765 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150766 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150766 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150767 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150767 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150768 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150768 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150769 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 5 | 6.1 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150769 |  | STR | Square D | 8536SCO3@B34 | 5 | 2 - 9 | 600 | 3 | 25 | 600 | 3 | 5 | 6.1 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150770 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150770 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150771 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150771 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150772 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150772 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150773 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150773 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150774 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150774 |  | STR | Square D | 8536SCO3@B44 | 5 | 6 - 27 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150775 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150775 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150776 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150776 |  | STR | Square D | 8536SCO3@B44 | 5 | 6 - 27 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150777 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150777 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150778 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150778 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150779 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150779 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150780 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150780 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150781 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150781 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150782 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150782 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150783 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150783 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150784 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150784 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150785 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150785 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150786 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150786 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150787 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150787 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150788 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150788 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150789 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150789 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150790 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150790 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150791 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150791 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150792 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150792 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150793 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150793 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150794 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150794 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150795 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150795 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150796 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150796 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150797 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150797 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150798 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150798 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150799 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150799 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150800 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150800 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150801 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150801 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150802 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150802 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150803 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150803 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150804 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150804 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150805 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150805 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150806 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150806 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150807 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150807 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150808 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150808 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150809 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150809 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150810 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150810 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150811 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150811 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150812 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150812 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150813 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150813 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150814 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150814 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150815 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150815 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150816 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150816 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150817 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150817 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150818 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150818 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150819 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150819 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150820 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150820 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150821 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150821 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150822 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150822 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150823 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150823 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150824 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150824 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150825 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150825 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150826 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150826 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150827 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150827 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150828 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150828 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150829 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150829 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150830 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150830 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150831 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150831 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150832 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150832 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150833 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150833 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150834 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150834 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150835 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150835 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150836 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150836 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150837 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150837 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150838 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150838 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150839 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150839 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150840 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150840 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150841 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150841 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150842 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150842 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150843 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150843 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150844 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150844 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150845 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150845 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150846 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150846 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150847 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150847 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150848 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150848 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150849 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150849 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150850 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150850 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150851 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150851 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150852 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150852 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150853 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150853 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150854 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150854 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150855 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150855 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150856 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150856 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150857 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150857 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150858 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150858 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150859 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150859 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150860 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150860 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE150861 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150861 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150862 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150862 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150863 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150863 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150864 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150864 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150865 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150865 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150866 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150866 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150867 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150867 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150868 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150868 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150869 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150869 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150870 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150870 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150871 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150871 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150872 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150872 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150873 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150873 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150874 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150874 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150875 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150875 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150876 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150876 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150877 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150877 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150878 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150878 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150879 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150879 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150880 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150880 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150881 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150881 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150882 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150882 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150883 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150883 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150884 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150884 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150885 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150885 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150886 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150886 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150887 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150887 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150888 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150888 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150889 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150889 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150890 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150890 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150891 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150891 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150892 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150892 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150893 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150893 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150894 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150894 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150895 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150895 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150896 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150896 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150897 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150897 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150898 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150898 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150899 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150899 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150900 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150900 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150901 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150901 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150902 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150902 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150903 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150903 |  | STR | Square D | 8536SCO3@B20 | 5 | 0.5 - 2.3 | 600 | 3 | 100 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150904 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150904 |  | STR | Square D | 8536SCO3@B24 | 5 | 0.5 - 2.3 | 600 | 3 | 50 | 600 | 3 | 0.5 | 0.9 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150905 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150905 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150906 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150906 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150907 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150907 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150908 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150908 |  | STR | Square D | 8536SCO3@B20 | 5 | 0.5 - 2.3 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150909 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150909 |  | STR | Square D | 8536SCO3@B24 | 5 | 0.5 - 2.3 | 600 | 3 | 50 | 600 | 3 | 0.75 | 1.3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150910 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150910 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150911 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150911 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150912 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150912 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150913 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150913 |  | STR | Square D | 8536SCO3@B20 | 5 | 0.5 - 2.3 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150914 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150914 |  | STR | Square D | 8536SCO3@B24 | 5 | 0.5 - 2.3 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150915 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150915 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150916 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150916 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150917 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150917 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150918 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150918 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150919 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150919 |  | STR | Square D | 8536SCO3@B34 | 5 | 2 - 9 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150920 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150920 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150921 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150921 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150922 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150922 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150923 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150923 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150924 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150924 |  | STR | Square D | 8536SCO3@B34 | 5 | 2 - 9 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150925 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150925 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150926 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150926 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150927 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150927 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150928 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150928 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150929 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150929 |  | STR | Square D | 8536SCO3@B34 | 5 | 2 - 9 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150930 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150930 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150931 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150931 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150932 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150932 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150933 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150933 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150934 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150934 |  | STR | Square D | 8536SCO3@B34 | 5 | 2 - 9 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150935 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150935 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150936 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150936 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150937 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150937 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150938 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150938 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150939 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150939 |  | STR | Square D | 8536SCO3@B44 | 5 | 6 - 27 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150940 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE150940 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = Use wire ties evenly spaced apart to secure conductors in place.
(7) = See Table 7 for minimum internal wiring between load side of short circuit protective device & line side of starter.
(8) = "@" refer to digest to complete contactor Catalog number for coil voltage and Form modifications.
(9) = Insulator to be provided underneath starter. (QMFZ2), Fastex, Type Formex GK-30, 1/32 inch minimum thickness by 4 inches x 5.7 inches.
Table 7 - Minimum Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
|  | Wire Code |  | Wire Size
|  | 7a |  | 12 AWG
|  | 7b |  | 8 AWG
|  | 7c |  | 2 AWG
|  | 7d |  | 1 AWG
|  | 7e |  | 250 MCM
|  | 7f |  | 300 MCM
|  | 7g |  | (2) 250 MCM

## Size2
Issued: 2007-01-23
Last Revised: 2007-01-23
|  |  |  | "@" refer to Digest to complete | [8 empty] | Use Square D Digest for selection of Melting Alloy and Bi-Metal Overloads only
starter Catalog number for coil
voltage codes and Form modifications
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE150941 | C | CB | Square D | HDL36080 | 25 | 80 | 600 | 3 | 25 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150941 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 25 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150942 | C | CB | Square D | HDL36090 | 25 | 90 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150942 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150943 | C | CB | Square D | HDL36070 | 25 | 70 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150943 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150944 | C | CB | Square D | HDL36110 | 25 | 110 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150944 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150945 | C | CB | Square D | HDL36060 | 18 | 60 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150945 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150946 | C | CB | Square D | HDL36045 | 14 | 45 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150946 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150947 | C | CB | Square D | HDL36070 | 18 | 70 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150947 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150948 | C | CB | Square D | HDL36060 | 14 | 60 | 600 | 3 | 14 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150948 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 14 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150949 | C | CB | Square D | HDL36090 | 18 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150949 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150950 | C | CB | Square D | HDL36070 | 14 | 70 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150950 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150951 | C | CB | Square D | HDL36080 | 25 | 80 | 600 | 3 | 25 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150951 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 25 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150952 | C | CB | Square D | HDL36090 | 25 | 90 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150952 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150953 | C | CB | Square D | HDL36070 | 25 | 70 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150953 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150954 | C | CB | Square D | HDL36110 | 25 | 110 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150954 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150955 | C | CB | Square D | HDL36060 | 18 | 60 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150955 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150956 | C | CB | Square D | HDL36045 | 14 | 45 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150956 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150957 | C | CB | Square D | HDL36070 | 18 | 70 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150957 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150958 | C | CB | Square D | HDL36060 | 14 | 60 | 600 | 3 | 14 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150958 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 14 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150959 | C | CB | Square D | HDL36090 | 18 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150959 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150960 | C | CB | Square D | HDL36070 | 14 | 70 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150960 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE150961 | C | CB | Square D | HDL36080 | 25 | 80 | 600 | 3 | 25 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150961 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 25 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150962 | C | CB | Square D | HDL36090 | 25 | 90 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150962 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150963 | C | CB | Square D | HDL36070 | 25 | 70 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150963 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150964 | C | CB | Square D | HDL36110 | 25 | 110 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150964 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150965 | C | CB | Square D | HDL36060 | 18 | 60 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150965 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150966 | C | CB | Square D | HDL36045 | 14 | 45 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150966 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150967 | C | CB | Square D | HDL36070 | 18 | 70 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150967 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150968 | C | CB | Square D | HDL36060 | 14 | 60 | 600 | 3 | 14 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150968 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 14 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150969 | C | CB | Square D | HDL36090 | 18 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150969 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150970 | C | CB | Square D | HDL36070 | 14 | 70 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150970 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150971 | C | CB | Square D | HDL36080 | 25 | 80 | 600 | 3 | 25 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150971 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 25 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150972 | C | CB | Square D | HDL36090 | 25 | 90 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150972 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150973 | C | CB | Square D | HDL36070 | 25 | 70 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150973 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150974 | C | CB | Square D | HDL36110 | 25 | 110 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150974 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150975 | C | CB | Square D | HDL36060 | 18 | 60 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150975 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150976 | C | CB | Square D | HDL36045 | 14 | 45 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150976 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150977 | C | CB | Square D | HDL36070 | 18 | 70 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150977 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150978 | C | CB | Square D | HDL36060 | 14 | 60 | 600 | 3 | 14 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150978 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 14 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150979 | C | CB | Square D | HDL36090 | 18 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150979 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150980 | C | CB | Square D | HDL36070 | 14 | 70 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150980 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150981 | C | CB | Square D | HDL36080 | 25 | 80 | 600 | 3 | 25 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150981 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 25 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150982 | C | CB | Square D | HDL36090 | 25 | 90 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150982 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150983 | C | CB | Square D | HDL36070 | 25 | 70 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150983 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150984 | C | CB | Square D | HDL36110 | 25 | 110 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150984 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150985 | C | CB | Square D | HDL36060 | 18 | 60 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150985 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150986 | C | CB | Square D | HDL36045 | 14 | 45 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150986 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150987 | C | CB | Square D | HDL36070 | 18 | 70 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150987 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150988 | C | CB | Square D | HDL36060 | 14 | 60 | 600 | 3 | 14 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150988 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 14 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150989 | C | CB | Square D | HDL36090 | 18 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150989 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150990 | C | CB | Square D | HDL36070 | 14 | 70 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150990 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150991 | C | CB | Square D | HDL36080 | 25 | 80 | 600 | 3 | 25 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150991 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 25 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150992 | C | CB | Square D | HDL36090 | 25 | 90 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150992 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150993 | C | CB | Square D | HDL36070 | 25 | 70 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150993 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150994 | C | CB | Square D | HDL36110 | 25 | 110 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150994 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150995 | C | CB | Square D | HDL36060 | 18 | 60 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150995 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150996 | C | CB | Square D | HDL36045 | 14 | 45 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150996 |  | STR | Square D | 8536SDO1@B54 | 5 | 10 - 45 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150997 | C | CB | Square D | HDL36070 | 18 | 70 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150997 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150998 | C | CB | Square D | HDL36060 | 14 | 60 | 600 | 3 | 14 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150998 |  | STR | Square D | 8536SDO1@B54 | 5 | 10 - 45 | 600 | 3 | 14 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150999 | C | CB | Square D | HDL36090 | 18 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE150999 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151000 | C | CB | Square D | HDL36070 | 14 | 70 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151000 |  | STR | Square D | 8536SDO1@B54 | 5 | 10 - 45 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151001 | C | CB | Square D | HGL36080 | 65 | 80 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151001 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151002 | C | CB | Square D | HGL36090 | 65 | 90 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151002 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151003 | C | CB | Square D | HGL36070 | 65 | 70 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151003 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151004 | C | CB | Square D | HGL36110 | 65 | 110 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151004 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151005 | C | CB | Square D | HGL36060 | 35 | 60 | 600 | 3 | 35 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151005 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 35 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151006 | C | CB | Square D | HGL36045 | 18 | 45 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151006 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151007 | C | CB | Square D | HGL36070 | 35 | 70 | 600 | 3 | 35 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151007 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 35 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151008 | C | CB | Square D | HGL36060 | 18 | 60 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151008 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151009 | C | CB | Square D | HGL36090 | 35 | 90 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151009 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151010 | C | CB | Square D | HGL36070 | 18 | 70 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151010 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151011 | C | CB | Square D | HGL36080 | 65 | 80 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151011 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151012 | C | CB | Square D | HGL36090 | 65 | 90 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151012 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151013 | C | CB | Square D | HGL36070 | 65 | 70 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151013 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151014 | C | CB | Square D | HGL36110 | 65 | 110 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151014 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151015 | C | CB | Square D | HGL36060 | 35 | 60 | 600 | 3 | 35 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151015 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 35 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151016 | C | CB | Square D | HGL36045 | 18 | 45 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151016 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151017 | C | CB | Square D | HGL36070 | 35 | 70 | 600 | 3 | 35 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151017 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 35 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151018 | C | CB | Square D | HGL36060 | 18 | 60 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151018 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151019 | C | CB | Square D | HGL36090 | 35 | 90 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151019 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151020 | C | CB | Square D | HGL36070 | 18 | 70 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151020 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151021 | C | CB | Square D | HGL36080 | 65 | 80 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151021 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151022 | C | CB | Square D | HGL36090 | 65 | 90 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151022 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151023 | C | CB | Square D | HGL36070 | 65 | 70 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151023 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151024 | C | CB | Square D | HGL36110 | 65 | 110 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151024 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151025 | C | CB | Square D | HGL36060 | 35 | 60 | 600 | 3 | 35 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151025 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 35 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151026 | C | CB | Square D | HGL36045 | 18 | 45 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151026 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151027 | C | CB | Square D | HGL36070 | 35 | 70 | 600 | 3 | 35 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151027 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 35 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151028 | C | CB | Square D | HGL36060 | 18 | 60 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151028 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151029 | C | CB | Square D | HGL36090 | 35 | 90 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151029 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151030 | C | CB | Square D | HGL36070 | 18 | 70 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151030 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151031 | C | CB | Square D | HGL36080 | 65 | 80 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151031 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151032 | C | CB | Square D | HGL36090 | 65 | 90 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151032 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151033 | C | CB | Square D | HGL36070 | 65 | 70 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151033 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151034 | C | CB | Square D | HGL36110 | 65 | 110 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151034 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151035 | C | CB | Square D | HGL36060 | 35 | 60 | 600 | 3 | 35 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151035 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 35 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151036 | C | CB | Square D | HGL36045 | 18 | 45 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151036 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151037 | C | CB | Square D | HGL36070 | 35 | 70 | 600 | 3 | 35 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151037 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 35 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151038 | C | CB | Square D | HGL36060 | 18 | 60 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151038 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151039 | C | CB | Square D | HGL36090 | 35 | 90 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151039 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151040 | C | CB | Square D | HGL36070 | 18 | 70 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151040 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151041 | C | CB | Square D | HGL36080 | 65 | 80 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151041 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151042 | C | CB | Square D | HGL36090 | 65 | 90 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151042 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151043 | C | CB | Square D | HGL36070 | 65 | 70 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151043 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151044 | C | CB | Square D | HGL36110 | 65 | 110 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151044 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151045 | C | CB | Square D | HGL36060 | 35 | 60 | 600 | 3 | 35 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151045 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 35 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151046 | C | CB | Square D | HGL36045 | 18 | 45 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151046 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151047 | C | CB | Square D | HGL36070 | 35 | 70 | 600 | 3 | 35 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151047 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 35 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151048 | C | CB | Square D | HGL36060 | 18 | 60 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151048 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151049 | C | CB | Square D | HGL36090 | 35 | 90 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151049 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151050 | C | CB | Square D | HGL36070 | 18 | 70 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151050 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151051 | C | CB | Square D | HGL36080 | 65 | 80 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151051 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151052 | C | CB | Square D | HGL36090 | 65 | 90 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151052 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151053 | C | CB | Square D | HGL36070 | 65 | 70 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151053 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151054 | C | CB | Square D | HGL36110 | 65 | 110 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151054 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151055 | C | CB | Square D | HGL36060 | 35 | 60 | 600 | 3 | 35 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151055 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 35 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151056 | C | CB | Square D | HGL36045 | 18 | 45 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151056 |  | STR | Square D | 8536SDO1@B54 | 5 | 10 - 45 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151057 | C | CB | Square D | HGL36070 | 35 | 70 | 600 | 3 | 35 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151057 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 35 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151058 | C | CB | Square D | HGL36060 | 18 | 60 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151058 |  | STR | Square D | 8536SDO1@B54 | 5 | 10 - 45 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151059 | C | CB | Square D | HGL36090 | 35 | 90 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151059 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151060 | C | CB | Square D | HGL36070 | 18 | 70 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151060 |  | STR | Square D | 8536SDO1@B54 | 5 | 10 - 45 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151061 | C | CB | Square D | HJL36080 | 100 | 80 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151061 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151062 | C | CB | Square D | HJL36090 | 100 | 90 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151062 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151063 | C | CB | Square D | HJL36070 | 100 | 70 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151063 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151064 | C | CB | Square D | HJL36110 | 100 | 110 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151064 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151065 | C | CB | Square D | HJL36060 | 65 | 60 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151065 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151066 | C | CB | Square D | HJL36045 | 25 | 45 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151066 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151067 | C | CB | Square D | HJL36070 | 65 | 70 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151067 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151068 | C | CB | Square D | HJL36060 | 25 | 60 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151068 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151069 | C | CB | Square D | HJL36090 | 65 | 90 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151069 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151070 | C | CB | Square D | HJL36070 | 25 | 70 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151070 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151071 | C | CB | Square D | HJL36080 | 100 | 80 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151071 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151072 | C | CB | Square D | HJL36090 | 100 | 90 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151072 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151073 | C | CB | Square D | HJL36070 | 100 | 70 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151073 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151074 | C | CB | Square D | HJL36110 | 100 | 110 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151074 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151075 | C | CB | Square D | HJL36060 | 65 | 60 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151075 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151076 | C | CB | Square D | HJL36045 | 25 | 45 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151076 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151077 | C | CB | Square D | HJL36070 | 65 | 70 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151077 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151078 | C | CB | Square D | HJL36060 | 25 | 60 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151078 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151079 | C | CB | Square D | HJL36090 | 65 | 90 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151079 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151080 | C | CB | Square D | HJL36070 | 25 | 70 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151080 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151081 | C | CB | Square D | HJL36080 | 100 | 80 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151081 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151082 | C | CB | Square D | HJL36090 | 100 | 90 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151082 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151083 | C | CB | Square D | HJL36070 | 100 | 70 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151083 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151084 | C | CB | Square D | HJL36110 | 100 | 110 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151084 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151085 | C | CB | Square D | HJL36060 | 65 | 60 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151085 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151086 | C | CB | Square D | HJL36045 | 25 | 45 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151086 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151087 | C | CB | Square D | HJL36070 | 65 | 70 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151087 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151088 | C | CB | Square D | HJL36060 | 25 | 60 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151088 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151089 | C | CB | Square D | HJL36090 | 65 | 90 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151089 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151090 | C | CB | Square D | HJL36070 | 25 | 70 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151090 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151091 | C | CB | Square D | HJL36080 | 100 | 80 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151091 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151092 | C | CB | Square D | HJL36090 | 100 | 90 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151092 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151093 | C | CB | Square D | HJL36070 | 100 | 70 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151093 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151094 | C | CB | Square D | HJL36110 | 100 | 110 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151094 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151095 | C | CB | Square D | HJL36060 | 65 | 60 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151095 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151096 | C | CB | Square D | HJL36045 | 25 | 45 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151096 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151097 | C | CB | Square D | HJL36070 | 65 | 70 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151097 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151098 | C | CB | Square D | HJL36060 | 25 | 60 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151098 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151099 | C | CB | Square D | HJL36090 | 65 | 90 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151099 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151100 | C | CB | Square D | HJL36070 | 25 | 70 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151100 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151101 | C | CB | Square D | HJL36080 | 100 | 80 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151101 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151102 | C | CB | Square D | HJL36090 | 100 | 90 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151102 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151103 | C | CB | Square D | HJL36070 | 100 | 70 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151103 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151104 | C | CB | Square D | HJL36110 | 100 | 110 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151104 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151105 | C | CB | Square D | HJL36060 | 65 | 60 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151105 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151106 | C | CB | Square D | HJL36045 | 25 | 45 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151106 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151107 | C | CB | Square D | HJL36070 | 65 | 70 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151107 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151108 | C | CB | Square D | HJL36060 | 25 | 60 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151108 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151109 | C | CB | Square D | HJL36090 | 65 | 90 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151109 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151110 | C | CB | Square D | HJL36070 | 25 | 70 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151110 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151111 | C | CB | Square D | HJL36080 | 100 | 80 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151111 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151112 | C | CB | Square D | HJL36090 | 100 | 90 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151112 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151113 | C | CB | Square D | HJL36070 | 100 | 70 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151113 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151114 | C | CB | Square D | HJL36110 | 100 | 110 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151114 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151115 | C | CB | Square D | HJL36060 | 65 | 60 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151115 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151116 | C | CB | Square D | HJL36045 | 25 | 45 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151116 |  | STR | Square D | 8536SDO1@B54 | 5 | 10 - 45 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151117 | C | CB | Square D | HJL36070 | 65 | 70 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151117 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151118 | C | CB | Square D | HJL36060 | 25 | 60 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151118 |  | STR | Square D | 8536SDO1@B54 | 5 | 10 - 45 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151119 | C | CB | Square D | HJL36090 | 65 | 90 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151119 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151120 | C | CB | Square D | HJL36070 | 25 | 70 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151120 |  | STR | Square D | 8536SDO1@B54 | 5 | 10 - 45 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151121 | C | CB | Square D | HLL36080 | 100 | 80 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151121 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151122 | C | CB | Square D | HLL36090 | 100 | 90 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151122 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151123 | C | CB | Square D | HLL36070 | 100 | 70 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151123 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151124 | C | CB | Square D | HLL36110 | 100 | 110 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151124 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151125 | C | CB | Square D | HLL36060 | 100 | 60 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151125 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151126 | C | CB | Square D | HLL36045 | 50 | 45 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151126 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151127 | C | CB | Square D | HLL36070 | 100 | 70 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151127 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151128 | C | CB | Square D | HLL36060 | 50 | 60 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151128 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151129 | C | CB | Square D | HLL36090 | 100 | 90 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151129 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151130 | C | CB | Square D | HLL36070 | 50 | 70 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151130 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151131 | C | CB | Square D | HLL36080 | 100 | 80 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151131 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151132 | C | CB | Square D | HLL36090 | 100 | 90 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151132 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151133 | C | CB | Square D | HLL36070 | 100 | 70 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151133 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151134 | C | CB | Square D | HLL36110 | 100 | 110 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151134 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151135 | C | CB | Square D | HLL36060 | 100 | 60 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151135 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151136 | C | CB | Square D | HLL36045 | 50 | 45 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151136 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151137 | C | CB | Square D | HLL36070 | 100 | 70 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151137 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151138 | C | CB | Square D | HLL36060 | 50 | 60 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151138 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151139 | C | CB | Square D | HLL36090 | 100 | 90 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151139 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151140 | C | CB | Square D | HLL36070 | 50 | 70 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151140 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE151141 | C | CB | Square D | HLL36080 | 100 | 80 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151141 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151142 | C | CB | Square D | HLL36090 | 100 | 90 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151142 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151143 | C | CB | Square D | HLL36070 | 100 | 70 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151143 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151144 | C | CB | Square D | HLL36110 | 100 | 110 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151144 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151145 | C | CB | Square D | HLL36060 | 100 | 60 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151145 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151146 | C | CB | Square D | HLL36045 | 50 | 45 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151146 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151147 | C | CB | Square D | HLL36070 | 100 | 70 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151147 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151148 | C | CB | Square D | HLL36060 | 50 | 60 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151148 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151149 | C | CB | Square D | HLL36090 | 100 | 90 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151149 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151150 | C | CB | Square D | HLL36070 | 50 | 70 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151150 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151151 | C | CB | Square D | HLL36080 | 100 | 80 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151151 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151152 | C | CB | Square D | HLL36090 | 100 | 90 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151152 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151153 | C | CB | Square D | HLL36070 | 100 | 70 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151153 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151154 | C | CB | Square D | HLL36110 | 100 | 110 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151154 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151155 | C | CB | Square D | HLL36060 | 100 | 60 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151155 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151156 | C | CB | Square D | HLL36045 | 50 | 45 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151156 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151157 | C | CB | Square D | HLL36070 | 100 | 70 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151157 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151158 | C | CB | Square D | HLL36060 | 50 | 60 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151158 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151159 | C | CB | Square D | HLL36090 | 100 | 90 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151159 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151160 | C | CB | Square D | HLL36070 | 50 | 70 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151160 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151161 | C | CB | Square D | HLL36080 | 100 | 80 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151161 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151162 | C | CB | Square D | HLL36090 | 100 | 90 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151162 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151163 | C | CB | Square D | HLL36070 | 100 | 70 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151163 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151164 | C | CB | Square D | HLL36110 | 100 | 110 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151164 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151165 | C | CB | Square D | HLL36060 | 100 | 60 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151165 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151166 | C | CB | Square D | HLL36045 | 50 | 45 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151166 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151167 | C | CB | Square D | HLL36070 | 100 | 70 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151167 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151168 | C | CB | Square D | HLL36060 | 50 | 60 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151168 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151169 | C | CB | Square D | HLL36090 | 100 | 90 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151169 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151170 | C | CB | Square D | HLL36070 | 50 | 70 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151170 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151171 | C | CB | Square D | HLL36080 | 100 | 80 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151171 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151172 | C | CB | Square D | HLL36090 | 100 | 90 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151172 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151173 | C | CB | Square D | HLL36070 | 100 | 70 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151173 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151174 | C | CB | Square D | HLL36110 | 100 | 110 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151174 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151175 | C | CB | Square D | HLL36060 | 100 | 60 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151175 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151176 | C | CB | Square D | HLL36045 | 50 | 45 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151176 |  | STR | Square D | 8536SDO1@B54 | 5 | 10 - 45 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151177 | C | CB | Square D | HLL36070 | 100 | 70 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151177 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151178 | C | CB | Square D | HLL36060 | 50 | 60 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151178 |  | STR | Square D | 8536SDO1@B54 | 5 | 10 - 45 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151179 | C | CB | Square D | HLL36090 | 100 | 90 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151179 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151180 | C | CB | Square D | HLL36070 | 50 | 70 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151180 |  | STR | Square D | 8536SDO1@B54 | 5 | 10 - 45 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE151181 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151181 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151182 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151182 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151183 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151183 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151184 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151184 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151185 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151185 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151186 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151186 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151187 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151187 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151188 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151188 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151189 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151189 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151190 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151190 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151191 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151191 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151192 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151192 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151193 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151193 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151194 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151194 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151195 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151195 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151196 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151196 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151197 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151197 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151198 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151198 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151199 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151199 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151200 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151200 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151201 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151201 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151202 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151202 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151203 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151203 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151204 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151204 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151205 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151205 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151206 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151206 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151207 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151207 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151208 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151208 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151209 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151209 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151210 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151210 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151211 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151211 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151212 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151212 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151213 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151213 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151214 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151214 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151215 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151215 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151216 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151216 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151217 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151217 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151218 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151218 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151219 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151219 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151220 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151220 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151221 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151221 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151222 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151222 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151223 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151223 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151224 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151224 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151225 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151225 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151226 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151226 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151227 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151227 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151228 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151228 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151229 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151229 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151230 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151230 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151231 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151231 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151232 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151232 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151233 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151233 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151234 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151234 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151235 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151235 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151236 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151236 |  | STR | Square D | 8536SDO1@B54 | 5 | 10 - 45 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151237 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151237 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151238 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151238 |  | STR | Square D | 8536SDO1@B54 | 5 | 10 - 45 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151239 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151239 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151240 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151240 |  | STR | Square D | 8536SDO1@B54 | 5 | 10 - 45 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151241 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151241 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151242 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151242 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151243 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151243 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151244 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151244 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151245 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151245 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151246 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151246 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151247 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151247 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151248 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151248 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151249 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151249 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151250 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151250 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151251 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151251 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151252 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151252 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151253 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151253 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151254 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151254 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151255 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151255 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151256 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151256 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151257 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151257 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151258 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151258 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151259 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151259 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151260 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151260 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151261 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151261 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151262 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151262 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151263 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151263 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151264 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151264 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151265 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151265 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151266 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151266 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151267 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151267 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151268 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151268 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151269 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151269 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151270 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151270 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151271 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151271 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151272 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151272 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151273 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151273 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151274 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151274 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151275 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151275 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151276 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151276 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151277 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151277 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151278 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151278 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151279 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151279 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151280 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151280 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151281 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151281 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151282 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151282 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151283 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151283 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151284 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151284 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151285 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151285 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151286 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151286 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151287 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151287 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151288 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151288 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151289 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151289 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151290 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151290 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151291 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151291 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151292 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151292 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151293 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151293 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151294 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151294 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151295 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151295 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151296 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151296 |  | STR | Square D | 8536SDO1@B54 | 5 | 10 - 45 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151297 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151297 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151298 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151298 |  | STR | Square D | 8536SDO1@B54 | 5 | 10 - 45 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151299 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151299 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151300 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE151300 |  | STR | Square D | 8536SDO1@B54 | 5 | 10 - 45 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = Use wire ties evenly spaced apart to secure conductors in place.
(7) = See Table 7 for minimum internal wiring between load side of short circuit protective device & line side of starter.
(8) = "@" refer to digest to complete contactor Catalog number for coil voltage and Form modifications.
(9) = Insulator to be provided underneath starter. (QMFZ2), Fastex, Type Formex GK-30, 1/32 inch minimum thickness by 4 inches x 5.7 inches.
Table 7 - Minimum Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
|  | Wire Code |  | Wire Size
|  | 7a |  | 12 AWG
|  | 7b |  | 8 AWG
|  | 7c |  | 2 AWG
|  | 7d |  | 1 AWG
|  | 7e |  | 250 MCM
|  | 7f |  | 300 MCM
|  | 7g |  | (2) 250 MCM

## Size3
Issued: 2007-01-23
Last Revised: 2007-01-23
|  |  |  | "@" refer to Digest to complete | [8 empty] | Use Square D Digest for selection of Melting Alloy and Bi-Metal Overloads only
starter Catalog number for coil
voltage codes and Form modifications
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE151333 | C | CB | Square D | HDL36090 | 18 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151333 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151334 | C | CB | Square D | HDL36070 | 14 | 70 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151334 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151335 | C | CB | Square D | HDL36100 | 18 | 100 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151335 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151336 | C | CB | Square D | HDL36080 | 14 | 80 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151336 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151337 | C | CB | Square D | HDL36110 | 14 | 110 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151337 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151338 | C | CB | Square D | HDL36090 | 18 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151338 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151339 | C | CB | Square D | HDL36070 | 14 | 70 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151339 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151340 | C | CB | Square D | HDL36100 | 18 | 100 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151340 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151341 | C | CB | Square D | HDL36080 | 14 | 80 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151341 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151342 | C | CB | Square D | HDL36110 | 14 | 110 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151342 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151343 | C | CB | Square D | HDL36090 | 18 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151343 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151344 | C | CB | Square D | HDL36070 | 14 | 70 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151344 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151345 | C | CB | Square D | HDL36100 | 18 | 100 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151345 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151346 | C | CB | Square D | HDL36080 | 14 | 80 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151346 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151347 | C | CB | Square D | HDL36110 | 14 | 110 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151347 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151348 | C | CB | Square D | HDL36090 | 18 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151348 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151349 | C | CB | Square D | HDL36070 | 14 | 70 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151349 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151350 | C | CB | Square D | HDL36100 | 18 | 100 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151350 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151351 | C | CB | Square D | HDL36080 | 14 | 80 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151351 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151352 | C | CB | Square D | HDL36110 | 14 | 110 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151352 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151353 | C | CB | Square D | HDL36090 | 18 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151353 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151354 | C | CB | Square D | HDL36070 | 14 | 70 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151354 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151355 | C | CB | Square D | HDL36100 | 18 | 100 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151355 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151356 | C | CB | Square D | HDL36080 | 14 | 80 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151356 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151357 | C | CB | Square D | HDL36110 | 14 | 110 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151357 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151358 | C | CB | Square D | HDL36090 | 18 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151358 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151359 | C | CB | Square D | HDL36070 | 14 | 70 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151359 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151360 | C | CB | Square D | HDL36100 | 18 | 100 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151360 |  | STR | Square D | 8536SEO1@B60 | 5 | 20 - 90 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151361 | C | CB | Square D | HDL36080 | 14 | 80 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151361 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151362 | C | CB | Square D | HDL36110 | 14 | 110 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151362 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151363 | C | CB | Square D | HGL36090 | 35 | 90 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151363 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151364 | C | CB | Square D | HGL36070 | 18 | 70 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151364 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151365 | C | CB | Square D | HGL36100 | 35 | 100 | 600 | 3 | 35 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151365 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 35 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151366 | C | CB | Square D | HGL36080 | 18 | 80 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151366 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151367 | C | CB | Square D | HGL36110 | 18 | 110 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151367 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151368 | C | CB | Square D | HGL36090 | 35 | 90 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151368 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151369 | C | CB | Square D | HGL36070 | 18 | 70 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151369 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151370 | C | CB | Square D | HGL36100 | 35 | 100 | 600 | 3 | 35 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151370 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 35 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151371 | C | CB | Square D | HGL36080 | 18 | 80 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151371 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151372 | C | CB | Square D | HGL36110 | 18 | 110 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151372 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151373 | C | CB | Square D | HGL36090 | 35 | 90 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151373 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151374 | C | CB | Square D | HGL36070 | 18 | 70 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151374 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151375 | C | CB | Square D | HGL36100 | 35 | 100 | 600 | 3 | 35 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151375 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 35 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151376 | C | CB | Square D | HGL36080 | 18 | 80 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151376 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151377 | C | CB | Square D | HGL36110 | 18 | 110 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151377 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151378 | C | CB | Square D | HGL36090 | 35 | 90 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151378 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151379 | C | CB | Square D | HGL36070 | 18 | 70 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151379 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151380 | C | CB | Square D | HGL36100 | 35 | 100 | 600 | 3 | 35 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151380 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 35 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151381 | C | CB | Square D | HGL36080 | 18 | 80 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151381 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151382 | C | CB | Square D | HGL36110 | 18 | 110 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151382 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151383 | C | CB | Square D | HGL36090 | 35 | 90 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151383 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151384 | C | CB | Square D | HGL36070 | 18 | 70 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151384 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151385 | C | CB | Square D | HGL36100 | 35 | 100 | 600 | 3 | 35 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151385 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 35 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151386 | C | CB | Square D | HGL36080 | 18 | 80 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151386 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151387 | C | CB | Square D | HGL36110 | 18 | 110 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151387 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151388 | C | CB | Square D | HGL36090 | 35 | 90 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151388 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151389 | C | CB | Square D | HGL36070 | 18 | 70 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151389 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151390 | C | CB | Square D | HGL36100 | 35 | 100 | 600 | 3 | 35 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151390 |  | STR | Square D | 8536SEO1@B60 | 5 | 20 - 90 | 600 | 3 | 35 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151391 | C | CB | Square D | HGL36080 | 18 | 80 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151391 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151392 | C | CB | Square D | HGL36110 | 18 | 110 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151392 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151393 | C | CB | Square D | HJL36090 | 65 | 90 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151393 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151394 | C | CB | Square D | HJL36070 | 25 | 70 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151394 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151395 | C | CB | Square D | HJL36100 | 65 | 100 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151395 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151396 | C | CB | Square D | HJL36080 | 25 | 80 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151396 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151397 | C | CB | Square D | HJL36110 | 25 | 110 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151397 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151398 | C | CB | Square D | HJL36090 | 65 | 90 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151398 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151399 | C | CB | Square D | HJL36070 | 25 | 70 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151399 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151400 | C | CB | Square D | HJL36100 | 65 | 100 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151400 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151401 | C | CB | Square D | HJL36080 | 25 | 80 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151401 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151402 | C | CB | Square D | HJL36110 | 25 | 110 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151402 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151403 | C | CB | Square D | HJL36090 | 65 | 90 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151403 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151404 | C | CB | Square D | HJL36070 | 25 | 70 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151404 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151405 | C | CB | Square D | HJL36100 | 65 | 100 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151405 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151406 | C | CB | Square D | HJL36080 | 25 | 80 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151406 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151407 | C | CB | Square D | HJL36110 | 25 | 110 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151407 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151408 | C | CB | Square D | HJL36090 | 65 | 90 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151408 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151409 | C | CB | Square D | HJL36070 | 25 | 70 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151409 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151410 | C | CB | Square D | HJL36100 | 65 | 100 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151410 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151411 | C | CB | Square D | HJL36080 | 25 | 80 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151411 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151412 | C | CB | Square D | HJL36110 | 25 | 110 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151412 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151413 | C | CB | Square D | HJL36090 | 65 | 90 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151413 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151414 | C | CB | Square D | HJL36070 | 25 | 70 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151414 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151415 | C | CB | Square D | HJL36100 | 65 | 100 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151415 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151416 | C | CB | Square D | HJL36080 | 25 | 80 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151416 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151417 | C | CB | Square D | HJL36110 | 25 | 110 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151417 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151418 | C | CB | Square D | HJL36090 | 65 | 90 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151418 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151419 | C | CB | Square D | HJL36070 | 25 | 70 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151419 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151420 | C | CB | Square D | HJL36100 | 65 | 100 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151420 |  | STR | Square D | 8536SEO1@B60 | 5 | 20 - 90 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151421 | C | CB | Square D | HJL36080 | 25 | 80 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151421 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151422 | C | CB | Square D | HJL36110 | 25 | 110 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151422 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151423 | C | CB | Square D | HLL36090 | 100 | 90 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151423 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151424 | C | CB | Square D | HLL36070 | 50 | 70 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151424 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151425 | C | CB | Square D | HLL36100 | 100 | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151425 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151426 | C | CB | Square D | HLL36080 | 50 | 80 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151426 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151427 | C | CB | Square D | HLL36110 | 50 | 110 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151427 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151428 | C | CB | Square D | HLL36090 | 100 | 90 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151428 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151429 | C | CB | Square D | HLL36070 | 50 | 70 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151429 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151430 | C | CB | Square D | HLL36100 | 100 | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151430 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151431 | C | CB | Square D | HLL36080 | 50 | 80 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151431 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151432 | C | CB | Square D | HLL36110 | 50 | 110 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151432 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE151433 | C | CB | Square D | HLL36090 | 100 | 90 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151433 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151434 | C | CB | Square D | HLL36070 | 50 | 70 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151434 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151435 | C | CB | Square D | HLL36100 | 100 | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151435 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151436 | C | CB | Square D | HLL36080 | 50 | 80 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151436 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151437 | C | CB | Square D | HLL36110 | 50 | 110 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151437 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151438 | C | CB | Square D | HLL36090 | 100 | 90 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151438 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151439 | C | CB | Square D | HLL36070 | 50 | 70 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151439 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151440 | C | CB | Square D | HLL36100 | 100 | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151440 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151441 | C | CB | Square D | HLL36080 | 50 | 80 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151441 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151442 | C | CB | Square D | HLL36110 | 50 | 110 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151442 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151443 | C | CB | Square D | HLL36090 | 100 | 90 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151443 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151444 | C | CB | Square D | HLL36070 | 50 | 70 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151444 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151445 | C | CB | Square D | HLL36100 | 100 | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151445 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151446 | C | CB | Square D | HLL36080 | 50 | 80 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151446 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151447 | C | CB | Square D | HLL36110 | 50 | 110 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151447 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151448 | C | CB | Square D | HLL36090 | 100 | 90 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151448 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151449 | C | CB | Square D | HLL36070 | 50 | 70 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151449 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151450 | C | CB | Square D | HLL36100 | 100 | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151450 |  | STR | Square D | 8536SEO1@B60 | 5 | 20 - 90 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151451 | C | CB | Square D | HLL36080 | 50 | 80 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151451 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151452 | C | CB | Square D | HLL36110 | 50 | 110 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151452 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE151453 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151453 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151454 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151454 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151455 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151455 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151456 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151456 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151457 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151457 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151458 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151458 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151459 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151459 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151460 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151460 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151461 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151461 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151462 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151462 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151463 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151463 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151464 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151464 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151465 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151465 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151466 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151466 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151467 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151467 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151468 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151468 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151469 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151469 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151470 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151470 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151471 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151471 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151472 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151472 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151473 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151473 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151474 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151474 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151475 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151475 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151476 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151476 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151477 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151477 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151478 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151478 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151479 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151479 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151480 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151480 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151481 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151481 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151482 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151482 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151483 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151483 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151484 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151484 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151485 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151485 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151486 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151486 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151487 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151487 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151488 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151488 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151489 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151489 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151490 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151490 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151491 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151491 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151492 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151492 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151493 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151493 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151494 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151494 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151495 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151495 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151496 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151496 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151497 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151497 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151498 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151498 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151499 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151499 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151500 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151500 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151501 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151501 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151502 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151502 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151503 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151503 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151504 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151504 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151505 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151505 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151506 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151506 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151507 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151507 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151508 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151508 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151509 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151509 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151510 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151510 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151511 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151511 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151512 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151512 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151513 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151513 |  | STR | Square D | 8536SEO1@B60 | 5 | 20 - 90 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151514 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151514 |  | STR | Square D | 8536SEO1@B60 | 5 | 20 - 90 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151515 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151515 |  | STR | Square D | 8536SEO1@B60 | 5 | 20 - 90 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151516 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151516 |  | STR | Square D | 8536SEO1@B60 | 5 | 20 - 90 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151517 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151517 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151518 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151518 |  | STR | Square D | 8536SEO1@B60 | 5 | 20 - 90 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151519 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151519 |  | STR | Square D | 8536SEO1@B60 | 5 | 20 - 90 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151520 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151520 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151521 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151521 |  | STR | Square D | 8536SEO1@B60 | 5 | 20 - 90 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151522 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151522 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151523 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151523 |  | STR | Square D | 8536SEO1@B60 | 5 | 20 - 90 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151524 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151524 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151525 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151525 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151526 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151526 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151527 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151527 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151528 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151528 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151529 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151529 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151530 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151530 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151531 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151531 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151532 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151532 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151533 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151533 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151534 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151534 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151535 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151535 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151536 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151536 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151537 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151537 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151538 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151538 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151539 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151539 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151540 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151540 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151541 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151541 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151542 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151542 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151543 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151543 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151544 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151544 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151545 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151545 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151546 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151546 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151547 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151547 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151548 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151548 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE151549 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151549 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151550 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151550 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151551 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151551 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151552 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151552 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151553 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151553 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151554 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151554 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151555 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151555 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151556 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151556 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151557 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151557 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151558 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151558 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151559 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151559 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151560 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151560 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151561 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151561 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151562 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151562 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151563 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151563 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151564 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151564 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151565 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151565 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151566 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151566 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151567 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151567 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151568 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151568 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151569 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151569 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151570 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151570 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151571 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151571 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151572 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151572 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151573 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151573 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151574 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151574 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151575 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151575 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151576 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151576 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151577 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151577 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151578 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151578 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151579 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151579 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151580 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151580 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151581 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151581 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151582 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151582 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151583 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151583 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151584 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151584 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151585 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151585 |  | STR | Square D | 8536SEO1@B60 | 5 | 20 - 90 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151586 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151586 |  | STR | Square D | 8536SEO1@B60 | 5 | 20 - 90 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151587 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151587 |  | STR | Square D | 8536SEO1@B60 | 5 | 20 - 90 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151588 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151588 |  | STR | Square D | 8536SEO1@B60 | 5 | 20 - 90 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151589 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151589 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151590 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151590 |  | STR | Square D | 8536SEO1@B60 | 5 | 20 - 90 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151591 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151591 |  | STR | Square D | 8536SEO1@B60 | 5 | 20 - 90 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151592 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151592 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151593 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151593 |  | STR | Square D | 8536SEO1@B60 | 5 | 20 - 90 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151594 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151594 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151595 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151595 |  | STR | Square D | 8536SEO1@B60 | 5 | 20 - 90 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151596 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
SE151596 |  | STR | Square D | 8536SEO1@B64 | 5 | 20 - 90 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2747 | 1, 5, 7c, 8 | E40610 V12 S1
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = Use wire ties evenly spaced apart to secure conductors in place.
(7) = See Table 7 for minimum internal wiring between load side of short circuit protective device & line side of starter.
(8) = "@" refer to digest to complete contactor Catalog number for coil voltage and Form modifications.
(9) = Insulator to be provided underneath starter. (QMFZ2), Fastex, Type Formex GK-30, 1/32 inch minimum thickness by 4 inches x 5.7 inches.
Table 7 - Minimum Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
|  | Wire Code |  | Wire Size
|  | 7a |  | 12 AWG
|  | 7b |  | 8 AWG
|  | 7c |  | 2 AWG
|  | 7d |  | 1 AWG
|  | 7e |  | 250 MCM
|  | 7f |  | 300 MCM
|  | 7g |  | (2) 250 MCM

## Size4
Issued: 2007-01-23
Last Revised: 2007-01-23
|  |  |  | "@" refer to Digest to complete | [8 empty] | Use Square D Digest for selection of Melting Alloy and Bi-Metal Overloads only
starter Catalog number for coil
voltage codes and Form modifications
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE151609 | C | CB | Square D | HGL36100 | 35 | 100 | 600 | 3 | 35 | 480 | 3 | 30 | 40 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151609 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 35 | 480 | 3 | 30 | 40 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151610 | C | CB | Square D | HGL36150 | 35 | 150 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151610 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151611 | C | CB | Square D | HGL36100 | 35 | 100 | 600 | 3 | 35 | 480 | 3 | 30 | 40 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151611 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 35 | 480 | 3 | 30 | 40 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151612 | C | CB | Square D | HGL36150 | 35 | 150 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151612 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151613 | C | CB | Square D | HGL36150 | 35 | 150 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151613 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151614 | C | CB | Square D | HGL36150 | 35 | 150 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151614 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151615 | C | CB | Square D | HGL36150 | 35 | 150 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151615 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151616 | C | CB | Square D | HGL36150 | 35 | 150 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151616 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151617 | C | CB | Square D | HJL36100 | 65 | 100 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151617 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151618 | C | CB | Square D | HJL36080 | 25 | 80 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151618 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151619 | C | CB | Square D | HJL36150 | 65 | 150 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151619 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151620 | C | CB | Square D | HJL36110 | 25 | 110 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151620 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151621 | C | CB | Square D | HJL36150 | 25 | 150 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151621 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151622 | C | CB | Square D | HJL36100 | 65 | 100 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151622 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151623 | C | CB | Square D | HJL36080 | 25 | 80 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151623 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151624 | C | CB | Square D | HJL36150 | 65 | 150 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151624 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151625 | C | CB | Square D | HJL36110 | 25 | 110 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151625 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151626 | C | CB | Square D | HJL36150 | 25 | 150 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151626 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151627 | C | CB | Square D | HJL36150 | 65 | 150 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151627 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151628 | C | CB | Square D | HJL36150 | 25 | 150 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151628 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151629 | C | CB | Square D | HJL36150 | 65 | 150 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151629 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151630 | C | CB | Square D | HJL36150 | 25 | 150 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151630 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151631 | C | CB | Square D | HJL36150 | 65 | 150 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151631 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151632 | C | CB | Square D | HJL36150 | 25 | 150 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151632 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151633 | C | CB | Square D | HJL36150 | 65 | 150 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151633 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151634 | C | CB | Square D | HJL36150 | 25 | 150 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151634 |  | STR | Square D | 8536SFO1@B74 | 10 | 60 - 135 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151635 | C | CB | Square D | HLL36100 | 100 | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151635 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151636 | C | CB | Square D | HLL36080 | 50 | 80 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151636 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151637 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151637 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151638 | C | CB | Square D | HLL36110 | 50 | 110 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151638 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151639 | C | CB | Square D | HLL36150 | 50 | 150 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151639 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151640 | C | CB | Square D | HLL36100 | 100 | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151640 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151641 | C | CB | Square D | HLL36080 | 50 | 80 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151641 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151642 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151642 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151643 | C | CB | Square D | HLL36110 | 50 | 110 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151643 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151644 | C | CB | Square D | HLL36150 | 50 | 150 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151644 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151645 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151645 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151646 | C | CB | Square D | HLL36150 | 50 | 150 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151646 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151647 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151647 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151648 | C | CB | Square D | HLL36150 | 50 | 150 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151648 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151649 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151649 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151650 | C | CB | Square D | HLL36150 | 50 | 150 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151650 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151651 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151651 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151652 | C | CB | Square D | HLL36150 | 50 | 150 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151652 |  | STR | Square D | 8536SFO1@B74 | 10 | 60 - 135 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151653 | C | CB | Square D | JGL36200 | 65 | 200 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151653 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151654 | C | CB | Square D | JGL36250 | 65 | 250 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151654 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151655 | C | CB | Square D | HGL36150 | 35 | 150 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151655 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151656 | C | CB | Square D | HGL36150 | 35 | 150 | 600 | 3 | 35 | 480 | 3 | 50 | 65 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151656 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 35 | 480 | 3 | 50 | 65 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151657 | C | CB | Square D | JGL36200 | 35 | 200 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151657 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151658 | C | CB | Square D | JGL36250 | 35 | 250 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151658 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151659 | C | CB | Square D | JGL36200 | 65 | 200 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151659 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151660 | C | CB | Square D | JGL36250 | 65 | 250 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151660 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151661 | C | CB | Square D | HGL36150 | 35 | 150 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151661 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151662 | C | CB | Square D | HGL36150 | 35 | 150 | 600 | 3 | 35 | 480 | 3 | 50 | 65 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151662 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 35 | 480 | 3 | 50 | 65 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151663 | C | CB | Square D | JGL36200 | 35 | 200 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151663 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151664 | C | CB | Square D | JGL36250 | 35 | 250 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151664 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151665 | C | CB | Square D | JGL36200 | 65 | 200 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151665 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151666 | C | CB | Square D | JGL36250 | 65 | 250 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151666 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151667 | C | CB | Square D | HGL36150 | 35 | 150 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151667 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151668 | C | CB | Square D | HGL36150 | 35 | 150 | 600 | 3 | 35 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151668 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 35 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151669 | C | CB | Square D | JGL36200 | 35 | 200 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151669 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151670 | C | CB | Square D | JGL36250 | 35 | 250 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151670 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151671 | C | CB | Square D | JGL36200 | 65 | 200 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151671 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151672 | C | CB | Square D | JGL36250 | 65 | 250 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151672 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151673 | C | CB | Square D | HGL36150 | 35 | 150 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151673 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151674 | C | CB | Square D | HGL36150 | 35 | 150 | 600 | 3 | 35 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151674 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 35 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151675 | C | CB | Square D | JGL36200 | 35 | 200 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151675 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151676 | C | CB | Square D | JGL36250 | 35 | 250 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151676 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151677 | C | CB | Square D | JGL36200 | 65 | 200 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151677 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151678 | C | CB | Square D | JGL36250 | 65 | 250 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151678 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151679 | C | CB | Square D | HGL36150 | 35 | 150 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151679 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151680 | C | CB | Square D | HGL36150 | 35 | 150 | 600 | 3 | 35 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151680 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 35 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151681 | C | CB | Square D | JGL36200 | 35 | 200 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151681 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151682 | C | CB | Square D | JGL36250 | 35 | 250 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151682 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151683 | C | CB | Square D | JGL36200 | 65 | 200 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151683 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151684 | C | CB | Square D | JGL36250 | 65 | 250 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151684 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151685 | C | CB | Square D | HGL36150 | 35 | 150 | 600 | 3 | 35 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151685 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 35 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151686 | C | CB | Square D | JGL36200 | 35 | 200 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151686 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151687 | C | CB | Square D | JGL36250 | 35 | 250 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151687 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151688 | C | CB | Square D | JJL36200 | 100 | 200 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151688 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151689 | C | CB | Square D | JJL36250 | 100 | 250 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151689 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151690 | C | CB | Square D | HJL36150 | 65 | 150 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151690 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151691 | C | CB | Square D | HJL36150 | 65 | 150 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151691 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151692 | C | CB | Square D | HJL36150 | 25 | 150 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151692 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151693 | C | CB | Square D | JJL36200 | 65 | 200 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151693 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151694 | C | CB | Square D | JJL36175 | 25 | 175 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151694 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151695 | C | CB | Square D | JJL36250 | 65 | 250 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151695 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151696 | C | CB | Square D | JJL36200 | 25 | 200 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151696 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151697 | C | CB | Square D | JJL36250 | 25 | 250 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151697 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151698 | C | CB | Square D | JJL36200 | 100 | 200 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151698 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151699 | C | CB | Square D | JJL36250 | 100 | 250 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151699 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151700 | C | CB | Square D | HJL36150 | 65 | 150 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151700 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151701 | C | CB | Square D | HJL36150 | 65 | 150 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151701 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151702 | C | CB | Square D | HJL36150 | 25 | 150 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151702 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151703 | C | CB | Square D | JJL36200 | 65 | 200 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151703 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151704 | C | CB | Square D | JJL36175 | 25 | 175 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151704 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151705 | C | CB | Square D | JJL36250 | 65 | 250 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151705 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151706 | C | CB | Square D | JJL36200 | 25 | 200 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151706 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151707 | C | CB | Square D | JJL36250 | 25 | 250 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151707 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151708 | C | CB | Square D | JJL36200 | 100 | 200 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151708 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151709 | C | CB | Square D | JJL36250 | 100 | 250 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151709 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151710 | C | CB | Square D | HJL36150 | 65 | 150 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151710 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151711 | C | CB | Square D | HJL36150 | 65 | 150 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151711 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151712 | C | CB | Square D | HJL36150 | 25 | 150 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151712 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151713 | C | CB | Square D | JJL36200 | 65 | 200 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151713 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151714 | C | CB | Square D | JJL36175 | 25 | 175 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151714 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151715 | C | CB | Square D | JJL36250 | 65 | 250 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151715 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151716 | C | CB | Square D | JJL36200 | 25 | 200 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151716 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151717 | C | CB | Square D | JJL36250 | 25 | 250 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151717 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151718 | C | CB | Square D | JJL36200 | 100 | 200 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151718 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151719 | C | CB | Square D | JJL36250 | 100 | 250 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151719 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151720 | C | CB | Square D | HJL36150 | 65 | 150 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151720 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151721 | C | CB | Square D | HJL36150 | 65 | 150 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151721 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151722 | C | CB | Square D | HJL36150 | 25 | 150 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151722 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151723 | C | CB | Square D | JJL36200 | 65 | 200 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151723 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151724 | C | CB | Square D | JJL36175 | 25 | 175 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151724 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151725 | C | CB | Square D | JJL36250 | 65 | 250 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151725 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151726 | C | CB | Square D | JJL36200 | 25 | 200 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151726 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151727 | C | CB | Square D | JJL36250 | 25 | 250 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151727 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151728 | C | CB | Square D | JJL36200 | 100 | 200 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151728 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151729 | C | CB | Square D | JJL36250 | 100 | 250 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151729 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151730 | C | CB | Square D | HJL36150 | 65 | 150 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151730 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151731 | C | CB | Square D | HJL36150 | 65 | 150 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151731 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151732 | C | CB | Square D | HJL36150 | 25 | 150 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151732 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151733 | C | CB | Square D | JJL36200 | 65 | 200 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151733 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151734 | C | CB | Square D | JJL36175 | 25 | 175 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151734 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151735 | C | CB | Square D | JJL36250 | 65 | 250 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151735 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151736 | C | CB | Square D | JJL36200 | 25 | 200 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151736 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151737 | C | CB | Square D | JJL36250 | 25 | 250 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151737 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151738 | C | CB | Square D | JJL36200 | 100 | 200 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151738 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151739 | C | CB | Square D | JJL36250 | 100 | 250 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151739 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151740 | C | CB | Square D | HJL36150 | 65 | 150 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151740 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151741 | C | CB | Square D | JJL36200 | 65 | 200 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151741 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151742 | C | CB | Square D | JJL36175 | 25 | 175 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151742 |  | STR | Square D | 8536SFO1@B74 | 10 | 60 - 135 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151743 | C | CB | Square D | JJL36250 | 65 | 250 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151743 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151744 | C | CB | Square D | JJL36200 | 25 | 200 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151744 |  | STR | Square D | 8536SFO1@B74 | 10 | 60 - 135 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151745 | C | CB | Square D | JJL36250 | 25 | 250 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151745 |  | STR | Square D | 8536SFO1@B74 | 10 | 60 - 135 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151746 | C | CB | Square D | JLL36200 | 100 | 200 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151746 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151747 | C | CB | Square D | JLL36250 | 100 | 250 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151747 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151748 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151748 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151749 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151749 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151750 | C | CB | Square D | HLL36150 | 50 | 150 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151750 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151751 | C | CB | Square D | JLL36200 | 100 | 200 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151751 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151752 | C | CB | Square D | JLL36175 | 50 | 175 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151752 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151753 | C | CB | Square D | JLL36250 | 100 | 250 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151753 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151754 | C | CB | Square D | JLL36200 | 50 | 200 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151754 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151755 | C | CB | Square D | JLL36250 | 50 | 250 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151755 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151756 | C | CB | Square D | JLL36200 | 100 | 200 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151756 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151757 | C | CB | Square D | JLL36250 | 100 | 250 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151757 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151758 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151758 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151759 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151759 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151760 | C | CB | Square D | HLL36150 | 50 | 150 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151760 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151761 | C | CB | Square D | JLL36200 | 100 | 200 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151761 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151762 | C | CB | Square D | JLL36175 | 50 | 175 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151762 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151763 | C | CB | Square D | JLL36250 | 100 | 250 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151763 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151764 | C | CB | Square D | JLL36200 | 50 | 200 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151764 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151765 | C | CB | Square D | JLL36250 | 50 | 250 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151765 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 3205 | 1, 3, 7d, 8 | E40610 V12 S1
SE151766 | C | CB | Square D | JLL36200 | 100 | 200 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151766 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151767 | C | CB | Square D | JLL36250 | 100 | 250 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151767 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151768 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151768 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151769 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151769 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151770 | C | CB | Square D | HLL36150 | 50 | 150 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151770 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151771 | C | CB | Square D | JLL36200 | 100 | 200 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151771 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151772 | C | CB | Square D | JLL36175 | 50 | 175 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151772 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151773 | C | CB | Square D | JLL36250 | 100 | 250 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151773 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151774 | C | CB | Square D | JLL36200 | 50 | 200 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151774 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151775 | C | CB | Square D | JLL36250 | 50 | 250 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151775 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151776 | C | CB | Square D | JLL36200 | 100 | 200 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151776 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151777 | C | CB | Square D | JLL36250 | 100 | 250 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151777 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151778 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151778 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151779 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151779 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151780 | C | CB | Square D | HLL36150 | 50 | 150 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151780 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151781 | C | CB | Square D | JLL36200 | 100 | 200 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151781 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151782 | C | CB | Square D | JLL36175 | 50 | 175 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151782 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151783 | C | CB | Square D | JLL36250 | 100 | 250 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151783 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151784 | C | CB | Square D | JLL36200 | 50 | 200 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151784 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151785 | C | CB | Square D | JLL36250 | 50 | 250 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151785 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151786 | C | CB | Square D | JLL36200 | 100 | 200 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151786 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151787 | C | CB | Square D | JLL36250 | 100 | 250 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151787 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151788 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151788 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151789 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151789 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151790 | C | CB | Square D | HLL36150 | 50 | 150 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151790 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151791 | C | CB | Square D | JLL36200 | 100 | 200 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151791 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151792 | C | CB | Square D | JLL36175 | 50 | 175 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151792 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151793 | C | CB | Square D | JLL36250 | 100 | 250 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151793 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151794 | C | CB | Square D | JLL36200 | 50 | 200 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151794 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151795 | C | CB | Square D | JLL36250 | 50 | 250 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151795 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151796 | C | CB | Square D | JLL36200 | 100 | 200 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151796 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151797 | C | CB | Square D | JLL36250 | 100 | 250 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151797 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151798 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151798 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151799 | C | CB | Square D | JLL36200 | 100 | 200 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151799 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151800 | C | CB | Square D | JLL36175 | 50 | 175 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151800 |  | STR | Square D | 8536SFO1@B74 | 10 | 60 - 135 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151801 | C | CB | Square D | JLL36250 | 100 | 250 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151801 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151802 | C | CB | Square D | JLL36200 | 50 | 200 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151802 |  | STR | Square D | 8536SFO1@B74 | 10 | 60 - 135 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151803 | C | CB | Square D | JLL36250 | 50 | 250 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151803 |  | STR | Square D | 8536SFO1@B74 | 10 | 60 - 135 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 3205 | 1, 7d, 8 | E40610 V12 S1
SE151804 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151804 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151805 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151805 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151806 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151806 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151807 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151807 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151808 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151808 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151809 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151809 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151810 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151810 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151811 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151811 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151812 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151812 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151813 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151813 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151814 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151814 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151815 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151815 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151816 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151816 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151817 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151817 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151818 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151818 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151819 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151819 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151820 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151820 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151821 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151821 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151822 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151822 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151823 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151823 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151824 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151824 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151825 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151825 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151826 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151826 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151827 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151827 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151828 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151828 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151829 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151829 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151830 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151830 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151831 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151831 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151832 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151832 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151833 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151833 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151834 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151834 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151835 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151835 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151836 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151836 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151837 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151837 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151838 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151838 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151839 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151839 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151840 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151840 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151841 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151841 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151842 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151842 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151843 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151843 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151844 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151844 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151845 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151845 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151846 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151846 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151847 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151847 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151848 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151848 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151849 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151849 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151850 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151850 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151851 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151851 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151852 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151852 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151853 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151853 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151854 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151854 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151855 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151855 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151856 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151856 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151857 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151857 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151858 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151858 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151859 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151859 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151860 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151860 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151861 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151861 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151862 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151862 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151863 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151863 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151864 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151864 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151865 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151865 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151866 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151866 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151867 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151867 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151868 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151868 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151869 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151869 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151870 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151870 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151871 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151871 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151872 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151872 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151873 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151873 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151874 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151874 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151875 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151875 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151876 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151876 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151877 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151877 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151878 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151878 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151879 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151879 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151880 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151880 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151881 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151881 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151882 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151882 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151883 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151883 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151884 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151884 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151885 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151885 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151886 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151886 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151887 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151887 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151888 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151888 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151889 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151889 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151890 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151890 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151891 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151891 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151892 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151892 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151893 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151893 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151894 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151894 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151895 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151895 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151896 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151896 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151897 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151897 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151898 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151898 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151899 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151899 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151900 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151900 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151901 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151901 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151902 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151902 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151903 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151903 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151904 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151904 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151905 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151905 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151906 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151906 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151907 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151907 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151908 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151908 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151909 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151909 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151910 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151910 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151911 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151911 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151912 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151912 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151913 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151913 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151914 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151914 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151915 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151915 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151916 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151916 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151917 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151917 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151918 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151918 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151919 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151919 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151920 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151920 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151921 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151921 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151922 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151922 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151923 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151923 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151924 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151924 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151925 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151925 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151926 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151926 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151927 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151927 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151928 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151928 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151929 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151929 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151930 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151930 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151931 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151931 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151932 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151932 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151933 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151933 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151934 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151934 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151935 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151935 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151936 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151936 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151937 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151937 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151938 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151938 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151939 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151939 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151940 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151940 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151941 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151941 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151942 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151942 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151943 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151943 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151944 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151944 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151945 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151945 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151946 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151946 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151947 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151947 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151948 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151948 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151949 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151949 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151950 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151950 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151951 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151951 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151952 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151952 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151953 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151953 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151954 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151954 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151955 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151955 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151956 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151956 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151957 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151957 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151958 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151958 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151959 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151959 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151960 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151960 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151961 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151961 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151962 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151962 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151963 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151963 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151964 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151964 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151965 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151965 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151966 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151966 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151967 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151967 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151968 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151968 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151969 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151969 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151970 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151970 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151971 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151971 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151972 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151972 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151973 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151973 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151974 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151974 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151975 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151975 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151976 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151976 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151977 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151977 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151978 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151978 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151979 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151979 |  | STR | Square D | 8536SFO1@ | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151980 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151980 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151981 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151981 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151982 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151982 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151983 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151983 |  | STR | Square D | 8536SFO1@Y59 | 10 | 135 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 3205 | 1, 3, 5, 7d, 8 | E40610 V12 S1
SE151984 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151984 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151985 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151985 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151986 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151986 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151987 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151987 |  | STR | Square D | 8536SFO1@H10 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151988 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151988 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151989 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151989 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151990 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151990 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151991 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151991 |  | STR | Square D | 8536SFO1@H20 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151992 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151992 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151993 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151993 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151994 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151994 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151995 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151995 |  | STR | Square D | 8536SFO1@H30 | 10 | 45 - 135 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151996 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151996 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151997 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151997 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151998 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151998 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151999 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
SE151999 |  | STR | Square D | 8536SFO1@B70 | 10 | 60 - 135 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 3205 | 1, 5, 7d, 8 | E40610 V12 S1
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = Use wire ties evenly spaced apart to secure conductors in place.
(7) = See Table 7 for minimum internal wiring between load side of short circuit protective device & line side of starter.
(8) = "@" refer to digest to complete contactor Catalog number for coil voltage and Form modifications.
(9) = Insulator to be provided underneath starter. (QMFZ2), Fastex, Type Formex GK-30, 1/32 inch minimum thickness by 4 inches x 5.7 inches.
Table 7 - Minimum Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
|  | Wire Code |  | Wire Size
|  | 7a |  | 12 AWG
|  | 7b |  | 8 AWG
|  | 7c |  | 2 AWG
|  | 7d |  | 1 AWG
|  | 7e |  | 250 MCM
|  | 7f |  | 300 MCM
|  | 7g |  | (2) 250 MCM

## Size5
Issued: 2007-01-23
Last Revised: 2007-01-23
|  |  |  | "@" refer to Digest to complete | [8 empty] | Use Square D Digest for selection of Melting Alloy and Bi-Metal Overloads only
starter Catalog number for coil
voltage codes and Form modifications
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE152108 | C | CB | Square D | JGL36250 | 35 | 250 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152108 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152109 | C | CB | Square D | JGL36250 | 35 | 250 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152109 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152110 | C | CB | Square D | JGL36250 | 35 | 250 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152110 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152111 | C | CB | Square D | JGL36250 | 35 | 250 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152111 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152112 | C | CB | Square D | JGL36250 | 35 | 250 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152112 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152113 | C | CB | Square D | JJL36250 | 65 | 250 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152113 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152114 | C | CB | Square D | JJL36200 | 25 | 200 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152114 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152115 | C | CB | Square D | JJL36250 | 25 | 250 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152115 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152116 | C | CB | Square D | JJL36250 | 65 | 250 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152116 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152117 | C | CB | Square D | JJL36200 | 25 | 200 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152117 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152118 | C | CB | Square D | JJL36250 | 25 | 250 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152118 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152119 | C | CB | Square D | JJL36250 | 65 | 250 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152119 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152120 | C | CB | Square D | JJL36250 | 25 | 250 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152120 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152121 | C | CB | Square D | JJL36250 | 65 | 250 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152121 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152122 | C | CB | Square D | JJL36250 | 25 | 250 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152122 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152123 | C | CB | Square D | JJL36250 | 65 | 250 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152123 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152124 | C | CB | Square D | JJL36250 | 25 | 250 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152124 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152125 | C | CB | Square D | JLL36250 | 100 | 250 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152125 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152126 | C | CB | Square D | JLL36200 | 50 | 200 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152126 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152127 | C | CB | Square D | JLL36250 | 50 | 250 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152127 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152128 | C | CB | Square D | JLL36250 | 100 | 250 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152128 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152129 | C | CB | Square D | JLL36200 | 50 | 200 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152129 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152130 | C | CB | Square D | JLL36250 | 50 | 250 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152130 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152131 | C | CB | Square D | JLL36250 | 100 | 250 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152131 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152132 | C | CB | Square D | JLL36250 | 50 | 250 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152132 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152133 | C | CB | Square D | JLL36250 | 100 | 250 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152133 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152134 | C | CB | Square D | JLL36250 | 50 | 250 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152134 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152135 | C | CB | Square D | JLL36250 | 100 | 250 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152135 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152136 | C | CB | Square D | JLL36250 | 50 | 250 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152136 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 6410 | 1, 3, 6, 7e, 8 | E40610 V12 S1
SE152137 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152137 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152138 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152138 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152139 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152139 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152140 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152140 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152141 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152141 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152142 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152142 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152143 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152143 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152144 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152144 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152145 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152145 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152146 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152146 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152147 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152147 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152148 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152148 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152149 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152149 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152150 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152150 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152151 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152151 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152152 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152152 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152153 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152153 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152154 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152154 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152155 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152155 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152156 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152156 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152157 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152157 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152158 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152158 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152159 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152159 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152160 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152160 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152161 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152161 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152162 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152162 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152163 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152163 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152164 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 25 | 600 | 3 | 150 | 144 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152164 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 25 | 600 | 3 | 150 | 144 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152165 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152165 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152166 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152166 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152167 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152167 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152168 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 25 | 600 | 3 | 150 | 144 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152168 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 25 | 600 | 3 | 150 | 144 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152169 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152169 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152170 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152170 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152171 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152171 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152172 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 25 | 600 | 3 | 150 | 144 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152172 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 25 | 600 | 3 | 150 | 144 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152173 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152173 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152174 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152174 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152175 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152175 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152176 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 25 | 600 | 3 | 150 | 144 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152176 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 25 | 600 | 3 | 150 | 144 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152177 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152177 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152178 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152178 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152179 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152179 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152180 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 25 | 600 | 3 | 150 | 144 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152180 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 25 | 600 | 3 | 150 | 144 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152181 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152181 |  | STR | Square D | 8536SGO1@B80 | 10 | 120 - 270 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152182 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152182 |  | STR | Square D | 8536SGO1@B80 | 10 | 120 - 270 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152183 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152183 |  | STR | Square D | 8536SGO1@B84 | 10 | 120 - 270 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152184 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 25 | 600 | 3 | 150 | 144 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152184 |  | STR | Square D | 8536SGO1@B84 | 10 | 120 - 270 | 600 | 3 | 25 | 600 | 3 | 150 | 144 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152185 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152185 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152186 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152186 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152187 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 50 | 600 | 3 | 125 | 125 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152187 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 50 | 600 | 3 | 125 | 125 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152188 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 50 | 600 | 3 | 150 | 144 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152188 |  | STR | Square D | 8536SGO1@ | 10 | 270 | 600 | 3 | 50 | 600 | 3 | 150 | 144 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152189 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152189 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152190 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152190 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152191 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 50 | 600 | 3 | 125 | 125 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152191 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 50 | 600 | 3 | 125 | 125 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152192 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 50 | 600 | 3 | 150 | 144 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152192 |  | STR | Square D | 8536SGO1@B | 10 | 270 | 600 | 3 | 50 | 600 | 3 | 150 | 144 | 6410 | 1, 3, 5, 6, 7e, 8 | E40610 V12 S1
SE152193 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152193 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152194 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152194 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152195 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 50 | 600 | 3 | 125 | 125 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152195 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 50 | 600 | 3 | 125 | 125 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152196 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 50 | 600 | 3 | 150 | 144 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152196 |  | STR | Square D | 8536SGO1@H10 | 10 | 90 - 270 | 600 | 3 | 50 | 600 | 3 | 150 | 144 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152197 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152197 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152198 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152198 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152199 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 50 | 600 | 3 | 125 | 125 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152199 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 50 | 600 | 3 | 125 | 125 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152200 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 50 | 600 | 3 | 150 | 144 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152200 |  | STR | Square D | 8536SGO1@H20 | 10 | 90 - 270 | 600 | 3 | 50 | 600 | 3 | 150 | 144 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152201 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152201 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152202 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152202 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152203 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 50 | 600 | 3 | 125 | 125 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152203 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 50 | 600 | 3 | 125 | 125 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152204 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 50 | 600 | 3 | 150 | 144 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152204 |  | STR | Square D | 8536SGO1@H30 | 10 | 90 - 270 | 600 | 3 | 50 | 600 | 3 | 150 | 144 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152205 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152205 |  | STR | Square D | 8536SGO1@B80 | 10 | 120 - 270 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152206 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152206 |  | STR | Square D | 8536SGO1@B80 | 10 | 120 - 270 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152207 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 50 | 600 | 3 | 125 | 125 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152207 |  | STR | Square D | 8536SGO1@B84 | 10 | 120 - 270 | 600 | 3 | 50 | 600 | 3 | 125 | 125 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152208 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 50 | 600 | 3 | 150 | 144 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
SE152208 |  | STR | Square D | 8536SGO1@B84 | 10 | 120 - 270 | 600 | 3 | 50 | 600 | 3 | 150 | 144 | 6410 | 1, 5, 6, 7e, 8 | E40610 V12 S1
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = Use wire ties evenly spaced apart to secure conductors in place.
(7) = See Table 7 for minimum internal wiring between load side of short circuit protective device & line side of starter.
(8) = "@" refer to digest to complete contactor Catalog number for coil voltage and Form modifications.
(9) = Insulator to be provided underneath starter. (QMFZ2), Fastex, Type Formex GK-30, 1/32 inch minimum thickness by 4 inches x 5.7 inches.
Table 7 - Minimum Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
|  | Wire Code |  | Wire Size
|  | 7a |  | 12 AWG
|  | 7b |  | 8 AWG
|  | 7c |  | 2 AWG
|  | 7d |  | 1 AWG
|  | 7e |  | 250 MCM
|  | 7f |  | 300 MCM
|  | 7g |  | (2) 250 MCM

## Size1-GJL
Issued: 2008-04-08
Last Revised: 2008-04-08
|  |  |  | "@" refer to Digest to complete | [8 empty] | Use Square D Digest for selection of Melting Alloy and Bi-Metal Overloads only
contactor Catalog number for coil
voltage codes and Form modifications
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE152269 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152269 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152270 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152270 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152271 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152271 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152272 | C | CB | Square D | GJL36015 | 65 | 15 | 480 | 3 | 65 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152272 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 65 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152273 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152273 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152274 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152274 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152275 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152275 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152276 | C | CB | Square D | GJL36015 | 65 | 15 | 480 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152276 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152277 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152277 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152278 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152278 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152279 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152279 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152280 | C | CB | Square D | GJL36015 | 65 | 15 | 480 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152280 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152281 | C | CB | Square D | GJL36020 | 100 | 20 | 480 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152281 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152282 | C | CB | Square D | GJL36020 | 100 | 20 | 480 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152282 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152283 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152283 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152284 | C | CB | Square D | GJL36015 | 65 | 15 | 480 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152284 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152285 | C | CB | Square D | GJL36020 | 100 | 20 | 480 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152285 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152286 | C | CB | Square D | GJL36020 | 100 | 20 | 480 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152286 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152287 | C | CB | Square D | GJL36020 | 100 | 20 | 480 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152287 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152288 | C | CB | Square D | GJL36015 | 65 | 15 | 480 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152288 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152289 | C | CB | Square D | GJL36030 | 100 | 30 | 480 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152289 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152290 | C | CB | Square D | GJL36030 | 100 | 30 | 480 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152290 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152291 | C | CB | Square D | GJL36030 | 100 | 30 | 480 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152291 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152292 | C | CB | Square D | GJL36015 | 65 | 15 | 480 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152292 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152293 | C | CB | Square D | GJL36050 | 100 | 50 | 480 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152293 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152294 | C | CB | Square D | GJL36050 | 100 | 50 | 480 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152294 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152295 | C | CB | Square D | GJL36040 | 100 | 40 | 480 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152295 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152296 | C | CB | Square D | GJL36020 | 65 | 20 | 480 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152296 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152298 | C | CB | Square D | GJL36030 | 65 | 30 | 480 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152298 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152299 | C | CB | Square D | GJL36040 | 65 | 40 | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152299 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152300 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152300 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 480 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152301 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152301 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 480 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152302 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152302 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 480 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152303 | C | CB | Square D | GJL36015 | 65 | 15 | 480 | 3 | 65 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152303 |  | STR | Square D | 8536SCO3@B20 | 5 | 0.5 - 2.3 | 480 | 3 | 65 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152304 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152304 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 480 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152305 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152305 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 480 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152306 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152306 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 480 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152307 | C | CB | Square D | GJL36015 | 65 | 15 | 480 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152307 |  | STR | Square D | 8536SCO3@B20 | 5 | 0.5 - 2.3 | 480 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152308 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152308 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 480 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152309 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152309 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 480 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152310 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152310 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 480 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152311 | C | CB | Square D | GJL36015 | 65 | 15 | 480 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152311 |  | STR | Square D | 8536SCO3@B20 | 5 | 0.5 - 2.3 | 480 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152312 | C | CB | Square D | GJL36020 | 100 | 20 | 480 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152312 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 480 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152313 | C | CB | Square D | GJL36020 | 100 | 20 | 480 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152313 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 480 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152314 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152314 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 480 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152315 | C | CB | Square D | GJL36015 | 65 | 15 | 480 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152315 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 480 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152316 | C | CB | Square D | GJL36020 | 100 | 20 | 480 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152316 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 480 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152317 | C | CB | Square D | GJL36020 | 100 | 20 | 480 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152317 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 480 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152318 | C | CB | Square D | GJL36020 | 100 | 20 | 480 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152318 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 480 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152319 | C | CB | Square D | GJL36015 | 65 | 15 | 480 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152319 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 480 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152320 | C | CB | Square D | GJL36030 | 100 | 30 | 480 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152320 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 480 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152321 | C | CB | Square D | GJL36030 | 100 | 30 | 480 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152321 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 480 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152322 | C | CB | Square D | GJL36030 | 100 | 30 | 480 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152322 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 480 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152323 | C | CB | Square D | GJL36015 | 65 | 15 | 480 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152323 |  | STR | Square D | 8536SCO3@B30 | 5 | 2 - 9 | 480 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152324 | C | CB | Square D | GJL36050 | 100 | 50 | 480 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152324 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 480 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152325 | C | CB | Square D | GJL36040 | 100 | 40 | 480 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152325 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 480 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152326 | C | CB | Square D | GJL36040 | 100 | 40 | 480 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152326 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 480 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152327 | C | CB | Square D | GJL36020 | 65 | 20 | 480 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152327 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 480 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152329 | C | CB | Square D | GJL36030 | 65 | 30 | 480 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152329 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 480 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152330 | C | CB | Square D | GJL36040 | 65 | 40 | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152330 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152331 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152331 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152332 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152332 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152333 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152333 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152334 | C | CB | Square D | GJL36015 | 65 | 15 | 480 | 3 | 65 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152334 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 65 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152335 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152335 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152336 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152336 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152337 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152337 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152338 | C | CB | Square D | GJL36015 | 65 | 15 | 480 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152338 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152339 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152339 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152340 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152340 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152341 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152341 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152342 | C | CB | Square D | GJL36015 | 65 | 15 | 480 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152342 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152343 | C | CB | Square D | GJL36020 | 100 | 20 | 480 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152343 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152344 | C | CB | Square D | GJL36020 | 100 | 20 | 480 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152344 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152345 | C | CB | Square D | GJL36015 | 100 | 15 | 480 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152345 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152346 | C | CB | Square D | GJL36015 | 65 | 15 | 480 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152346 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152347 | C | CB | Square D | GJL36020 | 100 | 20 | 480 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152347 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 100 | 200 | 3 | 2 | 7.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152348 | C | CB | Square D | GJL36020 | 100 | 20 | 480 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152348 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152349 | C | CB | Square D | GJL36020 | 100 | 20 | 480 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152349 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152350 | C | CB | Square D | GJL36015 | 65 | 15 | 480 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152350 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152351 | C | CB | Square D | GJL36030 | 100 | 30 | 480 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152351 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152352 | C | CB | Square D | GJL36030 | 100 | 30 | 480 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152352 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152353 | C | CB | Square D | GJL36030 | 100 | 30 | 480 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152353 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152354 | C | CB | Square D | GJL36015 | 65 | 15 | 480 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152354 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152355 | C | CB | Square D | GJL36050 | 100 | 50 | 480 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152355 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152356 | C | CB | Square D | GJL36050 | 100 | 50 | 480 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152356 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152357 | C | CB | Square D | GJL36040 | 100 | 40 | 480 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152357 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152358 | C | CB | Square D | GJL36020 | 65 | 20 | 480 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152358 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152360 | C | CB | Square D | GJL36030 | 65 | 30 | 480 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152360 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152361 | C | CB | Square D | GJL36040 | 65 | 40 | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152361 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 6, 7a, 8 | E40610 V12 S1
SE152362 | C | CB | Square D | GJL36030 | 100 | 30 | 480 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152362 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 480 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152363 | C | CB | Square D | GJL36030 | 100 | 30 | 480 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152363 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 480 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152364 | C | CB | Square D | GJL36030 | 100 | 30 | 480 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152364 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 480 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152365 | C | CB | Square D | GJL36050 | 100 | 50 | 480 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152365 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 480 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152366 | C | CB | Square D | GJL36050 | 100 | 50 | 480 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152366 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 480 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152367 | C | CB | Square D | GJL36040 | 100 | 40 | 480 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152367 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 480 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152369 | C | CB | Square D | GJL36030 | 65 | 30 | 480 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152369 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 480 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152370 | C | CB | Square D | GJL36040 | 65 | 40 | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152370 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152371 | C | CB | Square D | GJL36030 | 100 | 30 | 480 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152371 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 480 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152372 | C | CB | Square D | GJL36030 | 100 | 30 | 480 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152372 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 480 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152373 | C | CB | Square D | GJL36030 | 100 | 30 | 480 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152373 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 480 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152374 | C | CB | Square D | GJL36050 | 100 | 50 | 480 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152374 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 480 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152375 | C | CB | Square D | GJL36050 | 100 | 50 | 480 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152375 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 480 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152376 | C | CB | Square D | GJL36040 | 100 | 40 | 480 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152376 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 480 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152378 | C | CB | Square D | GJL36030 | 65 | 30 | 480 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152378 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 480 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152379 | C | CB | Square D | GJL36040 | 65 | 40 | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152379 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152380 | C | CB | Square D | GJL36030 | 100 | 30 | 480 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152380 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 480 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152381 | C | CB | Square D | GJL36030 | 100 | 30 | 480 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152381 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 480 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152382 | C | CB | Square D | GJL36030 | 100 | 30 | 480 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152382 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 480 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152383 | C | CB | Square D | GJL36050 | 100 | 50 | 480 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152383 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 480 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152384 | C | CB | Square D | GJL36050 | 100 | 50 | 480 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152384 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 480 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152385 | C | CB | Square D | GJL36040 | 100 | 40 | 480 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152385 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 480 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152387 | C | CB | Square D | GJL36030 | 65 | 30 | 480 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152387 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 480 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152388 | C | CB | Square D | GJL36040 | 65 | 40 | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152388 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 6, 7a, 8 | E40610 V12 S1
SE152413 | D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE152413 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE152414 | D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE152414 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE152415 | D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE152415 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE152417 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE152417 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE152418 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE152418 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE152419 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE152419 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE152421 | D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE152421 |  | STR | Square D | 8536SCO3@ | 5 | 27 | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE152446 | D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152446 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 480 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152447 | D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152447 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 480 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152448 | D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152448 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 480 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152450 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152450 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 480 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152451 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152451 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 480 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152452 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152452 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 480 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152454 | D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152454 |  | STR | Square D | 8536SCO3@B40 | 5 | 6 - 27 | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152479 | D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE152479 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE152480 | D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE152480 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE152481 | D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE152481 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE152483 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE152483 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE152484 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE152484 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE152485 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE152485 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE152487 | D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE152487 |  | STR | Square D | 8536SCO3@B | 5 | 27 | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 3, 5, 6, 7a, 8 | E40610 V12 S1
SE152491 | D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152491 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 480 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152492 | D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152492 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 480 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152493 | D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152493 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 480 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152494 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152494 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 480 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152495 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152495 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 480 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152496 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152496 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 480 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152498 | D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152498 |  | STR | Square D | 8536SCO3@H10 | 5 | 9 - 27 | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152502 | D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152502 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 480 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152503 | D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152503 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 480 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152504 | D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152504 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 480 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152505 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152505 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 480 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152506 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152506 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 480 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152507 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152507 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 480 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152509 | D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152509 |  | STR | Square D | 8536SCO3@H20 | 5 | 9 - 27 | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152513 | D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152513 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 480 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152514 | D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152514 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 480 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152515 | D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152515 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 480 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152516 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152516 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 480 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152517 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152517 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 480 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152518 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152518 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 480 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152520 | D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
SE152520 |  | STR | Square D | 8536SCO3@H30 | 5 | 9 - 27 | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 6, 7a, 8 | E40610 V12 S1
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = Use wire ties evenly spaced apart to secure conductors in place.
(7) = See Table 7 for minimum internal wiring between load side of short circuit protective device & line side of starter.
(8) = "@" refer to digest to complete contactor Catalog number for coil voltage and Form modifications.
(9) = Insulator to be provided underneath starter. (QMFZ2), Fastex, Type Formex GK-30, 1/32 inch minimum thickness by 4 inches x 5.7 inches.
Table 7 - Minimum Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
| Wire Code |  | Wire Size
| 7a |  | 12 AWG
| 7b |  | 8 AWG
| 7c |  | 2 AWG
| 7d |  | 1 AWG
| 7e |  | 250 MCM
| 7f |  | 300 MCM
| 7g |  | (2) 250 MCM
| 7h |  | 2/0 AWG
| 7i |  | 4/0 AWG
| 7j |  | (2) 4/0 AWG
| 7k |  | 10 AWG
| 7l |  | 6 AWG
| 7m |  | 4 AWG
| 7n |  | 3 AWG
| 7p |  | 1/0 AWG
| 7q |  | (2) 3/0 AWG
| 7r |  | (2) 2/0 AWG
| 7s |  | 3/0 AWG

## Size2-GJL
Issued: 2008-04-08
Last Revised: 2008-04-08
|  |  |  | "@" refer to Digest to complete | [8 empty] | Use Square D Digest for selection of Melting Alloy and Bi-Metal Overloads only
contactor Catalog number for coil
voltage codes and Form modifications
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE152521 | C | CB | Square D | GJL36090 | 100 | 90 | 480 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE152521 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 480 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE152522 | C | CB | Square D | GJL36090 | 100 | 90 | 480 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE152522 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 480 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE152523 | C | CB | Square D | GJL36070 | 100 | 70 | 480 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE152523 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 480 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE152524 | C | CB | Square D | GJL36100 | 100 | 100 | 480 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE152524 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 480 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE152525 | C | CB | Square D | GJL36060 | 65 | 60 | 480 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE152525 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 480 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE152526 | C | CB | Square D | GJL36070 | 65 | 70 | 480 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE152526 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 480 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE152527 | C | CB | Square D | GJL36090 | 65 | 90 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE152527 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE152528 | C | CB | Square D | GJL36090 | 100 | 90 | 480 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152528 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 480 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152529 | C | CB | Square D | GJL36090 | 100 | 90 | 480 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152529 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 480 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152530 | C | CB | Square D | GJL36070 | 100 | 70 | 480 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152530 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 480 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152531 | C | CB | Square D | GJL36100 | 100 | 100 | 480 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152531 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 480 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152532 | C | CB | Square D | GJL36060 | 65 | 60 | 480 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152532 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 480 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152533 | C | CB | Square D | GJL36070 | 65 | 70 | 480 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152533 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 480 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152534 | C | CB | Square D | GJL36090 | 65 | 90 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152534 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152535 | C | CB | Square D | GJL36090 | 100 | 90 | 480 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE152535 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 480 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE152536 | C | CB | Square D | GJL36090 | 100 | 90 | 480 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE152536 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 480 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE152537 | C | CB | Square D | GJL36070 | 100 | 70 | 480 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE152537 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 480 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE152538 | C | CB | Square D | GJL36100 | 100 | 100 | 480 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE152538 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 480 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE152539 | C | CB | Square D | GJL36060 | 65 | 60 | 480 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE152539 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 480 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE152540 | C | CB | Square D | GJL36070 | 65 | 70 | 480 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE152540 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 480 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE152541 | C | CB | Square D | GJL36090 | 65 | 90 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE152541 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 6, 7b, 8, 9 | E40610 V12 S1
SE152542 | C | CB | Square D | GJL36090 | 100 | 90 | 480 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152542 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 480 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152543 | C | CB | Square D | GJL36090 | 100 | 90 | 480 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152543 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 480 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152544 | C | CB | Square D | GJL36070 | 100 | 70 | 480 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152544 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 480 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152545 | C | CB | Square D | GJL36100 | 100 | 100 | 480 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152545 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 480 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152546 | C | CB | Square D | GJL36060 | 65 | 60 | 480 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152546 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 480 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152547 | C | CB | Square D | GJL36070 | 65 | 70 | 480 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152547 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 480 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152548 | C | CB | Square D | GJL36090 | 65 | 90 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152548 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152549 | C | CB | Square D | GJL36090 | 100 | 90 | 480 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152549 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 480 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152550 | C | CB | Square D | GJL36090 | 100 | 90 | 480 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152550 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 480 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152551 | C | CB | Square D | GJL36070 | 100 | 70 | 480 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152551 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 480 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152552 | C | CB | Square D | GJL36100 | 100 | 100 | 480 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152552 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 480 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152553 | C | CB | Square D | GJL36060 | 65 | 60 | 480 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152553 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 480 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152554 | C | CB | Square D | GJL36070 | 65 | 70 | 480 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152554 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 480 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152555 | C | CB | Square D | GJL36090 | 65 | 90 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152555 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152556 | C | CB | Square D | GJL36090 | 100 | 90 | 480 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152556 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 480 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152557 | C | CB | Square D | GJL36090 | 100 | 90 | 480 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152557 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 480 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152558 | C | CB | Square D | GJL36070 | 100 | 70 | 480 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152558 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 480 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152559 | C | CB | Square D | GJL36100 | 100 | 100 | 480 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152559 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 480 | 3 | 100 | 240 | 3 | 15 | 42 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152560 | C | CB | Square D | GJL36060 | 65 | 60 | 480 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152560 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 480 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152561 | C | CB | Square D | GJL36070 | 65 | 70 | 480 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152561 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 480 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152562 | C | CB | Square D | GJL36090 | 65 | 90 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152562 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 6, 7b, 8, 9 | E40610 V12 S1
SE152563 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE1 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 480 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE152564 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE1 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 480 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE152565 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE1 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 480 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE152566 | D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE1 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 480 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE152567 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE1 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 480 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE152568 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE1 |  | STR | Square D | 8536SDO1@ | 5 | 45 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE152569 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE1 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 480 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE152570 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE1 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 480 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE152571 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE1 |  | STR | Square D | 8536SDO1@B50 | 5 | 10 - 45 | 480 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE152572 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE1 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 480 | 3 | 100 | 200 | 3 | 10 | 32.2 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE152573 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE1 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 480 | 3 | 100 | 208 | 3 | 10 | 30.8 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE152574 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE1 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 480 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE152575 | D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE1 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 480 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE152576 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE1 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 480 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE152577 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE1 |  | STR | Square D | 8536SDO1@B | 5 | 45 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 1832 | 1, 3, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE152578 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE1 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 480 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE152579 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE1 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 480 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE152580 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE1 |  | STR | Square D | 8536SDO1@H10 | 5 | 15 - 45 | 480 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE152581 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE1 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 480 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE152582 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE1 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 480 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE152583 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE1 |  | STR | Square D | 8536SDO1@H20 | 5 | 15 - 45 | 480 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE152584 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE1 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 480 | 3 | 65 | 200 | 3 | 10 | 32.2 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE152585 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE1 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 480 | 3 | 65 | 208 | 3 | 10 | 30.8 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE152586 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
SE1 |  | STR | Square D | 8536SDO1@H30 | 5 | 15 - 45 | 480 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 6, 7b, 8, 9 | E40610 V12 S1
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = Use wire ties evenly spaced apart to secure conductors in place.
(7) = See Table 7 for minimum internal wiring between load side of short circuit protective device & line side of starter.
(8) = "@" refer to digest to complete contactor Catalog number for coil voltage and Form modifications.
(9) = Insulator to be provided underneath starter. (QMFZ2), Fastex, Type Formex GK-30, 1/32 inch minimum thickness by 4 inches x 5.7 inches.
Table 7 - Minimum Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
| Wire Code |  | Wire Size
| 7a |  | 12 AWG
| 7b |  | 8 AWG
| 7c |  | 2 AWG
| 7d |  | 1 AWG
| 7e |  | 250 MCM
| 7f |  | 300 MCM
| 7g |  | (2) 250 MCM
| 7h |  | 2/0 AWG
| 7i |  | 4/0 AWG
| 7j |  | (2) 4/0 AWG
| 7k |  | 10 AWG
| 7l |  | 6 AWG
| 7m |  | 4 AWG
| 7n |  | 3 AWG
| 7p |  | 1/0 AWG
| 7q |  | (2) 3/0 AWG
| 7r |  | (2) 2/0 AWG
| 7s |  | 3/0 AWG

## Size3-GJL
Issued: 2008-04-08
Last Revised: 2008-04-08
|  |  |  | "@" refer to Digest to complete | [8 empty] | Use Square D Digest for selection of Melting Alloy and Bi-Metal Overloads only
contactor Catalog number for coil
voltage codes and Form modifications
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE152587 | C | CB | Square D | GJL36090 | 65 | 90 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE152587 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE152588 | C | CB | Square D | GJL36100 | 65 | 100 | 480 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE152588 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 480 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE152589 | C | CB | Square D | GJL36090 | 65 | 90 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE152589 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE152590 | C | CB | Square D | GJL36100 | 65 | 100 | 480 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE152590 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 480 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 3, 7c, 8 | E40610 V12 S1
SE152591 | C | CB | Square D | GJL36090 | 65 | 90 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE152591 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE152592 | C | CB | Square D | GJL36100 | 65 | 100 | 480 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE152592 |  | STR | Square D | 8536SEO1@H10 | 5 | 30 - 90 | 480 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE152593 | C | CB | Square D | GJL36090 | 65 | 90 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE152593 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE152594 | C | CB | Square D | GJL36100 | 65 | 100 | 480 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE152594 |  | STR | Square D | 8536SEO1@H20 | 5 | 30 - 90 | 480 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE152595 | C | CB | Square D | GJL36090 | 65 | 90 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE152595 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE152596 | C | CB | Square D | GJL36100 | 65 | 100 | 480 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE152596 |  | STR | Square D | 8536SEO1@H30 | 5 | 30 - 90 | 480 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE152597 | C | CB | Square D | GJL36090 | 65 | 90 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE152597 |  | STR | Square D | 8536SEO1@64 | 5 | 20 - 90 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE152598 | C | CB | Square D | GJL36100 | 65 | 100 | 480 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE152598 |  | STR | Square D | 8536SEO1@60 | 5 | 20 - 90 | 480 | 3 | 65 | 480 | 3 | 30 | 40 | 2747 | 1, 7c, 8 | E40610 V12 S1
SE152599 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE152599 |  | STR | Square D | 8536SEO1@ | 5 | 90 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE152601 | D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
SE152601 |  | STR | Square D | 8536SEO1@Y59 | 5 | 90 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 2747 | 1, 3, 5, 7c, 8 | E40610 V12 S1
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = Use wire ties evenly spaced apart to secure conductors in place.
(7) = See Table 7 for minimum internal wiring between load side of short circuit protective device & line side of starter.
(8) = "@" refer to digest to complete contactor Catalog number for coil voltage and Form modifications.
(9) = Insulator to be provided underneath starter. (QMFZ2), Fastex, Type Formex GK-30, 1/32 inch minimum thickness by 4 inches x 5.7 inches.
Table 7 - Minimum Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
| Wire Code |  | Wire Size
| 7a |  | 12 AWG
| 7b |  | 8 AWG
| 7c |  | 2 AWG
| 7d |  | 1 AWG
| 7e |  | 250 MCM
| 7f |  | 300 MCM
| 7g |  | (2) 250 MCM
| 7h |  | 2/0 AWG
| 7i |  | 4/0 AWG
| 7j |  | (2) 4/0 AWG
| 7k |  | 10 AWG
| 7l |  | 6 AWG
| 7m |  | 4 AWG
| 7n |  | 3 AWG
| 7p |  | 1/0 AWG
| 7q |  | (2) 3/0 AWG
| 7r |  | (2) 2/0 AWG
| 7s |  | 3/0 AWG