## Type E - U Line
Last Revised: 2006-05-16
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu ft) | Conditions of Acceptability | Combination UL File
SE600000 | E | MSP | Telemecanique | LUB12 | 42 | 12 | 480Y/277 | 3 | 42 | 480Y/277 | 3 | 7.5 | 11 | 0.477 | 1, 5 | E134347 V3 S1
|  | Adapter | Telemecanique | LU9 SPO | - | - | - | -
|  | Control Unit | Telemecanique | LUC | - | - | 600 | 3
SE600010 | E | MSP | Telemecanique | LUB12 | 42 | 12 | 480Y/277 | 3 | 42 | 240 | 3 | 3 | 9.6 | 0.477 | 1, 5 | E134347 V3 S1
|  | Adapter | Telemecanique | LU9 SPO | - | - | - | -
|  | Control Unit | Telemecanique | LUC | - | - | 600 | 3
SE600020 | E | MSP | Telemecanique | LUB12 | 42 | 12 | 480Y/277 | 3 | 42 | 208 | 3 | 3 | 10.6 | 0.477 | 1, 5 | E134347 V3 S1
|  | Adapter | Telemecanique | LU9 SPO | - | - | - | -
|  | Control Unit | Telemecanique | LUC | - | - | 600 | 3
SE600030 | E | MSP | Telemecanique | LUB12 | 42 | 12 | 480Y/277 | 3 | 42 | 200 | 3 | 3 | 11 | 0.477 | 1, 5 | E134347 V3 S1
|  | Adapter | Telemecanique | LU9 SPO | - | - | - | -
|  | Control Unit | Telemecanique | LUC | - | - | 600 | 3
SE600040 | E | MSP | Telemecanique | LUB32 | 42 | 32 | 480Y/277 | 3 | 42 | 480Y/277 | 3 | 20 | 27 | 0.477 | 1, 5 | E134347 V3 S1
|  | Adapter | Telemecanique | LU9 SPO | - | - | - | -
|  | Control Unit | Telemecanique | LUC | - | - | 600 | 3
SE600050 | E | MSP | Telemecanique | LUB32 | 42 | 32 | 480Y/277 | 3 | 42 | 240 | 3 | 10 | 28 | 0.477 | 1, 5 | E134347 V3 S1
|  | Adapter | Telemecanique | LU9 SPO | - | - | - | -
|  | Control Unit | Telemecanique | LUC | - | - | 600 | 3
SE600060 | E | MSP | Telemecanique | LUB32 | 42 | 32 | 480Y/277 | 3 | 42 | 208 | 3 | 10 | 30.8 | 0.477 | 1, 5 | E134347 V3 S1
|  | Adapter | Telemecanique | LU9 SPO | - | - | - | -
|  | Control Unit | Telemecanique | LUC | - | - | 600 | 3
SE600070 | E | MSP | Telemecanique | LUB12 | 65 | 12 | 600 | 3 | 65 | 600 | 3 | 10 | 11 | 0.807 | 1, 5 | E134347 V3 S1
|  | Adapter | Telemecanique | LU9 SPO | - | - | - | -
|  | Control Unit | Telemecanique | LUC | - | - | 600 | 3
|  | Current Limiter | Telemecanique | LUA LB1 | - | - | - | -
SE600080 | E | MSP | Telemecanique | LUB12 | 65 | 12 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 0.807 | 1, 5 | E134347 V3 S1
|  | Adapter | Telemecanique | LU9 SPO | - | - | - | -
|  | Control Unit | Telemecanique | LUC | - | - | 600 | 3
|  | Current Limiter | Telemecanique | LUA LB1 | - | - | - | -
SE600090 | E | MSP | Telemecanique | LUB12 | 65 | 12 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 0.807 | 1, 5 | E134347 V3 S1
|  | Adapter | Telemecanique | LU9 SPO | - | - | - | -
|  | Control Unit | Telemecanique | LUC | - | - | 600 | 3
|  | Current Limiter | Telemecanique | LUA LB1 | - | - | - | -
SE600100 | E | MSP | Telemecanique | LUB12 | 65 | 12 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 0.807 | 1, 5 | E134347 V3 S1
|  | Adapter | Telemecanique | LU9 SPO | - | - | - | -
|  | Control Unit | Telemecanique | LUC | - | - | 600 | 3
|  | Current Limiter | Telemecanique | LUA LB1 | - | - | - | -
SE600110 | E | MSP | Telemecanique | LUB12 | 65 | 12 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 0.807 | 1, 5 | E134347 V3 S1
|  | Adapter | Telemecanique | LU9 SPO | - | - | - | -
|  | Control Unit | Telemecanique | LUC | - | - | 600 | 3
|  | Current Limiter | Telemecanique | LUA LB1 | - | - | - | -
SE600120 | E | MSP | Telemecanique | LUB32 | 65 | 32 | 600 | 3 | 65 | 600 | 3 | 25 | 27 | 0.807 | 1, 5 | E134347 V3 S1
|  | Adapter | Telemecanique | LU9 SPO | - | - | - | -
|  | Control Unit | Telemecanique | LUC | - | - | 600 | 3
|  | Current Limiter | Telemecanique | LUA LB1 | - | - | - | -
SE600130 | E | MSP | Telemecanique | LUB32 | 65 | 32 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 0.807 | 1, 5 | E134347 V3 S1
|  | Adapter | Telemecanique | LU9 SPO | - | - | - | -
|  | Control Unit | Telemecanique | LUC | - | - | 600 | 3
|  | Current Limiter | Telemecanique | LUA LB1 | - | - | - | -
SE600140 | E | MSP | Telemecanique | LUB32 | 65 | 32 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 0.807 | 1, 5 | E134347 V3 S1
|  | Adapter | Telemecanique | LU9 SPO | - | - | - | -
|  | Control Unit | Telemecanique | LUC | - | - | 600 | 3
|  | Current Limiter | Telemecanique | LUA LB1 | - | - | - | -
SE600150 | E | MSP | Telemecanique | LUB32 | 65 | 32 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 0.807 | 1, 5 | E134347 V3 S1
|  | Adapter | Telemecanique | LU9 SPO | - | - | - | -
|  | Control Unit | Telemecanique | LUC | - | - | 600 | 3
|  | Current Limiter | Telemecanique | LUA LB1 | - | - | - | -
SE600160 | E | MSP | Telemecanique | LUB12 | 130 | 12 | 480 | 3 | 130 | 480 | 3 | 7.5 | 11 | 0.807 | 1, 5 | E134347 V3 S1
|  | Adapter | Telemecanique | LU9 SPO | - | - | - | -
|  | Control Unit | Telemecanique | LUC | - | - | 600 | 3
|  | Current Limiter | Telemecanique | LUA LB1 | - | - | - | -
SE600170 | E | MSP | Telemecanique | LUB12 | 130 | 12 | 480 | 3 | 130 | 240 | 3 | 3 | 9.6 | 0.807 | 1, 5 | E134347 V3 S1
|  | Adapter | Telemecanique | LU9 SPO | - | - | - | -
|  | Control Unit | Telemecanique | LUC | - | - | 600 | 3
|  | Current Limiter | Telemecanique | LUA LB1 | - | - | - | -
SE600180 | E | MSP | Telemecanique | LUB12 | 130 | 12 | 480 | 3 | 130 | 208 | 3 | 3 | 10.6 | 0.807 | 1, 5 | E134347 V3 S1
|  | Adapter | Telemecanique | LU9 SPO | - | - | - | -
|  | Control Unit | Telemecanique | LUC | - | - | 600 | 3
|  | Current Limiter | Telemecanique | LUA LB1 | - | - | - | -
SE600190 | E | MSP | Telemecanique | LUB12 | 130 | 12 | 480 | 3 | 130 | 200 | 3 | 3 | 11 | 0.807 | 1, 5 | E134347 V3 S1
|  | Adapter | Telemecanique | LU9 SPO | - | - | - | -
|  | Control Unit | Telemecanique | LUC | - | - | 600 | 3
|  | Current Limiter | Telemecanique | LUA LB1 | - | - | - | -
SE600200 | E | MSP | Telemecanique | LUB32 | 130 | 32 | 480 | 3 | 130 | 480 | 3 | 20 | 27 | 0.807 | 1, 5 | E134347 V3 S1
|  | Adapter | Telemecanique | LU9 SPO | - | - | - | -
|  | Control Unit | Telemecanique | LUC | - | - | 600 | 3
|  | Current Limiter | Telemecanique | LUA LB1 | - | - | - | -
SE600210 | E | MSP | Telemecanique | LUB32 | 130 | 32 | 480 | 3 | 130 | 240 | 3 | 10 | 28 | 0.807 | 1, 5 | E134347 V3 S1
|  | Adapter | Telemecanique | LU9 SPO | - | - | - | -
|  | Control Unit | Telemecanique | LUC | - | - | 600 | 3
|  | Current Limiter | Telemecanique | LUA LB1 | - | - | - | -
SE600220 | E | MSP | Telemecanique | LUB32 | 130 | 32 | 480 | 3 | 130 | 208 | 3 | 10 | 30.8 | 0.807 | 1, 5 | E134347 V3 S1
|  | Adapter | Telemecanique | LU9 SPO | - | - | - | -
|  | Control Unit | Telemecanique | LUC | - | - | 600 | 3
|  | Current Limiter | Telemecanique | LUA LB1 | - | - | - | -