## NEMA Ty. S & M.A. OLR
| Combination motor controllers for use in industrial control panels | [17 empty] | Last Revised: 2006-05-17
ID Number | Combination Type | Individual Component | [6 empty] | Combination SCCR | [5 empty] | Conditions of Acceptability | Combination UL File | Other UL File Reference(s) | Comments
|  | Type | Manufacturer | Catalog Designation | Ratings |  |  |  | kA | Volts | Ph | HP | NEC FLC | Min. Enclosure | [5 empty] | Enclosure
[5 empty] | kA | Max Amps | Volts | Poles | [5 empty] | Vol. (cu ft) | [5 empty] | Vol (cu in)
| C | CB | Square D | FAL32015 | 25 | 15 | 208 | 3 | 5 | 208 | 3 | 1 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201000 |  | MC | Square D | 8502-SBO2V | 5 | na
|  | OLR | Square D | 9065-SEO5 | 5 | na
| C | CB | Square D | FAL32015 | 25 | 15 | 208 | 3 | 5 | 208 | 3 | 1 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201010 |  | STR | Square D | 8536-SBO2V | 5 | na
| C | CB | Square D | FAL32015 | 25 | 15 | 208 | 3 | 5 | 208 | 3 | 2 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201020 |  | MC | Square D | 8502-SBO2V | 5 | na
|  | OLR | Square D | 9065-SEO5 | 5 | na
| C | CB | Square D | FAL32015 | 25 | 15 | 208 | 3 | 5 | 208 | 3 | 2 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201030 |  | STR | Square D | 8536-SBO2V | 5 | na
| C | CB | Square D | FAL32020 | 25 | 20 | 208 | 3 | 5 | 208 | 3 | 3 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201040 |  | MC | Square D | 8502-SBO2V | 5 | na
|  | OLR | Square D | 9065-SEO5 | 5 | na
| C | CB | Square D | FAL32020 | 25 | 20 | 208 | 3 | 5 | 208 | 3 | 3 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201050 |  | STR | Square D | 8536-SBO2V | 5 | na
| C | CB | Square D | FAL32035 | 25 | 35 | 208 | 3 | 5 | 208 | 3 | 5 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201060 |  | MC | Square D | 8502-SCO2V | 5 | na
|  | OLR | Square D | 9065-SEO5 | 5 | na
| C | CB | Square D | FAL32035 | 25 | 35 | 208 | 3 | 5 | 208 | 3 | 5 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201070 |  | STR | Square D | 8536-SCO3V | 5 | na
| C | CB | Square D | FAL32050 | 25 | 50 | 208 | 3 | 5 | 208 | 3 | 7.5 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201080 |  | MC | Square D | 8502-SCO2V | 5 | na
|  | OLR | Square D | 9065-SEO5 | 5 | na
| C | CB | Square D | FAL32050 | 25 | 50 | 208 | 3 | 5 | 208 | 3 | 7.5 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201090 |  | STR | Square D | 8536-SCO3V | 5 | na
| C | CB | Square D | FAL32060 | 25 | 60 | 208 | 3 | 5 | 208 | 3 | 10 |  | 1.2448 | 1 (1.24) | E152395 Vol. 1 Sec. 13 |  |  |  | 2151
SE201100 |  | MC | Square D | 8502-SDO2V | 5 | na
|  | OLR | Square D | 9065-SEO8 | 5 | na
| C | CB | Square D | FAL32060 | 25 | 60 | 208 | 3 | 5 | 208 | 3 | 10 |  | 1.2448 | 1 (1.24) | E152395 Vol. 1 Sec. 13 |  |  |  | 2151
SE201110 |  | STR | Square D | 8536-SDO1V | 5 | na
| C | CB | Square D | FAL32090 | 25 | 90 | 208 | 3 | 5 | 208 | 3 | 15 |  | 3.0955 | 1 (3.10) | E152395 Vol. 1 Sec. 14 |  |  |  | 5349
SE201120 |  | MC | Square D | 8502-SEO2V | 5 | na
|  | OLR | Square D | 9065-SEO12 | 5 | na
| C | CB | Square D | FAL32090 | 25 | 90 | 208 | 3 | 5 | 208 | 3 | 15 |  | 3.0955 | 1 (3.10) | E152395 Vol. 1 Sec. 14 |  |  |  | 5349
SE201130 |  | STR | Square D | 8536-SEO1V | 5 | na
| C | CB | Square D | FAL32100 | 25 | 100 | 208 | 3 | 5 | 208 | 3 | 20 |  | 3.0955 | 1 (3.10) | E152395 Vol. 1 Sec. 14 |  |  |  | 5349
SE201140 |  | MC | Square D | 8502-SEO2V | 5 | na
|  | OLR | Square D | 9065-SEO12 | 5 | na
| C | CB | Square D | FAL32100 | 25 | 100 | 208 | 3 | 5 | 208 | 3 | 20 |  | 3.0955 | 1 (3.10) | E152395 Vol. 1 Sec. 14 |  |  |  | 5349
SE201150 |  | STR | Square D | 8536-SEO1V | 5 | na
| C | CB | Square D | KAL32110 | 42 | 110 | 208 | 3 | 5 | 208 | 3 | 25 |  | 3.0955 | 1 (3.10) | E152395 Vol. 1 Sec. 14 |  |  |  | 5349
SE201160 |  | MC | Square D | 8502-SEO2V | 5 | na
|  | OLR | Square D | 9065-SEO12 | 5 | na
| C | CB | Square D | KAL32110 | 42 | 110 | 208 | 3 | 5 | 208 | 3 | 25 |  | 3.0955 | 1 (3.10) | E152395 Vol. 1 Sec. 14 |  |  |  | 5349
SE201170 |  | STR | Square D | 8536-SEO1V | 5 | na
| C | CB | Square D | KAL32125 | 42 | 125 | 208 | 3 | 10 | 208 | 3 | 30 |  | 4.0833 | 1 (4.08) | E152395 Vol. 1 Sec. 11 |  |  |  | 7056
SE201180 |  | MC | Square D | 8502-SFO2V | 5 | na
|  | OLR | Square D | 9065-SEO15 | 5 | na
| C | CB | Square D | KAL32125 | 42 | 125 | 208 | 3 | 10 | 208 | 3 | 30 |  | 4.0833 | 1 (4.08) | E152395 Vol. 1 Sec. 11 |  |  |  | 7056
SE201190 |  | STR | Square D | 8536-SFO1V | 5 | na
| C | CB | Square D | KAL32200 | 42 | 200 | 208 | 3 | 10 | 208 | 3 | 40 |  | 4.0833 | 1 (4.08) | E152395 Vol. 1 Sec. 11 |  |  |  | 7056
SE201200 |  | MC | Square D | 8502-SFO2V | 5 | na
|  | OLR | Square D | 9065-SEO15 | 5 | na
| C | CB | Square D | KAL32200 | 42 | 200 | 208 | 3 | 10 | 208 | 3 | 40 |  | 4.0833 | 1 (4.08) | E152395 Vol. 1 Sec. 11 |  |  |  | 7056
SE201210 |  | STR | Square D | 8536-SFO1V | 5 | na
| C | CB | Square D | LAL32200 | 42 | 200 | 208 | 3 | 10 | 208 | 3 | 50 |  | 9.1146 | 1 (9.11) | E152395 Vol. 1 Sec. 10 |  |  |  | 15750
SE201230 |  | STR | Square D | 8536-SGO1V | 5 | na
| C | CB | Square D | LAL32250 | 42 | 250 | 208 | 3 | 10 | 208 | 3 | 60 |  | 9.1146 | 1 (9.11) | E152395 Vol. 1 Sec. 10 |  |  |  | 15750
SE201250 |  | STR | Square D | 8536-SGO1V | 10 | na
| C | CB | Square D | FAL32015 | 25 | 15 | 240 | 3 | 5 | 240 | 3 | 1 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201260 |  | MC | Square D | 8502-SBO2V | 5 | na
|  | OLR | Square D | 9065-SEO5 | 5 | na
| C | CB | Square D | FAL32015 | 25 | 15 | 240 | 3 | 5 | 240 | 3 | 1 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201270 |  | STR | Square D | 8536-SBO2V | 5 | na
| C | CB | Square D | FAL32015 | 25 | 15 | 240 | 3 | 5 | 240 | 3 | 2 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201280 |  | MC | Square D | 8502-SBO2V | 5 | na
|  | OLR | Square D | 9065-SEO5 | 5 | na
| C | CB | Square D | FAL32015 | 25 | 15 | 240 | 3 | 5 | 240 | 3 | 2 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201290 |  | STR | Square D | 8536-SBO2V | 5 | na
| C | CB | Square D | FAL32020 | 25 | 20 | 240 | 3 | 5 | 240 | 3 | 3 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201300 |  | MC | Square D | 8502-SBO2V | 5 | na
|  | OLR | Square D | 9065-SEO5 | 5 | na
| C | CB | Square D | FAL32020 | 25 | 20 | 240 | 3 | 5 | 240 | 3 | 3 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201310 |  | STR | Square D | 8536-SBO2V | 5 | na
| C | CB | Square D | FAL32030 | 25 | 30 | 240 | 3 | 5 | 240 | 3 | 5 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201320 |  | MC | Square D | 8502-SCO2V | 5 | na
|  | OLR | Square D | 9065-SEO5 | 5 | na
| C | CB | Square D | FAL32030 | 25 | 30 | 240 | 3 | 5 | 240 | 3 | 5 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201330 |  | STR | Square D | 8536-SCO3V | 5 | na
| C | CB | Square D | FAL32045 | 25 | 45 | 240 | 3 | 5 | 240 | 3 | 7.5 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201340 |  | MC | Square D | 8502-SCO2V | 5 | na
|  | OLR | Square D | 9065-SEO5 | 5 | na
| C | CB | Square D | FAL32045 | 25 | 45 | 240 | 3 | 5 | 240 | 3 | 7.5 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201350 |  | STR | Square D | 8536-SCO3V | 5 | na
| C | CB | Square D | FAL32060 | 25 | 60 | 240 | 3 | 5 | 240 | 3 | 10 |  | 1.2448 | 1 (1.24) | E152395 Vol. 1 Sec. 13 |  |  |  | 2151
SE201360 |  | MC | Square D | 8502-SDO2V | 5 | na
|  | OLR | Square D | 9065-SEO8 | 5 | na
| C | CB | Square D | FAL32060 | 25 | 60 | 240 | 3 | 5 | 240 | 3 | 10 |  | 1.2448 | 1 (1.24) | E152395 Vol. 1 Sec. 13 |  |  |  | 2151
SE201370 |  | STR | Square D | 8536-SDO1V | 5 | na
| C | CB | Square D | FAL32080 | 25 | 80 | 240 | 3 | 5 | 240 | 3 | 15 |  | 1.2448 | 1 (1.24) | E152395 Vol. 1 Sec. 13 |  |  |  | 2151
SE201380 |  | MC | Square D | 8502-SEO2V | 5 | na
|  | OLR | Square D | 9065-SEO12 | 5 | na
| C | CB | Square D | FAL32080 | 25 | 80 | 240 | 3 | 5 | 240 | 3 | 15 |  | 1.2448 | 1 (1.24) | E152395 Vol. 1 Sec. 13 |  |  |  | 2151
SE201390 |  | STR | Square D | 8536-SEO1V | 5 | na
| C | CB | Square D | FAL32090 | 25 | 90 | 220 | 3 | 5 | 220 | 3 | 20 |  | 3.0955 | 1 (3.10) | E152395 Vol. 1 Sec. 14 |  |  |  | 5349
SE201400 |  | MC | Square D | 8502-SEO2V | 5 | na
|  | OLR | Square D | 9065-SEO12 | 5 | na
| C | CB | Square D | FAL32090 | 25 | 90 | 220 | 3 | 5 | 220 | 3 | 20 |  | 3.0955 | 1 (3.10) | E152395 Vol. 1 Sec. 14 |  |  |  | 5349
SE201410 |  | STR | Square D | 8536-SEO1V | 5 | na
| C | CB | Square D | FAL32100 | 25 | 100 | 240 | 3 | 5 | 240 | 3 | 25 |  | 3.0955 | 1 (3.10) | E152395 Vol. 1 Sec. 14 |  |  |  | 5349
SE201420 |  | MC | Square D | 8502-SEO2V | 5 | na
|  | OLR | Square D | 9065-SEO12 | 5 | na
| C | CB | Square D | FAL32100 | 25 | 100 | 240 | 3 | 5 | 240 | 3 | 25 |  | 3.0955 | 1 (3.10) | E152395 Vol. 1 Sec. 14 |  |  |  | 5349
SE201430 |  | STR | Square D | 8536-SEO1V | 5 | na
| C | CB | Square D | KAL32110 | 42 | 110 | 240 | 3 | 5 | 240 | 3 | 30 |  | 3.0955 | 1 (3.10) | E152395 Vol. 1 Sec. 14 |  |  |  | 5349
SE201440 |  | MC | Square D | 8502-SEO2V | 5 | na
|  | OLR | Square D | 9065-SEO12 | 5 | na
| C | CB | Square D | KAL32110 | 42 | 110 | 240 | 3 | 5 | 240 | 3 | 30 |  | 3.0955 | 1 (3.10) | E152395 Vol. 1 Sec. 14 |  |  |  | 5349
SE201450 |  | STR | Square D | 8536-SEO1V | 5 | na
| C | CB | Square D | KAL32150 | 42 | 150 | 240 | 3 | 10 | 240 | 3 | 40 |  | 4.0833 | 1 (4.08) | E152395 Vol. 1 Sec. 11 |  |  |  | 7056
SE201460 |  | MC | Square D | 8502-SFO2V | 5 | na
|  | OLR | Square D | 9065-SEO15 | 5 | na
| C | CB | Square D | KAL32150 | 42 | 150 | 240 | 3 | 10 | 240 | 3 | 40 |  | 4.0833 | 1 (4.08) | E152395 Vol. 1 Sec. 11 |  |  |  | 7056
SE201470 |  | STR | Square D | 8536-SFO1V | 5 | na
| C | CB | Square D | KAL32200 | 42 | 200 | 240 | 3 | 10 | 240 | 3 | 50 |  | 4.0833 | 1 (4.08) | E152395 Vol. 1 Sec. 11 |  |  |  | 7056
SE201480 |  | MC | Square D | 8502-SFO2V | 5 | na
|  | OLR | Square D | 9065-SEO15 | 5 | na
| C | CB | Square D | KAL32200 | 42 | 200 | 240 | 3 | 10 | 240 | 3 | 50 |  | 4.0833 | 1 (4.08) | E152395 Vol. 1 Sec. 11 |  |  |  | 7056
SE201490 |  | STR | Square D | 8536-SFO1V | 5 | na
| C | CB | Square D | LAL32225 | 42 | 225 | 240 | 3 | 10 | 240 | 3 | 60 |  | 9.1146 | 1 (9.11) | E152395 Vol. 1 Sec. 10 |  |  |  | 15750
SE201510 |  | STR | Square D | 8536-SGO1V | 10 | na
| C | CB | Square D | LAL32250 | 42 | 250 | 240 | 3 | 10 | 240 | 3 | 75 |  | 9.1146 | 1 (9.11) | E152395 Vol. 1 Sec. 10 |  |  |  | 15750
SE201530 |  | STR | Square D | 8536-SGO1V | 10 | na
| C | CB | Square D | FAL34015 | 18 | 15 | 480 | 3 | 5 | 480 | 3 | 1 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201540 |  | MC | Square D | 8502-SBO2V | 5 | na
|  | OLR | Square D | 9065-SEO5 | 5 | na
| C | CB | Square D | FAL34015 | 18 | 15 | 480 | 3 | 5 | 480 | 3 | 1 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201550 |  | STR | Square D | 8536-SBO2V | 5 | na
| C | CB | Square D | FAL34015 | 18 | 15 | 480 | 3 | 5 | 480 | 3 | 2 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201560 |  | MC | Square D | 8502-SBO2V | 5 | na
|  | OLR | Square D | 9065-SEO5 | 5 | na
| C | CB | Square D | FAL34015 | 18 | 15 | 480 | 3 | 5 | 480 | 3 | 2 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201570 |  | STR | Square D | 8536-SBO2V | 5 | na
| C | CB | Square D | FAL34015 | 18 | 15 | 480 | 3 | 5 | 480 | 3 | 3 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201580 |  | MC | Square D | 8502-SBO2V | 5 | na
|  | OLR | Square D | 9065-SEO5 | 5 | na
| C | CB | Square D | FAL34015 | 18 | 15 | 480 | 3 | 5 | 480 | 3 | 3 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201590 |  | STR | Square D | 8536-SBO2V | 5 | na
| C | CB | Square D | FAL34015 | 18 | 15 | 480 | 3 | 5 | 480 | 3 | 5 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201600 |  | MC | Square D | 8502-SBO2V | 5 | na
|  | OLR | Square D | 9065-SEO5 | 5 | na
| C | CB | Square D | FAL34015 | 18 | 15 | 480 | 3 | 5 | 480 | 3 | 5 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201610 |  | STR | Square D | 8536-SBO2V | 5 | na
| C | CB | Square D | FAL34020 | 18 | 20 | 480 | 3 | 5 | 480 | 3 | 7.5 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201620 |  | MC | Square D | 8502-SCO2V | 5 | na
|  | OLR | Square D | 9065-SEO5 | 5 | na
| C | CB | Square D | FAL34020 | 18 | 20 | 480 | 3 | 5 | 480 | 3 | 7.5 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201630 |  | STR | Square D | 8536-SCO3V | 5 | na
| C | CB | Square D | FAL34025 | 18 | 25 | 480 | 3 | 5 | 480 | 3 | 10 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201640 |  | MC | Square D | 8502-SCO2V | 5 | na
|  | OLR | Square D | 9065-SEO5 | 5 | na
| C | CB | Square D | FAL34025 | 18 | 25 | 480 | 3 | 5 | 480 | 3 | 10 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201650 |  | STR | Square D | 8536-SCO3V | 5 | na
| C | CB | Square D | FAL34040 | 18 | 40 | 480 | 3 | 5 | 480 | 3 | 15 |  | 1.2448 | 1 (1.24) | E152395 Vol. 1 Sec. 13 |  |  |  | 2151
SE201660 |  | MC | Square D | 8502-SDO2V | 5 | na
|  | OLR | Square D | 9065-SEO8 | 5 | na
| C | CB | Square D | FAL34040 | 18 | 40 | 480 | 3 | 5 | 480 | 3 | 15 |  | 1.2448 | 1 (1.24) | E152395 Vol. 1 Sec. 13 |  |  |  | 2151
SE201670 |  | STR | Square D | 8536-SDO1V | 5 | na
| C | CB | Square D | FAL34060 | 18 | 60 | 480 | 3 | 5 | 480 | 3 | 20 |  | 1.2448 | 1 (1.24) | E152395 Vol. 1 Sec. 13 |  |  |  | 2151
SE201680 |  | MC | Square D | 8502-SDO2V | 5 | na
|  | OLR | Square D | 9065-SEO8 | 5 | na
| C | CB | Square D | FAL34060 | 18 | 60 | 480 | 3 | 5 | 480 | 3 | 20 |  | 1.2448 | 1 (1.24) | E152395 Vol. 1 Sec. 13 |  |  |  | 2151
SE201690 |  | STR | Square D | 8536-SDO1V | 5 | na
| C | CB | Square D | FAL34070 | 18 | 70 | 480 | 3 | 5 | 480 | 3 | 25 |  | 1.2448 | 1 (1.24) | E152395 Vol. 1 Sec. 13 |  |  |  | 2151
SE201700 |  | MC | Square D | 8502-SDO2V | 5 | na
|  | OLR | Square D | 9065-SEO8 | 5 | na
| C | CB | Square D | FAL34070 | 18 | 70 | 480 | 3 | 5 | 480 | 3 | 25 |  | 1.2448 | 1 (1.24) | E152395 Vol. 1 Sec. 13 |  |  |  | 2151
SE201710 |  | STR | Square D | 8536-SDO1V | 5 | na
| C | CB | Square D | FAL34080 | 18 | 80 | 480 | 3 | 5 | 480 | 3 | 30 |  | 3.0955 | 1 (3.10) | E152395 Vol. 1 Sec. 14 |  |  |  | 5349
SE201720 |  | MC | Square D | 8502-SEO2V | 5 | na
|  | OLR | Square D | 9065-SEO12 | 5 | na
| C | CB | Square D | FAL34080 | 18 | 80 | 480 | 3 | 5 | 480 | 3 | 30 |  | 3.0955 | 1 (3.10) | E152395 Vol. 1 Sec. 14 |  |  |  | 5349
SE201730 |  | STR | Square D | 8536-SEO1V | 5 | na
| C | CB | Square D | FAL34090 | 18 | 90 | 480 | 3 | 5 | 480 | 3 | 40 |  | 3.0955 | 1 (3.10) | E152395 Vol. 1 Sec. 14 |  |  |  | 5349
SE201740 |  | MC | Square D | 8502-SEO2V | 5 | na
|  | OLR | Square D | 9065-SEO12 | 5 | na
| C | CB | Square D | FAL34090 | 18 | 90 | 480 | 3 | 5 | 480 | 3 | 40 |  | 3.0955 | 1 (3.10) | E152395 Vol. 1 Sec. 14 |  |  |  | 5349
SE201750 |  | STR | Square D | 8536-SEO1V | 5 | na
| C | CB | Square D | FAL34100 | 18 | 100 | 480 | 3 | 5 | 480 | 3 | 50 |  | 3.0955 | 1 (3.10) | E152395 Vol. 1 Sec. 14 |  |  |  | 5349
SE201760 |  | MC | Square D | 8502-SEO2V | 5 | na
|  | OLR | Square D | 9065-SEO12 | 5 | na
| C | CB | Square D | FAL34100 | 18 | 100 | 480 | 3 | 5 | 480 | 3 | 50 |  | 3.0955 | 1 (3.10) | E152395 Vol. 1 Sec. 14 |  |  |  | 5349
SE201770 |  | STR | Square D | 8536-SEO1V | 5 | na
| C | CB | Square D | KAL34110 | 25 | 110 | 480 | 3 | 10 | 480 | 3 | 60 |  | 4.0833 | 1 (4.08) | E152395 Vol. 1 Sec. 11 |  |  |  | 7056
SE201780 |  | MC | Square D | 8502-SFO2V | 10 | na
|  | OLR | Square D | 9065-SEO15 | 10 | na
| C | CB | Square D | KAL34110 | 25 | 110 | 480 | 3 | 10 | 480 | 3 | 60 |  | 4.0833 | 1 (4.08) | E152395 Vol. 1 Sec. 11 |  |  |  | 7056
SE201790 |  | STR | Square D | 8536-SFO1V | 10 | na
| C | CB | Square D | KAL34125 | 25 | 125 | 480 | 3 | 10 | 480 | 3 | 75 |  | 4.0833 | 1 (4.08) | E152395 Vol. 1 Sec. 11 |  |  |  | 7056
SE201800 |  | MC | Square D | 8502-SFO2V | 10 | na
|  | OLR | Square D | 9065-SEO15 | 10 | na
| C | CB | Square D | KAL34125 | 25 | 125 | 480 | 3 | 10 | 480 | 3 | 75 |  | 4.0833 | 1 (4.08) | E152395 Vol. 1 Sec. 11 |  |  |  | 7056
SE201810 |  | STR | Square D | 8536-SFO1V | 10 | na
| C | CB | Square D | KAL34200 | 25 | 200 | 480 | 3 | 10 | 480 | 3 | 100 |  | 4.0833 | 1 (4.08) | E152395 Vol. 1 Sec. 11 |  |  |  | 7056
SE201820 |  | MC | Square D | 8502-SFO2V | 10 | na
|  | OLR | Square D | 9065-SEO15 | 10 | na
| C | CB | Square D | KAL34200 | 25 | 200 | 480 | 3 | 10 | 480 | 3 | 100 |  | 4.0833 | 1 (4.08) | E152395 Vol. 1 Sec. 11 |  |  |  | 7056
SE201830 |  | STR | Square D | 8536-SFO1V | 10 | na
| C | CB | Square D | LAL34225 | 30 | 225 | 480 | 3 | 10 | 480 | 3 | 125 |  | 9.1146 | 1 (9.11) | E152395 Vol. 1 Sec. 10 |  |  |  | 15750
SE201850 |  | STR | Square D | 8536-SGO1V | 10 | na
| C | CB | Square D | LAL34250 | 30 | 250 | 480 | 3 | 10 | 480 | 3 | 150 |  | 9.1146 | 1 (9.11) | E152395 Vol. 1 Sec. 10 |  |  |  | 15750
SE201870 |  | STR | Square D | 8536-SGO1V | 10 | na
| C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 5 | 600 | 3 | 1 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201880 |  | MC | Square D | 8502-SBO2V | 5 | na
|  | OLR | Square D | 9065-SEO5 | 5 | na
| C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 5 | 600 | 3 | 1 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201890 |  | STR | Square D | 8536-SBO2V | 5 | na
| C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 5 | 600 | 3 | 2 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201900 |  | MC | Square D | 8502-SBO2V | 5 | na
|  | OLR | Square D | 9065-SEO5 | 5 | na
| C | CB | Square D | FAL36015 | 18 | 15 | 600 | 3 | 5 | 600 | 3 | 2 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201910 |  | STR | Square D | 8536-SBO2V | 5 | na
| C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 5 | 600 | 3 | 3 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201920 |  | MC | Square D | 8502-SBO2V | 5 | na
|  | OLR | Square D | 9065-SEO5 | 5 | na
| C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 5 | 600 | 3 | 3 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201930 |  | STR | Square D | 8536-SBO2V | 5 | na
| C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 5 | 600 | 3 | 5 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201940 |  | MC | Square D | 8502-SBO2V | 5 | na
|  | OLR | Square D | 9065-SEO5 | 5 | na
| C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 5 | 600 | 3 | 5 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201950 |  | STR | Square D | 8536-SBO2V | 5 | na
| C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 5 | 600 | 3 | 7.5 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201960 |  | MC | Square D | 8502-SCO2V | 5 | na
|  | OLR | Square D | 9065-SEO5 | 5 | na
| C | CB | Square D | FAL36015 | 14 | 15 | 600 | 3 | 5 | 600 | 3 | 7.5 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201970 |  | STR | Square D | 8536-SCO3V | 5 | na
| C | CB | Square D | FAL36020 | 14 | 20 | 600 | 3 | 5 | 600 | 3 | 10 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201980 |  | MC | Square D | 8502-SCO2V | 5 | na
|  | OLR | Square D | 9065-SEO5 | 5 | na
| C | CB | Square D | FAL36020 | 14 | 20 | 600 | 3 | 5 | 600 | 3 | 10 |  | 0.80324 | 1 (0.80) | E152395 Vol. 1 Sec. 15 |  |  |  | 1388
SE201990 |  | STR | Square D | 8536-SCO3V | 5 | na
| C | CB | Square D | FAL36035 | 14 | 35 | 600 | 3 | 5 | 600 | 3 | 15 |  | 1.2448 | 1 (1.24) | E152395 Vol. 1 Sec. 13 |  |  |  | 2151
SE202000 |  | MC | Square D | 8502-SDO2V | 5 | na
|  | OLR | Square D | 9065-SEO8 | 5 | na
| C | CB | Square D | FAL36035 | 14 | 35 | 600 | 3 | 5 | 600 | 3 | 15 |  | 1.2448 | 1 (1.24) | E152395 Vol. 1 Sec. 13 |  |  |  | 2151
SE202010 |  | STR | Square D | 8536-SDO1V | 5 | na
| C | CB | Square D | FAL36045 | 14 | 45 | 600 | 3 | 5 | 600 | 3 | 20 |  | 1.2448 | 1 (1.24) | E152395 Vol. 1 Sec. 13 |  |  |  | 2151
SE202020 |  | MC | Square D | 8502-SDO2V | 5 | na
|  | OLR | Square D | 9065-SEO8 | 5 | na
| C | CB | Square D | FAL36045 | 14 | 45 | 600 | 3 | 5 | 600 | 3 | 20 |  | 1.2448 | 1 (1.24) | E152395 Vol. 1 Sec. 13 |  |  |  | 2151
SE202030 |  | STR | Square D | 8536-SDO1V | 5 | na
| C | CB | Square D | FAL36060 | 14 | 60 | 600 | 3 | 5 | 600 | 3 | 25 |  | 1.2448 | 1 (1.24) | E152395 Vol. 1 Sec. 13 |  |  |  | 2151
SE202040 |  | MC | Square D | 8502-SDO2V | 5 | na
|  | OLR | Square D | 9065-SEO8 | 5 | na
| C | CB | Square D | FAL36060 | 14 | 60 | 600 | 3 | 5 | 600 | 3 | 25 |  | 1.2448 | 1 (1.24) | E152395 Vol. 1 Sec. 13 |  |  |  | 2151
SE202050 |  | STR | Square D | 8536-SDO1V | 5 | na
| C | CB | Square D | FAL36060 | 14 | 60 | 600 | 3 | 5 | 600 | 3 | 30 |  | 3.0955 | 1 (3.10) | E152395 Vol. 1 Sec. 14 |  |  |  | 5349
SE202060 |  | MC | Square D | 8502-SEO2V | 5 | na
|  | OLR | Square D | 9065-SEO12 | 5 | na
| C | CB | Square D | FAL36060 | 14 | 60 | 600 | 3 | 5 | 600 | 3 | 30 |  | 3.0955 | 1 (3.10) | E152395 Vol. 1 Sec. 14 |  |  |  | 5349
SE202070 |  | STR | Square D | 8536-SEO1V | 5 | na
| C | CB | Square D | FAL36080 | 14 | 80 | 600 | 3 | 5 | 600 | 3 | 40 |  | 3.0955 | 1 (3.10) | E152395 Vol. 1 Sec. 14 |  |  |  | 5349
SE202080 |  | MC | Square D | 8502-SEO2V | 5 | na
|  | OLR | Square D | 9065-SEO12 | 5 | na
| C | CB | Square D | FAL36080 | 14 | 80 | 600 | 3 | 5 | 600 | 3 | 40 |  | 3.0955 | 1 (3.10) | E152395 Vol. 1 Sec. 14 |  |  |  | 5349
SE202090 |  | STR | Square D | 8536-SEO1V | 5 | na
| C | CB | Square D | FAL36090 | 14 | 90 | 600 | 3 | 5 | 600 | 3 | 50 |  | 3.0955 | 1 (3.10) | E152395 Vol. 1 Sec. 14 |  |  |  | 5349
SE202100 |  | MC | Square D | 8502-SEO2V | 5 | na
|  | OLR | Square D | 9065-SEO12 | 5 | na
| C | CB | Square D | FAL36090 | 14 | 90 | 600 | 3 | 5 | 600 | 3 | 50 |  | 3.0955 | 1 (3.10) | E152395 Vol. 1 Sec. 14 |  |  |  | 5349
SE202110 |  | STR | Square D | 8536-SEO1V | 5 | na
| C | CB | Square D | FAL36100 | 14 | 100 | 600 | 3 | 10 | 600 | 3 | 60 |  | 4.0833 | 1 (4.08) | E152395 Vol. 1 Sec. 11 |  |  |  | 7056
SE202120 |  | MC | Square D | 8502-SFO2V | 10 | na
|  | OLR | Square D | 9065-SEO15 | 10 | na
| C | CB | Square D | FAL36100 | 14 | 100 | 600 | 3 | 10 | 600 | 3 | 60 |  | 4.0833 | 1 (4.08) | E152395 Vol. 1 Sec. 11 |  |  |  | 7056
SE202130 |  | STR | Square D | 8536-SFO1V | 10 | na
| C | CB | Square D | KAL36110 | 22 | 110 | 600 | 3 | 10 | 600 | 3 | 75 |  | 4.0833 | 1 (4.08) | E152395 Vol. 1 Sec. 11 |  |  |  | 7056
SE202140 |  | MC | Square D | 8502-SFO2V | 10 | na
|  | OLR | Square D | 9065-SEO15 | 10 | na
| C | CB | Square D | KAL36110 | 22 | 110 | 600 | 3 | 10 | 600 | 3 | 75 |  | 4.0833 | 1 (4.08) | E152395 Vol. 1 Sec. 11 |  |  |  | 7056
SE202150 |  | STR | Square D | 8536-SFO1V | 10 | na
| C | CB | Square D | KAL36150 | 22 | 150 | 600 | 3 | 10 | 600 | 3 | 100 |  | 4.0833 | 1 (4.08) | E152395 Vol. 1 Sec. 11 |  |  |  | 7056
SE202160 |  | MC | Square D | 8502-SFO2V | 10 | na
|  | OLR | Square D | 9065-SEO15 | 10 | na
| C | CB | Square D | KAL36150 | 22 | 150 | 600 | 3 | 10 | 600 | 3 | 100 |  | 4.0833 | 1 (4.08) | E152395 Vol. 1 Sec. 11 |  |  |  | 7056
SE202170 |  | STR | Square D | 8536-SFO1V | 10 | na
| C | CB | Square D | KAL36200 | 22 | 200 | 600 | 3 | 10 | 600 | 3 | 125 |  | 9.1146 | 1 (9.11) | E152395 Vol. 1 Sec. 10 |  |  |  | 15750
SE202190 |  | STR | Square D | 8536-SGO1V | 10 | na
| C | CB | Square D | LAL36200 | 22 | 200 | 600 | 3 | 10 | 600 | 3 | 150 |  | 9.1146 | 1 (9.11) | E152395 Vol. 1 Sec. 10 |  |  |  | 15750
SE202210 |  | STR | Square D | 8536-SGO1V | 10 | na
| C | CB | Square D | LAL36250 | 22 | 250 | 600 | 3 | 10 | 600 | 3 | 200 |  | 9.1146 | 1 (9.11) | E152395 Vol. 1 Sec. 10 |  |  |  | 15750
SE202230 |  | STR | Square D | 8536-SGO1V | 10 | na

## IEC Ty. D_F - Bimet. OLR
| Combination motor controllers for use in industrial control panels | [17 empty] | Last Revised: 2006-05-17
ID Number | Combination Type | Individual Component | [6 empty] | Combination SCCR | [5 empty] | Conditions of Acceptability | Combination UL File | Other UL File Reference(s) | Comments
|  | Type | Manufacturer | Catalog Designation | Ratings |  |  |  | kA | Volts | Ph | HP | NEC FLC | Min. Enclosure | [5 empty] | Enclosure
[5 empty] | kA | Max Amps | Volts | Poles | [5 empty] | Vol. (cu ft) | [5 empty] | Vol (cu in)
| D | ICB | Square D | GJL36015M03 | - | 15 | 480 | 3 | 65 | 480 | 3 | 1 | 2.1 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300010 |  | MC | Telemecanique | LCxD32 | 5 | na | 480 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD07 | 5 | na | 480 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 480 | 3 | 65 | 480 | 3 | 2 | 3.4 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300020 |  | MC | Telemecanique | LCxD32 | 5 | na | 480 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD08 | 5 | na | 480 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 480 | 3 | 65 | 480 | 3 | 2 | 3.4 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300030 |  | MC | Telemecanique | LCxD32 | 5 | na | 480 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD1508 | 5 | na | 480 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 480 | 3 | 65 | 480 | 3 | 3 | 4.8 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300040 |  | MC | Telemecanique | LCxD32 | 5 | na | 480 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD10 | 5 | na | 480 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 480 | 3 | 65 | 480 | 3 | 3 | 4.8 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300050 |  | MC | Telemecanique | LCxD32 | 5 | na | 480 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD1510 | 5 | na | 480 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 480 | 3 | 65 | 480 | 3 | 5 | 7.6 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300060 |  | MC | Telemecanique | LCxD32 | 5 | na | 480 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD14 | 5 | na | 480 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 480 | 3 | 65 | 480 | 3 | 5 | 7.6 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300070 |  | MC | Telemecanique | LCxD32 | 5 | na | 480 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD1514 | 5 | na | 480 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 480 | 3 | 65 | 480 | 3 | 7.5 | 11 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300080 |  | MC | Telemecanique | LCxD32 | 5 | na | 480 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD16 | 5 | na | 480 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 480 | 3 | 65 | 480 | 3 | 7.5 | 11 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300090 |  | MC | Telemecanique | LCxD32 | 5 | na | 480 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD1516 | 5 | na | 480 | 3
| D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300100 |  | MC | Telemecanique | LCxD32 | 5 | na | 480 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD21 | 5 | na | 480 | 3
| D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 65 | 480 | 3 | 10 | 14 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300110 |  | MC | Telemecanique | LCxD32 | 5 | na | 480 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD1521 | 5 | na | 480 | 3
| D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 65 | 480 | 3 | 15 | 21 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300120 |  | MC | Telemecanique | LCxD32 | 5 | na | 480 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD22 | 5 | na | 480 | 3
| D | ICB | Square D | GJL36030M04 | - | 30 | 480 | 3 | 65 | 480 | 3 | 15 | 21 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300130 |  | MC | Telemecanique | LCxD32 | 5 | na | 480 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD1522 | 5 | na | 480 | 3
| D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 480 | 3 | 20 | 27 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300140 |  | MC | Telemecanique | LCxD32 | 5 | na | 480 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD32 | 5 | na | 480 | 3
| D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 480 | 3 | 20 | 27 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300150 |  | MC | Telemecanique | LCxD32 | 5 | na | 480 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD1532 | 5 | na | 480 | 3
| D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300160 |  | MC | Telemecanique | LCxD40 | 5 | na | 480 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD3355 | 5 | na | 480 | 3
| D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 480 | 3 | 25 | 34 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300170 |  | MC | Telemecanique | LCxD40 | 5 | na | 480 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LR2D3555 | 5 | na | 480 | 3
| D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 480 | 3 | 30 | 40 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300180 |  | MC | Telemecanique | LCxD50 | 5 | na | 480 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD3357 | 5 | na | 480 | 3
| D | ICB | Square D | GJL36050M05 | - | 50 | 480 | 3 | 65 | 480 | 3 | 30 | 40 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300190 |  | MC | Telemecanique | LCxD50 | 5 | na | 480 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LR2D3557 | 5 | na | 480 | 3
| D | ICB | Square D | FAL36100-18M | - | 100 | 480 | 3 | 18 | 480 | 3 | 40 | 52 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300200 |  | MC | Telemecanique | LCxD65 | 5 | na | 480 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD3359 | 5 | na | 480 | 3
| D | ICB | Square D | FAL36100-18M | - | 100 | 480 | 3 | 18 | 480 | 3 | 40 | 52 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300210 |  | MC | Telemecanique | LCxD65 | 5 | na | 480 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LR2D3559 | 5 | na | 480 | 3
| D | ICB | Square D | KAL36250-30M | - | 250 | 480 | 3 | 22 | 480 | 3 | 100 | 124 | 7.4653 | 1 (7.47), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 12900 | 1728
SE300290 |  | MC | Telemecanique | LCxD150 | 10 | na | 480 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LR9D5569 | 10 | na | 480 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 600Y/347 | 3 | 18 | 600Y/347 | 3 | 1 | 1.7 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300300 |  | MC | Telemecanique | LCxD32 | 5 | na | 600 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD07 | 5 | na | 600 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 600Y/347 | 3 | 18 | 600Y/347 | 3 | 2 | 2.7 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300310 |  | MC | Telemecanique | LCxD32 | 5 | na | 600 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD08 | 5 | na | 600 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 600Y/347 | 3 | 18 | 600Y/347 | 3 | 2 | 2.7 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300320 |  | MC | Telemecanique | LCxD32 | 5 | na | 600 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD1508 | 5 | na | 600 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 600Y/347 | 3 | 18 | 600Y/347 | 3 | 3 | 3.9 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300330 |  | MC | Telemecanique | LCxD32 | 5 | na | 600 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD08 | 5 | na | 600 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 600Y/347 | 3 | 18 | 600Y/347 | 3 | 3 | 3.9 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300340 |  | MC | Telemecanique | LCxD32 | 5 | na | 600 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD1508 | 5 | na | 600 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 600Y/347 | 3 | 18 | 600Y/347 | 3 | 5 | 6.1 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300350 |  | MC | Telemecanique | LCxD32 | 5 | na | 600 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD12 | 5 | na | 600 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 600Y/347 | 3 | 18 | 600Y/347 | 3 | 5 | 6.1 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300360 |  | MC | Telemecanique | LCxD32 | 5 | na | 600 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD1512 | 5 | na | 600 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 600Y/347 | 3 | 18 | 600Y/347 | 3 | 7.5 | 9 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300370 |  | MC | Telemecanique | LCxD32 | 5 | na | 600 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD14 | 5 | na | 600 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 600Y/347 | 3 | 18 | 600Y/347 | 3 | 7.5 | 9 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300380 |  | MC | Telemecanique | LCxD32 | 5 | na | 600 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD1514 | 5 | na | 600 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 600Y/347 | 3 | 18 | 600Y/347 | 3 | 10 | 11 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300390 |  | MC | Telemecanique | LCxD32 | 5 | na | 600 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD16 | 5 | na | 600 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 600Y/347 | 3 | 18 | 600Y/347 | 3 | 10 | 11 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300400 |  | MC | Telemecanique | LCxD32 | 5 | na | 600 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD1516 | 5 | na | 600 | 3
| D | ICB | Square D | GJL36030M04 | - | 30 | 600Y/347 | 3 | 18 | 600Y/347 | 3 | 15 | 17 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300410 |  | MC | Telemecanique | LCxD32 | 5 | na | 600 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD21 | 5 | na | 600 | 3
| D | ICB | Square D | GJL36030M04 | - | 30 | 600Y/347 | 3 | 18 | 600Y/347 | 3 | 15 | 17 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300420 |  | MC | Telemecanique | LCxD32 | 5 | na | 600 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD1521 | 5 | na | 600 | 3
| D | ICB | Square D | GJL36030M04 | - | 30 | 600Y/347 | 3 | 18 | 600Y/347 | 3 | 20 | 22 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300430 |  | MC | Telemecanique | LCxD32 | 5 | na | 600 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD22 | 5 | na | 600 | 3
| D | ICB | Square D | GJL36030M04 | - | 30 | 600Y/347 | 3 | 18 | 600Y/347 | 3 | 20 | 22 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300440 |  | MC | Telemecanique | LCxD32 | 5 | na | 600 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD1522 | 5 | na | 600 | 3
| D | ICB | Square D | GJL36050M05 | - | 50 | 600Y/347 | 3 | 18 | 600Y/347 | 3 | 25 | 27 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300450 |  | MC | Telemecanique | LCxD32 | 5 | na | 600 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD32 | 5 | na | 600 | 3
| D | ICB | Square D | GJL36050M05 | - | 50 | 600Y/347 | 3 | 18 | 600Y/347 | 3 | 25 | 27 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300460 |  | MC | Telemecanique | LCxD32 | 5 | na | 600 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD1530 | 5 | na | 600 | 3
| D | ICB | Square D | GJL36050M05 | - | 50 | 600Y/347 | 3 | 18 | 600Y/347 | 3 | 30 | 32 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300470 |  | MC | Telemecanique | LCxD40 | 5 | na | 600 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD3355 | 5 | na | 600 | 3
| D | ICB | Square D | GJL36050M05 | - | 50 | 600Y/347 | 3 | 18 | 600Y/347 | 3 | 30 | 32 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300480 |  | MC | Telemecanique | LCxD40 | 5 | na | 600 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LR2D3555 | 5 | na | 600 | 3
| D | ICB | Square D | GJL36050M05 | - | 50 | 600Y/347 | 3 | 18 | 600Y/347 | 3 | 40 | 41 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300490 |  | MC | Telemecanique | LCxD50 | 5 | na | 600 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD3357 | 5 | na | 600 | 3
| D | ICB | Square D | GJL36050M05 | - | 50 | 600Y/347 | 3 | 18 | 600Y/347 | 3 | 40 | 41 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300500 |  | MC | Telemecanique | LCxD50 | 5 | na | 600 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LR2D3557 | 5 | na | 600 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 208 | 3 | 65 | 208 | 3 | 1 | 4.6 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300510 |  | MC | Telemecanique | LCxD32 | 5 | na | 208 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD10 | 5 | na | 208 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 208 | 3 | 65 | 208 | 3 | 1 | 4.6 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300520 |  | MC | Telemecanique | LCxD32 | 5 | na | 208 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD1510 | 5 | na | 208 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 208 | 3 | 65 | 208 | 3 | 2 | 7.5 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300530 |  | MC | Telemecanique | LCxD32 | 5 | na | 208 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD14 | 5 | na | 208 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 208 | 3 | 65 | 208 | 3 | 2 | 7.5 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300540 |  | MC | Telemecanique | LCxD32 | 5 | na | 208 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD1514 | 5 | na | 208 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 208 | 3 | 65 | 208 | 3 | 3 | 10.6 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300550 |  | MC | Telemecanique | LCxD32 | 5 | na | 208 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD16 | 5 | na | 208 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 208 | 3 | 65 | 208 | 3 | 3 | 10.6 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300560 |  | MC | Telemecanique | LCxD32 | 5 | na | 208 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD1516 | 5 | na | 208 | 3
| D | ICB | Square D | GJL36030M04 | - | 30 | 208 | 3 | 65 | 208 | 3 | 5 | 16.7 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300570 |  | MC | Telemecanique | LCxD32 | 5 | na | 208 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD21 | 5 | na | 208 | 3
| D | ICB | Square D | GJL36030M04 | - | 30 | 208 | 3 | 65 | 208 | 3 | 5 | 16.7 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300580 |  | MC | Telemecanique | LCxD32 | 5 | na | 208 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD1521 | 5 | na | 208 | 3
| D | ICB | Square D | GJL36030M04 | - | 30 | 208 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300590 |  | MC | Telemecanique | LCxD32 | 5 | na | 208 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD32 | 5 | na | 208 | 3
| D | ICB | Square D | GJL36030M04 | - | 30 | 208 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300600 |  | MC | Telemecanique | LCxD32 | 5 | na | 208 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD1530 | 5 | na | 208 | 3
| D | ICB | Square D | GJL36050M05 | - | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300610 |  | MC | Telemecanique | LCxD40 | 5 | na | 208 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD3355 | 5 | na | 208 | 3
| D | ICB | Square D | GJL36050M05 | - | 50 | 208 | 3 | 65 | 208 | 3 | 10 | 30.8 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300620 |  | MC | Telemecanique | LCxD40 | 5 | na | 208 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LR2D3555 | 5 | na | 208 | 3
| D | ICB | Square D | GJL36050M05 | - | 50 | 208 | 3 | 65 | 208 | 3 | 15 | 46.2 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300630 |  | MC | Telemecanique | LCxD50 | 5 | na | 208 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD3357 | 5 | na | 208 | 3
| D | ICB | Square D | GJL36050M05 | - | 50 | 208 | 3 | 65 | 208 | 3 | 15 | 46.2 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300640 |  | MC | Telemecanique | LCxD50 | 5 | na | 208 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LR2D3557 | 5 | na | 208 | 3
| D | ICB | Square D | FAL36100-18M | - | 100 | 208 | 3 | 22 | 208 | 3 | 20 | 59.4 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300650 |  | MC | Telemecanique | LCxD65 | 5 | na | 208 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD3359 | 5 | na | 208 | 3
| D | ICB | Square D | FAL36100-18M | - | 100 | 208 | 3 | 22 | 208 | 3 | 20 | 59.4 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300660 |  | MC | Telemecanique | LCxD65 | 5 | na | 208 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LR2D3559 | 5 | na | 208 | 3
| D | ICB | Square D | FAL36100-18M | - | 100 | 208 | 3 | 22 | 208 | 3 | 25 | 74.8 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300670 |  | MC | Telemecanique | LCxD80 | 5 | na | 208 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD3363 | 5 | na | 208 | 3
| D | ICB | Square D | FAL36100-18M | - | 100 | 208 | 3 | 22 | 208 | 3 | 25 | 74.8 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300680 |  | MC | Telemecanique | LCxD80 | 5 | na | 208 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LR2D3563 | 5 | na | 208 | 3
| D | ICB | Square D | FAL36150-24M | - | 150 | 208 | 3 | 22 | 208 | 3 | 30 | 88 | 7.4653 | 1 (7.47), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 12900 | 1728
SE300700 |  | MC | Telemecanique | LCxD115 | 10 | na | 208 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LR9D5567 | 10 | na | 208 | 3
| D | ICB | Square D | KAL36250-30M | - | 250 | 208 | 3 | 42 | 208 | 3 | 40 | 114 | 7.4653 | 1 (7.47), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 12900 | 1728
SE300720 |  | MC | Telemecanique | LCxD150 | 10 | na | 208 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LR9D5569 | 10 | na | 208 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 240 | 3 | 65 | 240 | 3 | 1 | 4.2 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300730 |  | MC | Telemecanique | LCxD32 | 5 | na | 240 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD10 | 5 | na | 240 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 240 | 3 | 65 | 240 | 3 | 1 | 4.2 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300740 |  | MC | Telemecanique | LCxD32 | 5 | na | 240 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD1510 | 5 | na | 240 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 240 | 3 | 65 | 240 | 3 | 2 | 6.8 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300750 |  | MC | Telemecanique | LCxD32 | 5 | na | 240 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD12 | 5 | na | 240 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 240 | 3 | 65 | 240 | 3 | 2 | 6.8 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300760 |  | MC | Telemecanique | LCxD32 | 5 | na | 240 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD1512 | 5 | na | 240 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 240 | 3 | 65 | 240 | 3 | 3 | 9.6 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300770 |  | MC | Telemecanique | LCxD32 | 5 | na | 240 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD16 | 5 | na | 240 | 3
| D | ICB | Square D | GJL36015M03 | - | 15 | 240 | 3 | 65 | 240 | 3 | 3 | 9.6 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300780 |  | MC | Telemecanique | LCxD32 | 5 | na | 240 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD1516 | 5 | na | 240 | 3
| D | ICB | Square D | GJL36030M04 | - | 30 | 240 | 3 | 65 | 240 | 3 | 5 | 15.2 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300790 |  | MC | Telemecanique | LCxD32 | 5 | na | 240 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD21 | 5 | na | 240 | 3
| D | ICB | Square D | GJL36030M04 | - | 30 | 240 | 3 | 65 | 240 | 3 | 5 | 15.2 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300800 |  | MC | Telemecanique | LCxD32 | 5 | na | 240 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD1521 | 5 | na | 240 | 3
| D | ICB | Square D | GJL36030M04 | - | 30 | 240 | 3 | 65 | 240 | 3 | 7.5 | 22 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300810 |  | MC | Telemecanique | LCxD32 | 5 | na | 240 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD22 | 5 | na | 240 | 3
| D | ICB | Square D | GJL36030M04 | - | 30 | 240 | 3 | 65 | 240 | 3 | 7.5 | 22 | 3.798 | 1 (3.80), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 6563 | 1728
SE300820 |  | MC | Telemecanique | LCxD32 | 5 | na | 240 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD1522 | 5 | na | 240 | 3
| D | ICB | Square D | GJL36050M05 | - | 50 | 240 | 3 | 65 | 240 | 3 | 10 | 28 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300830 |  | MC | Telemecanique | LCxD40 | 5 | na | 240 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD3353 | 5 | na | 240 | 3
| D | ICB | Square D | GJL36050M05 | - | 50 | 240 | 3 | 65 | 240 | 3 | 10 | 28 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300840 |  | MC | Telemecanique | LCxD40 | 5 | na | 240 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LR2D3553 | 5 | na | 240 | 3
| D | ICB | Square D | GJL36050M05 | - | 50 | 240 | 3 | 65 | 240 | 3 | 15 | 42 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300850 |  | MC | Telemecanique | LCxD50 | 5 | na | 240 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD3357 | 5 | na | 240 | 3
| D | ICB | Square D | GJL36050M05 | - | 50 | 240 | 3 | 65 | 240 | 3 | 15 | 42 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300860 |  | MC | Telemecanique | LCxD50 | 5 | na | 240 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LR2D3557 | 5 | na | 240 | 3
| D | ICB | Square D | FAL36100-18M | - | 100 | 240 | 3 | 22 | 240 | 3 | 20 | 54 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300870 |  | MC | Telemecanique | LCxD65 | 5 | na | 240 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD3359 | 5 | na | 240 | 3
| D | ICB | Square D | FAL36100-18M | - | 100 | 240 | 3 | 22 | 240 | 3 | 20 | 54 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300880 |  | MC | Telemecanique | LCxD65 | 5 | na | 240 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LR2D3559 | 5 | na | 240 | 3
| D | ICB | Square D | FAL36100-18M | - | 100 | 240 | 3 | 22 | 240 | 3 | 25 | 68 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300890 |  | MC | Telemecanique | LCxD80 | 5 | na | 240 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LRD3363 | 5 | na | 240 | 3
| D | ICB | Square D | FAL36100-18M | - | 100 | 240 | 3 | 22 | 240 | 3 | 25 | 68 | 4.5787 | 1 (4.58), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 7912 | 1728
SE300900 |  | MC | Telemecanique | LCxD80 | 5 | na | 240 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LR2D3563 | 5 | na | 240 | 3
| D | ICB | Square D | FAL36150-24M | - | 150 | 240 | 3 | 22 | 240 | 3 | 30 | 80 | 7.4653 | 1 (7.47), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 12900 | 1728
SE300920 |  | MC | Telemecanique | LCxD115 | 10 | na | 240 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LR9D5567 | 10 | na | 240 | 3
| D | ICB | Square D | KAL36250-30M | - | 250 | 240 | 3 | 42 | 240 | 3 | 50 | 130 | 7.4653 | 1 (7.47), 5 | E169932 Vol. 1 Sec. 6 |  |  |  | 12900 | 1728
SE300960 |  | MC | Telemecanique | LCxD150 | 10 | na | 240 | 3 | [12 empty] | 3.798
|  | OLR | Telemecanique | LR9D5569 | 10 | na | 240 | 3
| LCx | where x = | 1 or 2
Motor Controller cat. Nos. have a voltage code at the end