## C.O.A.
Conditions of Acceptability:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = Use wire ties evenly spaced apart to secure conductors in place.
(7) = See Table 7 for minimum internal wiring between load side of short circuit protective device & line side of starter.
(8) = "@" refer to digest to complete contactor Catalog number for coil voltage and Form modifications.
(9) = Insulator to be provided underneath starter. (QMFZ2), Fastex, Type Formex GK-30, 1/32 inch minimum thickness by 4 inches x 5.7 inches.
Table 7 - Minimum Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation)
Wire Code | Wire Size
7a | 12 AWG
7b | 8 AWG
7c | 2 AWG
7d | 1 AWG
7e | 250 MCM
7f | 300 MCM
7g | (2) 250 MCM
7h | 2/0 AWG
7i | 4/0 AWG
7j | (2) 4/0 AWG
7k | 10 AWG
7l | 6 AWG
7m | 4 AWG
7n | 3 AWG
7p | 1/0 AWG
7q | (2) 3/0 AWG
7r | (2) 2/0 AWG
7s | 3/0 AWG

## HD-TM
Issued: 2007-03-07
Last Revised: 2008-03-11
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE152723 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 7a | E40610 V12 S15
SE152723 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 7a | E40610 V12 S15
SE152723 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 25 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 7a | E40610 V12 S15
SE152724 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 7a | E40610 V12 S15
SE152724 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 7a | E40610 V12 S15
SE152724 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 25 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 7a | E40610 V12 S15
SE152725 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 7a | E40610 V12 S15
SE152725 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 7a | E40610 V12 S15
SE152725 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 25 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 7a | E40610 V12 S15
SE152726 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 7a | E40610 V12 S15
SE152726 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 7a | E40610 V12 S15
SE152726 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 25 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 7a | E40610 V12 S15
SE152727 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 7a | E40610 V12 S15
SE152727 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 7a | E40610 V12 S15
SE152727 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 25 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 7a | E40610 V12 S15
SE152728 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 7a | E40610 V12 S15
SE152728 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 7a | E40610 V12 S15
SE152728 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 25 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 7a | E40610 V12 S15
SE152729 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 7a | E40610 V12 S15
SE152729 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 18 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 7a | E40610 V12 S15
SE152729 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 18 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 7a | E40610 V12 S15
SE152730 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 0.75 | 1.3 | 2289 | 1, 7b | E40610 V12 S15
SE152730 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 0.75 | 1.3 | 2289 | 1, 7b | E40610 V12 S15
SE152730 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 14 | 600 | 3 | 0.75 | 1.3 | 2289 | 1, 7b | E40610 V12 S15
SE152731 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 200 | 3 | 1 | 4.8 | 1832 | 1, 7a | E40610 V12 S15
SE152731 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 200 | 3 | 1 | 4.8 | 1832 | 1, 7a | E40610 V12 S15
SE152731 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 25 | 200 | 3 | 1 | 4.8 | 1832 | 1, 7a | E40610 V12 S15
SE152732 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 208 | 3 | 1 | 4.6 | 1832 | 1, 7a | E40610 V12 S15
SE152732 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 208 | 3 | 1 | 4.6 | 1832 | 1, 7a | E40610 V12 S15
SE152732 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 25 | 208 | 3 | 1 | 4.6 | 1832 | 1, 7a | E40610 V12 S15
SE152733 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 240 | 3 | 1 | 4.2 | 1832 | 1, 7a | E40610 V12 S15
SE152733 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 240 | 3 | 1 | 4.2 | 1832 | 1, 7a | E40610 V12 S15
SE152733 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 25 | 240 | 3 | 1 | 4.2 | 1832 | 1, 7a | E40610 V12 S15
SE152734 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 1 | 2.1 | 1832 | 1, 7a | E40610 V12 S15
SE152734 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 18 | 480 | 3 | 1 | 2.1 | 1832 | 1, 7a | E40610 V12 S15
SE152734 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 18 | 480 | 3 | 1 | 2.1 | 1832 | 1, 7a | E40610 V12 S15
SE152735 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 1 | 1.7 | 2289 | 1, 7b | E40610 V12 S15
SE152735 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 1 | 1.7 | 2289 | 1, 7b | E40610 V12 S15
SE152735 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 14 | 600 | 3 | 1 | 1.7 | 2289 | 1, 7b | E40610 V12 S15
SE152736 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 7a | E40610 V12 S15
SE152736 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 7a | E40610 V12 S15
SE152736 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 25 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 7a | E40610 V12 S15
SE152737 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 7a | E40610 V12 S15
SE152737 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 7a | E40610 V12 S15
SE152737 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 25 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 7a | E40610 V12 S15
SE152738 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 240 | 3 | 1.5 | 6 | 1832 | 1, 7a | E40610 V12 S15
SE152738 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 240 | 3 | 1.5 | 6 | 1832 | 1, 7a | E40610 V12 S15
SE152738 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 25 | 240 | 3 | 1.5 | 6 | 1832 | 1, 7a | E40610 V12 S15
SE152739 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 1.5 | 3 | 1832 | 1, 7a | E40610 V12 S15
SE152739 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 18 | 480 | 3 | 1.5 | 3 | 1832 | 1, 7a | E40610 V12 S15
SE152739 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 18 | 480 | 3 | 1.5 | 3 | 1832 | 1, 7a | E40610 V12 S15
SE152740 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 7b | E40610 V12 S15
SE152740 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 7b | E40610 V12 S15
SE152740 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 14 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 7b | E40610 V12 S15
SE152741 | C | CB | Square D | HDL36020 | 25 | 20 | 600 | 3 | 25 | 200 | 3 | 2 | 7.82 | 1832 | 1, 7a | E40610 V12 S15
SE152741 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 200 | 3 | 2 | 7.82 | 1832 | 1, 7a | E40610 V12 S15
SE152741 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 25 | 200 | 3 | 2 | 7.82 | 1832 | 1, 7a | E40610 V12 S15
SE152742 | C | CB | Square D | HDL36020 | 25 | 20 | 600 | 3 | 25 | 208 | 3 | 2 | 7.5 | 1832 | 1, 7a | E40610 V12 S15
SE152742 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 208 | 3 | 2 | 7.5 | 1832 | 1, 7a | E40610 V12 S15
SE152742 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 25 | 208 | 3 | 2 | 7.5 | 1832 | 1, 7a | E40610 V12 S15
SE152743 | C | CB | Square D | HDL36020 | 25 | 20 | 600 | 3 | 25 | 240 | 3 | 2 | 6.8 | 1832 | 1, 7a | E40610 V12 S15
SE152743 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 240 | 3 | 2 | 6.8 | 1832 | 1, 7a | E40610 V12 S15
SE152743 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 25 | 240 | 3 | 2 | 6.8 | 1832 | 1, 7a | E40610 V12 S15
SE152744 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 2 | 3.4 | 1832 | 1, 7a | E40610 V12 S15
SE152744 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 18 | 480 | 3 | 2 | 3.4 | 1832 | 1, 7a | E40610 V12 S15
SE152744 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 18 | 480 | 3 | 2 | 3.4 | 1832 | 1, 7a | E40610 V12 S15
SE152745 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 2 | 2.7 | 2289 | 1, 7b | E40610 V12 S15
SE152745 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 2 | 2.7 | 2289 | 1, 7b | E40610 V12 S15
SE152745 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 14 | 600 | 3 | 2 | 2.7 | 2289 | 1, 7b | E40610 V12 S15
SE152746 | C | CB | Square D | HDL36030 | 25 | 30 | 600 | 3 | 25 | 200 | 3 | 3 | 11 | 1832 | 1, 7a | E40610 V12 S15
SE152746 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 200 | 3 | 3 | 11 | 1832 | 1, 7a | E40610 V12 S15
SE152746 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 25 | 200 | 3 | 3 | 11 | 1832 | 1, 7a | E40610 V12 S15
SE152747 | C | CB | Square D | HDL36030 | 25 | 30 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a | E40610 V12 S15
SE152747 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a | E40610 V12 S15
SE152747 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a | E40610 V12 S15
SE152748 | C | CB | Square D | HDL36025 | 25 | 25 | 600 | 3 | 25 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a | E40610 V12 S15
SE152748 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a | E40610 V12 S15
SE152748 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 25 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a | E40610 V12 S15
SE152749 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 3 | 4.8 | 1832 | 1, 7a | E40610 V12 S15
SE152749 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 18 | 480 | 3 | 3 | 4.8 | 1832 | 1, 7a | E40610 V12 S15
SE152749 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 18 | 480 | 3 | 3 | 4.8 | 1832 | 1, 7a | E40610 V12 S15
SE152750 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 3 | 3.9 | 2289 | 1, 7b | E40610 V12 S15
SE152750 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 3 | 3.9 | 2289 | 1, 7b | E40610 V12 S15
SE152750 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 14 | 600 | 3 | 3 | 3.9 | 2289 | 1, 7b | E40610 V12 S15
SE152751 | C | CB | Square D | HDL36050 | 25 | 50 | 600 | 3 | 25 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a | E40610 V12 S15
SE152751 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a | E40610 V12 S15
SE152751 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 25 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a | E40610 V12 S15
SE152752 | C | CB | Square D | HDL36050 | 25 | 50 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a | E40610 V12 S15
SE152752 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a | E40610 V12 S15
SE152752 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a | E40610 V12 S15
SE152753 | C | CB | Square D | HDL36040 | 25 | 40 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a | E40610 V12 S15
SE152753 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a | E40610 V12 S15
SE152753 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a | E40610 V12 S15
SE152754 | C | CB | Square D | HDL36020 | 18 | 20 | 600 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1, 7a | E40610 V12 S15
SE152754 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1, 7a | E40610 V12 S15
SE152754 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1, 7a | E40610 V12 S15
SE152755 | C | CB | Square D | HDL36020 | 14 | 20 | 600 | 3 | 14 | 600 | 3 | 5 | 6.1 | 2289 | 1, 7b | E40610 V12 S15
SE152755 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 5 | 6.1 | 2289 | 1, 7b | E40610 V12 S15
SE152755 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 14 | 600 | 3 | 5 | 6.1 | 2289 | 1, 7b | E40610 V12 S15
SE152756 | C | CB | Square D | HDL36070 | 25 | 70 | 600 | 3 | 25 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 7k | E40610 V12 S15
SE152756 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 25 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 7k | E40610 V12 S15
SE152756 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 25 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 7k | E40610 V12 S15
SE152757 | C | CB | Square D | HDL36070 | 25 | 70 | 600 | 3 | 25 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 7k | E40610 V12 S15
SE152757 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 25 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 7k | E40610 V12 S15
SE152757 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 25 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 7k | E40610 V12 S15
SE152758 | C | CB | Square D | HDL36060 | 25 | 60 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a | E40610 V12 S15
SE152758 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a | E40610 V12 S15
SE152758 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a | E40610 V12 S15
SE152759 | C | CB | Square D | HDL36030 | 18 | 30 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a | E40610 V12 S15
SE152759 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a | E40610 V12 S15
SE152759 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a | E40610 V12 S15
SE152760 | C | CB | Square D | HDL36025 | 14 | 25 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 2289 | 1, 7b | E40610 V12 S15
SE152760 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 2289 | 1, 7b | E40610 V12 S15
SE152760 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 2289 | 1, 7b | E40610 V12 S15
SE152761 | C | CB | Square D | HDL36090 | 25 | 90 | 600 | 3 | 25 | 200 | 3 | 10 | 32.2 | 2289 | 1, 7b | E40610 V12 S15
SE152761 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 200 | 3 | 10 | 32.2 | 2289 | 1, 7b | E40610 V12 S15
SE152761 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 25 | 200 | 3 | 10 | 32.2 | 2289 | 1, 7b | E40610 V12 S15
SE152762 | C | CB | Square D | HDL36090 | 25 | 90 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 2289 | 1, 7b | E40610 V12 S15
SE152762 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 2289 | 1, 7b | E40610 V12 S15
SE152762 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 2289 | 1, 7b | E40610 V12 S15
SE152763 | C | CB | Square D | HDL36070 | 25 | 70 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 1832 | 1, 7k | E40610 V12 S15
SE152763 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 1832 | 1, 7k | E40610 V12 S15
SE152763 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 1832 | 1, 7k | E40610 V12 S15
SE152764 | C | CB | Square D | HDL36040 | 18 | 40 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 7a | E40610 V12 S15
SE152764 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 7a | E40610 V12 S15
SE152764 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 7a | E40610 V12 S15
SE152765 | C | CB | Square D | HDL36030 | 14 | 30 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 2289 | 1, 7b | E40610 V12 S15
SE152765 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 2289 | 1, 7b | E40610 V12 S15
SE152765 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 2289 | 1, 7b | E40610 V12 S15
SE152766 | C | CB | Square D | HDL36125 | 25 | 125 | 600 | 3 | 25 | 200 | 3 | 15 | 48.3 | 2289 | 1, 7l | E40610 V12 S15
SE152766 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 25 | 200 | 3 | 15 | 48.3 | 2289 | 1, 7l | E40610 V12 S15
SE152766 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 25 | 200 | 3 | 15 | 48.3 | 2289 | 1, 7l | E40610 V12 S15
SE152767 | C | CB | Square D | HDL36125 | 25 | 125 | 600 | 3 | 25 | 208 | 3 | 15 | 46.2 | 2289 | 1, 7l | E40610 V12 S15
SE152767 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 25 | 208 | 3 | 15 | 46.2 | 2289 | 1, 7l | E40610 V12 S15
SE152767 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 25 | 208 | 3 | 15 | 46.2 | 2289 | 1, 7l | E40610 V12 S15
SE152768 | C | CB | Square D | HDL36110 | 25 | 110 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 2289 | 1, 7b | E40610 V12 S15
SE152768 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 2289 | 1, 7b | E40610 V12 S15
SE152768 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 2289 | 1, 7b | E40610 V12 S15
SE152769 | C | CB | Square D | HDL36060 | 18 | 60 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 7a | E40610 V12 S15
SE152769 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 7a | E40610 V12 S15
SE152769 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 7a | E40610 V12 S15
SE152770 | C | CB | Square D | HDL36045 | 14 | 45 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 2289 | 1, 7b | E40610 V12 S15
SE152770 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 2289 | 1, 7b | E40610 V12 S15
SE152770 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 2289 | 1, 7b | E40610 V12 S15
SE152771 | C | CB | Square D | HDL36150 | 25 | 150 | 600 | 3 | 25 | 200 | 3 | 20 | 62.1 | 2289 | 1, 7l | E40610 V12 S15
SE152771 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 25 | 200 | 3 | 20 | 62.1 | 2289 | 1, 7l | E40610 V12 S15
SE152771 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 25 | 200 | 3 | 20 | 62.1 | 2289 | 1, 7l | E40610 V12 S15
SE152772 | C | CB | Square D | HDL36150 | 25 | 150 | 600 | 3 | 25 | 208 | 3 | 20 | 59.4 | 2289 | 1, 7l | E40610 V12 S15
SE152772 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 25 | 208 | 3 | 20 | 59.4 | 2289 | 1, 7l | E40610 V12 S15
SE152772 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 25 | 208 | 3 | 20 | 59.4 | 2289 | 1, 7l | E40610 V12 S15
SE152773 | C | CB | Square D | HDL36150 | 25 | 150 | 600 | 3 | 25 | 240 | 3 | 20 | 54 | 2289 | 1, 7l | E40610 V12 S15
SE152773 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 25 | 240 | 3 | 20 | 54 | 2289 | 1, 7l | E40610 V12 S15
SE152773 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 25 | 240 | 3 | 20 | 54 | 2289 | 1, 7l | E40610 V12 S15
SE152774 | C | CB | Square D | HDL36070 | 18 | 70 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 7k | E40610 V12 S15
SE152774 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 7k | E40610 V12 S15
SE152774 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 7k | E40610 V12 S15
SE152775 | C | CB | Square D | HDL36060 | 14 | 60 | 600 | 3 | 14 | 600 | 3 | 20 | 22 | 2289 | 1, 7b | E40610 V12 S15
SE152775 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 20 | 22 | 2289 | 1, 7b | E40610 V12 S15
SE152775 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 14 | 600 | 3 | 20 | 22 | 2289 | 1, 7b | E40610 V12 S15
SE152776 | C | CB | Square D | HDL36150 | 25 | 150 | 600 | 3 | 25 | 240 | 3 | 25 | 68 | 2289 | 1, 7l | E40610 V12 S15
SE152776 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 25 | 240 | 3 | 25 | 68 | 2289 | 1, 7l | E40610 V12 S15
SE152776 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 25 | 240 | 3 | 25 | 68 | 2289 | 1, 7l | E40610 V12 S15
SE152777 | C | CB | Square D | HDL36090 | 18 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2289 | 1, 7b | E40610 V12 S15
SE152777 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2289 | 1, 7b | E40610 V12 S15
SE152777 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2289 | 1, 7b | E40610 V12 S15
SE152778 | C | CB | Square D | HDL36070 | 14 | 70 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 2289 | 1, 7b | E40610 V12 S15
SE152778 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 2289 | 1, 7b | E40610 V12 S15
SE152778 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 2289 | 1, 7b | E40610 V12 S15
SE152779 | C | CB | Square D | HDL36100 | 18 | 100 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2289 | 1, 7b | E40610 V12 S15
SE152779 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2289 | 1, 7b | E40610 V12 S15
SE152779 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2289 | 1, 7b | E40610 V12 S15
SE152780 | C | CB | Square D | HDL36080 | 14 | 80 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2289 | 1, 7b | E40610 V12 S15
SE152780 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2289 | 1, 7b | E40610 V12 S15
SE152780 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2289 | 1, 7b | E40610 V12 S15
SE152781 | C | CB | Square D | HDL36150 | 18 | 150 | 600 | 3 | 18 | 480 | 3 | 40 | 52 | 2289 | 1, 7l | E40610 V12 S15
SE152781 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 18 | 480 | 3 | 40 | 52 | 2289 | 1, 7l | E40610 V12 S15
SE152781 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 18 | 480 | 3 | 40 | 52 | 2289 | 1, 7l | E40610 V12 S15
SE152782 | C | CB | Square D | HDL36110 | 14 | 110 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2289 | 1, 7b | E40610 V12 S15
SE152782 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2289 | 1, 7b | E40610 V12 S15
SE152782 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2289 | 1, 7b | E40610 V12 S15
SE152783 | C | CB | Square D | HDL36150 | 18 | 150 | 600 | 3 | 18 | 480 | 3 | 50 | 65 | 2289 | 1, 7l | E40610 V12 S15
SE152783 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 18 | 480 | 3 | 50 | 65 | 2289 | 1, 7l | E40610 V12 S15
SE152783 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 18 | 480 | 3 | 50 | 65 | 2289 | 1, 7l | E40610 V12 S15
SE152784 | C | CB | Square D | HDL36150 | 14 | 150 | 600 | 3 | 14 | 600 | 3 | 50 | 52 | 2289 | 1, 7l | E40610 V12 S15
SE152784 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 14 | 600 | 3 | 50 | 52 | 2289 | 1, 7l | E40610 V12 S15
SE152784 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 14 | 600 | 3 | 50 | 52 | 2289 | 1, 7l | E40610 V12 S15
SE152785 | C | CB | Square D | HDL36175 | 14 | 175 | 600 | 3 | 14 | 600 | 3 | 60 | 62 | 2289 | 1, 7l | E40610 V12 S15
SE152785 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 14 | 600 | 3 | 60 | 62 | 2289 | 1, 7l | E40610 V12 S15
SE152785 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 14 | 600 | 3 | 60 | 62 | 2289 | 1, 7l | E40610 V12 S15
SE152786 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 7a | E40610 V12 S16
SE152786 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 25 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 7a | E40610 V12 S16
SE152786 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 25 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 7a | E40610 V12 S16
SE152787 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 7a | E40610 V12 S16
SE152787 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 25 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 7a | E40610 V12 S16
SE152787 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 25 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 7a | E40610 V12 S16
SE152788 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 7a | E40610 V12 S16
SE152788 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 25 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 7a | E40610 V12 S16
SE152788 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 25 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 7a | E40610 V12 S16
SE152789 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 7a | E40610 V12 S16
SE152789 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 25 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 7a | E40610 V12 S16
SE152789 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 25 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 7a | E40610 V12 S16
SE152790 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 7a | E40610 V12 S16
SE152790 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 25 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 7a | E40610 V12 S16
SE152790 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 25 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 7a | E40610 V12 S16
SE152791 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 7a | E40610 V12 S16
SE152791 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 25 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 7a | E40610 V12 S16
SE152791 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 25 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 7a | E40610 V12 S16
SE152792 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 7a | E40610 V12 S16
SE152792 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 18 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 7a | E40610 V12 S16
SE152792 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 18 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 7a | E40610 V12 S16
SE152793 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 0.75 | 1.3 | 2289 | 1, 7b | E40610 V12 S16
SE152793 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 0.75 | 1.3 | 2289 | 1, 7b | E40610 V12 S16
SE152793 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 14 | 600 | 3 | 0.75 | 1.3 | 2289 | 1, 7b | E40610 V12 S16
SE152794 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 200 | 3 | 1 | 4.8 | 1832 | 1, 7a | E40610 V12 S16
SE152794 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 25 | 200 | 3 | 1 | 4.8 | 1832 | 1, 7a | E40610 V12 S16
SE152794 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 25 | 200 | 3 | 1 | 4.8 | 1832 | 1, 7a | E40610 V12 S16
SE152795 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 208 | 3 | 1 | 4.6 | 1832 | 1, 7a | E40610 V12 S16
SE152795 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 25 | 208 | 3 | 1 | 4.6 | 1832 | 1, 7a | E40610 V12 S16
SE152795 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 25 | 208 | 3 | 1 | 4.6 | 1832 | 1, 7a | E40610 V12 S16
SE152796 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 240 | 3 | 1 | 4.2 | 1832 | 1, 7a | E40610 V12 S16
SE152796 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 25 | 240 | 3 | 1 | 4.2 | 1832 | 1, 7a | E40610 V12 S16
SE152796 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 25 | 240 | 3 | 1 | 4.2 | 1832 | 1, 7a | E40610 V12 S16
SE152797 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 1 | 2.1 | 1832 | 1, 7a | E40610 V12 S16
SE152797 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 18 | 480 | 3 | 1 | 2.1 | 1832 | 1, 7a | E40610 V12 S16
SE152797 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 18 | 480 | 3 | 1 | 2.1 | 1832 | 1, 7a | E40610 V12 S16
SE152798 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 1 | 1.7 | 2289 | 1, 7b | E40610 V12 S16
SE152798 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 1 | 1.7 | 2289 | 1, 7b | E40610 V12 S16
SE152798 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 14 | 600 | 3 | 1 | 1.7 | 2289 | 1, 7b | E40610 V12 S16
SE152799 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 7a | E40610 V12 S16
SE152799 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 25 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 7a | E40610 V12 S16
SE152799 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 25 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 7a | E40610 V12 S16
SE152800 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 7a | E40610 V12 S16
SE152800 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 25 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 7a | E40610 V12 S16
SE152800 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 25 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 7a | E40610 V12 S16
SE152801 | C | CB | Square D | HDL36015 | 25 | 15 | 600 | 3 | 25 | 240 | 3 | 1.5 | 6 | 1832 | 1, 7a | E40610 V12 S16
SE152801 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 25 | 240 | 3 | 1.5 | 6 | 1832 | 1, 7a | E40610 V12 S16
SE152801 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 25 | 240 | 3 | 1.5 | 6 | 1832 | 1, 7a | E40610 V12 S16
SE152802 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 1.5 | 3 | 1832 | 1, 7a | E40610 V12 S16
SE152802 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 18 | 480 | 3 | 1.5 | 3 | 1832 | 1, 7a | E40610 V12 S16
SE152802 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 18 | 480 | 3 | 1.5 | 3 | 1832 | 1, 7a | E40610 V12 S16
SE152803 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 7b | E40610 V12 S16
SE152803 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 7b | E40610 V12 S16
SE152803 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 14 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 7b | E40610 V12 S16
SE152804 | C | CB | Square D | HDL36020 | 25 | 20 | 600 | 3 | 25 | 200 | 3 | 2 | 7.82 | 1832 | 1, 7a | E40610 V12 S16
SE152804 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 25 | 200 | 3 | 2 | 7.82 | 1832 | 1, 7a | E40610 V12 S16
SE152804 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 25 | 200 | 3 | 2 | 7.82 | 1832 | 1, 7a | E40610 V12 S16
SE152805 | C | CB | Square D | HDL36020 | 25 | 20 | 600 | 3 | 25 | 208 | 3 | 2 | 7.5 | 1832 | 1, 7a | E40610 V12 S16
SE152805 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 25 | 208 | 3 | 2 | 7.5 | 1832 | 1, 7a | E40610 V12 S16
SE152805 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 25 | 208 | 3 | 2 | 7.5 | 1832 | 1, 7a | E40610 V12 S16
SE152806 | C | CB | Square D | HDL36020 | 25 | 20 | 600 | 3 | 25 | 240 | 3 | 2 | 6.8 | 1832 | 1, 7a | E40610 V12 S16
SE152806 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 25 | 240 | 3 | 2 | 6.8 | 1832 | 1, 7a | E40610 V12 S16
SE152806 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 25 | 240 | 3 | 2 | 6.8 | 1832 | 1, 7a | E40610 V12 S16
SE152807 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 2 | 3.4 | 1832 | 1, 7a | E40610 V12 S16
SE152807 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 18 | 480 | 3 | 2 | 3.4 | 1832 | 1, 7a | E40610 V12 S16
SE152807 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 18 | 480 | 3 | 2 | 3.4 | 1832 | 1, 7a | E40610 V12 S16
SE152808 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 2 | 2.7 | 2289 | 1, 7b | E40610 V12 S16
SE152808 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 2 | 2.7 | 2289 | 1, 7b | E40610 V12 S16
SE152808 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 14 | 600 | 3 | 2 | 2.7 | 2289 | 1, 7b | E40610 V12 S16
SE152809 | C | CB | Square D | HDL36030 | 25 | 30 | 600 | 3 | 25 | 200 | 3 | 3 | 11 | 1832 | 1, 7a | E40610 V12 S16
SE152809 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 25 | 200 | 3 | 3 | 11 | 1832 | 1, 7a | E40610 V12 S16
SE152809 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 25 | 200 | 3 | 3 | 11 | 1832 | 1, 7a | E40610 V12 S16
SE152810 | C | CB | Square D | HDL36030 | 25 | 30 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a | E40610 V12 S16
SE152810 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a | E40610 V12 S16
SE152810 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 25 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a | E40610 V12 S16
SE152811 | C | CB | Square D | HDL36025 | 25 | 25 | 600 | 3 | 25 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a | E40610 V12 S16
SE152811 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 25 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a | E40610 V12 S16
SE152811 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 25 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a | E40610 V12 S16
SE152812 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 3 | 4.8 | 1832 | 1, 7a | E40610 V12 S16
SE152812 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 18 | 480 | 3 | 3 | 4.8 | 1832 | 1, 7a | E40610 V12 S16
SE152812 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 18 | 480 | 3 | 3 | 4.8 | 1832 | 1, 7a | E40610 V12 S16
SE152813 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 3 | 3.9 | 2289 | 1, 7b | E40610 V12 S16
SE152813 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 3 | 3.9 | 2289 | 1, 7b | E40610 V12 S16
SE152813 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 14 | 600 | 3 | 3 | 3.9 | 2289 | 1, 7b | E40610 V12 S16
SE152814 | C | CB | Square D | HDL36050 | 25 | 50 | 600 | 3 | 25 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a | E40610 V12 S16
SE152814 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 25 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a | E40610 V12 S16
SE152814 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 25 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a | E40610 V12 S16
SE152815 | C | CB | Square D | HDL36050 | 25 | 50 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a | E40610 V12 S16
SE152815 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a | E40610 V12 S16
SE152815 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 25 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a | E40610 V12 S16
SE152816 | C | CB | Square D | HDL36040 | 25 | 40 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a | E40610 V12 S16
SE152816 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a | E40610 V12 S16
SE152816 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 25 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a | E40610 V12 S16
SE152817 | C | CB | Square D | HDL36020 | 18 | 20 | 600 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1, 7a | E40610 V12 S16
SE152817 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1, 7a | E40610 V12 S16
SE152817 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 18 | 480 | 3 | 5 | 7.6 | 1832 | 1, 7a | E40610 V12 S16
SE152818 | C | CB | Square D | HDL36020 | 14 | 20 | 600 | 3 | 14 | 600 | 3 | 5 | 6.1 | 2289 | 1, 7b | E40610 V12 S16
SE152818 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 5 | 6.1 | 2289 | 1, 7b | E40610 V12 S16
SE152818 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 14 | 600 | 3 | 5 | 6.1 | 2289 | 1, 7b | E40610 V12 S16
SE152819 | C | CB | Square D | HDL36070 | 25 | 70 | 600 | 3 | 25 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 7k | E40610 V12 S16
SE152819 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 25 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 7k | E40610 V12 S16
SE152819 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 25 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 7k | E40610 V12 S16
SE152820 | C | CB | Square D | HDL36070 | 25 | 70 | 600 | 3 | 25 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 7k | E40610 V12 S16
SE152820 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 25 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 7k | E40610 V12 S16
SE152820 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 25 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 7k | E40610 V12 S16
SE152821 | C | CB | Square D | HDL36060 | 25 | 60 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a | E40610 V12 S16
SE152821 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a | E40610 V12 S16
SE152821 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 25 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a | E40610 V12 S16
SE152822 | C | CB | Square D | HDL36030 | 18 | 30 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a | E40610 V12 S16
SE152822 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a | E40610 V12 S16
SE152822 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 18 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a | E40610 V12 S16
SE152823 | C | CB | Square D | HDL36025 | 14 | 25 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 2289 | 1, 7b | E40610 V12 S16
SE152823 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 2289 | 1, 7b | E40610 V12 S16
SE152823 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 14 | 600 | 3 | 7.5 | 9 | 2289 | 1, 7b | E40610 V12 S16
SE152824 | C | CB | Square D | HDL36090 | 25 | 90 | 600 | 3 | 25 | 200 | 3 | 10 | 32.2 | 2289 | 1, 7b | E40610 V12 S16
SE152824 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 25 | 200 | 3 | 10 | 32.2 | 2289 | 1, 7b | E40610 V12 S16
SE152824 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 25 | 200 | 3 | 10 | 32.2 | 2289 | 1, 7b | E40610 V12 S16
SE152825 | C | CB | Square D | HDL36090 | 25 | 90 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 2289 | 1, 7b | E40610 V12 S16
SE152825 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 2289 | 1, 7b | E40610 V12 S16
SE152825 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 25 | 208 | 3 | 10 | 30.8 | 2289 | 1, 7b | E40610 V12 S16
SE152826 | C | CB | Square D | HDL36070 | 25 | 70 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 1832 | 1, 7k | E40610 V12 S16
SE152826 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 1832 | 1, 7k | E40610 V12 S16
SE152826 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 25 | 240 | 3 | 10 | 28 | 1832 | 1, 7k | E40610 V12 S16
SE152827 | C | CB | Square D | HDL36040 | 18 | 40 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 7a | E40610 V12 S16
SE152827 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 7a | E40610 V12 S16
SE152827 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 18 | 480 | 3 | 10 | 14 | 1832 | 1, 7a | E40610 V12 S16
SE152828 | C | CB | Square D | HDL36030 | 14 | 30 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 2289 | 1, 7b | E40610 V12 S16
SE152828 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 2289 | 1, 7b | E40610 V12 S16
SE152828 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 14 | 600 | 3 | 10 | 11 | 2289 | 1, 7b | E40610 V12 S16
SE152829 | C | CB | Square D | HDL36125 | 25 | 125 | 600 | 3 | 25 | 200 | 3 | 15 | 48.3 | 2289 | 1, 7l | E40610 V12 S16
SE152829 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 25 | 200 | 3 | 15 | 48.3 | 2289 | 1, 7l | E40610 V12 S16
SE152829 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 25 | 200 | 3 | 15 | 48.3 | 2289 | 1, 7l | E40610 V12 S16
SE152830 | C | CB | Square D | HDL36125 | 25 | 125 | 600 | 3 | 25 | 208 | 3 | 15 | 46.2 | 2289 | 1, 7l | E40610 V12 S16
SE152830 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 25 | 208 | 3 | 15 | 46.2 | 2289 | 1, 7l | E40610 V12 S16
SE152830 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 25 | 208 | 3 | 15 | 46.2 | 2289 | 1, 7l | E40610 V12 S16
SE152831 | C | CB | Square D | HDL36110 | 25 | 110 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 2289 | 1, 7b | E40610 V12 S16
SE152831 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 2289 | 1, 7b | E40610 V12 S16
SE152831 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 25 | 240 | 3 | 15 | 42 | 2289 | 1, 7b | E40610 V12 S16
SE152832 | C | CB | Square D | HDL36060 | 18 | 60 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 7a | E40610 V12 S16
SE152832 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 7a | E40610 V12 S16
SE152832 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 18 | 480 | 3 | 15 | 21 | 1832 | 1, 7a | E40610 V12 S16
SE152833 | C | CB | Square D | HDL36045 | 14 | 45 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 2289 | 1, 7b | E40610 V12 S16
SE152833 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 2289 | 1, 7b | E40610 V12 S16
SE152833 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 14 | 600 | 3 | 15 | 17 | 2289 | 1, 7b | E40610 V12 S16
SE152834 | C | CB | Square D | HDL36150 | 25 | 150 | 600 | 3 | 25 | 200 | 3 | 20 | 62.1 | 3663 | 1, 7l | E40610 V12 S16
SE152834 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 25 | 200 | 3 | 20 | 62.1 | 3663 | 1, 7l | E40610 V12 S16
SE152834 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 25 | 200 | 3 | 20 | 62.1 | 3663 | 1, 7l | E40610 V12 S16
SE152835 | C | CB | Square D | HDL36150 | 25 | 150 | 600 | 3 | 25 | 208 | 3 | 20 | 59.4 | 3663 | 1, 7l | E40610 V12 S16
SE152835 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 25 | 208 | 3 | 20 | 59.4 | 3663 | 1, 7l | E40610 V12 S16
SE152835 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 25 | 208 | 3 | 20 | 59.4 | 3663 | 1, 7l | E40610 V12 S16
SE152836 | C | CB | Square D | HDL36150 | 25 | 150 | 600 | 3 | 25 | 240 | 3 | 20 | 54 | 2289 | 1, 7l | E40610 V12 S16
SE152836 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 25 | 240 | 3 | 20 | 54 | 2289 | 1, 7l | E40610 V12 S16
SE152836 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 25 | 240 | 3 | 20 | 54 | 2289 | 1, 7l | E40610 V12 S16
SE152837 | C | CB | Square D | HDL36070 | 18 | 70 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 7k | E40610 V12 S16
SE152837 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 7k | E40610 V12 S16
SE152837 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 18 | 480 | 3 | 20 | 27 | 1832 | 1, 7k | E40610 V12 S16
SE152838 | C | CB | Square D | HDL36060 | 14 | 60 | 600 | 3 | 14 | 600 | 3 | 20 | 22 | 2289 | 1, 7b | E40610 V12 S16
SE152838 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 20 | 22 | 2289 | 1, 7b | E40610 V12 S16
SE152838 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 14 | 600 | 3 | 20 | 22 | 2289 | 1, 7b | E40610 V12 S16
SE152839 | C | CB | Square D | HDL36150 | 25 | 150 | 600 | 3 | 25 | 240 | 3 | 25 | 68 | 3663 | 1, 7l | E40610 V12 S16
SE152839 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 25 | 240 | 3 | 25 | 68 | 3663 | 1, 7l | E40610 V12 S16
SE152839 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 25 | 240 | 3 | 25 | 68 | 3663 | 1, 7l | E40610 V12 S16
SE152840 | C | CB | Square D | HDL36090 | 18 | 90 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2289 | 1, 7l | E40610 V12 S16
SE152840 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2289 | 1, 7l | E40610 V12 S16
SE152840 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 18 | 480 | 3 | 25 | 34 | 2289 | 1, 7l | E40610 V12 S16
SE152841 | C | CB | Square D | HDL36070 | 14 | 70 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 2289 | 1, 7l | E40610 V12 S16
SE152841 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 2289 | 1, 7l | E40610 V12 S16
SE152841 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 14 | 600 | 3 | 25 | 27 | 2289 | 1, 7l | E40610 V12 S16
SE152842 | C | CB | Square D | HDL36100 | 18 | 100 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2289 | 1, 7b | E40610 V12 S16
SE152842 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2289 | 1, 7b | E40610 V12 S16
SE152842 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 18 | 480 | 3 | 30 | 40 | 2289 | 1, 7b | E40610 V12 S16
SE152843 | C | CB | Square D | HDL36080 | 14 | 80 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2289 | 1, 7b | E40610 V12 S16
SE152843 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2289 | 1, 7b | E40610 V12 S16
SE152843 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 14 | 600 | 3 | 30 | 32 | 2289 | 1, 7b | E40610 V12 S16
SE152844 | C | CB | Square D | HDL36150 | 18 | 150 | 600 | 3 | 18 | 480 | 3 | 40 | 52 | 2289 | 1, 7l | E40610 V12 S16
SE152844 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 18 | 480 | 3 | 40 | 52 | 2289 | 1, 7b | E40610 V12 S16
SE152844 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 18 | 480 | 3 | 40 | 52 | 2289 | 1, 7b | E40610 V12 S16
SE152845 | C | CB | Square D | HDL36110 | 14 | 110 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2289 | 1, 7b | E40610 V12 S16
SE152845 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2289 | 1, 7b | E40610 V12 S16
SE152845 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 14 | 600 | 3 | 40 | 41 | 2289 | 1, 7b | E40610 V12 S16
SE152846 | C | CB | Square D | HDL36150 | 18 | 150 | 600 | 3 | 18 | 480 | 3 | 50 | 65 | 3663 | 1, 7l | E40610 V12 S16
SE152846 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 18 | 480 | 3 | 50 | 65 | 3663 | 1, 7b | E40610 V12 S16
SE152846 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 18 | 480 | 3 | 50 | 65 | 3663 | 1, 7b | E40610 V12 S16
SE152847 | C | CB | Square D | HDL36150 | 14 | 150 | 600 | 3 | 14 | 600 | 3 | 50 | 52 | 2289 | 1, 7l | E40610 V12 S16
SE152847 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 14 | 600 | 3 | 50 | 52 | 2289 | 1, 7b | E40610 V12 S16
SE152847 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 14 | 600 | 3 | 50 | 52 | 2289 | 1, 7b | E40610 V12 S16
SE152848 | C | CB | Square D | HDL36175 | 14 | 175 | 600 | 3 | 14 | 600 | 3 | 60 | 62 | 3663 | 1, 7l | E40610 V12 S16
SE152848 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 14 | 600 | 3 | 60 | 62 | 3663 | 1, 7b | E40610 V12 S16
SE152848 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 14 | 600 | 3 | 60 | 62 | 3663 | 1, 7b | E40610 V12 S16
SE154000 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 7a | E40610 V12 S15
SE154000 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 18 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 7a | E40610 V12 S15
SE154000 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 18 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 7a | E40610 V12 S15
SE154001 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 0.5 | 0.9 | 2289 | 1, 7b | E40610 V12 S15
SE154001 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 0.5 | 0.9 | 2289 | 1, 7b | E40610 V12 S15
SE154001 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 14 | 600 | 3 | 0.5 | 0.9 | 2289 | 1, 7b | E40610 V12 S15
SE154002 | C | CB | Square D | HDL36015 | 18 | 15 | 600 | 3 | 18 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 7a | E40610 V12 S16
SE154002 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 18 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 7a | E40610 V12 S16
SE154002 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 18 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 7a | E40610 V12 S16
SE154003 | C | CB | Square D | HDL36015 | 14 | 15 | 600 | 3 | 14 | 600 | 3 | 0.5 | 0.9 | 2289 | 1, 7b | E40610 V12 S16
SE154003 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 14 | 600 | 3 | 0.5 | 0.9 | 2289 | 1, 7b | E40610 V12 S16
SE154003 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 14 | 600 | 3 | 0.5 | 0.9 | 2289 | 1, 7b | E40610 V12 S16

## HG-TM
Issued: 2007-03-07
Last Revised: 2008-03-11
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE152897 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 7a | E40610 V12 S15
SE152897 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 7a | E40610 V12 S15
SE152897 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 65 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 7a | E40610 V12 S15
SE152898 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 7a | E40610 V12 S15
SE152898 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 7a | E40610 V12 S15
SE152898 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 65 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 7a | E40610 V12 S15
SE152899 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 7a | E40610 V12 S15
SE152899 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 7a | E40610 V12 S15
SE152899 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 65 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 7a | E40610 V12 S15
SE152900 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 7a | E40610 V12 S15
SE152900 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 7a | E40610 V12 S15
SE152900 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 65 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 7a | E40610 V12 S15
SE152901 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 7a | E40610 V12 S15
SE152901 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 7a | E40610 V12 S15
SE152901 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 65 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 7a | E40610 V12 S15
SE152902 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 7a | E40610 V12 S15
SE152902 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 7a | E40610 V12 S15
SE152902 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 65 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 7a | E40610 V12 S15
SE152903 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 7a | E40610 V12 S15
SE152903 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 35 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 7a | E40610 V12 S15
SE152903 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 35 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 7a | E40610 V12 S15
SE152904 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 0.75 | 1.3 | 2289 | 1, 7b | E40610 V12 S15
SE152904 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 0.75 | 1.3 | 2289 | 1, 7b | E40610 V12 S15
SE152904 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 18 | 600 | 3 | 0.75 | 1.3 | 2289 | 1, 7b | E40610 V12 S15
SE152905 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 1 | 4.8 | 1832 | 1, 7a | E40610 V12 S15
SE152905 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 200 | 3 | 1 | 4.8 | 1832 | 1, 7a | E40610 V12 S15
SE152905 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 65 | 200 | 3 | 1 | 4.8 | 1832 | 1, 7a | E40610 V12 S15
SE152906 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 1 | 4.6 | 1832 | 1, 7a | E40610 V12 S15
SE152906 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 208 | 3 | 1 | 4.6 | 1832 | 1, 7a | E40610 V12 S15
SE152906 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 65 | 208 | 3 | 1 | 4.6 | 1832 | 1, 7a | E40610 V12 S15
SE152907 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 1 | 4.2 | 1832 | 1, 7a | E40610 V12 S15
SE152907 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 240 | 3 | 1 | 4.2 | 1832 | 1, 7a | E40610 V12 S15
SE152907 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 65 | 240 | 3 | 1 | 4.2 | 1832 | 1, 7a | E40610 V12 S15
SE152908 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 1 | 2.1 | 1832 | 1, 7a | E40610 V12 S15
SE152908 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 35 | 480 | 3 | 1 | 2.1 | 1832 | 1, 7a | E40610 V12 S15
SE152908 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 35 | 480 | 3 | 1 | 2.1 | 1832 | 1, 7a | E40610 V12 S15
SE152909 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 1 | 1.7 | 2289 | 1, 7b | E40610 V12 S15
SE152909 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 1 | 1.7 | 2289 | 1, 7b | E40610 V12 S15
SE152909 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 18 | 600 | 3 | 1 | 1.7 | 2289 | 1, 7b | E40610 V12 S15
SE152910 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 7a | E40610 V12 S15
SE152910 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 7a | E40610 V12 S15
SE152910 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 65 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 7a | E40610 V12 S15
SE152911 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 7a | E40610 V12 S15
SE152911 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 7a | E40610 V12 S15
SE152911 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 65 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 7a | E40610 V12 S15
SE152912 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 1.5 | 6 | 1832 | 1, 7a | E40610 V12 S15
SE152912 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 240 | 3 | 1.5 | 6 | 1832 | 1, 7a | E40610 V12 S15
SE152912 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 65 | 240 | 3 | 1.5 | 6 | 1832 | 1, 7a | E40610 V12 S15
SE152913 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 1.5 | 3 | 1832 | 1, 7a | E40610 V12 S15
SE152913 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 35 | 480 | 3 | 1.5 | 3 | 1832 | 1, 7a | E40610 V12 S15
SE152913 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 35 | 480 | 3 | 1.5 | 3 | 1832 | 1, 7a | E40610 V12 S15
SE152914 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 7b | E40610 V12 S15
SE152914 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 7b | E40610 V12 S15
SE152914 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 18 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 7b | E40610 V12 S15
SE152915 | C | CB | Square D | HGL36020 | 65 | 20 | 600 | 3 | 65 | 200 | 3 | 2 | 7.82 | 1832 | 1, 7a | E40610 V12 S15
SE152915 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 200 | 3 | 2 | 7.82 | 1832 | 1, 7a | E40610 V12 S15
SE152915 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 65 | 200 | 3 | 2 | 7.82 | 1832 | 1, 7a | E40610 V12 S15
SE152916 | C | CB | Square D | HGL36020 | 65 | 20 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1, 7a | E40610 V12 S15
SE152916 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1, 7a | E40610 V12 S15
SE152916 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1, 7a | E40610 V12 S15
SE152917 | C | CB | Square D | HGL36020 | 65 | 20 | 600 | 3 | 65 | 240 | 3 | 2 | 6.8 | 1832 | 1, 7a | E40610 V12 S15
SE152917 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 240 | 3 | 2 | 6.8 | 1832 | 1, 7a | E40610 V12 S15
SE152917 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 65 | 240 | 3 | 2 | 6.8 | 1832 | 1, 7a | E40610 V12 S15
SE152918 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 2 | 3.4 | 1832 | 1, 7a | E40610 V12 S15
SE152918 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 35 | 480 | 3 | 2 | 3.4 | 1832 | 1, 7a | E40610 V12 S15
SE152918 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 35 | 480 | 3 | 2 | 3.4 | 1832 | 1, 7a | E40610 V12 S15
SE152919 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 2289 | 1, 7b | E40610 V12 S15
SE152919 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 2289 | 1, 7b | E40610 V12 S15
SE152919 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 2289 | 1, 7b | E40610 V12 S15
SE152920 | C | CB | Square D | HGL36030 | 65 | 30 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 7a | E40610 V12 S15
SE152920 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 7a | E40610 V12 S15
SE152920 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 7a | E40610 V12 S15
SE152921 | C | CB | Square D | HGL36030 | 65 | 30 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a | E40610 V12 S15
SE152921 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a | E40610 V12 S15
SE152921 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a | E40610 V12 S15
SE152922 | C | CB | Square D | HGL36025 | 65 | 25 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a | E40610 V12 S15
SE152922 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a | E40610 V12 S15
SE152922 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a | E40610 V12 S15
SE152923 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 3 | 4.8 | 1832 | 1, 7a | E40610 V12 S15
SE152923 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 35 | 480 | 3 | 3 | 4.8 | 1832 | 1, 7a | E40610 V12 S15
SE152923 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 35 | 480 | 3 | 3 | 4.8 | 1832 | 1, 7a | E40610 V12 S15
SE152924 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 3 | 3.9 | 2289 | 1, 7b | E40610 V12 S15
SE152924 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 3 | 3.9 | 2289 | 1, 7b | E40610 V12 S15
SE152924 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 18 | 600 | 3 | 3 | 3.9 | 2289 | 1, 7b | E40610 V12 S15
SE152925 | C | CB | Square D | HGL36050 | 65 | 50 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a | E40610 V12 S15
SE152925 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a | E40610 V12 S15
SE152925 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a | E40610 V12 S15
SE152926 | C | CB | Square D | HGL36050 | 65 | 50 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a | E40610 V12 S15
SE152926 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a | E40610 V12 S15
SE152926 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a | E40610 V12 S15
SE152927 | C | CB | Square D | HGL36040 | 65 | 40 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a | E40610 V12 S15
SE152927 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a | E40610 V12 S15
SE152927 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a | E40610 V12 S15
SE152928 | C | CB | Square D | HGL36020 | 35 | 20 | 600 | 3 | 35 | 480 | 3 | 5 | 7.6 | 1832 | 1, 7a | E40610 V12 S15
SE152928 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 35 | 480 | 3 | 5 | 7.6 | 1832 | 1, 7a | E40610 V12 S15
SE152928 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 35 | 480 | 3 | 5 | 7.6 | 1832 | 1, 7a | E40610 V12 S15
SE152929 | C | CB | Square D | HGL36020 | 18 | 20 | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 2289 | 1, 7b | E40610 V12 S15
SE152929 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 2289 | 1, 7b | E40610 V12 S15
SE152929 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 2289 | 1, 7b | E40610 V12 S15
SE152930 | C | CB | Square D | HGL36070 | 65 | 70 | 600 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 7k | E40610 V12 S15
SE152930 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 7k | E40610 V12 S15
SE152930 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 7k | E40610 V12 S15
SE152931 | C | CB | Square D | HGL36070 | 65 | 70 | 600 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 7k | E40610 V12 S15
SE152931 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 7k | E40610 V12 S15
SE152931 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 7k | E40610 V12 S15
SE152932 | C | CB | Square D | HGL36060 | 65 | 60 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a | E40610 V12 S15
SE152932 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a | E40610 V12 S15
SE152932 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a | E40610 V12 S15
SE152933 | C | CB | Square D | HGL36030 | 35 | 30 | 600 | 3 | 35 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a | E40610 V12 S15
SE152933 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 35 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a | E40610 V12 S15
SE152933 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 35 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a | E40610 V12 S15
SE152934 | C | CB | Square D | HGL36025 | 18 | 25 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 2289 | 1, 7b | E40610 V12 S15
SE152934 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 2289 | 1, 7b | E40610 V12 S15
SE152934 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 2289 | 1, 7b | E40610 V12 S15
SE152935 | C | CB | Square D | HGL36090 | 65 | 90 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 2289 | 1, 7b | E40610 V12 S15
SE152935 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 2289 | 1, 7b | E40610 V12 S15
SE152935 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 2289 | 1, 7b | E40610 V12 S15
SE152936 | C | CB | Square D | HGL36090 | 65 | 90 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 2289 | 1, 7b | E40610 V12 S15
SE152936 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 2289 | 1, 7b | E40610 V12 S15
SE152936 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 2289 | 1, 7b | E40610 V12 S15
SE152937 | C | CB | Square D | HGL36070 | 65 | 70 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 7k | E40610 V12 S15
SE152937 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 7k | E40610 V12 S15
SE152937 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 7k | E40610 V12 S15
SE152938 | C | CB | Square D | HGL36040 | 35 | 40 | 600 | 3 | 35 | 480 | 3 | 10 | 14 | 1832 | 1, 7a | E40610 V12 S15
SE152938 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 35 | 480 | 3 | 10 | 14 | 1832 | 1, 7a | E40610 V12 S15
SE152938 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 35 | 480 | 3 | 10 | 14 | 1832 | 1, 7a | E40610 V12 S15
SE152939 | C | CB | Square D | HGL36030 | 18 | 30 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 2289 | 1, 7b | E40610 V12 S15
SE152939 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 2289 | 1, 7b | E40610 V12 S15
SE152939 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 2289 | 1, 7b | E40610 V12 S15
SE152940 | C | CB | Square D | HGL36125 | 65 | 125 | 600 | 3 | 65 | 200 | 3 | 15 | 48.3 | 2289 | 1, 7l | E40610 V12 S15
SE152940 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 65 | 200 | 3 | 15 | 48.3 | 2289 | 1, 7l | E40610 V12 S15
SE152940 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 65 | 200 | 3 | 15 | 48.3 | 2289 | 1, 7l | E40610 V12 S15
SE152941 | C | CB | Square D | HGL36125 | 65 | 125 | 600 | 3 | 65 | 208 | 3 | 15 | 46.2 | 2289 | 1, 7l | E40610 V12 S15
SE152941 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 65 | 208 | 3 | 15 | 46.2 | 2289 | 1, 7l | E40610 V12 S15
SE152941 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 65 | 208 | 3 | 15 | 46.2 | 2289 | 1, 7l | E40610 V12 S15
SE152942 | C | CB | Square D | HGL36110 | 65 | 110 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 2289 | 1, 7b | E40610 V12 S15
SE152942 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 2289 | 1, 7b | E40610 V12 S15
SE152942 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 2289 | 1, 7b | E40610 V12 S15
SE152943 | C | CB | Square D | HGL36060 | 35 | 60 | 600 | 3 | 35 | 480 | 3 | 15 | 21 | 1832 | 1, 7a | E40610 V12 S15
SE152943 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 35 | 480 | 3 | 15 | 21 | 1832 | 1, 7a | E40610 V12 S15
SE152943 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 35 | 480 | 3 | 15 | 21 | 1832 | 1, 7a | E40610 V12 S15
SE152944 | C | CB | Square D | HGL36045 | 18 | 45 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 2289 | 1, 7b | E40610 V12 S15
SE152944 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 2289 | 1, 7b | E40610 V12 S15
SE152944 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 2289 | 1, 7b | E40610 V12 S15
SE152945 | C | CB | Square D | HGL36150 | 65 | 150 | 600 | 3 | 65 | 200 | 3 | 20 | 62.1 | 2289 | 1, 7l | E40610 V12 S15
SE152945 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 65 | 200 | 3 | 20 | 62.1 | 2289 | 1, 7l | E40610 V12 S15
SE152945 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 65 | 200 | 3 | 20 | 62.1 | 2289 | 1, 7l | E40610 V12 S15
SE152946 | C | CB | Square D | HGL36150 | 65 | 150 | 600 | 3 | 65 | 208 | 3 | 20 | 59.4 | 2289 | 1, 7l | E40610 V12 S15
SE152946 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 65 | 208 | 3 | 20 | 59.4 | 2289 | 1, 7l | E40610 V12 S15
SE152946 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 65 | 208 | 3 | 20 | 59.4 | 2289 | 1, 7l | E40610 V12 S15
SE152947 | C | CB | Square D | HGL36150 | 65 | 150 | 600 | 3 | 65 | 240 | 3 | 20 | 54 | 2289 | 1, 7l | E40610 V12 S15
SE152947 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 65 | 240 | 3 | 20 | 54 | 2289 | 1, 7l | E40610 V12 S15
SE152947 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 65 | 240 | 3 | 20 | 54 | 2289 | 1, 7l | E40610 V12 S15
SE152948 | C | CB | Square D | HGL36070 | 35 | 70 | 600 | 3 | 35 | 480 | 3 | 20 | 27 | 1832 | 1, 7k | E40610 V12 S15
SE152948 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 35 | 480 | 3 | 20 | 27 | 1832 | 1, 7k | E40610 V12 S15
SE152948 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 35 | 480 | 3 | 20 | 27 | 1832 | 1, 7k | E40610 V12 S15
SE152949 | C | CB | Square D | HGL36060 | 18 | 60 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 2289 | 1, 7b | E40610 V12 S15
SE152949 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 2289 | 1, 7b | E40610 V12 S15
SE152949 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 2289 | 1, 7b | E40610 V12 S15
SE152950 | C | CB | Square D | HGL36150 | 65 | 150 | 600 | 3 | 65 | 240 | 3 | 25 | 68 | 2289 | 1, 7l | E40610 V12 S15
SE152950 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 65 | 240 | 3 | 25 | 68 | 2289 | 1, 7l | E40610 V12 S15
SE152950 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 65 | 240 | 3 | 25 | 68 | 2289 | 1, 7l | E40610 V12 S15
SE152951 | C | CB | Square D | HGL36090 | 35 | 90 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 2289 | 1, 7b | E40610 V12 S15
SE152951 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 2289 | 1, 7b | E40610 V12 S15
SE152951 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 2289 | 1, 7b | E40610 V12 S15
SE152952 | C | CB | Square D | HGL36070 | 18 | 70 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2289 | 1, 7b | E40610 V12 S15
SE152952 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2289 | 1, 7b | E40610 V12 S15
SE152952 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2289 | 1, 7b | E40610 V12 S15
SE152953 | C | CB | Square D | HGL36100 | 35 | 100 | 600 | 3 | 35 | 480 | 3 | 30 | 40 | 2289 | 1, 7b | E40610 V12 S15
SE152953 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 35 | 480 | 3 | 30 | 40 | 2289 | 1, 7b | E40610 V12 S15
SE152953 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 35 | 480 | 3 | 30 | 40 | 2289 | 1, 7b | E40610 V12 S15
SE152954 | C | CB | Square D | HGL36080 | 18 | 80 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2289 | 1, 7b | E40610 V12 S15
SE152954 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2289 | 1, 7b | E40610 V12 S15
SE152954 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2289 | 1, 7b | E40610 V12 S15
SE152955 | C | CB | Square D | HGL36150 | 35 | 150 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 2289 | 1, 7l | E40610 V12 S15
SE152955 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 2289 | 1, 7l | E40610 V12 S15
SE152955 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 2289 | 1, 7l | E40610 V12 S15
SE152956 | C | CB | Square D | HGL36110 | 18 | 110 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2289 | 1, 7b | E40610 V12 S15
SE152956 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2289 | 1, 7b | E40610 V12 S15
SE152956 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2289 | 1, 7b | E40610 V12 S15
SE152957 | C | CB | Square D | HGL36150 | 35 | 150 | 600 | 3 | 35 | 480 | 3 | 50 | 65 | 2289 | 1, 7l | E40610 V12 S15
SE152957 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 35 | 480 | 3 | 50 | 65 | 2289 | 1, 7l | E40610 V12 S15
SE152957 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 35 | 480 | 3 | 50 | 65 | 2289 | 1, 7l | E40610 V12 S15
SE152958 | C | CB | Square D | HGL36150 | 18 | 150 | 600 | 3 | 18 | 600 | 3 | 50 | 52 | 2289 | 1, 7l | E40610 V12 S15
SE152958 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 18 | 600 | 3 | 50 | 52 | 2289 | 1, 7l | E40610 V12 S15
SE152958 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 18 | 600 | 3 | 50 | 52 | 2289 | 1, 7l | E40610 V12 S15
SE152959 | C | CB | Square D | HGL36175 | 18 | 175 | 600 | 3 | 18 | 600 | 3 | 60 | 62 | 2289 | 1, 7l | E40610 V12 S15
SE152959 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 18 | 600 | 3 | 60 | 62 | 2289 | 1, 7l | E40610 V12 S15
SE152959 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 18 | 600 | 3 | 60 | 62 | 2289 | 1, 7l | E40610 V12 S15
SE152960 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 7a | E40610 V12 S16
SE152960 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 7a | E40610 V12 S16
SE152960 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 65 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 7a | E40610 V12 S16
SE152961 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 7a | E40610 V12 S16
SE152961 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 7a | E40610 V12 S16
SE152961 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 65 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 7a | E40610 V12 S16
SE152962 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 7a | E40610 V12 S16
SE152962 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 7a | E40610 V12 S16
SE152962 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 65 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 7a | E40610 V12 S16
SE152963 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 7a | E40610 V12 S16
SE152963 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 7a | E40610 V12 S16
SE152963 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 65 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 7a | E40610 V12 S16
SE152964 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 7a | E40610 V12 S16
SE152964 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 7a | E40610 V12 S16
SE152964 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 65 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 7a | E40610 V12 S16
SE152965 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 7a | E40610 V12 S16
SE152965 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 7a | E40610 V12 S16
SE152965 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 65 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 7a | E40610 V12 S16
SE152966 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 7a | E40610 V12 S16
SE152966 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 35 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 7a | E40610 V12 S16
SE152966 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 35 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 7a | E40610 V12 S16
SE152967 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 0.75 | 1.3 | 2289 | 1, 7b | E40610 V12 S16
SE152967 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 0.75 | 1.3 | 2289 | 1, 7b | E40610 V12 S16
SE152967 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 18 | 600 | 3 | 0.75 | 1.3 | 2289 | 1, 7b | E40610 V12 S16
SE152968 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 1 | 4.8 | 1832 | 1, 7a | E40610 V12 S16
SE152968 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 200 | 3 | 1 | 4.8 | 1832 | 1, 7a | E40610 V12 S16
SE152968 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 65 | 200 | 3 | 1 | 4.8 | 1832 | 1, 7a | E40610 V12 S16
SE152969 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 1 | 4.6 | 1832 | 1, 7a | E40610 V12 S16
SE152969 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 208 | 3 | 1 | 4.6 | 1832 | 1, 7a | E40610 V12 S16
SE152969 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 65 | 208 | 3 | 1 | 4.6 | 1832 | 1, 7a | E40610 V12 S16
SE152970 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 1 | 4.2 | 1832 | 1, 7a | E40610 V12 S16
SE152970 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 240 | 3 | 1 | 4.2 | 1832 | 1, 7a | E40610 V12 S16
SE152970 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 65 | 240 | 3 | 1 | 4.2 | 1832 | 1, 7a | E40610 V12 S16
SE152971 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 1 | 2.1 | 1832 | 1, 7a | E40610 V12 S16
SE152971 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 35 | 480 | 3 | 1 | 2.1 | 1832 | 1, 7a | E40610 V12 S16
SE152971 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 35 | 480 | 3 | 1 | 2.1 | 1832 | 1, 7a | E40610 V12 S16
SE152972 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 1 | 1.7 | 2289 | 1, 7b | E40610 V12 S16
SE152972 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 1 | 1.7 | 2289 | 1, 7b | E40610 V12 S16
SE152972 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 18 | 600 | 3 | 1 | 1.7 | 2289 | 1, 7b | E40610 V12 S16
SE152973 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 7a | E40610 V12 S16
SE152973 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 7a | E40610 V12 S16
SE152973 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 65 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 7a | E40610 V12 S16
SE152974 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 7a | E40610 V12 S16
SE152974 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 7a | E40610 V12 S16
SE152974 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 65 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 7a | E40610 V12 S16
SE152975 | C | CB | Square D | HGL36015 | 65 | 15 | 600 | 3 | 65 | 240 | 3 | 1.5 | 6 | 1832 | 1, 7a | E40610 V12 S16
SE152975 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 240 | 3 | 1.5 | 6 | 1832 | 1, 7a | E40610 V12 S16
SE152975 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 65 | 240 | 3 | 1.5 | 6 | 1832 | 1, 7a | E40610 V12 S16
SE152976 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 1.5 | 3 | 1832 | 1, 7a | E40610 V12 S16
SE152976 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 35 | 480 | 3 | 1.5 | 3 | 1832 | 1, 7a | E40610 V12 S16
SE152976 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 35 | 480 | 3 | 1.5 | 3 | 1832 | 1, 7a | E40610 V12 S16
SE152977 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 7b | E40610 V12 S16
SE152977 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 7b | E40610 V12 S16
SE152977 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 18 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 7b | E40610 V12 S16
SE152978 | C | CB | Square D | HGL36020 | 65 | 20 | 600 | 3 | 65 | 200 | 3 | 2 | 7.82 | 1832 | 1, 7a | E40610 V12 S16
SE152978 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 200 | 3 | 2 | 7.82 | 1832 | 1, 7a | E40610 V12 S16
SE152978 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 65 | 200 | 3 | 2 | 7.82 | 1832 | 1, 7a | E40610 V12 S16
SE152979 | C | CB | Square D | HGL36020 | 65 | 20 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1, 7a | E40610 V12 S16
SE152979 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1, 7a | E40610 V12 S16
SE152979 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 65 | 208 | 3 | 2 | 7.5 | 1832 | 1, 7a | E40610 V12 S16
SE152980 | C | CB | Square D | HGL36020 | 65 | 20 | 600 | 3 | 65 | 240 | 3 | 2 | 6.8 | 1832 | 1, 7a | E40610 V12 S16
SE152980 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 240 | 3 | 2 | 6.8 | 1832 | 1, 7a | E40610 V12 S16
SE152980 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 65 | 240 | 3 | 2 | 6.8 | 1832 | 1, 7a | E40610 V12 S16
SE152981 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 2 | 3.4 | 1832 | 1, 7a | E40610 V12 S16
SE152981 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 35 | 480 | 3 | 2 | 3.4 | 1832 | 1, 7a | E40610 V12 S16
SE152981 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 35 | 480 | 3 | 2 | 3.4 | 1832 | 1, 7a | E40610 V12 S16
SE152982 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 2289 | 1, 7b | E40610 V12 S16
SE152982 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 2289 | 1, 7b | E40610 V12 S16
SE152982 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 18 | 600 | 3 | 2 | 2.7 | 2289 | 1, 7b | E40610 V12 S16
SE152983 | C | CB | Square D | HGL36030 | 65 | 30 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 7a | E40610 V12 S16
SE152983 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 7a | E40610 V12 S16
SE152983 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 65 | 200 | 3 | 3 | 11 | 1832 | 1, 7a | E40610 V12 S16
SE152984 | C | CB | Square D | HGL36030 | 65 | 30 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a | E40610 V12 S16
SE152984 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a | E40610 V12 S16
SE152984 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 65 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a | E40610 V12 S16
SE152985 | C | CB | Square D | HGL36025 | 65 | 25 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a | E40610 V12 S16
SE152985 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a | E40610 V12 S16
SE152985 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 65 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a | E40610 V12 S16
SE152986 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 3 | 4.8 | 1832 | 1, 7a | E40610 V12 S16
SE152986 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 35 | 480 | 3 | 3 | 4.8 | 1832 | 1, 7a | E40610 V12 S16
SE152986 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 35 | 480 | 3 | 3 | 4.8 | 1832 | 1, 7a | E40610 V12 S16
SE152987 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 3 | 3.9 | 2289 | 1, 7b | E40610 V12 S16
SE152987 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 3 | 3.9 | 2289 | 1, 7b | E40610 V12 S16
SE152987 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 18 | 600 | 3 | 3 | 3.9 | 2289 | 1, 7b | E40610 V12 S16
SE152988 | C | CB | Square D | HGL36050 | 65 | 50 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a | E40610 V12 S16
SE152988 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a | E40610 V12 S16
SE152988 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 65 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a | E40610 V12 S16
SE152989 | C | CB | Square D | HGL36050 | 65 | 50 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a | E40610 V12 S16
SE152989 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a | E40610 V12 S16
SE152989 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 65 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a | E40610 V12 S16
SE152990 | C | CB | Square D | HGL36040 | 65 | 40 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a | E40610 V12 S16
SE152990 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a | E40610 V12 S16
SE152990 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 65 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a | E40610 V12 S16
SE152991 | C | CB | Square D | HGL36020 | 35 | 20 | 600 | 3 | 35 | 480 | 3 | 5 | 7.6 | 1832 | 1, 7a | E40610 V12 S16
SE152991 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 35 | 480 | 3 | 5 | 7.6 | 1832 | 1, 7a | E40610 V12 S16
SE152991 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 35 | 480 | 3 | 5 | 7.6 | 1832 | 1, 7a | E40610 V12 S16
SE152992 | C | CB | Square D | HGL36020 | 18 | 20 | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 2289 | 1, 7b | E40610 V12 S16
SE152992 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 2289 | 1, 7b | E40610 V12 S16
SE152992 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 18 | 600 | 3 | 5 | 6.1 | 2289 | 1, 7b | E40610 V12 S16
SE152993 | C | CB | Square D | HGL36070 | 65 | 70 | 600 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 7k | E40610 V12 S16
SE152993 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 7k | E40610 V12 S16
SE152993 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 65 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 7k | E40610 V12 S16
SE152994 | C | CB | Square D | HGL36070 | 65 | 70 | 600 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 7k | E40610 V12 S16
SE152994 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 7k | E40610 V12 S16
SE152994 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 65 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 7k | E40610 V12 S16
SE152995 | C | CB | Square D | HGL36060 | 65 | 60 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a | E40610 V12 S16
SE152995 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a | E40610 V12 S16
SE152995 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 65 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a | E40610 V12 S16
SE152996 | C | CB | Square D | HGL36030 | 35 | 30 | 600 | 3 | 35 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a | E40610 V12 S16
SE152996 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 35 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a | E40610 V12 S16
SE152996 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 35 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a | E40610 V12 S16
SE152997 | C | CB | Square D | HGL36025 | 18 | 25 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 2289 | 1, 7b | E40610 V12 S16
SE152997 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 2289 | 1, 7b | E40610 V12 S16
SE152997 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 18 | 600 | 3 | 7.5 | 9 | 2289 | 1, 7b | E40610 V12 S16
SE152998 | C | CB | Square D | HGL36090 | 65 | 90 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 2289 | 1, 7b | E40610 V12 S16
SE152998 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 2289 | 1, 7b | E40610 V12 S16
SE152998 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 65 | 200 | 3 | 10 | 32.2 | 2289 | 1, 7b | E40610 V12 S16
SE152999 | C | CB | Square D | HGL36090 | 65 | 90 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 2289 | 1, 7b | E40610 V12 S16
SE152999 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 2289 | 1, 7b | E40610 V12 S16
SE152999 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 65 | 208 | 3 | 10 | 30.8 | 2289 | 1, 7b | E40610 V12 S16
SE153000 | C | CB | Square D | HGL36070 | 65 | 70 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 7k | E40610 V12 S16
SE153000 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 7k | E40610 V12 S16
SE153000 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 65 | 240 | 3 | 10 | 28 | 1832 | 1, 7k | E40610 V12 S16
SE153001 | C | CB | Square D | HGL36040 | 35 | 40 | 600 | 3 | 35 | 480 | 3 | 10 | 14 | 1832 | 1, 7a | E40610 V12 S16
SE153001 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 35 | 480 | 3 | 10 | 14 | 1832 | 1, 7a | E40610 V12 S16
SE153001 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 35 | 480 | 3 | 10 | 14 | 1832 | 1, 7a | E40610 V12 S16
SE153002 | C | CB | Square D | HGL36030 | 18 | 30 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 2289 | 1, 7b | E40610 V12 S16
SE153002 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 2289 | 1, 7b | E40610 V12 S16
SE153002 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 18 | 600 | 3 | 10 | 11 | 2289 | 1, 7b | E40610 V12 S16
SE153003 | C | CB | Square D | HGL36125 | 65 | 125 | 600 | 3 | 65 | 200 | 3 | 15 | 48.3 | 2289 | 1, 7l | E40610 V12 S16
SE153003 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 65 | 200 | 3 | 15 | 48.3 | 2289 | 1, 7l | E40610 V12 S16
SE153003 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 65 | 200 | 3 | 15 | 48.3 | 2289 | 1, 7l | E40610 V12 S16
SE153004 | C | CB | Square D | HGL36125 | 65 | 125 | 600 | 3 | 65 | 208 | 3 | 15 | 46.2 | 2289 | 1, 7l | E40610 V12 S16
SE153004 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 65 | 208 | 3 | 15 | 46.2 | 2289 | 1, 7l | E40610 V12 S16
SE153004 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 65 | 208 | 3 | 15 | 46.2 | 2289 | 1, 7l | E40610 V12 S16
SE153005 | C | CB | Square D | HGL36110 | 65 | 110 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 2289 | 1, 7b | E40610 V12 S16
SE153005 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 2289 | 1, 7b | E40610 V12 S16
SE153005 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 65 | 240 | 3 | 15 | 42 | 2289 | 1, 7b | E40610 V12 S16
SE153006 | C | CB | Square D | HGL36060 | 35 | 60 | 600 | 3 | 35 | 480 | 3 | 15 | 21 | 1832 | 1, 7a | E40610 V12 S16
SE153006 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 35 | 480 | 3 | 15 | 21 | 1832 | 1, 7a | E40610 V12 S16
SE153006 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 35 | 480 | 3 | 15 | 21 | 1832 | 1, 7a | E40610 V12 S16
SE153007 | C | CB | Square D | HGL36045 | 18 | 45 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 2289 | 1, 7b | E40610 V12 S16
SE153007 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 2289 | 1, 7b | E40610 V12 S16
SE153007 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 18 | 600 | 3 | 15 | 17 | 2289 | 1, 7b | E40610 V12 S16
SE153008 | C | CB | Square D | HGL36150 | 65 | 150 | 600 | 3 | 65 | 200 | 3 | 20 | 62.1 | 3663 | 1, 7l | E40610 V12 S16
SE153008 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 65 | 200 | 3 | 20 | 62.1 | 3663 | 1, 7l | E40610 V12 S16
SE153008 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 65 | 200 | 3 | 20 | 62.1 | 3663 | 1, 7l | E40610 V12 S16
SE153009 | C | CB | Square D | HGL36150 | 65 | 150 | 600 | 3 | 65 | 208 | 3 | 20 | 59.4 | 3663 | 1, 7l | E40610 V12 S16
SE153009 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 65 | 208 | 3 | 20 | 59.4 | 3663 | 1, 7l | E40610 V12 S16
SE153009 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 65 | 208 | 3 | 20 | 59.4 | 3663 | 1, 7l | E40610 V12 S16
SE153010 | C | CB | Square D | HGL36150 | 65 | 150 | 600 | 3 | 65 | 240 | 3 | 20 | 54 | 2289 | 1, 7l | E40610 V12 S16
SE153010 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 65 | 240 | 3 | 20 | 54 | 2289 | 1, 7l | E40610 V12 S16
SE153010 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 65 | 240 | 3 | 20 | 54 | 2289 | 1, 7l | E40610 V12 S16
SE153011 | C | CB | Square D | HGL36070 | 35 | 70 | 600 | 3 | 35 | 480 | 3 | 20 | 27 | 1832 | 1, 7k | E40610 V12 S16
SE153011 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 35 | 480 | 3 | 20 | 27 | 1832 | 1, 7k | E40610 V12 S16
SE153011 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 35 | 480 | 3 | 20 | 27 | 1832 | 1, 7k | E40610 V12 S16
SE153012 | C | CB | Square D | HGL36060 | 18 | 60 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 2289 | 1, 7b | E40610 V12 S16
SE153012 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 2289 | 1, 7b | E40610 V12 S16
SE153012 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 18 | 600 | 3 | 20 | 22 | 2289 | 1, 7b | E40610 V12 S16
SE153013 | C | CB | Square D | HGL36150 | 65 | 150 | 600 | 3 | 65 | 240 | 3 | 25 | 68 | 3663 | 1, 7l | E40610 V12 S16
SE153013 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 65 | 240 | 3 | 25 | 68 | 3663 | 1, 7l | E40610 V12 S16
SE153013 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 65 | 240 | 3 | 25 | 68 | 3663 | 1, 7l | E40610 V12 S16
SE153014 | C | CB | Square D | HGL36090 | 35 | 90 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 2289 | 1, 7b | E40610 V12 S16
SE153014 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 2289 | 1, 7b | E40610 V12 S16
SE153014 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 35 | 480 | 3 | 25 | 34 | 2289 | 1, 7b | E40610 V12 S16
SE153015 | C | CB | Square D | HGL36070 | 18 | 70 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2289 | 1, 7b | E40610 V12 S16
SE153015 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2289 | 1, 7b | E40610 V12 S16
SE153015 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 18 | 600 | 3 | 25 | 27 | 2289 | 1, 7b | E40610 V12 S16
SE153016 | C | CB | Square D | HGL36100 | 35 | 100 | 600 | 3 | 35 | 480 | 3 | 30 | 40 | 2289 | 1, 7b | E40610 V12 S16
SE153016 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 35 | 480 | 3 | 30 | 40 | 2289 | 1, 7b | E40610 V12 S16
SE153016 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 35 | 480 | 3 | 30 | 40 | 2289 | 1, 7b | E40610 V12 S16
SE153017 | C | CB | Square D | HGL36080 | 18 | 80 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2289 | 1, 7b | E40610 V12 S16
SE153017 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2289 | 1, 7b | E40610 V12 S16
SE153017 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 18 | 600 | 3 | 30 | 32 | 2289 | 1, 7b | E40610 V12 S16
SE153018 | C | CB | Square D | HGL36150 | 35 | 150 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 2289 | 1, 7l | E40610 V12 S16
SE153018 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 2289 | 1, 7l | E40610 V12 S16
SE153018 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 35 | 480 | 3 | 40 | 52 | 2289 | 1, 7l | E40610 V12 S16
SE153019 | C | CB | Square D | HGL36110 | 18 | 110 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2289 | 1, 7b | E40610 V12 S16
SE153019 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2289 | 1, 7b | E40610 V12 S16
SE153019 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 18 | 600 | 3 | 40 | 41 | 2289 | 1, 7b | E40610 V12 S16
SE153020 | C | CB | Square D | HGL36150 | 35 | 150 | 600 | 3 | 35 | 480 | 3 | 50 | 65 | 3663 | 1, 7l | E40610 V12 S16
SE153020 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 35 | 480 | 3 | 50 | 65 | 3663 | 1, 7l | E40610 V12 S16
SE153020 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 35 | 480 | 3 | 50 | 65 | 3663 | 1, 7l | E40610 V12 S16
SE153021 | C | CB | Square D | HGL36150 | 18 | 150 | 600 | 3 | 18 | 600 | 3 | 50 | 52 | 2289 | 1, 7l | E40610 V12 S16
SE153021 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 18 | 600 | 3 | 50 | 52 | 2289 | 1, 7l | E40610 V12 S16
SE153021 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 18 | 600 | 3 | 50 | 52 | 2289 | 1, 7l | E40610 V12 S16
SE153022 | C | CB | Square D | HGL36175 | 18 | 175 | 600 | 3 | 18 | 600 | 3 | 60 | 62 | 3663 | 1, 7l | E40610 V12 S16
SE153022 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 18 | 600 | 3 | 60 | 62 | 3663 | 1, 7l | E40610 V12 S16
SE153022 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 18 | 600 | 3 | 60 | 62 | 3663 | 1, 7l | E40610 V12 S16
SE154004 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 7a | E40610 V12 S15
SE154004 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 35 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 7a | E40610 V12 S15
SE154004 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 35 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 7a | E40610 V12 S15
SE154005 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 0.5 | 0.9 | 2289 | 1, 7b | E40610 V12 S15
SE154005 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 0.5 | 0.9 | 2289 | 1, 7b | E40610 V12 S15
SE154005 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 18 | 600 | 3 | 0.5 | 0.9 | 2289 | 1, 7b | E40610 V12 S15
SE154006 | C | CB | Square D | HGL36015 | 35 | 15 | 600 | 3 | 35 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 7a | E40610 V12 S16
SE154006 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 35 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 7a | E40610 V12 S16
SE154006 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 35 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 7a | E40610 V12 S16
SE154007 | C | CB | Square D | HGL36015 | 18 | 15 | 600 | 3 | 18 | 600 | 3 | 0.5 | 0.9 | 2289 | 1, 7b | E40610 V12 S16
SE154007 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 18 | 600 | 3 | 0.5 | 0.9 | 2289 | 1, 7b | E40610 V12 S16
SE154007 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 18 | 600 | 3 | 0.5 | 0.9 | 2289 | 1, 7b | E40610 V12 S16

## HJ-TM
Issued: 2007-03-07
Last Revised: 2008-03-11
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE153071 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 7a | E40610 V12 S15
SE153071 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 7a | E40610 V12 S15
SE153071 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 7a | E40610 V12 S15
SE153072 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 7a | E40610 V12 S15
SE153072 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 7a | E40610 V12 S15
SE153072 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 7a | E40610 V12 S15
SE153073 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 7a | E40610 V12 S15
SE153073 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 7a | E40610 V12 S15
SE153073 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 7a | E40610 V12 S15
SE153074 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 7a | E40610 V12 S15
SE153074 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 7a | E40610 V12 S15
SE153074 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 7a | E40610 V12 S15
SE153075 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 7a | E40610 V12 S15
SE153075 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 7a | E40610 V12 S15
SE153075 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 7a | E40610 V12 S15
SE153076 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 7a | E40610 V12 S15
SE153076 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 7a | E40610 V12 S15
SE153076 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 7a | E40610 V12 S15
SE153077 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 7a | E40610 V12 S15
SE153077 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 7a | E40610 V12 S15
SE153077 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 7a | E40610 V12 S15
SE153078 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 0.75 | 1.3 | 2289 | 1, 7b | E40610 V12 S15
SE153078 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 0.75 | 1.3 | 2289 | 1, 7b | E40610 V12 S15
SE153078 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 25 | 600 | 3 | 0.75 | 1.3 | 2289 | 1, 7b | E40610 V12 S15
SE153079 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 7a | E40610 V12 S15
SE153079 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 7a | E40610 V12 S15
SE153079 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 7a | E40610 V12 S15
SE153080 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 7a | E40610 V12 S15
SE153080 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 7a | E40610 V12 S15
SE153080 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 7a | E40610 V12 S15
SE153081 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 7a | E40610 V12 S15
SE153081 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 7a | E40610 V12 S15
SE153081 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 7a | E40610 V12 S15
SE153082 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 7a | E40610 V12 S15
SE153082 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 7a | E40610 V12 S15
SE153082 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 7a | E40610 V12 S15
SE153083 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 1 | 1.7 | 2289 | 1, 7b | E40610 V12 S15
SE153083 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 1 | 1.7 | 2289 | 1, 7b | E40610 V12 S15
SE153083 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 25 | 600 | 3 | 1 | 1.7 | 2289 | 1, 7b | E40610 V12 S15
SE153084 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 7a | E40610 V12 S15
SE153084 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 7a | E40610 V12 S15
SE153084 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 7a | E40610 V12 S15
SE153085 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 7a | E40610 V12 S15
SE153085 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 7a | E40610 V12 S15
SE153085 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 7a | E40610 V12 S15
SE153086 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 7a | E40610 V12 S15
SE153086 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 7a | E40610 V12 S15
SE153086 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 7a | E40610 V12 S15
SE153087 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 7a | E40610 V12 S15
SE153087 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 7a | E40610 V12 S15
SE153087 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 7a | E40610 V12 S15
SE153088 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 7b | E40610 V12 S15
SE153088 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 7b | E40610 V12 S15
SE153088 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 25 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 7b | E40610 V12 S15
SE153089 | C | CB | Square D | HJL36020 | 100 | 20 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 7a | E40610 V12 S15
SE153089 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 7a | E40610 V12 S15
SE153089 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 7a | E40610 V12 S15
SE153090 | C | CB | Square D | HJL36020 | 100 | 20 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 7a | E40610 V12 S15
SE153090 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 7a | E40610 V12 S15
SE153090 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 7a | E40610 V12 S15
SE153091 | C | CB | Square D | HJL36020 | 100 | 20 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 7a | E40610 V12 S15
SE153091 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 7a | E40610 V12 S15
SE153091 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 7a | E40610 V12 S15
SE153092 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 7a | E40610 V12 S15
SE153092 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 7a | E40610 V12 S15
SE153092 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 7a | E40610 V12 S15
SE153093 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 2 | 2.7 | 2289 | 1, 7b | E40610 V12 S15
SE153093 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 2 | 2.7 | 2289 | 1, 7b | E40610 V12 S15
SE153093 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 25 | 600 | 3 | 2 | 2.7 | 2289 | 1, 7b | E40610 V12 S15
SE153094 | C | CB | Square D | HJL36030 | 100 | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 7a | E40610 V12 S15
SE153094 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 7a | E40610 V12 S15
SE153094 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 7a | E40610 V12 S15
SE153095 | C | CB | Square D | HJL36030 | 100 | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a | E40610 V12 S15
SE153095 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a | E40610 V12 S15
SE153095 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a | E40610 V12 S15
SE153096 | C | CB | Square D | HJL36025 | 100 | 25 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a | E40610 V12 S15
SE153096 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a | E40610 V12 S15
SE153096 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a | E40610 V12 S15
SE153097 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 7a | E40610 V12 S15
SE153097 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 7a | E40610 V12 S15
SE153097 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 7a | E40610 V12 S15
SE153098 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 3 | 3.9 | 2289 | 1, 7b | E40610 V12 S15
SE153098 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 3 | 3.9 | 2289 | 1, 7b | E40610 V12 S15
SE153098 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 25 | 600 | 3 | 3 | 3.9 | 2289 | 1, 7b | E40610 V12 S15
SE153099 | C | CB | Square D | HJL36050 | 100 | 50 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a | E40610 V12 S15
SE153099 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a | E40610 V12 S15
SE153099 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a | E40610 V12 S15
SE153100 | C | CB | Square D | HJL36050 | 100 | 50 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a | E40610 V12 S15
SE153100 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a | E40610 V12 S15
SE153100 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a | E40610 V12 S15
SE153101 | C | CB | Square D | HJL36040 | 100 | 40 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a | E40610 V12 S15
SE153101 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a | E40610 V12 S15
SE153101 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a | E40610 V12 S15
SE153102 | C | CB | Square D | HJL36020 | 65 | 20 | 600 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 7a | E40610 V12 S15
SE153102 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 7a | E40610 V12 S15
SE153102 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 7a | E40610 V12 S15
SE153103 | C | CB | Square D | HJL36020 | 25 | 20 | 600 | 3 | 25 | 600 | 3 | 5 | 6.1 | 2289 | 1, 7b | E40610 V12 S15
SE153103 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 5 | 6.1 | 2289 | 1, 7b | E40610 V12 S15
SE153103 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 25 | 600 | 3 | 5 | 6.1 | 2289 | 1, 7b | E40610 V12 S15
SE153104 | C | CB | Square D | HJL36070 | 100 | 70 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 7k | E40610 V12 S15
SE153104 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 7k | E40610 V12 S15
SE153104 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 7k | E40610 V12 S15
SE153105 | C | CB | Square D | HJL36070 | 100 | 70 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 7k | E40610 V12 S15
SE153105 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 7k | E40610 V12 S15
SE153105 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 7k | E40610 V12 S15
SE153106 | C | CB | Square D | HJL36060 | 100 | 60 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a | E40610 V12 S15
SE153106 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a | E40610 V12 S15
SE153106 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a | E40610 V12 S15
SE153107 | C | CB | Square D | HJL36030 | 65 | 30 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a | E40610 V12 S15
SE153107 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a | E40610 V12 S15
SE153107 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a | E40610 V12 S15
SE153108 | C | CB | Square D | HJL36025 | 25 | 25 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 2289 | 1, 7b | E40610 V12 S15
SE153108 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 2289 | 1, 7b | E40610 V12 S15
SE153108 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 2289 | 1, 7b | E40610 V12 S15
SE153109 | C | CB | Square D | HJL36090 | 100 | 90 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2289 | 1, 7b | E40610 V12 S15
SE153109 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2289 | 1, 7b | E40610 V12 S15
SE153109 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2289 | 1, 7b | E40610 V12 S15
SE153110 | C | CB | Square D | HJL36090 | 100 | 90 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2289 | 1, 7b | E40610 V12 S15
SE153110 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2289 | 1, 7b | E40610 V12 S15
SE153110 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2289 | 1, 7b | E40610 V12 S15
SE153111 | C | CB | Square D | HJL36070 | 100 | 70 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 7k | E40610 V12 S15
SE153111 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 7k | E40610 V12 S15
SE153111 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 7k | E40610 V12 S15
SE153112 | C | CB | Square D | HJL36040 | 65 | 40 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 7a | E40610 V12 S15
SE153112 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 7a | E40610 V12 S15
SE153112 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 7a | E40610 V12 S15
SE153113 | C | CB | Square D | HJL36030 | 25 | 30 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 2289 | 1, 7b | E40610 V12 S15
SE153113 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 2289 | 1, 7b | E40610 V12 S15
SE153113 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 2289 | 1, 7b | E40610 V12 S15
SE153114 | C | CB | Square D | HJL36125 | 100 | 125 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 7l | E40610 V12 S15
SE153114 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 7l | E40610 V12 S15
SE153114 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 7l | E40610 V12 S15
SE153115 | C | CB | Square D | HJL36125 | 100 | 125 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 7l | E40610 V12 S15
SE153115 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 7l | E40610 V12 S15
SE153115 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 7l | E40610 V12 S15
SE153116 | C | CB | Square D | HJL36110 | 100 | 110 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 7b | E40610 V12 S15
SE153116 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 7b | E40610 V12 S15
SE153116 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 7b | E40610 V12 S15
SE153117 | C | CB | Square D | HJL36060 | 65 | 60 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 7a | E40610 V12 S15
SE153117 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 7a | E40610 V12 S15
SE153117 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 7a | E40610 V12 S15
SE153118 | C | CB | Square D | HJL36045 | 25 | 45 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 2289 | 1, 7b | E40610 V12 S15
SE153118 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 2289 | 1, 7b | E40610 V12 S15
SE153118 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 2289 | 1, 7b | E40610 V12 S15
SE153119 | C | CB | Square D | HJL36150 | 100 | 150 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2289 | 1, 7l | E40610 V12 S15
SE153119 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2289 | 1, 7l | E40610 V12 S15
SE153119 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2289 | 1, 7l | E40610 V12 S15
SE153120 | C | CB | Square D | HJL36150 | 100 | 150 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 2289 | 1, 7l | E40610 V12 S15
SE153120 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 2289 | 1, 7l | E40610 V12 S15
SE153120 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 2289 | 1, 7l | E40610 V12 S15
SE153121 | C | CB | Square D | HJL36150 | 100 | 150 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 7l | E40610 V12 S15
SE153121 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 7l | E40610 V12 S15
SE153121 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 7l | E40610 V12 S15
SE153122 | C | CB | Square D | HJL36070 | 65 | 70 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 7k | E40610 V12 S15
SE153122 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 7k | E40610 V12 S15
SE153122 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 7k | E40610 V12 S15
SE153123 | C | CB | Square D | HJL36060 | 25 | 60 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 2289 | 1, 7b | E40610 V12 S15
SE153123 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 2289 | 1, 7b | E40610 V12 S15
SE153123 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 2289 | 1, 7b | E40610 V12 S15
SE153124 | C | CB | Square D | HJL36150 | 100 | 150 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2289 | 1, 7l | E40610 V12 S15
SE153124 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2289 | 1, 7l | E40610 V12 S15
SE153124 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2289 | 1, 7l | E40610 V12 S15
SE153125 | C | CB | Square D | HJL36090 | 65 | 90 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2289 | 1, 7b | E40610 V12 S15
SE153125 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2289 | 1, 7b | E40610 V12 S15
SE153125 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2289 | 1, 7b | E40610 V12 S15
SE153126 | C | CB | Square D | HJL36070 | 25 | 70 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2289 | 1, 7b | E40610 V12 S15
SE153126 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2289 | 1, 7b | E40610 V12 S15
SE153126 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2289 | 1, 7b | E40610 V12 S15
SE153127 | C | CB | Square D | HJL36100 | 65 | 100 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2289 | 1, 7b | E40610 V12 S15
SE153127 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2289 | 1, 7b | E40610 V12 S15
SE153127 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2289 | 1, 7b | E40610 V12 S15
SE153128 | C | CB | Square D | HJL36080 | 25 | 80 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2289 | 1, 7b | E40610 V12 S15
SE153128 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2289 | 1, 7b | E40610 V12 S15
SE153128 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2289 | 1, 7b | E40610 V12 S15
SE153129 | C | CB | Square D | HJL36150 | 65 | 150 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 2289 | 1, 7l | E40610 V12 S15
SE153129 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 2289 | 1, 7l | E40610 V12 S15
SE153129 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 2289 | 1, 7l | E40610 V12 S15
SE153130 | C | CB | Square D | HJL36110 | 25 | 110 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2289 | 1, 7b | E40610 V12 S15
SE153130 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2289 | 1, 7b | E40610 V12 S15
SE153130 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2289 | 1, 7b | E40610 V12 S15
SE153131 | C | CB | Square D | HJL36150 | 65 | 150 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 2289 | 1, 7l | E40610 V12 S15
SE153131 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 2289 | 1, 7l | E40610 V12 S15
SE153131 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 2289 | 1, 7l | E40610 V12 S15
SE153132 | C | CB | Square D | HJL36150 | 25 | 150 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2289 | 1, 7l | E40610 V12 S15
SE153132 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2289 | 1, 7l | E40610 V12 S15
SE153132 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2289 | 1, 7l | E40610 V12 S15
SE153133 | C | CB | Square D | HJL36175 | 25 | 175 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 2289 | 1, 7l | E40610 V12 S15
SE153133 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 2289 | 1, 7l | E40610 V12 S15
SE153133 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 2289 | 1, 7l | E40610 V12 S15
SE153134 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 7a | E40610 V12 S16
SE153134 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 7a | E40610 V12 S16
SE153134 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 7a | E40610 V12 S16
SE153135 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 7a | E40610 V12 S16
SE153135 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 7a | E40610 V12 S16
SE153135 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 7a | E40610 V12 S16
SE153136 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 7a | E40610 V12 S16
SE153136 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 7a | E40610 V12 S16
SE153136 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 7a | E40610 V12 S16
SE153137 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 7a | E40610 V12 S16
SE153137 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 7a | E40610 V12 S16
SE153137 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 7a | E40610 V12 S16
SE153138 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 7a | E40610 V12 S16
SE153138 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 7a | E40610 V12 S16
SE153138 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 7a | E40610 V12 S16
SE153139 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 7a | E40610 V12 S16
SE153139 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 7a | E40610 V12 S16
SE153139 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 7a | E40610 V12 S16
SE153140 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 7a | E40610 V12 S16
SE153140 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 7a | E40610 V12 S16
SE153140 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 7a | E40610 V12 S16
SE153141 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 0.75 | 1.3 | 2289 | 1, 7b | E40610 V12 S16
SE153141 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 0.75 | 1.3 | 2289 | 1, 7b | E40610 V12 S16
SE153141 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 25 | 600 | 3 | 0.75 | 1.3 | 2289 | 1, 7b | E40610 V12 S16
SE153142 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 7a | E40610 V12 S16
SE153142 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 7a | E40610 V12 S16
SE153142 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 7a | E40610 V12 S16
SE153143 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 7a | E40610 V12 S16
SE153143 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 7a | E40610 V12 S16
SE153143 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 7a | E40610 V12 S16
SE153144 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 7a | E40610 V12 S16
SE153144 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 7a | E40610 V12 S16
SE153144 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 7a | E40610 V12 S16
SE153145 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 7a | E40610 V12 S16
SE153145 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 7a | E40610 V12 S16
SE153145 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 7a | E40610 V12 S16
SE153146 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 1 | 1.7 | 2289 | 1, 7b | E40610 V12 S16
SE153146 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 1 | 1.7 | 2289 | 1, 7b | E40610 V12 S16
SE153146 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 25 | 600 | 3 | 1 | 1.7 | 2289 | 1, 7b | E40610 V12 S16
SE153147 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 7a | E40610 V12 S16
SE153147 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 7a | E40610 V12 S16
SE153147 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 7a | E40610 V12 S16
SE153148 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 7a | E40610 V12 S16
SE153148 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 7a | E40610 V12 S16
SE153148 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 7a | E40610 V12 S16
SE153149 | C | CB | Square D | HJL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 7a | E40610 V12 S16
SE153149 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 7a | E40610 V12 S16
SE153149 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 7a | E40610 V12 S16
SE153150 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 7a | E40610 V12 S16
SE153150 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 7a | E40610 V12 S16
SE153150 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 7a | E40610 V12 S16
SE153151 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 7b | E40610 V12 S16
SE153151 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 7b | E40610 V12 S16
SE153151 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 25 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 7b | E40610 V12 S16
SE153152 | C | CB | Square D | HJL36020 | 100 | 20 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 7a | E40610 V12 S16
SE153152 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 7a | E40610 V12 S16
SE153152 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 7a | E40610 V12 S16
SE153153 | C | CB | Square D | HJL36020 | 100 | 20 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 7a | E40610 V12 S16
SE153153 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 7a | E40610 V12 S16
SE153153 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 7a | E40610 V12 S16
SE153154 | C | CB | Square D | HJL36020 | 100 | 20 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 7a | E40610 V12 S16
SE153154 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 7a | E40610 V12 S16
SE153154 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 7a | E40610 V12 S16
SE153155 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 7a | E40610 V12 S16
SE153155 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 7a | E40610 V12 S16
SE153155 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 7a | E40610 V12 S16
SE153156 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 2 | 2.7 | 2289 | 1, 7b | E40610 V12 S16
SE153156 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 2 | 2.7 | 2289 | 1, 7b | E40610 V12 S16
SE153156 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 25 | 600 | 3 | 2 | 2.7 | 2289 | 1, 7b | E40610 V12 S16
SE153157 | C | CB | Square D | HJL36030 | 100 | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 7a | E40610 V12 S16
SE153157 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 7a | E40610 V12 S16
SE153157 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 7a | E40610 V12 S16
SE153158 | C | CB | Square D | HJL36030 | 100 | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a | E40610 V12 S16
SE153158 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a | E40610 V12 S16
SE153158 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a | E40610 V12 S16
SE153159 | C | CB | Square D | HJL36025 | 100 | 25 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a | E40610 V12 S16
SE153159 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a | E40610 V12 S16
SE153159 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a | E40610 V12 S16
SE153160 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 7a | E40610 V12 S16
SE153160 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 7a | E40610 V12 S16
SE153160 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 7a | E40610 V12 S16
SE153161 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 3 | 3.9 | 2289 | 1, 7b | E40610 V12 S16
SE153161 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 3 | 3.9 | 2289 | 1, 7b | E40610 V12 S16
SE153161 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 25 | 600 | 3 | 3 | 3.9 | 2289 | 1, 7b | E40610 V12 S16
SE153162 | C | CB | Square D | HJL36050 | 100 | 50 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a | E40610 V12 S16
SE153162 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a | E40610 V12 S16
SE153162 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a | E40610 V12 S16
SE153163 | C | CB | Square D | HJL36050 | 100 | 50 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a | E40610 V12 S16
SE153163 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a | E40610 V12 S16
SE153163 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a | E40610 V12 S16
SE153164 | C | CB | Square D | HJL36040 | 100 | 40 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a | E40610 V12 S16
SE153164 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a | E40610 V12 S16
SE153164 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a | E40610 V12 S16
SE153165 | C | CB | Square D | HJL36020 | 65 | 20 | 600 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 7a | E40610 V12 S16
SE153165 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 7a | E40610 V12 S16
SE153165 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 7a | E40610 V12 S16
SE153166 | C | CB | Square D | HJL36020 | 25 | 20 | 600 | 3 | 25 | 600 | 3 | 5 | 6.1 | 2289 | 1, 7b | E40610 V12 S16
SE153166 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 5 | 6.1 | 2289 | 1, 7b | E40610 V12 S16
SE153166 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 25 | 600 | 3 | 5 | 6.1 | 2289 | 1, 7b | E40610 V12 S16
SE153167 | C | CB | Square D | HJL36070 | 100 | 70 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 7k | E40610 V12 S16
SE153167 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 7k | E40610 V12 S16
SE153167 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 7k | E40610 V12 S16
SE153168 | C | CB | Square D | HJL36070 | 100 | 70 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 7k | E40610 V12 S16
SE153168 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 7k | E40610 V12 S16
SE153168 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 7k | E40610 V12 S16
SE153169 | C | CB | Square D | HJL36060 | 100 | 60 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a | E40610 V12 S16
SE153169 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a | E40610 V12 S16
SE153169 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a | E40610 V12 S16
SE153170 | C | CB | Square D | HJL36030 | 65 | 30 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a | E40610 V12 S16
SE153170 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a | E40610 V12 S16
SE153170 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a | E40610 V12 S16
SE153171 | C | CB | Square D | HJL36025 | 25 | 25 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 2289 | 1, 7b | E40610 V12 S16
SE153171 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 2289 | 1, 7b | E40610 V12 S16
SE153171 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 2289 | 1, 7b | E40610 V12 S16
SE153172 | C | CB | Square D | HJL36090 | 100 | 90 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2289 | 1, 7b | E40610 V12 S16
SE153172 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2289 | 1, 7b | E40610 V12 S16
SE153172 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2289 | 1, 7b | E40610 V12 S16
SE153173 | C | CB | Square D | HJL36090 | 100 | 90 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2289 | 1, 7b | E40610 V12 S16
SE153173 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2289 | 1, 7b | E40610 V12 S16
SE153173 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2289 | 1, 7b | E40610 V12 S16
SE153174 | C | CB | Square D | HJL36070 | 100 | 70 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 7k | E40610 V12 S16
SE153174 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 7k | E40610 V12 S16
SE153174 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 7k | E40610 V12 S16
SE153175 | C | CB | Square D | HJL36040 | 65 | 40 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 7a | E40610 V12 S16
SE153175 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 7a | E40610 V12 S16
SE153175 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 7a | E40610 V12 S16
SE153176 | C | CB | Square D | HJL36030 | 25 | 30 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 2289 | 1, 7b | E40610 V12 S16
SE153176 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 2289 | 1, 7b | E40610 V12 S16
SE153176 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 2289 | 1, 7b | E40610 V12 S16
SE153177 | C | CB | Square D | HJL36125 | 100 | 125 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 7l | E40610 V12 S16
SE153177 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 7l | E40610 V12 S16
SE153177 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 7l | E40610 V12 S16
SE153178 | C | CB | Square D | HJL36125 | 100 | 125 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 7l | E40610 V12 S16
SE153178 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 7l | E40610 V12 S16
SE153178 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 7l | E40610 V12 S16
SE153179 | C | CB | Square D | HJL36110 | 100 | 110 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 7b | E40610 V12 S16
SE153179 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 7b | E40610 V12 S16
SE153179 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 7b | E40610 V12 S16
SE153180 | C | CB | Square D | HJL36060 | 65 | 60 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 7a | E40610 V12 S16
SE153180 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 7a | E40610 V12 S16
SE153180 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 7a | E40610 V12 S16
SE153181 | C | CB | Square D | HJL36045 | 25 | 45 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 2289 | 1, 7b | E40610 V12 S16
SE153181 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 2289 | 1, 7b | E40610 V12 S16
SE153181 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 2289 | 1, 7b | E40610 V12 S16
SE153182 | C | CB | Square D | HJL36150 | 100 | 150 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 3663 | 1, 7l | E40610 V12 S16
SE153182 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 3663 | 1, 7l | E40610 V12 S16
SE153182 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 3663 | 1, 7l | E40610 V12 S16
SE153183 | C | CB | Square D | HJL36150 | 100 | 150 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 3663 | 1, 7l | E40610 V12 S16
SE153183 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 3663 | 1, 7l | E40610 V12 S16
SE153183 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 3663 | 1, 7l | E40610 V12 S16
SE153184 | C | CB | Square D | HJL36150 | 100 | 150 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 7l | E40610 V12 S16
SE153184 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 7l | E40610 V12 S16
SE153184 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 7l | E40610 V12 S16
SE153185 | C | CB | Square D | HJL36070 | 65 | 70 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 7k | E40610 V12 S16
SE153185 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 7k | E40610 V12 S16
SE153185 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 7k | E40610 V12 S16
SE153186 | C | CB | Square D | HJL36060 | 25 | 60 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 2289 | 1, 7b | E40610 V12 S16
SE153186 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 2289 | 1, 7b | E40610 V12 S16
SE153186 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 2289 | 1, 7b | E40610 V12 S16
SE153187 | C | CB | Square D | HJL36150 | 100 | 150 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 3663 | 1, 7l | E40610 V12 S16
SE153187 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 3663 | 1, 7l | E40610 V12 S16
SE153187 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 3663 | 1, 7l | E40610 V12 S16
SE153188 | C | CB | Square D | HJL36090 | 65 | 90 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2289 | 1, 7b | E40610 V12 S16
SE153188 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2289 | 1, 7b | E40610 V12 S16
SE153188 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2289 | 1, 7b | E40610 V12 S16
SE153189 | C | CB | Square D | HJL36070 | 25 | 70 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2289 | 1, 7b | E40610 V12 S16
SE153189 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2289 | 1, 7b | E40610 V12 S16
SE153189 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2289 | 1, 7b | E40610 V12 S16
SE153190 | C | CB | Square D | HJL36100 | 65 | 100 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2289 | 1, 7b | E40610 V12 S16
SE153190 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2289 | 1, 7b | E40610 V12 S16
SE153190 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2289 | 1, 7b | E40610 V12 S16
SE153191 | C | CB | Square D | HJL36080 | 25 | 80 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2289 | 1, 7b | E40610 V12 S16
SE153191 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2289 | 1, 7b | E40610 V12 S16
SE153191 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2289 | 1, 7b | E40610 V12 S16
SE153192 | C | CB | Square D | HJL36150 | 65 | 150 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 2289 | 1, 7l | E40610 V12 S16
SE153192 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 2289 | 1, 7l | E40610 V12 S16
SE153192 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 2289 | 1, 7l | E40610 V12 S16
SE153193 | C | CB | Square D | HJL36110 | 25 | 110 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2289 | 1, 7b | E40610 V12 S16
SE153193 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2289 | 1, 7b | E40610 V12 S16
SE153193 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2289 | 1, 7b | E40610 V12 S16
SE153194 | C | CB | Square D | HJL36150 | 65 | 150 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3663 | 1, 7l | E40610 V12 S16
SE153194 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3663 | 1, 7l | E40610 V12 S16
SE153194 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3663 | 1, 7l | E40610 V12 S16
SE153195 | C | CB | Square D | HJL36150 | 25 | 150 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2289 | 1, 7l | E40610 V12 S16
SE153195 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2289 | 1, 7l | E40610 V12 S16
SE153195 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2289 | 1, 7l | E40610 V12 S16
SE153196 | C | CB | Square D | HJL36175 | 25 | 175 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3663 | 1, 7l | E40610 V12 S16
SE153196 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3663 | 1, 7l | E40610 V12 S16
SE153196 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3663 | 1, 7l | E40610 V12 S16
SE154008 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 7a | E40610 V12 S15
SE154008 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 7a | E40610 V12 S15
SE154008 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 65 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 7a | E40610 V12 S15
SE154009 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 0.5 | 0.9 | 2289 | 1, 7b | E40610 V12 S15
SE154009 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 0.5 | 0.9 | 2289 | 1, 7b | E40610 V12 S15
SE154009 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 25 | 600 | 3 | 0.5 | 0.9 | 2289 | 1, 7b | E40610 V12 S15
SE154010 | C | CB | Square D | HJL36015 | 65 | 15 | 600 | 3 | 65 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 7a | E40610 V12 S16
SE154010 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 7a | E40610 V12 S16
SE154010 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 65 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 7a | E40610 V12 S16
SE154011 | C | CB | Square D | HJL36015 | 25 | 15 | 600 | 3 | 25 | 600 | 3 | 0.5 | 0.9 | 2289 | 1, 7b | E40610 V12 S16
SE154011 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 0.5 | 0.9 | 2289 | 1, 7b | E40610 V12 S16
SE154011 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 25 | 600 | 3 | 0.5 | 0.9 | 2289 | 1, 7b | E40610 V12 S16

## HL-TM
Issued: 2007-03-07
Last Revised: 2008-03-11
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE153245 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 7a | E40610 V12 S15
SE153245 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 7a | E40610 V12 S15
SE153245 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 7a | E40610 V12 S15
SE153246 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 7a | E40610 V12 S15
SE153246 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 7a | E40610 V12 S15
SE153246 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 7a | E40610 V12 S15
SE153247 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 7a | E40610 V12 S15
SE153247 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 7a | E40610 V12 S15
SE153247 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 7a | E40610 V12 S15
SE153248 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 7a | E40610 V12 S15
SE153248 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 7a | E40610 V12 S15
SE153248 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 7a | E40610 V12 S15
SE153249 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 7a | E40610 V12 S15
SE153249 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 7a | E40610 V12 S15
SE153249 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 7a | E40610 V12 S15
SE153250 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 7a | E40610 V12 S15
SE153250 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 7a | E40610 V12 S15
SE153250 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 7a | E40610 V12 S15
SE153251 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 7a | E40610 V12 S15
SE153251 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 7a | E40610 V12 S15
SE153251 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 7a | E40610 V12 S15
SE153252 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 0.75 | 1.3 | 2289 | 1, 7b | E40610 V12 S15
SE153252 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 0.75 | 1.3 | 2289 | 1, 7b | E40610 V12 S15
SE153252 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 50 | 600 | 3 | 0.75 | 1.3 | 2289 | 1, 7b | E40610 V12 S15
SE153253 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 7a | E40610 V12 S15
SE153253 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 7a | E40610 V12 S15
SE153253 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 7a | E40610 V12 S15
SE153254 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 7a | E40610 V12 S15
SE153254 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 7a | E40610 V12 S15
SE153254 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 7a | E40610 V12 S15
SE153255 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 7a | E40610 V12 S15
SE153255 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 7a | E40610 V12 S15
SE153255 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 7a | E40610 V12 S15
SE153256 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 7a | E40610 V12 S15
SE153256 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 7a | E40610 V12 S15
SE153256 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 7a | E40610 V12 S15
SE153257 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 2289 | 1, 7b | E40610 V12 S15
SE153257 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 2289 | 1, 7b | E40610 V12 S15
SE153257 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 2289 | 1, 7b | E40610 V12 S15
SE153258 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 7a | E40610 V12 S15
SE153258 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 7a | E40610 V12 S15
SE153258 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 7a | E40610 V12 S15
SE153259 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 7a | E40610 V12 S15
SE153259 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 7a | E40610 V12 S15
SE153259 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 7a | E40610 V12 S15
SE153260 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 7a | E40610 V12 S15
SE153260 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 7a | E40610 V12 S15
SE153260 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 7a | E40610 V12 S15
SE153261 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 7a | E40610 V12 S15
SE153261 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 7a | E40610 V12 S15
SE153261 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 7a | E40610 V12 S15
SE153262 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 7b | E40610 V12 S15
SE153262 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 7b | E40610 V12 S15
SE153262 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 7b | E40610 V12 S15
SE153263 | C | CB | Square D | HLL36020 | 100 | 20 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 7a | E40610 V12 S15
SE153263 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 7a | E40610 V12 S15
SE153263 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 7a | E40610 V12 S15
SE153264 | C | CB | Square D | HLL36020 | 100 | 20 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 7a | E40610 V12 S15
SE153264 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 7a | E40610 V12 S15
SE153264 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 7a | E40610 V12 S15
SE153265 | C | CB | Square D | HLL36020 | 100 | 20 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 7a | E40610 V12 S15
SE153265 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 7a | E40610 V12 S15
SE153265 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 7a | E40610 V12 S15
SE153266 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 7a | E40610 V12 S15
SE153266 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 7a | E40610 V12 S15
SE153266 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 7a | E40610 V12 S15
SE153267 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 2289 | 1, 7b | E40610 V12 S15
SE153267 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 2289 | 1, 7b | E40610 V12 S15
SE153267 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 2289 | 1, 7b | E40610 V12 S15
SE153268 | C | CB | Square D | HLL36030 | 100 | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 7a | E40610 V12 S15
SE153268 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 7a | E40610 V12 S15
SE153268 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 7a | E40610 V12 S15
SE153269 | C | CB | Square D | HLL36030 | 100 | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a | E40610 V12 S15
SE153269 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a | E40610 V12 S15
SE153269 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a | E40610 V12 S15
SE153270 | C | CB | Square D | HLL36025 | 100 | 25 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a | E40610 V12 S15
SE153270 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a | E40610 V12 S15
SE153270 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a | E40610 V12 S15
SE153271 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 7a | E40610 V12 S15
SE153271 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 7a | E40610 V12 S15
SE153271 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 7a | E40610 V12 S15
SE153272 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 2289 | 1, 7b | E40610 V12 S15
SE153272 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 2289 | 1, 7b | E40610 V12 S15
SE153272 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 2289 | 1, 7b | E40610 V12 S15
SE153273 | C | CB | Square D | HLL36050 | 100 | 50 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a | E40610 V12 S15
SE153273 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a | E40610 V12 S15
SE153273 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a | E40610 V12 S15
SE153274 | C | CB | Square D | HLL36050 | 100 | 50 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a | E40610 V12 S15
SE153274 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a | E40610 V12 S15
SE153274 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a | E40610 V12 S15
SE153275 | C | CB | Square D | HLL36040 | 100 | 40 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a | E40610 V12 S15
SE153275 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a | E40610 V12 S15
SE153275 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a | E40610 V12 S15
SE153276 | C | CB | Square D | HLL36020 | 100 | 20 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 7a | E40610 V12 S15
SE153276 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 7a | E40610 V12 S15
SE153276 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 7a | E40610 V12 S15
SE153277 | C | CB | Square D | HLL36020 | 50 | 20 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 2289 | 1, 7b | E40610 V12 S15
SE153277 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 2289 | 1, 7b | E40610 V12 S15
SE153277 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 2289 | 1, 7b | E40610 V12 S15
SE153278 | C | CB | Square D | HLL36070 | 100 | 70 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 7k | E40610 V12 S15
SE153278 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 7k | E40610 V12 S15
SE153278 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 7k | E40610 V12 S15
SE153279 | C | CB | Square D | HLL36070 | 100 | 70 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 7k | E40610 V12 S15
SE153279 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 7k | E40610 V12 S15
SE153279 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 7k | E40610 V12 S15
SE153280 | C | CB | Square D | HLL36060 | 100 | 60 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a | E40610 V12 S15
SE153280 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a | E40610 V12 S15
SE153280 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a | E40610 V12 S15
SE153281 | C | CB | Square D | HLL36030 | 100 | 30 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a | E40610 V12 S15
SE153281 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a | E40610 V12 S15
SE153281 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a | E40610 V12 S15
SE153282 | C | CB | Square D | HLL36025 | 50 | 25 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 2289 | 1, 7b | E40610 V12 S15
SE153282 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 2289 | 1, 7b | E40610 V12 S15
SE153282 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 2289 | 1, 7b | E40610 V12 S15
SE153283 | C | CB | Square D | HLL36090 | 100 | 90 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2289 | 1, 7b | E40610 V12 S15
SE153283 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2289 | 1, 7b | E40610 V12 S15
SE153283 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2289 | 1, 7b | E40610 V12 S15
SE153284 | C | CB | Square D | HLL36090 | 100 | 90 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2289 | 1, 7b | E40610 V12 S15
SE153284 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2289 | 1, 7b | E40610 V12 S15
SE153284 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2289 | 1, 7b | E40610 V12 S15
SE153285 | C | CB | Square D | HLL36070 | 100 | 70 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 7k | E40610 V12 S15
SE153285 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 7k | E40610 V12 S15
SE153285 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 7k | E40610 V12 S15
SE153286 | C | CB | Square D | HLL36040 | 100 | 40 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 7a | E40610 V12 S15
SE153286 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 7a | E40610 V12 S15
SE153286 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 7a | E40610 V12 S15
SE153287 | C | CB | Square D | HLL36030 | 50 | 30 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 2289 | 1, 7b | E40610 V12 S15
SE153287 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 2289 | 1, 7b | E40610 V12 S15
SE153287 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 2289 | 1, 7b | E40610 V12 S15
SE153288 | C | CB | Square D | HLL36125 | 100 | 125 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 7l | E40610 V12 S15
SE153288 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 7l | E40610 V12 S15
SE153288 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 7l | E40610 V12 S15
SE153289 | C | CB | Square D | HLL36125 | 100 | 125 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 7l | E40610 V12 S15
SE153289 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 7l | E40610 V12 S15
SE153289 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 7l | E40610 V12 S15
SE153290 | C | CB | Square D | HLL36110 | 100 | 110 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 7b | E40610 V12 S15
SE153290 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 7b | E40610 V12 S15
SE153290 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 7b | E40610 V12 S15
SE153291 | C | CB | Square D | HLL36060 | 100 | 60 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 7a | E40610 V12 S15
SE153291 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 7a | E40610 V12 S15
SE153291 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 7a | E40610 V12 S15
SE153292 | C | CB | Square D | HLL36045 | 50 | 45 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 2289 | 1, 7b | E40610 V12 S15
SE153292 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 2289 | 1, 7b | E40610 V12 S15
SE153292 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 2289 | 1, 7b | E40610 V12 S15
SE153293 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2289 | 1, 7l | E40610 V12 S15
SE153293 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2289 | 1, 7l | E40610 V12 S15
SE153293 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2289 | 1, 7l | E40610 V12 S15
SE153294 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 2289 | 1, 7l | E40610 V12 S15
SE153294 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 2289 | 1, 7l | E40610 V12 S15
SE153294 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 2289 | 1, 7l | E40610 V12 S15
SE153295 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 7l | E40610 V12 S15
SE153295 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 7l | E40610 V12 S15
SE153295 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 7l | E40610 V12 S15
SE153296 | C | CB | Square D | HLL36070 | 100 | 70 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 7k | E40610 V12 S15
SE153296 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 7k | E40610 V12 S15
SE153296 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 7k | E40610 V12 S15
SE153297 | C | CB | Square D | HLL36060 | 50 | 60 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 2289 | 1, 7b | E40610 V12 S15
SE153297 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 2289 | 1, 7b | E40610 V12 S15
SE153297 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 2289 | 1, 7b | E40610 V12 S15
SE153298 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2289 | 1, 7l | E40610 V12 S15
SE153298 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2289 | 1, 7l | E40610 V12 S15
SE153298 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2289 | 1, 7l | E40610 V12 S15
SE153299 | C | CB | Square D | HLL36090 | 100 | 90 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2289 | 1, 7b | E40610 V12 S15
SE153299 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2289 | 1, 7b | E40610 V12 S15
SE153299 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2289 | 1, 7b | E40610 V12 S15
SE153300 | C | CB | Square D | HLL36070 | 50 | 70 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2289 | 1, 7b | E40610 V12 S15
SE153300 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2289 | 1, 7b | E40610 V12 S15
SE153300 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2289 | 1, 7b | E40610 V12 S15
SE153301 | C | CB | Square D | HLL36100 | 100 | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2289 | 1, 7b | E40610 V12 S15
SE153301 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2289 | 1, 7b | E40610 V12 S15
SE153301 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2289 | 1, 7b | E40610 V12 S15
SE153302 | C | CB | Square D | HLL36080 | 50 | 80 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2289 | 1, 7b | E40610 V12 S15
SE153302 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2289 | 1, 7b | E40610 V12 S15
SE153302 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2289 | 1, 7b | E40610 V12 S15
SE153303 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2289 | 1, 7l | E40610 V12 S15
SE153303 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2289 | 1, 7l | E40610 V12 S15
SE153303 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2289 | 1, 7l | E40610 V12 S15
SE153304 | C | CB | Square D | HLL36110 | 50 | 110 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2289 | 1, 7b | E40610 V12 S15
SE153304 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2289 | 1, 7b | E40610 V12 S15
SE153304 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2289 | 1, 7b | E40610 V12 S15
SE153305 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 2289 | 1, 7l | E40610 V12 S15
SE153305 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 2289 | 1, 7l | E40610 V12 S15
SE153305 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 2289 | 1, 7l | E40610 V12 S15
SE153306 | C | CB | Square D | HLL36150 | 50 | 150 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2289 | 1, 7l | E40610 V12 S15
SE153306 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2289 | 1, 7l | E40610 V12 S15
SE153306 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2289 | 1, 7l | E40610 V12 S15
SE153307 | C | CB | Square D | HLL36175 | 50 | 175 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 2289 | 1, 7l | E40610 V12 S15
SE153307 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 2289 | 1, 7l | E40610 V12 S15
SE153307 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 2289 | 1, 7l | E40610 V12 S15
SE153308 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 7a | E40610 V12 S16
SE153308 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 7a | E40610 V12 S16
SE153308 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 7a | E40610 V12 S16
SE153309 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 7a | E40610 V12 S16
SE153309 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 7a | E40610 V12 S16
SE153309 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 7a | E40610 V12 S16
SE153310 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 7a | E40610 V12 S16
SE153310 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 7a | E40610 V12 S16
SE153310 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 7a | E40610 V12 S16
SE153311 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 7a | E40610 V12 S16
SE153311 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 7a | E40610 V12 S16
SE153311 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 7a | E40610 V12 S16
SE153312 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 7a | E40610 V12 S16
SE153312 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 7a | E40610 V12 S16
SE153312 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 7a | E40610 V12 S16
SE153313 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 7a | E40610 V12 S16
SE153313 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 7a | E40610 V12 S16
SE153313 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 7a | E40610 V12 S16
SE153314 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 7a | E40610 V12 S16
SE153314 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 7a | E40610 V12 S16
SE153314 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 7a | E40610 V12 S16
SE153315 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 0.75 | 1.3 | 2289 | 1, 7b | E40610 V12 S16
SE153315 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 0.75 | 1.3 | 2289 | 1, 7b | E40610 V12 S16
SE153315 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 50 | 600 | 3 | 0.75 | 1.3 | 2289 | 1, 7b | E40610 V12 S16
SE153316 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 7a | E40610 V12 S16
SE153316 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 7a | E40610 V12 S16
SE153316 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 7a | E40610 V12 S16
SE153317 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 7a | E40610 V12 S16
SE153317 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 7a | E40610 V12 S16
SE153317 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 7a | E40610 V12 S16
SE153318 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 7a | E40610 V12 S16
SE153318 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 7a | E40610 V12 S16
SE153318 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 7a | E40610 V12 S16
SE153319 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 7a | E40610 V12 S16
SE153319 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 7a | E40610 V12 S16
SE153319 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 7a | E40610 V12 S16
SE153320 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 2289 | 1, 7b | E40610 V12 S16
SE153320 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 2289 | 1, 7b | E40610 V12 S16
SE153320 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 2289 | 1, 7b | E40610 V12 S16
SE153321 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 7a | E40610 V12 S16
SE153321 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 7a | E40610 V12 S16
SE153321 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 7a | E40610 V12 S16
SE153322 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 7a | E40610 V12 S16
SE153322 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 7a | E40610 V12 S16
SE153322 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 7a | E40610 V12 S16
SE153323 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 7a | E40610 V12 S16
SE153323 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 7a | E40610 V12 S16
SE153323 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 7a | E40610 V12 S16
SE153324 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 7a | E40610 V12 S16
SE153324 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 7a | E40610 V12 S16
SE153324 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 7a | E40610 V12 S16
SE153325 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 7b | E40610 V12 S16
SE153325 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 7b | E40610 V12 S16
SE153325 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 7b | E40610 V12 S16
SE153326 | C | CB | Square D | HLL36020 | 100 | 20 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 7a | E40610 V12 S16
SE153326 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 7a | E40610 V12 S16
SE153326 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 7a | E40610 V12 S16
SE153327 | C | CB | Square D | HLL36020 | 100 | 20 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 7a | E40610 V12 S16
SE153327 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 7a | E40610 V12 S16
SE153327 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 7a | E40610 V12 S16
SE153328 | C | CB | Square D | HLL36020 | 100 | 20 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 7a | E40610 V12 S16
SE153328 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 7a | E40610 V12 S16
SE153328 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 7a | E40610 V12 S16
SE153329 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 7a | E40610 V12 S16
SE153329 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 7a | E40610 V12 S16
SE153329 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 7a | E40610 V12 S16
SE153330 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 2289 | 1, 7b | E40610 V12 S16
SE153330 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 2289 | 1, 7b | E40610 V12 S16
SE153330 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 2289 | 1, 7b | E40610 V12 S16
SE153331 | C | CB | Square D | HLL36030 | 100 | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 7a | E40610 V12 S16
SE153331 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 7a | E40610 V12 S16
SE153331 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 7a | E40610 V12 S16
SE153332 | C | CB | Square D | HLL36030 | 100 | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a | E40610 V12 S16
SE153332 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a | E40610 V12 S16
SE153332 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 7a | E40610 V12 S16
SE153333 | C | CB | Square D | HLL36025 | 100 | 25 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a | E40610 V12 S16
SE153333 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a | E40610 V12 S16
SE153333 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 7a | E40610 V12 S16
SE153334 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 7a | E40610 V12 S16
SE153334 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 7a | E40610 V12 S16
SE153334 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 7a | E40610 V12 S16
SE153335 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 2289 | 1, 7b | E40610 V12 S16
SE153335 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 2289 | 1, 7b | E40610 V12 S16
SE153335 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 2289 | 1, 7b | E40610 V12 S16
SE153336 | C | CB | Square D | HLL36050 | 100 | 50 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a | E40610 V12 S16
SE153336 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a | E40610 V12 S16
SE153336 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 7a | E40610 V12 S16
SE153337 | C | CB | Square D | HLL36050 | 100 | 50 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a | E40610 V12 S16
SE153337 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a | E40610 V12 S16
SE153337 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 7a | E40610 V12 S16
SE153338 | C | CB | Square D | HLL36040 | 100 | 40 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a | E40610 V12 S16
SE153338 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a | E40610 V12 S16
SE153338 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 7a | E40610 V12 S16
SE153339 | C | CB | Square D | HLL36020 | 100 | 20 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 7a | E40610 V12 S16
SE153339 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 7a | E40610 V12 S16
SE153339 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 7a | E40610 V12 S16
SE153340 | C | CB | Square D | HLL36020 | 50 | 20 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 2289 | 1, 7b | E40610 V12 S16
SE153340 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 2289 | 1, 7b | E40610 V12 S16
SE153340 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 2289 | 1, 7b | E40610 V12 S16
SE153341 | C | CB | Square D | HLL36070 | 100 | 70 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 7k | E40610 V12 S16
SE153341 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 7k | E40610 V12 S16
SE153341 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 7k | E40610 V12 S16
SE153342 | C | CB | Square D | HLL36070 | 100 | 70 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 7k | E40610 V12 S16
SE153342 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 7k | E40610 V12 S16
SE153342 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 7k | E40610 V12 S16
SE153343 | C | CB | Square D | HLL36060 | 100 | 60 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a | E40610 V12 S16
SE153343 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a | E40610 V12 S16
SE153343 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 7a | E40610 V12 S16
SE153344 | C | CB | Square D | HLL36030 | 100 | 30 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a | E40610 V12 S16
SE153344 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a | E40610 V12 S16
SE153344 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 7a | E40610 V12 S16
SE153345 | C | CB | Square D | HLL36025 | 50 | 25 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 2289 | 1, 7b | E40610 V12 S16
SE153345 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 2289 | 1, 7b | E40610 V12 S16
SE153345 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 2289 | 1, 7b | E40610 V12 S16
SE153346 | C | CB | Square D | HLL36090 | 100 | 90 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2289 | 1, 7b | E40610 V12 S16
SE153346 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2289 | 1, 7b | E40610 V12 S16
SE153346 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2289 | 1, 7b | E40610 V12 S16
SE153347 | C | CB | Square D | HLL36090 | 100 | 90 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2289 | 1, 7b | E40610 V12 S16
SE153347 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2289 | 1, 7b | E40610 V12 S16
SE153347 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2289 | 1, 7b | E40610 V12 S16
SE153348 | C | CB | Square D | HLL36070 | 100 | 70 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 7k | E40610 V12 S16
SE153348 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 7k | E40610 V12 S16
SE153348 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 7k | E40610 V12 S16
SE153349 | C | CB | Square D | HLL36040 | 100 | 40 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 7a | E40610 V12 S16
SE153349 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 7a | E40610 V12 S16
SE153349 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 7a | E40610 V12 S16
SE153350 | C | CB | Square D | HLL36030 | 50 | 30 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 2289 | 1, 7b | E40610 V12 S16
SE153350 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 2289 | 1, 7b | E40610 V12 S16
SE153350 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 2289 | 1, 7b | E40610 V12 S16
SE153351 | C | CB | Square D | HLL36125 | 100 | 125 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 7l | E40610 V12 S16
SE153351 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 7l | E40610 V12 S16
SE153351 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 7l | E40610 V12 S16
SE153352 | C | CB | Square D | HLL36125 | 100 | 125 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 7l | E40610 V12 S16
SE153352 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 7l | E40610 V12 S16
SE153352 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 7l | E40610 V12 S16
SE153353 | C | CB | Square D | HLL36110 | 100 | 110 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 7b | E40610 V12 S16
SE153353 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 7b | E40610 V12 S16
SE153353 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 7b | E40610 V12 S16
SE153354 | C | CB | Square D | HLL36060 | 100 | 60 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 7a | E40610 V12 S16
SE153354 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 7a | E40610 V12 S16
SE153354 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 7a | E40610 V12 S16
SE153355 | C | CB | Square D | HLL36045 | 50 | 45 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 2289 | 1, 7b | E40610 V12 S16
SE153355 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 2289 | 1, 7b | E40610 V12 S16
SE153355 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 2289 | 1, 7b | E40610 V12 S16
SE153356 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 3663 | 1, 7l | E40610 V12 S16
SE153356 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 3663 | 1, 7l | E40610 V12 S16
SE153356 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 3663 | 1, 7l | E40610 V12 S16
SE153357 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 3663 | 1, 7l | E40610 V12 S16
SE153357 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 3663 | 1, 7l | E40610 V12 S16
SE153357 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 3663 | 1, 7l | E40610 V12 S16
SE153358 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 7l | E40610 V12 S16
SE153358 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 7l | E40610 V12 S16
SE153358 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 7l | E40610 V12 S16
SE153359 | C | CB | Square D | HLL36070 | 100 | 70 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 7k | E40610 V12 S16
SE153359 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 7k | E40610 V12 S16
SE153359 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 7k | E40610 V12 S16
SE153360 | C | CB | Square D | HLL36060 | 50 | 60 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 2289 | 1, 7b | E40610 V12 S16
SE153360 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 2289 | 1, 7b | E40610 V12 S16
SE153360 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 2289 | 1, 7b | E40610 V12 S16
SE153361 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 3663 | 1, 7l | E40610 V12 S16
SE153361 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 3663 | 1, 7l | E40610 V12 S16
SE153361 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 3663 | 1, 7l | E40610 V12 S16
SE153362 | C | CB | Square D | HLL36090 | 100 | 90 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2289 | 1, 7b | E40610 V12 S16
SE153362 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2289 | 1, 7b | E40610 V12 S16
SE153362 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2289 | 1, 7b | E40610 V12 S16
SE153363 | C | CB | Square D | HLL36070 | 50 | 70 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2289 | 1, 7b | E40610 V12 S16
SE153363 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2289 | 1, 7b | E40610 V12 S16
SE153363 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2289 | 1, 7b | E40610 V12 S16
SE153364 | C | CB | Square D | HLL36100 | 100 | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2289 | 1, 7b | E40610 V12 S16
SE153364 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2289 | 1, 7b | E40610 V12 S16
SE153364 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2289 | 1, 7b | E40610 V12 S16
SE153365 | C | CB | Square D | HLL36080 | 50 | 80 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2289 | 1, 7b | E40610 V12 S16
SE153365 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2289 | 1, 7b | E40610 V12 S16
SE153365 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2289 | 1, 7b | E40610 V12 S16
SE153366 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2289 | 1, 7l | E40610 V12 S16
SE153366 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2289 | 1, 7l | E40610 V12 S16
SE153366 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2289 | 1, 7l | E40610 V12 S16
SE153367 | C | CB | Square D | HLL36110 | 50 | 110 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2289 | 1, 7b | E40610 V12 S16
SE153367 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2289 | 1, 7b | E40610 V12 S16
SE153367 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2289 | 1, 7b | E40610 V12 S16
SE153368 | C | CB | Square D | HLL36150 | 100 | 150 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3663 | 1, 7l | E40610 V12 S16
SE153368 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3663 | 1, 7l | E40610 V12 S16
SE153368 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3663 | 1, 7l | E40610 V12 S16
SE153369 | C | CB | Square D | HLL36150 | 50 | 150 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2289 | 1, 7l | E40610 V12 S16
SE153369 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2289 | 1, 7l | E40610 V12 S16
SE153369 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2289 | 1, 7l | E40610 V12 S16
SE153370 | C | CB | Square D | HLL36175 | 50 | 175 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3663 | 1, 7l | E40610 V12 S16
SE153370 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3663 | 1, 7l | E40610 V12 S16
SE153370 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3663 | 1, 7l | E40610 V12 S16
SE154012 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 7a | E40610 V12 S15
SE154012 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 7a | E40610 V12 S15
SE154012 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 7a | E40610 V12 S15
SE154013 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 0.5 | 0.9 | 2289 | 1, 7b | E40610 V12 S15
SE154013 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 0.5 | 0.9 | 2289 | 1, 7b | E40610 V12 S15
SE154013 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 50 | 600 | 3 | 0.5 | 0.9 | 2289 | 1, 7b | E40610 V12 S15
SE154014 | C | CB | Square D | HLL36015 | 100 | 15 | 600 | 3 | 100 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 7a | E40610 V12 S16
SE154014 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 7a | E40610 V12 S16
SE154014 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 100 | 480 | 3 | 0.5 | 1.1 | 1832 | 1, 7a | E40610 V12 S16
SE154015 | C | CB | Square D | HLL36015 | 50 | 15 | 600 | 3 | 50 | 600 | 3 | 0.5 | 0.9 | 2289 | 1, 7b | E40610 V12 S16
SE154015 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 0.5 | 0.9 | 2289 | 1, 7b | E40610 V12 S16
SE154015 |  | OLR | Telemecanique | LRD05 | 5 | 0.63 - 1 | 600 | 3 | 50 | 600 | 3 | 0.5 | 0.9 | 2289 | 1, 7b | E40610 V12 S16

## HJ-MCP
Issued: 2007-03-15
Last Revised: 2007-03-15
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE153419 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153419 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153419 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153420 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153420 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153420 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153421 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153421 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153421 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153422 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153422 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153422 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153423 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153423 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153423 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153424 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153424 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153424 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153425 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153425 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153425 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153426 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153426 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153426 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153427 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153427 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153427 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153428 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153428 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153428 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153429 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153429 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153429 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153430 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 1 | 1.7 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153430 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 1 | 1.7 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153430 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 25 | 600 | 3 | 1 | 1.7 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153431 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153431 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153431 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153432 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153432 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153432 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153433 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153433 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153433 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153434 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153434 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153434 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153435 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153435 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153435 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 25 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153436 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153436 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153436 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153437 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153437 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153437 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153438 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153438 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153438 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153439 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153439 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153439 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153440 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 2 | 2.7 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153440 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 2 | 2.7 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153440 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 25 | 600 | 3 | 2 | 2.7 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153441 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153441 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153441 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153442 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153442 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153442 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153443 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153443 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153443 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153444 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153444 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153444 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153445 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 3 | 3.9 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153445 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 3 | 3.9 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153445 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 25 | 600 | 3 | 3 | 3.9 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153446 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153446 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153446 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153447 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153447 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153447 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153448 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153448 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153448 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153449 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153449 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153449 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153450 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 5 | 6.1 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153450 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 5 | 6.1 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153450 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 25 | 600 | 3 | 5 | 6.1 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153451 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 7k | E40610 V12 S15
SE153451 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 7k | E40610 V12 S15
SE153451 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 7k | E40610 V12 S15
SE153452 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 7k | E40610 V12 S15
SE153452 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 7k | E40610 V12 S15
SE153452 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 7k | E40610 V12 S15
SE153453 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153453 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153453 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153454 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153454 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153454 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153455 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153455 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153455 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153456 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153456 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153456 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153457 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153457 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153457 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153458 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 7k | E40610 V12 S15
SE153458 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 7k | E40610 V12 S15
SE153458 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 7k | E40610 V12 S15
SE153459 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153459 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153459 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153460 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153460 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153460 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153461 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153461 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153461 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153462 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153462 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153462 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153463 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153463 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153463 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153464 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153464 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153464 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153465 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153465 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153465 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153466 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153466 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153466 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153467 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153467 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153467 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153468 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153468 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153468 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153469 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 5, 7k | E40610 V12 S15
SE153469 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 5, 7k | E40610 V12 S15
SE153469 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 5, 7k | E40610 V12 S15
SE153470 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153470 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153470 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153471 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153471 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153471 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153472 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153472 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153472 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153473 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153473 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153473 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153474 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153474 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153474 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153475 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153475 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153475 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153476 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153476 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153476 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153477 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153477 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153477 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153478 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153478 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153478 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153479 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153479 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153479 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153480 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153480 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153480 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153481 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153481 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153481 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153482 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153482 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153482 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153483 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153483 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153483 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153484 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153484 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153484 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153485 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153485 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153485 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153486 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153486 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153486 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153487 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153487 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153487 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 65 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153488 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153488 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153488 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153489 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153489 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153489 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153490 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153490 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153490 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153491 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153491 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153491 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 65 | 480 | 3 | 1 | 2.1 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153492 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 1 | 1.7 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153492 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 1 | 1.7 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153492 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 25 | 600 | 3 | 1 | 1.7 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153493 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153493 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153493 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153494 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153494 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153494 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153495 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153495 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153495 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153496 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153496 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153496 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 65 | 480 | 3 | 1.5 | 3 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153497 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153497 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153497 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 25 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153498 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153498 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153498 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153499 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153499 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153499 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153500 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153500 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153500 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153501 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153501 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153501 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 65 | 480 | 3 | 2 | 3.4 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153502 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 2 | 2.7 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153502 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 2 | 2.7 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153502 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 25 | 600 | 3 | 2 | 2.7 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153503 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153503 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153503 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153504 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153504 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153504 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153505 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153505 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153505 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153506 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153506 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153506 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 65 | 480 | 3 | 3 | 4.8 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153507 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 3 | 3.9 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153507 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 3 | 3.9 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153507 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 25 | 600 | 3 | 3 | 3.9 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153508 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153508 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153508 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153509 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153509 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153509 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153510 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153510 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153510 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153511 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153511 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153511 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 65 | 480 | 3 | 5 | 7.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153512 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 5 | 6.1 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153512 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 5 | 6.1 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153512 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 25 | 600 | 3 | 5 | 6.1 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153513 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 7k | E40610 V12 S16
SE153513 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 7k | E40610 V12 S16
SE153513 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 7k | E40610 V12 S16
SE153514 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 7k | E40610 V12 S16
SE153514 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 7k | E40610 V12 S16
SE153514 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 7k | E40610 V12 S16
SE153515 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153515 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153515 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153516 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153516 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153516 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 65 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153517 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153517 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153517 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 25 | 600 | 3 | 7.5 | 9 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153518 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153518 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153518 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153519 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153519 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153519 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153520 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 7k | E40610 V12 S16
SE153520 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 7k | E40610 V12 S16
SE153520 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 7k | E40610 V12 S16
SE153521 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153521 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153521 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 65 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153522 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153522 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153522 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 25 | 600 | 3 | 10 | 11 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153523 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153523 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153523 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153524 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153524 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153524 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153525 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153525 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153525 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153526 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153526 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153526 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 65 | 480 | 3 | 15 | 21 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153527 | D | ICB | Square D | HJL36030M71 | - | 30 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153527 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153527 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 25 | 600 | 3 | 15 | 17 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153528 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 3663 | 1, 5, 7l | E40610 V12 S16
SE153528 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 3663 | 1, 5, 7l | E40610 V12 S16
SE153528 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 3663 | 1, 5, 7l | E40610 V12 S16
SE153529 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 3663 | 1, 5, 7l | E40610 V12 S16
SE153529 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 3663 | 1, 5, 7l | E40610 V12 S16
SE153529 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 3663 | 1, 5, 7l | E40610 V12 S16
SE153530 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153530 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153530 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153531 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 5, 7k | E40610 V12 S16
SE153531 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 5, 7k | E40610 V12 S16
SE153531 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 65 | 480 | 3 | 20 | 27 | 1832 | 1, 5, 7k | E40610 V12 S16
SE153532 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153532 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153532 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 25 | 600 | 3 | 20 | 22 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153533 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 3663 | 1, 5, 7l | E40610 V12 S16
SE153533 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 3663 | 1, 5, 7l | E40610 V12 S16
SE153533 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 3663 | 1, 5, 7l | E40610 V12 S16
SE153534 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153534 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153534 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 65 | 480 | 3 | 25 | 34 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153535 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153535 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153535 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 25 | 600 | 3 | 25 | 27 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153536 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153536 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153536 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 65 | 480 | 3 | 30 | 40 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153537 | D | ICB | Square D | HJL36050M72 | - | 50 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153537 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153537 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 25 | 600 | 3 | 30 | 32 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153538 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153538 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153538 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 65 | 480 | 3 | 40 | 52 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153539 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153539 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153539 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 25 | 600 | 3 | 40 | 41 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153540 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3663 | 1, 5, 7l | E40610 V12 S16
SE153540 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3663 | 1, 5, 7l | E40610 V12 S16
SE153540 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 65 | 480 | 3 | 50 | 65 | 3663 | 1, 5, 7l | E40610 V12 S16
SE153541 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153541 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153541 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 25 | 600 | 3 | 50 | 52 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153542 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3663 | 1, 5, 7l | E40610 V12 S16
SE153542 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3663 | 1, 5, 7l | E40610 V12 S16
SE153542 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3663 | 1, 5, 7l | E40610 V12 S16

## HL-MCP
Issued: 2007-03-15
Last Revised: 2007-03-15
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE153543 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153543 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153543 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153544 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153544 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153544 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153545 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153545 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153545 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153546 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153546 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153546 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153547 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153547 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153547 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153548 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153548 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153548 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153549 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153549 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153549 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153550 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153550 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153550 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153551 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153551 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153551 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153552 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153552 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153552 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153553 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153553 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153553 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153554 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153554 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153554 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153555 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153555 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153555 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153556 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153556 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153556 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153557 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153557 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153557 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153558 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153558 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153558 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153559 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153559 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153559 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153560 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153560 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153560 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153561 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153561 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153561 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153562 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153562 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153562 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153563 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153563 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153563 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153564 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153564 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153564 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153565 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153565 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153565 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153566 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153566 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153566 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153567 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153567 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153567 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153568 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153568 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153568 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153569 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153569 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153569 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153570 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153570 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153570 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153571 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153571 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153571 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153572 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153572 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153572 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153573 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153573 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153573 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153574 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153574 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153574 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153575 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 7k | E40610 V12 S15
SE153575 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 7k | E40610 V12 S15
SE153575 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 7k | E40610 V12 S15
SE153576 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 7k | E40610 V12 S15
SE153576 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 7k | E40610 V12 S15
SE153576 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 7k | E40610 V12 S15
SE153577 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153577 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153577 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153578 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153578 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153578 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153579 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153579 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153579 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153580 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153580 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153580 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153581 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153581 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153581 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153582 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 7k | E40610 V12 S15
SE153582 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 7k | E40610 V12 S15
SE153582 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 7k | E40610 V12 S15
SE153583 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153583 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153583 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153584 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153584 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153584 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153585 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153585 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153585 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153586 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153586 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153586 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153587 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153587 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153587 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153588 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153588 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153588 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 5, 7a | E40610 V12 S15
SE153589 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153589 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153589 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153590 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153590 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153590 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153591 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153591 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153591 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153592 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153592 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153592 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153593 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 5, 7k | E40610 V12 S15
SE153593 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 5, 7k | E40610 V12 S15
SE153593 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 5, 7k | E40610 V12 S15
SE153594 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153594 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153594 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153595 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153595 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153595 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153596 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153596 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153596 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153597 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153597 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153597 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153598 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153598 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153598 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153599 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153599 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153599 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153600 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153600 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153600 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153601 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153601 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153601 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2289 | 1, 5, 7b | E40610 V12 S15
SE153602 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153602 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153602 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153603 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153603 |  | MC | Telemecanique | LC1D65 | 5 | 65 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153603 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153604 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153604 |  | MC | Telemecanique | LC1D80 | 5 | 80 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153604 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153605 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153605 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153605 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153606 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153606 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153606 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153607 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153607 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153607 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153608 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153608 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153608 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153609 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153609 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153609 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153610 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153610 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153610 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153611 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153611 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153611 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153612 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153612 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153612 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153613 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153613 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153613 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153614 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153614 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153614 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153615 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153615 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153615 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153616 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153616 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153616 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 50 | 600 | 3 | 1 | 1.7 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153617 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153617 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153617 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153618 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153618 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153618 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153619 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153619 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153619 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153620 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153620 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153620 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153621 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153621 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153621 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 50 | 600 | 3 | 1.5 | 2.4 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153622 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153622 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153622 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153623 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153623 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153623 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153624 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153624 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153624 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153625 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153625 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153625 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153626 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153626 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153626 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 50 | 600 | 3 | 2 | 2.7 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153627 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153627 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153627 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153628 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153628 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153628 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153629 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153629 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153629 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153630 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153630 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153630 |  | OLR | Telemecanique | LRD10 | 5 | 4 - 6 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153631 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153631 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153631 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 50 | 600 | 3 | 3 | 3.9 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153632 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153632 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153632 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 200 | 3 | 5 | 17.5 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153633 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153633 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153633 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 208 | 3 | 5 | 16.7 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153634 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153634 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153634 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153635 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153635 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153635 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153636 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153636 |  | MC | Telemecanique | LC2D240 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153636 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 50 | 600 | 3 | 5 | 6.1 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153637 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 7k | E40610 V12 S16
SE153637 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 7k | E40610 V12 S16
SE153637 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1832 | 1, 5, 7k | E40610 V12 S16
SE153638 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 7k | E40610 V12 S16
SE153638 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 7k | E40610 V12 S16
SE153638 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1832 | 1, 5, 7k | E40610 V12 S16
SE153639 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153639 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153639 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153640 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153640 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153640 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153641 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153641 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153641 |  | OLR | Telemecanique | LRD14 | 5 | 7 - 10 | 600 | 3 | 50 | 600 | 3 | 7.5 | 9 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153642 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153642 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153642 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153643 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153643 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153643 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153644 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 7k | E40610 V12 S16
SE153644 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 7k | E40610 V12 S16
SE153644 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1832 | 1, 5, 7k | E40610 V12 S16
SE153645 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153645 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153645 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153646 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153646 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153646 |  | OLR | Telemecanique | LRD16 | 5 | 9 - 13 | 600 | 3 | 50 | 600 | 3 | 10 | 11 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153647 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153647 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153647 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 200 | 3 | 15 | 48.3 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153648 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153648 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153648 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 208 | 3 | 15 | 46.2 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153649 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153649 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153649 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153650 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153650 |  | MC | Telemecanique | LC2D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153650 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1832 | 1, 5, 7a | E40610 V12 S16
SE153651 | D | ICB | Square D | HLL36030M71 | - | 30 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153651 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153651 |  | OLR | Telemecanique | LRD21 | 5 | 12 - 18 | 600 | 3 | 50 | 600 | 3 | 15 | 17 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153652 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 3663 | 1, 5, 7l | E40610 V12 S16
SE153652 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 3663 | 1, 5, 7l | E40610 V12 S16
SE153652 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 200 | 3 | 20 | 62.1 | 3663 | 1, 5, 7l | E40610 V12 S16
SE153653 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 3663 | 1, 5, 7l | E40610 V12 S16
SE153653 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 3663 | 1, 5, 7l | E40610 V12 S16
SE153653 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 208 | 3 | 20 | 59.4 | 3663 | 1, 5, 7l | E40610 V12 S16
SE153654 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153654 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153654 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 100 | 240 | 3 | 20 | 54 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153655 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 5, 7k | E40610 V12 S16
SE153655 |  | MC | Telemecanique | LC2D32 | 5 | 32 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 5, 7k | E40610 V12 S16
SE153655 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1832 | 1, 5, 7k | E40610 V12 S16
SE153656 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153656 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153656 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 50 | 600 | 3 | 20 | 22 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153657 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 3663 | 1, 5, 7l | E40610 V12 S16
SE153657 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 3663 | 1, 5, 7l | E40610 V12 S16
SE153657 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 240 | 3 | 25 | 68 | 3663 | 1, 5, 7l | E40610 V12 S16
SE153658 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153658 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153658 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153659 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153659 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153659 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 50 | 600 | 3 | 25 | 27 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153660 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153660 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153660 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153661 | D | ICB | Square D | HLL36050M72 | - | 50 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153661 |  | MC | Telemecanique | LC2D40 | 5 | 40 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153661 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 50 | 600 | 3 | 30 | 32 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153662 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153662 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153662 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 100 | 480 | 3 | 40 | 52 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153663 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153663 |  | MC | Telemecanique | LC2D50 | 5 | 50 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153663 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 50 | 600 | 3 | 40 | 41 | 2289 | 1, 5, 7b | E40610 V12 S16
SE153664 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3663 | 1, 5, 7l | E40610 V12 S16
SE153664 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3663 | 1, 5, 7l | E40610 V12 S16
SE153664 |  | OLR | Telemecanique | LRD3361 | 5 | 55 - 70 | 600 | 3 | 100 | 480 | 3 | 50 | 65 | 3663 | 1, 5, 7l | E40610 V12 S16
SE153665 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153665 |  | MC | Telemecanique | LC2D65 | 5 | 65 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153665 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 50 | 600 | 3 | 50 | 52 | 2289 | 1, 5, 7l | E40610 V12 S16
SE153666 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3663 | 1, 5, 7l | E40610 V12 S16
SE153666 |  | MC | Telemecanique | LC2D80 | 5 | 80 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3663 | 1, 5, 7l | E40610 V12 S16
SE153666 |  | OLR | Telemecanique | LRD3359 | 5 | 48 - 65 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3663 | 1, 5, 7l | E40610 V12 S16

## D80-F185
Issued: 2007-01-23
Last Revised: 2008-04-15
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE153667 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153667 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153667 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153668 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153668 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153668 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153669 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153669 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153669 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153670 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153669 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153670 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153671 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153671 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153671 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153672 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153672 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153672 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153673 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153673 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153673 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153674 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153674 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153674 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153675 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153675 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153675 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153676 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 5, 7d | E40610 V12 S15
SE153676 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 5, 7d | E40610 V12 S15
SE153676 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 5, 7d | E40610 V12 S15
SE153677 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 5, 7d | E40610 V12 S15
SE153677 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 5, 7d | E40610 V12 S15
SE153677 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 5, 7d | E40610 V12 S15
SE153678 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 5, 7d | E40610 V12 S15
SE153678 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 5, 7d | E40610 V12 S15
SE153678 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 5, 7d | E40610 V12 S15
SE153679 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153679 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153679 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153680 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153680 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153680 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153681 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153681 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153681 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153682 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153681 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153682 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 2289 | 1, 5, 7l | E40610 V12 S15
SE153683 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153683 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153683 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153684 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153684 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153684 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153685 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153685 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153685 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153686 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153686 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153686 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153687 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153687 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153687 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 2747 | 1, 5, 7n | E40610 V12 S15
SE153688 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 42 | 600 | 3 | 100 | 99 | 3205 | 1, 5, 7d | E40610 V12 S15
SE153688 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 42 | 600 | 3 | 100 | 99 | 3205 | 1, 5, 7d | E40610 V12 S15
SE153688 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 42 | 600 | 3 | 100 | 99 | 3205 | 1, 5, 7d | E40610 V12 S15
SE153689 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 5, 7d | E40610 V12 S15
SE153689 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 5, 7d | E40610 V12 S15
SE153689 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 200 | 3 | 40 | 120 | 3205 | 1, 5, 7d | E40610 V12 S15
SE153690 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 5, 7d | E40610 V12 S15
SE153690 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 5, 7d | E40610 V12 S15
SE153690 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 5, 7d | E40610 V12 S15
SE153691 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 5, 7d | E40610 V12 S15
SE153691 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 5, 7d | E40610 V12 S15
SE153691 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 5, 7d | E40610 V12 S15
SE153692 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 3205 | 1, 5, 7d | E40610 V12 S15
SE153692 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 3205 | 1, 5, 7d | E40610 V12 S15
SE153692 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 3205 | 1, 5, 7d | E40610 V12 S15
SE157900 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157900 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157900 |  | OLR | Telemecanique | LR9F5369 | 5 | 90 - 150 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157900 |  | OLR | Telemecanique | LR9F5569 | 5 | 90 - 150 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157901 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 100 | 200 | 3 | 50 | 150 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157901 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 200 | 3 | 50 | 150 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157901 |  | OLR | Telemecanique | LR9F5369 | 5 | 90 - 150 | 600 | 3 | 100 | 200 | 3 | 50 | 150 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157901 |  | OLR | Telemecanique | LR9F5569 | 5 | 90 - 150 | 600 | 3 | 100 | 200 | 3 | 50 | 150 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157902 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157902 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157902 |  | OLR | Telemecanique | LR9F5369 | 5 | 90 - 150 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157902 |  | OLR | Telemecanique | LR9F5569 | 5 | 90 - 150 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157903 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157903 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157903 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157903 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157904 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157904 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157904 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157904 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 5036 | 1, 5, 7p | E40610 V12 S15
SE153698 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 5, 7d | E40610 V12 S15
SE153698 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 5, 7d | E40610 V12 S15
SE153698 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 5, 7d | E40610 V12 S15
SE153699 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 3205 | 1, 5, 7d | E40610 V12 S15
SE153699 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 3205 | 1, 5, 7d | E40610 V12 S15
SE153699 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 3205 | 1, 5, 7d | E40610 V12 S15
SE157905 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 50 | 600 | 3 | 125 | 125 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157905 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 50 | 600 | 3 | 125 | 125 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157905 |  | OLR | Telemecanique | LR9F5369 | 5 | 90 - 150 | 600 | 3 | 50 | 600 | 3 | 125 | 125 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157905 |  | OLR | Telemecanique | LR9F5569 | 5 | 90 - 150 | 600 | 3 | 50 | 600 | 3 | 125 | 125 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157906 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 200 | 3 | 50 | 150 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157906 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 200 | 3 | 50 | 150 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157906 |  | OLR | Telemecanique | LR9F5369 | 5 | 90 - 150 | 600 | 3 | 100 | 200 | 3 | 50 | 150 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157906 |  | OLR | Telemecanique | LR9F5569 | 5 | 90 - 150 | 600 | 3 | 100 | 200 | 3 | 50 | 150 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157907 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157907 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157907 |  | OLR | Telemecanique | LR9F5369 | 5 | 90 - 150 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157907 |  | OLR | Telemecanique | LR9F5569 | 5 | 90 - 150 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157908 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157908 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157908 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157908 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157909 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157909 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157909 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 5036 | 1, 5, 7p | E40610 V12 S15
SE157909 |  | OLR | Telemecanique | LR9F5571 | 5 | 132 - 220 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 5036 | 1, 5, 7p | E40610 V12 S15
SE153705 | C | CB | Square D | JGL36200 | 65 | 200 | 600 | 3 | 65 | 200 | 3 | 25 | 78.2 | 2289 | 1, 7l | E40610 V12 S15
SE153705 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 65 | 200 | 3 | 25 | 78.2 | 2289 | 1, 7l | E40610 V12 S15
SE153705 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 65 | 200 | 3 | 25 | 78.2 | 2289 | 1, 7l | E40610 V12 S15
SE153706 | C | CB | Square D | JGL36200 | 65 | 200 | 600 | 3 | 65 | 208 | 3 | 25 | 74.8 | 2289 | 1, 7l | E40610 V12 S15
SE153706 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 65 | 208 | 3 | 25 | 74.8 | 2289 | 1, 7l | E40610 V12 S15
SE153706 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 65 | 208 | 3 | 25 | 74.8 | 2289 | 1, 7l | E40610 V12 S15
SE153707 | C | CB | Square D | JGL36200 | 65 | 200 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 2289 | 1, 7l | E40610 V12 S15
SE153707 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 2289 | 1, 7l | E40610 V12 S15
SE153707 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 2289 | 1, 7l | E40610 V12 S15
SE153708 | C | CB | Square D | JGL36200 | 35 | 200 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 2289 | 1, 7l | E40610 V12 S15
SE153707 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 2289 | 1, 7l | E40610 V12 S15
SE153708 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 2289 | 1, 7l | E40610 V12 S15
SE153709 | C | CB | Square D | JGL36250 | 65 | 250 | 600 | 3 | 65 | 200 | 3 | 30 | 92 | 2747 | 1, 7n | E40610 V12 S15
SE153709 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 65 | 200 | 3 | 30 | 92 | 2747 | 1, 7n | E40610 V12 S15
SE153709 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 65 | 200 | 3 | 30 | 92 | 2747 | 1, 7n | E40610 V12 S15
SE153710 | C | CB | Square D | JGL36200 | 65 | 200 | 600 | 3 | 65 | 208 | 3 | 30 | 88 | 2747 | 1, 7n | E40610 V12 S15
SE153710 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 65 | 208 | 3 | 30 | 88 | 2747 | 1, 7n | E40610 V12 S15
SE153710 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 65 | 208 | 3 | 30 | 88 | 2747 | 1, 7n | E40610 V12 S15
SE153711 | C | CB | Square D | JGL36250 | 65 | 250 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 2747 | 1, 7n | E40610 V12 S15
SE153711 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 2747 | 1, 7n | E40610 V12 S15
SE153711 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 2747 | 1, 7n | E40610 V12 S15
SE153712 | C | CB | Square D | JGL36250 | 35 | 250 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 2747 | 1, 7n | E40610 V12 S15
SE153712 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 2747 | 1, 7n | E40610 V12 S15
SE153712 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 2747 | 1, 7n | E40610 V12 S15
SE153713 | C | CB | Square D | JGL36250 | 65 | 250 | 600 | 3 | 65 | 208 | 3 | 40 | 114 | 3205 | 1, 7d | E40610 V12 S15
SE153713 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 65 | 208 | 3 | 40 | 114 | 3205 | 1, 7d | E40610 V12 S15
SE153713 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 65 | 208 | 3 | 40 | 114 | 3205 | 1, 7d | E40610 V12 S15
SE153714 | C | CB | Square D | JJL36200 | 100 | 200 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2289 | 1, 7l | E40610 V12 S15
SE153714 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2289 | 1, 7l | E40610 V12 S15
SE153714 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2289 | 1, 7l | E40610 V12 S15
SE153715 | C | CB | Square D | JJL36200 | 100 | 200 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2289 | 1, 7l | E40610 V12 S15
SE153715 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2289 | 1, 7l | E40610 V12 S15
SE153715 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2289 | 1, 7l | E40610 V12 S15
SE153716 | C | CB | Square D | JJL36200 | 100 | 200 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2289 | 1, 7l | E40610 V12 S15
SE153716 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2289 | 1, 7l | E40610 V12 S15
SE153716 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2289 | 1, 7l | E40610 V12 S15
SE153717 | C | CB | Square D | JJL36200 | 65 | 200 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 2289 | 1, 7l | E40610 V12 S15
SE153716 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 2289 | 1, 7l | E40610 V12 S15
SE153717 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 2289 | 1, 7l | E40610 V12 S15
SE153718 | C | CB | Square D | JJL36200 | 25 | 200 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 2747 | 1, 7n | E40610 V12 S15
SE153718 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 2747 | 1, 7n | E40610 V12 S15
SE153718 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 2747 | 1, 7n | E40610 V12 S15
SE153719 | C | CB | Square D | JJL36250 | 100 | 250 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 2747 | 1, 7n | E40610 V12 S15
SE153719 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 2747 | 1, 7n | E40610 V12 S15
SE153719 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 2747 | 1, 7n | E40610 V12 S15
SE153720 | C | CB | Square D | JJL36200 | 100 | 200 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 2747 | 1, 7n | E40610 V12 S15
SE153720 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 2747 | 1, 7n | E40610 V12 S15
SE153720 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 2747 | 1, 7n | E40610 V12 S15
SE153721 | C | CB | Square D | JJL36250 | 100 | 250 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 2747 | 1, 7n | E40610 V12 S15
SE153721 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 2747 | 1, 7n | E40610 V12 S15
SE153721 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 2747 | 1, 7n | E40610 V12 S15
SE153722 | C | CB | Square D | JJL36250 | 65 | 250 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 2747 | 1, 7n | E40610 V12 S15
SE153722 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 2747 | 1, 7n | E40610 V12 S15
SE153722 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 2747 | 1, 7n | E40610 V12 S15
SE153723 | C | CB | Square D | JJL36250 | 25 | 250 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 7d | E40610 V12 S15
SE153723 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 7d | E40610 V12 S15
SE153723 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 3205 | 1, 7d | E40610 V12 S15
SE153724 | C | CB | Square D | JJL36250 | 100 | 250 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 7d | E40610 V12 S15
SE153724 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 7d | E40610 V12 S15
SE153724 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 7d | E40610 V12 S15
SE153725 | C | CB | Square D | JLL36200 | 100 | 200 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2289 | 1, 7l | E40610 V12 S15
SE153725 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2289 | 1, 7l | E40610 V12 S15
SE153725 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 100 | 200 | 3 | 25 | 78.2 | 2289 | 1, 7l | E40610 V12 S15
SE153726 | C | CB | Square D | JLL36200 | 100 | 200 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2289 | 1, 7l | E40610 V12 S15
SE153726 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2289 | 1, 7l | E40610 V12 S15
SE153726 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 2289 | 1, 7l | E40610 V12 S15
SE153727 | C | CB | Square D | JLL36200 | 100 | 200 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2289 | 1, 7l | E40610 V12 S15
SE153727 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2289 | 1, 7l | E40610 V12 S15
SE153727 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 2289 | 1, 7l | E40610 V12 S15
SE153728 | C | CB | Square D | JLL36200 | 100 | 200 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 2289 | 1, 7l | E40610 V12 S15
SE153727 |  | MC | Telemecanique | LC1D80 | 10 | 80 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 2289 | 1, 7l | E40610 V12 S15
SE153728 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 2289 | 1, 7l | E40610 V12 S15
SE153729 | C | CB | Square D | JLL36200 | 50 | 200 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 2747 | 1, 7n | E40610 V12 S15
SE153729 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 2747 | 1, 7n | E40610 V12 S15
SE153729 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 2747 | 1, 7n | E40610 V12 S15
SE153730 | C | CB | Square D | JLL36250 | 100 | 250 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 2747 | 1, 7n | E40610 V12 S15
SE153730 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 2747 | 1, 7n | E40610 V12 S15
SE153730 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 100 | 200 | 3 | 30 | 92 | 2747 | 1, 7n | E40610 V12 S15
SE153731 | C | CB | Square D | JLL36200 | 100 | 200 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 2747 | 1, 7n | E40610 V12 S15
SE153731 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 2747 | 1, 7n | E40610 V12 S15
SE153731 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 2747 | 1, 7n | E40610 V12 S15
SE153732 | C | CB | Square D | JLL36250 | 100 | 250 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 2747 | 1, 7n | E40610 V12 S15
SE153732 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 2747 | 1, 7n | E40610 V12 S15
SE153732 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 2747 | 1, 7n | E40610 V12 S15
SE153733 | C | CB | Square D | JLL36250 | 100 | 250 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 2747 | 1, 7n | E40610 V12 S15
SE153733 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 2747 | 1, 7n | E40610 V12 S15
SE153733 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 2747 | 1, 7n | E40610 V12 S15
SE153734 | C | CB | Square D | JLL36250 | 50 | 250 | 600 | 3 | 42 | 600 | 3 | 100 | 99 | 3205 | 1. 7d | E40610 V12 S15
SE153734 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 42 | 600 | 3 | 100 | 99 | 3205 | 1. 7d | E40610 V12 S15
SE153734 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 42 | 600 | 3 | 100 | 99 | 3205 | 1. 7d | E40610 V12 S15
SE153735 | C | CB | Square D | JLL36250 | 100 | 250 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 7d | E40610 V12 S15
SE153735 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 7d | E40610 V12 S15
SE153735 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 3205 | 1, 7d | E40610 V12 S15
SE154016 | C | CB | Square D | JGL36250 | 65 | 250 | 600 | 3 | 65 | 240 | 3 | 50 | 130 | 3205 | 1, 7d | E40610 V12 S15
SE154016 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 65 | 240 | 3 | 50 | 130 | 3205 | 1, 7l | E40610 V12 S15
SE154016 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 65 | 240 | 3 | 50 | 130 | 3205 | 1, 7l | E40610 V12 S15
SE154017 | C | CB | Square D | JJL36250 | 100 | 250 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 7d | E40610 V12 S15
SE154017 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 7l | E40610 V12 S15
SE154017 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 7l | E40610 V12 S15
SE154018 | C | CB | Square D | JLL36250 | 125 | 250 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 7d | E40610 V12 S15
SE154018 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 7l | E40610 V12 S15
SE154018 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 3205 | 1, 7l | E40610 V12 S15
SE154019 | C | CB | Square D | JGL36200 | 18 | 200 | 600 | 3 | 18 | 600 | 3 | 75 | 77 | 2747 | 1, 7n | E40610 V12 S15
SE154019 |  | MC | Telemecanique | LC1D115 | 10 | 115 | 600 | 3 | 18 | 600 | 3 | 75 | 77 | 2747 | 1, 7l | E40610 V12 S15
SE154019 |  | OLR | Telemecanique | LRD3363 | 5 | 63 - 80 | 600 | 3 | 18 | 600 | 3 | 75 | 77 | 2747 | 1, 7l | E40610 V12 S15
SE154020 | C | CB | Square D | JGL36250 | 18 | 250 | 600 | 3 | 18 | 600 | 3 | 100 | 99 | 3205 | 1, 7d | E40610 V12 S15
SE154020 |  | MC | Telemecanique | LC1D150 | 10 | 150 | 600 | 3 | 18 | 600 | 3 | 100 | 99 | 3205 | 1, 7l | E40610 V12 S15
SE154020 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 18 | 600 | 3 | 100 | 99 | 3205 | 1, 7l | E40610 V12 S15

## D80-F185-R
Issued: 2008-01-14
Last Revised: 2008-10-01
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Minimum Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE153900 | C | CB | Square D | JDL36200 | 25 | 200 | 600 | 3 | 25 | 208 | 3 | 25 | 74.8 | 3662 | 1, 7L | E40610 V12 S16
SE153900 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 25 | 208 | 3 | 25 | 74.8 | 3662 | 1, 7L | E40610 V12 S16
SE153900 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 25 | 208 | 3 | 25 | 74.8 | 3662 | 1, 7L | E40610 V12 S16
SE153901 | C | CB | Square D | JDL36200 | 25 | 200 | 600 | 3 | 25 | 208 | 3 | 30 | 88 | 5036 | 1, 7n | E40610 V12 S16
SE153901 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 25 | 208 | 3 | 30 | 88 | 5036 | 1, 7n | E40610 V12 S16
SE153901 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 25 | 208 | 3 | 30 | 88 | 5036 | 1, 7n | E40610 V12 S16
SE153902 | C | CB | Square D | JDL36250 | 25 | 250 | 600 | 3 | 25 | 208 | 3 | 40 | 114 | 5036 | 1, 7d | E40610 V12 S16
SE153902 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 25 | 208 | 3 | 40 | 114 | 5036 | 1, 7d | E40610 V12 S16
SE153902 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 25 | 208 | 3 | 40 | 114 | 5036 | 1, 7d | E40610 V12 S16
SE153903 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 3662 | 1, 5, 7L | E40610 V12 S16
SE153903 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 3662 | 1, 5, 7L | E40610 V12 S16
SE153903 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 3662 | 1, 5, 7L | E40610 V12 S16
SE153904 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 5036 | 1, 5, 7n | E40610 V12 S16
SE153904 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 5036 | 1, 5, 7n | E40610 V12 S16
SE153904 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 5036 | 1, 5, 7n | E40610 V12 S16
SE153905 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 5036 | 1, 5, 7d | E40610 V12 S16
SE153905 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 5036 | 1, 5, 7d | E40610 V12 S16
SE153905 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 5036 | 1, 5, 7d | E40610 V12 S16
SE153906 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153906 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153906 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153906 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153906 |  | OLR | Telemecanique | LR9F5369 | 5 | 90 - 150 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153907 | C | CB | Square D | JGL36200 | 65 | 200 | 600 | 3 | 65 | 208 | 3 | 25 | 74.8 | 3662 | 1, 7L | E40610 V12 S16
SE153907 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 65 | 208 | 3 | 25 | 74.8 | 3662 | 1, 7L | E40610 V12 S16
SE153907 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 65 | 208 | 3 | 25 | 74.8 | 3662 | 1, 7L | E40610 V12 S16
SE153908 | C | CB | Square D | JGL36200 | 65 | 200 | 600 | 3 | 65 | 208 | 3 | 30 | 88 | 5036 | 1, 7n | E40610 V12 S16
SE153908 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 65 | 208 | 3 | 30 | 88 | 5036 | 1, 7n | E40610 V12 S16
SE153908 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 65 | 208 | 3 | 30 | 88 | 5036 | 1, 7n | E40610 V12 S16
SE153909 | C | CB | Square D | JGL36250 | 65 | 250 | 600 | 3 | 65 | 208 | 3 | 40 | 114 | 5036 | 1, 7d | E40610 V12 S16
SE153909 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 65 | 208 | 3 | 40 | 114 | 5036 | 1, 7d | E40610 V12 S16
SE153909 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 65 | 208 | 3 | 40 | 114 | 5036 | 1, 7d | E40610 V12 S16
SE153910 | C | CB | Square D | JJL36200 | 100 | 200 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 3662 | 1, 7L | E40610 V12 S16
SE153910 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 3662 | 1, 7L | E40610 V12 S16
SE153910 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 3662 | 1, 7L | E40610 V12 S16
SE153911 | C | CB | Square D | JJL36200 | 100 | 200 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 5036 | 1, 7n | E40610 V12 S16
SE153911 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 5036 | 1, 7n | E40610 V12 S16
SE153911 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 5036 | 1, 7n | E40610 V12 S16
SE153912 | C | CB | Square D | JJL36250 | 100 | 250 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 5036 | 1, 7d | E40610 V12 S16
SE153912 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 5036 | 1, 7d | E40610 V12 S16
SE153912 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 5036 | 1, 7d | E40610 V12 S16
SE153913 | C | CB | Square D | JLL36200 | 125 | 200 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 3662 | 1, 7L | E40610 V12 S16
SE153913 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 3662 | 1, 7L | E40610 V12 S16
SE153913 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 3662 | 1, 7L | E40610 V12 S16
SE153914 | C | CB | Square D | JLL36200 | 125 | 200 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 5036 | 1, 7n | E40610 V12 S16
SE153914 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 5036 | 1, 7n | E40610 V12 S16
SE153914 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 5036 | 1, 7n | E40610 V12 S16
SE153915 | C | CB | Square D | JLL36250 | 125 | 250 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 5036 | 1, 7d | E40610 V12 S16
SE153915 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 5036 | 1, 7d | E40610 V12 S16
SE153915 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 5036 | 1, 7d | E40610 V12 S16
SE153916 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 3662 | 1, 5, 7L | E40610 V12 S16
SE153916 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 3662 | 1, 5, 7L | E40610 V12 S16
SE153916 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 100 | 208 | 3 | 25 | 74.8 | 3662 | 1, 5, 7L | E40610 V12 S16
SE153917 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 5036 | 1, 5, 7n | E40610 V12 S16
SE153917 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 5036 | 1, 5, 7n | E40610 V12 S16
SE153917 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 100 | 208 | 3 | 30 | 88 | 5036 | 1, 5, 7n | E40610 V12 S16
SE153918 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 5036 | 1, 5, 7d | E40610 V12 S16
SE153918 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 5036 | 1, 5, 7d | E40610 V12 S16
SE153918 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 208 | 3 | 40 | 114 | 5036 | 1, 5, 7d | E40610 V12 S16
SE153919 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153919 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153919 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153919 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153919 |  | OLR | Telemecanique | LR9F5369 | 5 | 90 - 150 | 600 | 3 | 100 | 208 | 3 | 50 | 143 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153920 | C | CB | Square D | JDL36200 | 25 | 200 | 600 | 3 | 25 | 240 | 3 | 30 | 80 | 3662 | 1, 7L | E40610 V12 S16
SE153920 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 25 | 240 | 3 | 30 | 80 | 3662 | 1, 7L | E40610 V12 S16
SE153920 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 25 | 240 | 3 | 30 | 80 | 3662 | 1, 7L | E40610 V12 S16
SE153921 | C | CB | Square D | JDL36250 | 25 | 250 | 600 | 3 | 25 | 240 | 3 | 40 | 104 | 5036 | 1, 7n | E40610 V12 S16
SE153921 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 25 | 240 | 3 | 40 | 104 | 5036 | 1, 7n | E40610 V12 S16
SE153921 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 25 | 240 | 3 | 40 | 104 | 5036 | 1, 7n | E40610 V12 S16
SE153922 | C | CB | Square D | JDL36250 | 25 | 250 | 600 | 3 | 25 | 240 | 3 | 50 | 130 | 5036 | 1, 7d | E40610 V12 S16
SE153922 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 25 | 240 | 3 | 50 | 130 | 5036 | 1, 7d | E40610 V12 S16
SE153922 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 25 | 240 | 3 | 50 | 130 | 5036 | 1, 7d | E40610 V12 S16
SE153923 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3662 | 1, 5, 7L | E40610 V12 S16
SE153923 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3662 | 1, 5, 7L | E40610 V12 S16
SE153923 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3662 | 1, 5, 7L | E40610 V12 S16
SE153924 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 5036 | 1, 5, 7n | E40610 V12 S16
SE153924 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 5036 | 1, 5, 7n | E40610 V12 S16
SE153924 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 5036 | 1, 5, 7n | E40610 V12 S16
SE153925 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 5036 | 1, 5, 7d | E40610 V12 S16
SE153925 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 5036 | 1, 5, 7d | E40610 V12 S16
SE153925 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 5036 | 1, 5, 7d | E40610 V12 S16
SE153926 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153926 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153926 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153926 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153926 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153927 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3662 | 1, 5, 7L | E40610 V12 S16
SE153927 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3662 | 1, 5, 7L | E40610 V12 S16
SE153927 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3662 | 1, 5, 7L | E40610 V12 S16
SE153928 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 5036 | 1, 5, 7n | E40610 V12 S16
SE153928 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 5036 | 1, 5, 7n | E40610 V12 S16
SE153928 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 5036 | 1, 5, 7n | E40610 V12 S16
SE153929 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 5036 | 1, 5, 7d | E40610 V12 S16
SE153929 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 5036 | 1, 5, 7d | E40610 V12 S16
SE153929 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 5036 | 1, 5, 7d | E40610 V12 S16
SE153930 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153930 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153930 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153930 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153930 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 240 | 3 | 60 | 154 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153931 | C | CB | Square D | JGL36200 | 65 | 200 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3662 | 1, 7L | E40610 V12 S16
SE153931 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3662 | 1, 7L | E40610 V12 S16
SE153931 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 65 | 240 | 3 | 30 | 80 | 3662 | 1, 7L | E40610 V12 S16
SE153932 | C | CB | Square D | JGL36250 | 65 | 250 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 5036 | 1, 7n | E40610 V12 S16
SE153932 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 5036 | 1, 7n | E40610 V12 S16
SE153932 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 65 | 240 | 3 | 40 | 104 | 5036 | 1, 7n | E40610 V12 S16
SE153933 | C | CB | Square D | JGL36250 | 65 | 250 | 600 | 3 | 65 | 240 | 3 | 50 | 130 | 5036 | 1, 7d | E40610 V12 S16
SE153933 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 65 | 240 | 3 | 50 | 130 | 5036 | 1, 7d | E40610 V12 S16
SE153933 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 65 | 240 | 3 | 50 | 130 | 5036 | 1, 7d | E40610 V12 S16
SE153934 | C | CB | Square D | JJL36200 | 100 | 200 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3662 | 1, 7L | E40610 V12 S16
SE153934 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3662 | 1, 7L | E40610 V12 S16
SE153934 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3662 | 1, 7L | E40610 V12 S16
SE153935 | C | CB | Square D | JJL36250 | 100 | 250 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 5036 | 1, 7n | E40610 V12 S16
SE153935 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 5036 | 1, 7n | E40610 V12 S16
SE153935 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 5036 | 1, 7n | E40610 V12 S16
SE153936 | C | CB | Square D | JJL36250 | 100 | 250 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 5036 | 1, 7d | E40610 V12 S16
SE153936 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 5036 | 1, 7d | E40610 V12 S16
SE153936 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 5036 | 1, 7d | E40610 V12 S16
SE153937 | C | CB | Square D | JLL36200 | 125 | 200 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3662 | 1, 7L | E40610 V12 S16
SE153937 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3662 | 1, 7L | E40610 V12 S16
SE153937 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 100 | 240 | 3 | 30 | 80 | 3662 | 1, 7L | E40610 V12 S16
SE153938 | C | CB | Square D | JLL36250 | 125 | 250 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 5036 | 1, 7n | E40610 V12 S16
SE153938 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 5036 | 1, 7n | E40610 V12 S16
SE153938 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 240 | 3 | 40 | 104 | 5036 | 1, 7n | E40610 V12 S16
SE153939 | C | CB | Square D | JLL36250 | 125 | 250 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 5036 | 1, 7d | E40610 V12 S16
SE153939 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 5036 | 1, 7d | E40610 V12 S16
SE153939 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 240 | 3 | 50 | 130 | 5036 | 1, 7d | E40610 V12 S16
SE153940 | C | CB | Square D | JDL36200 | 18 | 200 | 600 | 3 | 18 | 480 | 3 | 60 | 77 | 3662 | 1, 7L | E40610 V12 S16
SE153940 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 18 | 480 | 3 | 60 | 77 | 3662 | 1, 7L | E40610 V12 S16
SE153940 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 18 | 480 | 3 | 60 | 77 | 3662 | 1, 7L | E40610 V12 S16
SE153941 | C | CB | Square D | JDL36250 | 18 | 200 | 600 | 3 | 18 | 480 | 3 | 75 | 96 | 5036 | 1, 7n | E40610 V12 S16
SE153941 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 18 | 480 | 3 | 75 | 96 | 5036 | 1, 7n | E40610 V12 S16
SE153941 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 18 | 480 | 3 | 75 | 96 | 5036 | 1, 7n | E40610 V12 S16
SE153942 | C | CB | Square D | JDL36250 | 18 | 250 | 600 | 3 | 18 | 480 | 3 | 100 | 124 | 5036 | 1, 7d | E40610 V12 S16
SE153942 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 18 | 480 | 3 | 100 | 124 | 5036 | 1, 7d | E40610 V12 S16
SE153942 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 18 | 480 | 3 | 100 | 124 | 5036 | 1, 7d | E40610 V12 S16
SE153943 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3662 | 1, 5, 7L | E40610 V12 S16
SE153943 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3662 | 1, 5, 7L | E40610 V12 S16
SE153943 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3662 | 1, 5, 7L | E40610 V12 S16
SE153944 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 5036 | 1, 5, 7n | E40610 V12 S16
SE153944 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 5036 | 1, 5, 7n | E40610 V12 S16
SE153944 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 5036 | 1, 5, 7n | E40610 V12 S16
SE153945 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 5036 | 1, 5, 7d | E40610 V12 S16
SE153945 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 5036 | 1, 5, 7d | E40610 V12 S16
SE153945 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 5036 | 1, 5, 7d | E40610 V12 S16
SE153946 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153946 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153946 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153946 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 65 | 480 | 3 | 125 | 156 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153946 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 65 | 480 | 3 | 125 | 156 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153947 | C | CB | Square D | JGL36200 | 35 | 200 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 3662 | 1, 7L | E40610 V12 S16
SE153947 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 3662 | 1, 7L | E40610 V12 S16
SE153947 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 35 | 480 | 3 | 60 | 77 | 3662 | 1, 7L | E40610 V12 S16
SE153948 | C | CB | Square D | JGL36250 | 35 | 200 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 5036 | 1, 7n | E40610 V12 S16
SE153948 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 5036 | 1, 7n | E40610 V12 S16
SE153948 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 35 | 480 | 3 | 75 | 96 | 5036 | 1, 7n | E40610 V12 S16
SE153949 | C | CB | Square D | JGL36250 | 35 | 250 | 600 | 3 | 35 | 480 | 3 | 100 | 124 | 5036 | 1, 7d | E40610 V12 S16
SE153949 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 35 | 480 | 3 | 100 | 124 | 5036 | 1, 7d | E40610 V12 S16
SE153949 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 35 | 480 | 3 | 100 | 124 | 5036 | 1, 7d | E40610 V12 S16
SE153950 | C | CB | Square D | JJL36200 | 65 | 200 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3662 | 1, 7L | E40610 V12 S16
SE153950 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3662 | 1, 7L | E40610 V12 S16
SE153950 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 65 | 480 | 3 | 60 | 77 | 3662 | 1, 7L | E40610 V12 S16
SE153951 | C | CB | Square D | JJL36250 | 65 | 200 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 5036 | 1, 7n | E40610 V12 S16
SE153951 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 5036 | 1, 7n | E40610 V12 S16
SE153951 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 65 | 480 | 3 | 75 | 96 | 5036 | 1, 7n | E40610 V12 S16
SE153952 | C | CB | Square D | JJL36250 | 65 | 250 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 5036 | 1, 7d | E40610 V12 S16
SE153952 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 5036 | 1, 7d | E40610 V12 S16
SE153952 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 65 | 480 | 3 | 100 | 124 | 5036 | 1, 7d | E40610 V12 S16
SE153953 | C | CB | Square D | JLL36200 | 100 | 200 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3662 | 1, 7L | E40610 V12 S16
SE153953 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3662 | 1, 7L | E40610 V12 S16
SE153953 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3662 | 1, 7L | E40610 V12 S16
SE153954 | C | CB | Square D | JLL36250 | 100 | 200 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 5036 | 1, 7n | E40610 V12 S16
SE153954 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 5036 | 1, 7n | E40610 V12 S16
SE153954 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 5036 | 1, 7n | E40610 V12 S16
SE153955 | C | CB | Square D | JLL36250 | 100 | 250 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 5036 | 1, 7d | E40610 V12 S16
SE153955 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 5036 | 1, 7d | E40610 V12 S16
SE153955 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 5036 | 1, 7d | E40610 V12 S16
SE153956 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3662 | 1, 5, 7L | E40610 V12 S16
SE153956 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3662 | 1, 5, 7L | E40610 V12 S16
SE153956 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 100 | 480 | 3 | 60 | 77 | 3662 | 1, 5, 7L | E40610 V12 S16
SE153957 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 5036 | 1, 5, 7n | E40610 V12 S16
SE153957 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 5036 | 1, 5, 7n | E40610 V12 S16
SE153957 |  | OLR | Telemecanique | LR9D5367 | 5 | 60 - 100 | 600 | 3 | 100 | 480 | 3 | 75 | 96 | 5036 | 1, 5, 7n | E40610 V12 S16
SE153958 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 5036 | 1, 5, 7d | E40610 V12 S16
SE153958 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 5036 | 1, 5, 7d | E40610 V12 S16
SE153958 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 100 | 480 | 3 | 100 | 124 | 5036 | 1, 5, 7d | E40610 V12 S16
SE153959 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153959 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153959 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153959 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 100 | 480 | 3 | 125 | 156 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153959 |  | OLR | Telemecanique | LR9F5371 | 5 | 132 - 220 | 600 | 3 | 100 | 480 | 3 | 125 | 156 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153960 | C | CB | Square D | JDL36175 | 14 | 175 | 600 | 3 | 14 | 600 | 3 | 60 | 62 | 3662 | 1, 7L | E40610 V12 S16
SE153960 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 14 | 600 | 3 | 60 | 62 | 3662 | 1, 7L | E40610 V12 S16
SE153960 |  | OLR | Telemecanique | LR2D3359 | 5 | 48 - 65 | 600 | 3 | 14 | 600 | 3 | 60 | 62 | 3662 | 1, 7L | E40610 V12 S16
SE153961 | C | CB | Square D | JDL36200 | 14 | 200 | 600 | 3 | 14 | 600 | 3 | 75 | 77 | 5036 | 1, 7n | E40610 V12 S16
SE153961 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 14 | 600 | 3 | 75 | 77 | 5036 | 1, 7n | E40610 V12 S16
SE153961 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 14 | 600 | 3 | 75 | 77 | 5036 | 1, 7n | E40610 V12 S16
SE153962 | D | ICB | Square D | HJL36100M73 | - | 100 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3662 | 1, 5, 7L | E40610 V12 S16
SE153962 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3662 | 1, 5, 7L | E40610 V12 S16
SE153962 |  | OLR | Telemecanique | LR2D3359 | 5 | 48 - 65 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3662 | 1, 5, 7L | E40610 V12 S16
SE153963 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 5036 | 1, 5, 7n | E40610 V12 S16
SE153963 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 5036 | 1, 5, 7n | E40610 V12 S16
SE153963 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 5036 | 1, 5, 7n | E40610 V12 S16
SE153964 | D | ICB | Square D | HJL36150M74 | - | 150 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 5036 | 1, 5, 7d | E40610 V12 S16
SE153964 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 25 | = | 3 | 100 | 99 | 5036 | 1, 5, 7d | E40610 V12 S16
SE153964 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 5036 | 1, 5, 7d | E40610 V12 S16
SE153965 | D | ICB | Square D | JJL36250M75 | - | 250 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153965 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 25 | = | 3 | 125 | 125 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153965 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 25 | = | 3 | 125 | 125 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153965 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 25 | 600 | 3 | 125 | 125 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153965 |  | OLR | Telemecanique | LR9F5369 | 5 | 90 - 150 | 600 | 3 | 25 | 600 | 3 | 125 | 125 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153966 | C | CB | Square D | JGL36175 | 18 | 175 | 600 | 3 | 18 | 600 | 3 | 60 | 62 | 3662 | 1, 7L | E40610 V12 S16
SE153966 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 18 | 600 | 3 | 60 | 62 | 3662 | 1, 7L | E40610 V12 S16
SE153966 |  | OLR | Telemecanique | LR2D3359 | 5 | 48 - 65 | 600 | 3 | 18 | 600 | 3 | 60 | 62 | 3662 | 1, 7L | E40610 V12 S16
SE153967 | C | CB | Square D | JGL36200 | 18 | 200 | 600 | 3 | 18 | 600 | 3 | 75 | 77 | 5036 | 1, 7n | E40610 V12 S16
SE153967 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 18 | 600 | 3 | 75 | 77 | 5036 | 1, 7n | E40610 V12 S16
SE153967 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 18 | 600 | 3 | 75 | 77 | 5036 | 1, 7n | E40610 V12 S16
SE153968 | C | CB | Square D | JJL36175 | 25 | 175 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3662 | 1, 7L | E40610 V12 S16
SE153968 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3662 | 1, 7L | E40610 V12 S16
SE153968 |  | OLR | Telemecanique | LR2D3359 | 5 | 48 - 65 | 600 | 3 | 25 | 600 | 3 | 60 | 62 | 3662 | 1, 7L | E40610 V12 S16
SE153969 | C | CB | Square D | JJL36200 | 25 | 200 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 5036 | 1, 7n | E40610 V12 S16
SE153969 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 5036 | 1, 7n | E40610 V12 S16
SE153969 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 25 | 600 | 3 | 75 | 77 | 5036 | 1, 7n | E40610 V12 S16
SE153970 | C | CB | Square D | JLL36175 | 50 | 175 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3662 | 1, 7L | E40610 V12 S16
SE153970 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3662 | 1, 7L | E40610 V12 S16
SE153970 |  | OLR | Telemecanique | LR2D3359 | 5 | 48 - 65 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3662 | 1, 7L | E40610 V12 S16
SE153971 | C | CB | Square D | JLL36200 | 50 | 200 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 5036 | 1, 7n | E40610 V12 S16
SE153971 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 5036 | 1, 7n | E40610 V12 S16
SE153971 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 5036 | 1, 7n | E40610 V12 S16
SE153972 | D | ICB | Square D | HLL36100M73 | - | 100 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3662 | 1, 5, 7L | E40610 V12 S16
SE153972 |  | MC | Telemecanique | LC2D80 | 10 | 80 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3662 | 1, 5, 7L | E40610 V12 S16
SE153972 |  | OLR | Telemecanique | LR2D3359 | 5 | 48 - 65 | 600 | 3 | 50 | 600 | 3 | 60 | 62 | 3662 | 1, 5, 7L | E40610 V12 S16
SE153973 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 5036 | 1, 5, 7n | E40610 V12 S16
SE153973 |  | MC | Telemecanique | LC2D115 | 10 | 115 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 5036 | 1, 5, 7n | E40610 V12 S16
SE153973 |  | OLR | Telemecanique | LR2D3363 | 5 | 63 - 80 | 600 | 3 | 50 | 600 | 3 | 75 | 77 | 5036 | 1, 5, 7n | E40610 V12 S16
SE153974 | D | ICB | Square D | HLL36150M74 | - | 150 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 5036 | 1, 5, 7d | E40610 V12 S16
SE153974 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 50 | = | 3 | 100 | 99 | 5036 | 1, 5, 7d | E40610 V12 S16
SE153974 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 5036 | 1, 5, 7d | E40610 V12 S16
SE153975 | D | ICB | Square D | JLL36250M75 | - | 250 | 600 | 3 | 50 | 600 | 3 | 125 | 125 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153975 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 50 | = | 3 | 125 | 125 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153975 |  | MC | Telemecanique | LC1F185 | 10 | 185 | 600 | 3 | 50 | = | 3 | 125 | 125 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153975 |  | INTERLOCK | Telemecanique | LA9FG970 or LA9FG4G | NA | NA | NA | NA | 50 | 600 | 3 | 125 | 125 | 6409 | 1, 5, 7p | E40610 V12 S16
SE153975 |  | OLR | Telemecanique | LR9F5369 | 5 | 90 - 150 | 600 | 3 | 50 | 600 | 3 | 125 | 125 | 6409 | 1, 5, 7p | E40610 V12 S16
SE157920 | C | CB | Square D | JDL36250 | 14 | 250 | 600 | 3 | 14 | 600 | 3 | 100 | 99 | 5036 | 1, 7d | E40610 V12 S16
SE157920 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 14 | 600 | 3 | 100 | 99 | 5036 | 1, 7d | E40610 V12 S16
SE157920 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 14 | 600 | 3 | 100 | 99 | 5036 | 1, 7d | E40610 V12 S16
SE157921 | C | CB | Square D | JGL36250 | 18 | 250 | 600 | 3 | 18 | 600 | 3 | 100 | 99 | 5036 | 1, 7d | E40610 V12 S16
SE157921 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 18 | 600 | 3 | 100 | 99 | 5036 | 1, 7d | E40610 V12 S16
SE157921 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 18 | 600 | 3 | 100 | 99 | 5036 | 1, 7d | E40610 V12 S16
SE157922 | C | CB | Square D | JJL36250 | 25 | 250 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 5036 | 1, 7d | E40610 V12 S16
SE157922 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 5036 | 1, 7d | E40610 V12 S16
SE157922 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 25 | 600 | 3 | 100 | 99 | 5036 | 1, 7d | E40610 V12 S16
SE157923 | C | CB | Square D | JLL36250 | 50 | 250 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 5036 | 1, 7d | E40610 V12 S16
SE157923 |  | MC | Telemecanique | LC2D150 | 10 | 150 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 5036 | 1, 7d | E40610 V12 S16
SE157923 |  | OLR | Telemecanique | LR9D5369 | 5 | 90 - 150 | 600 | 3 | 50 | 600 | 3 | 100 | 99 | 5036 | 1, 7d | E40610 V12 S16
Conditions of Acceptability For Combination Motor Controllers:
Unless specified otherwise in the individual Recognitions, consideration is to be given to the following Conditions of Acceptability when these
components are employed as a combination motor controller in the end-use equipment: Specific Conditions of Use - Number refers to specific
condition number as defined below and number in parenthesis identifies specific information applicable to the combination motor controller.
C.O. A #:
|  | 1 | All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet
or cubic inches. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
|  | 2 | When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other
components shall not be installed in this area.
|  | 3 | When specified, the overload relay heater table shall be provided with the equipment.
|  | 4 | Unless otherwise specified, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current &
connected to the terminals supplied with the individual components.
|  | 5 | The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination
Motor Controllers).
|  | 6 | Use wire ties evenly spaced apart to secure conductors in place.
|  | 7 | See Table 7 for minimum internal wiring between load side of short circuit protective device & line side of starter.
|  | 8 | "@" refer to Square D Digest to complete contactor Catalog number for coil voltage and Form modifications.
|  | 9 | Insulator to be provided underneath starter. (QMFZ2), Fastex, Type Formex GK-30, 1/32 inch minimum thickness by 4 inches x 5.7 inches.
Table 7 - Minimum Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
|  | Wire Code |  | Wire Size
|  | 7a |  | 12 AWG
|  | 7b |  | 8 AWG
|  | 7c |  | 2 AWG
|  | 7d |  | 1 AWG
|  | 7e |  | 250 MCM
|  | 7f |  | 300 MCM
|  | 7g |  | (2) 250 MCM
|  | 7h |  | 2/0 AWG
|  | 7i |  | 4/0 AWG
|  | 7j |  | (2) 4/0 AWG
|  | 7k |  | 10 AWG
|  | 7l |  | 6 AWG
|  | 7m |  | 4 AWG
|  | 7n |  | 3 AWG
|  | 7p |  | 1/0 AWG
|  | 7q |  | (2) 3/0 AWG
|  | 7r |  | (2) 2/0 AWG
|  | 7s |  | 3/0 AWG

## GJL
Issued: 2007-03-21
Last Revised: 2007-03-21
ID Number UL | Combination Type | Component Type | Component Manufacturer | Component Catalog Designation | Component kA | Component Max Amps | Component Volts | Component Poles | Combination kA | Combination Volts | Combination Phase | Maximum Combination HP | Maximum Combination NEC FLC | Min Enclosure Volume (cu in) | Conditions of Acceptability | Combination UL File
SE153802 | C | CB | Square D | GJL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153802 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153802 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153803 | C | CB | Square D | GJL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153803 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153803 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153804 | C | CB | Square D | GJL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153804 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153804 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153805 | C | CB | Square D | GJL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153805 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153805 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153806 | C | CB | Square D | GJL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153806 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153806 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153807 | C | CB | Square D | GJL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153807 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153807 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153808 | C | CB | Square D | GJL36015 | 65 | 15 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153808 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153808 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153809 | C | CB | Square D | GJL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153809 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153809 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153810 | C | CB | Square D | GJL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153810 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153810 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153811 | C | CB | Square D | GJL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153811 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153811 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153812 | C | CB | Square D | GJL36015 | 65 | 15 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153812 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153812 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153813 | C | CB | Square D | GJL36015 | 100 | 15 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153813 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153813 |  | OLR | Telemecanique | LRD10 | 5 | 4.0 - 6 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153814 | C | CB | Square D | GJL36015 | 100 | 15 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153814 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153814 |  | OLR | Telemecanique | LRD10 | 5 | 4.0 - 6 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153815 | C | CB | Square D | GJL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153815 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153815 |  | OLR | Telemecanique | LRD10 | 5 | 4.0 - 6 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153816 | C | CB | Square D | GJL36015 | 65 | 15 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153816 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153816 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153817 | C | CB | Square D | GJL36020 | 100 | 20 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153817 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153817 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153818 | C | CB | Square D | GJL36020 | 100 | 20 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153818 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153818 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153819 | C | CB | Square D | GJL36015 | 100 | 15 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153819 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153819 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153820 | C | CB | Square D | GJL36015 | 65 | 15 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153820 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153820 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153821 | C | CB | Square D | GJL36030 | 100 | 30 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153821 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153821 |  | OLR | Telemecanique | LRD16 | 5 | 9.0 - 13 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153822 | C | CB | Square D | GJL36030 | 100 | 30 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153822 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153822 |  | OLR | Telemecanique | LRD16 | 5 | 9.0 - 13 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153823 | C | CB | Square D | GJL36030 | 100 | 30 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153823 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153823 |  | OLR | Telemecanique | LRD14 | 5 | 7.0 - 10 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153824 | C | CB | Square D | GJL36015 | 65 | 15 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153824 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153824 |  | OLR | Telemecanique | LRD10 | 5 | 4.0 - 6 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153825 | C | CB | Square D | GJL36040 | 100 | 40 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153825 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153825 |  | OLR | Telemecanique | LRD21 | 5 | 12.0 - 18 | 600 | 3 | 100 | 240 | 3 | 5 | 15.2 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153826 | C | CB | Square D | GJL36020 | 65 | 20 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153826 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153826 |  | OLR | Telemecanique | LRD14 | 5 | 7.0 - 10 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153827 | C | CB | Square D | GJL36070 | 100 | 70 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1831 | 1, 6, 7k | E40610 V12 S15
SE153827 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1831 | 1, 6, 7k | E40610 V12 S15
SE153827 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 200 | 3 | 7.5 | 25.3 | 1831 | 1, 6, 7k | E40610 V12 S15
SE153828 | C | CB | Square D | GJL36070 | 100 | 70 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1831 | 1, 6, 7k | E40610 V12 S15
SE153828 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1831 | 1, 6, 7k | E40610 V12 S15
SE153828 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 208 | 3 | 7.5 | 24.2 | 1831 | 1, 6, 7k | E40610 V12 S15
SE153829 | C | CB | Square D | GJL36060 | 100 | 60 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153829 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153829 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 240 | 3 | 7.5 | 22 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153830 | C | CB | Square D | GJL36030 | 65 | 30 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153830 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153830 |  | OLR | Telemecanique | LRD16 | 5 | 9.0 - 13 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153831 | C | CB | Square D | GJL36090 | 100 | 90 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2289 | 1, 6, 7b | E40610 V12 S15
SE153831 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2289 | 1, 6, 7b | E40610 V12 S15
SE153831 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 200 | 3 | 10 | 32.2 | 2289 | 1, 6, 7b | E40610 V12 S15
SE153832 | C | CB | Square D | GJL36090 | 100 | 90 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2289 | 1, 6, 7b | E40610 V12 S15
SE153832 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2289 | 1, 6, 7b | E40610 V12 S15
SE153832 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 208 | 3 | 10 | 30.8 | 2289 | 1, 6, 7b | E40610 V12 S15
SE153833 | C | CB | Square D | GJL36070 | 100 | 70 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1831 | 1, 6, 7k | E40610 V12 S15
SE153833 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1831 | 1, 6, 7k | E40610 V12 S15
SE153833 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 240 | 3 | 10 | 28 | 1831 | 1, 6, 7k | E40610 V12 S15
SE153834 | C | CB | Square D | GJL36040 | 65 | 40 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153834 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153834 |  | OLR | Telemecanique | LRD21 | 5 | 12.0 - 18 | 600 | 3 | 100 | 480 | 3 | 10 | 14 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153835 | C | CB | Square D | GJL36100 | 100 | 100 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 6, 7b | E40610 V12 S15
SE153835 |  | MC | Telemecanique | LC1D50 | 5 | 50 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 6, 7b | E40610 V12 S15
SE153835 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 240 | 3 | 15 | 42 | 2289 | 1, 6, 7b | E40610 V12 S15
SE153836 | C | CB | Square D | GJL36060 | 65 | 60 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153836 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153836 |  | OLR | Telemecanique | LRD22 | 5 | 16 - 24 | 600 | 3 | 100 | 480 | 3 | 15 | 21 | 1831 | 1, 6, 7a | E40610 V12 S15
SE153837 | C | CB | Square D | GJL36070 | 65 | 70 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1831 | 1, 6, 7k | E40610 V12 S15
SE153837 |  | MC | Telemecanique | LC1D32 | 5 | 32 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1831 | 1, 6, 7k | E40610 V12 S15
SE153837 |  | OLR | Telemecanique | LRD32 | 5 | 23 - 32 | 600 | 3 | 100 | 480 | 3 | 20 | 27 | 1831 | 1, 6, 7k | E40610 V12 S15
SE153838 | C | CB | Square D | GJL36090 | 65 | 90 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2289 | 1, 6, 7b | E40610 V12 S15
SE153838 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2289 | 1, 6, 7b | E40610 V12 S15
SE153838 |  | OLR | Telemecanique | LRD3355 | 5 | 30 - 40 | 600 | 3 | 100 | 480 | 3 | 25 | 34 | 2289 | 1, 6, 7b | E40610 V12 S15
SE153839 | C | CB | Square D | GJL36100 | 65 | 100 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2289 | 1, 6, 7b | E40610 V12 S15
SE153839 |  | MC | Telemecanique | LC1D40 | 5 | 40 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2289 | 1, 6, 7b | E40610 V12 S15
SE153839 |  | OLR | Telemecanique | LRD3357 | 5 | 37 - 50 | 600 | 3 | 100 | 480 | 3 | 30 | 40 | 2289 | 1, 6, 7b | E40610 V12 S15
SE153840 | D | ICB | Square D | GJL36007M01 | - | 7 | 480 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153840 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153840 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 200 | 3 | 0.5 | 2.5 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153841 | D | ICB | Square D | GJL36007M01 | - | 7 | 480 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153841 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153841 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 208 | 3 | 0.5 | 2.4 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153842 | D | ICB | Square D | GJL36007M01 | - | 7 | 480 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153842 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153842 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 0.5 | 2.2 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153843 | D | ICB | Square D | GJL36007M02 | - | 7 | 480 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153843 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153843 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 0.75 | 3.7 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153844 | D | ICB | Square D | GJL36007M02 | - | 7 | 480 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153844 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153844 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 0.75 | 3.5 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153845 | D | ICB | Square D | GJL36007M02 | - | 7 | 480 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153845 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153845 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 240 | 3 | 0.75 | 3.2 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153846 | D | ICB | Square D | GJL36003M01 | - | 3 | 480 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153846 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153846 |  | OLR | Telemecanique | LRD06 | 5 | 1 - 1.6 | 600 | 3 | 100 | 480 | 3 | 0.75 | 1.6 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153847 | D | ICB | Square D | GJL36007M02 | - | 7 | 480 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153847 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153847 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 200 | 3 | 1 | 4.8 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153848 | D | ICB | Square D | GJL36007M02 | - | 7 | 480 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153848 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153848 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 208 | 3 | 1 | 4.6 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153849 | D | ICB | Square D | GJL36007M02 | - | 7 | 480 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153849 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153849 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 240 | 3 | 1 | 4.2 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153850 | D | ICB | Square D | GJL36003M01 | - | 3 | 480 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153850 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153850 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 480 | 3 | 1 | 2.1 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153851 | D | ICB | Square D | GJL36015M03 | - | 15 | 480 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153851 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153851 |  | OLR | Telemecanique | LRD10 | 5 | 4.0 - 6 | 600 | 3 | 100 | 200 | 3 | 1.5 | 6.9 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153852 | D | ICB | Square D | GJL36015M03 | - | 15 | 480 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153852 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153852 |  | OLR | Telemecanique | LRD10 | 5 | 4.0 - 6 | 600 | 3 | 100 | 208 | 3 | 1.5 | 6.6 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153853 | D | ICB | Square D | GJL36015M03 | - | 15 | 480 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153853 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153853 |  | OLR | Telemecanique | LRD10 | 5 | 4.0 - 6 | 600 | 3 | 100 | 240 | 3 | 1.5 | 6 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153854 | D | ICB | Square D | GJL36007M02 | - | 7 | 480 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153854 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153854 |  | OLR | Telemecanique | LRD07 | 5 | 1.6 - 2.5 | 600 | 3 | 100 | 480 | 3 | 1.5 | 3 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153855 | D | ICB | Square D | GJL36015M03 | - | 15 | 480 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153855 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153855 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 200 | 3 | 2 | 7.82 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153856 | D | ICB | Square D | GJL36015M03 | - | 15 | 480 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153856 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153856 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 208 | 3 | 2 | 7.5 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153857 | D | ICB | Square D | GJL36015M03 | - | 15 | 480 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153857 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153857 |  | OLR | Telemecanique | LRD12 | 5 | 5.5 - 8 | 600 | 3 | 100 | 240 | 3 | 2 | 6.8 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153858 | D | ICB | Square D | GJL36007M02 | - | 7 | 480 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153858 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153858 |  | OLR | Telemecanique | LRD08 | 5 | 2.5 - 4 | 600 | 3 | 100 | 480 | 3 | 2 | 3.4 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153859 | D | ICB | Square D | GJL36015M03 | - | 15 | 480 | 3 | 100 | 200 | 3 | 3 | 11 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153859 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153859 |  | OLR | Telemecanique | LRD16 | 5 | 9.0 - 13 | 600 | 3 | 100 | 200 | 3 | 3 | 11 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153860 | D | ICB | Square D | GJL36015M03 | - | 15 | 480 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153860 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153860 |  | OLR | Telemecanique | LRD16 | 5 | 9.0 - 13 | 600 | 3 | 100 | 208 | 3 | 3 | 10.6 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153861 | D | ICB | Square D | GJL36015M03 | - | 15 | 480 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153861 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153861 |  | OLR | Telemecanique | LRD14 | 5 | 7.0 - 10 | 600 | 3 | 100 | 240 | 3 | 3 | 9.6 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153862 | D | ICB | Square D | GJL36007M02 | - | 7 | 480 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153862 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153862 |  | OLR | Telemecanique | LRD10 | 5 | 4.0 - 6 | 600 | 3 | 100 | 480 | 3 | 3 | 4.8 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153863 | D | ICB | Square D | GJL36015M03 | - | 15 | 480 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153863 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153863 |  | OLR | Telemecanique | LRD14 | 5 | 7.0 - 10 | 600 | 3 | 100 | 480 | 3 | 5 | 7.6 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153864 | D | ICB | Square D | GJL36015M03 | - | 15 | 480 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153864 |  | MC | Telemecanique | LC1D25 | 5 | 25 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1831 | 1, 5, 7a | E40610 V12 S15
SE153864 |  | OLR | Telemecanique | LRD16 | 5 | 9.0 - 13 | 600 | 3 | 100 | 480 | 3 | 7.5 | 11 | 1831 | 1, 5, 7a | E40610 V12 S15

## FVB_IEC_PP_L_M_P
Issued: 2013-10-30
Revised: 2017-09-12
| Listed Combination Motor Controller Information |  |  |  | Component Description | [6 empty] | Combination Motor Controller Ratings
Database Identification Number | UL File Number | Report Issue Date YYYY-MM-DD | Volume / Section (Vol#).(Sec#) | Construction Type | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, ph | SCCR, kA | Full Load Current, A | Hp | Short Circuit Current Rating, kA | Horsepower Rating | Current Rating, FLA or FLA/LRA | Voltage and Number of Phases | Enclosure Volume, cubic inches | Conditions of Use | Schematic
SE159000.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | LLL36400 | 600, 3 | 50 | 400 | - | 100 | 60 | 169 | 208, 3 | 6455 | 1, 6, 7s | NA
[5 empty] | MC | Telemecanique | LC1F265 | 600, 3 | 10 | 265 | 175 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F5371 | 600, 3 | 5 | 132 - 220 | 200 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159000.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F5571 | 600, 3 | 5 | 132 - 220 | 200 | 100 | 60 | 169 | 208, 3 | 6455 | 1, 6, 7s | NA
SE159001.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | LLL36400 | 600, 3 | 50 | 400 | - | 100 | 75 | 211 | 208, 3 | 6455 | 1, 6, 7i | NA
[5 empty] | MC | Telemecanique | LC1F330 | 600, 3 | 18 | 330 | 250 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F5371 | 600, 3 | 5 | 132 - 220 | 200 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159001.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F5571 | 600, 3 | 5 | 132 - 220 | 200 | 100 | 75 | 211 | 208, 3 | 6455 | 1, 6, 7i | NA
SE159002.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | LLL36600 | 600, 3 | 50 | 600 | - | 100 | 100 | 273 | 208, 3 | 7377 | 1, 6, 7f | NA
[5 empty] | MC | Telemecanique | LC1F400 | 600, 3 | 18 | 400 | 300 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7375 | 600, 3 | 5 | 200 - 330 | 300 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159002.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7575 | 600, 3 | 5 | 200 - 330 | 300 | 100 | 100 | 273 | 208, 3 | 7377 | 1, 6, 7f | NA
SE159003.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | MJL36600 | 600, 3 | 25 | 600 | - | 65 | 125 | 343 | 208, 3 | 26129 | 1, 6, 7j | NA
[5 empty] | MC | Telemecanique | LC1F500 | 600, 3 | 30 | 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7379 | 600, 3 | 5 | 300 - 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159003.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7579 | 600, 3 | 5 | 300 - 500 | 500 | 65 | 125 | 343 | 208, 3 | 26129 | 1, 6, 7j | NA
SE159004.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | MJL36600 | 600, 3 | 25 | 600 | - | 65 | 150 | 396 | 208, 3 | 26129 | 1, 6, 7j | NA
[5 empty] | MC | Telemecanique | LC1F630 | 600, 3 | 42 | 630 | 800 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7379 | 600, 3 | 5 | 300 - 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159004.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7579 | 600, 3 | 5 | 300 - 500 | 500 | 65 | 150 | 396 | 208, 3 | 26129 | 1, 6, 7j | NA
SE159005.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | PLL34060 | 480, 3 | 100 | 600 | - | 100 | 125 | 343 | 208, 3 | 26129 | 1, 6, 7j | NA
[5 empty] | MC | Telemecanique | LC1F500 | 600, 3 | 30 | 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7379 | 600, 3 | 5 | 300 - 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159005.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7579 | 600, 3 | 5 | 300 - 500 | 500 | 100 | 125 | 343 | 208, 3 | 26129 | 1, 6, 7j | NA
SE159006.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | PLL34060 | 480, 3 | 100 | 600 | - | 100 | 150 | 396 | 208, 3 | 26129 | 1, 6, 7j | NA
[5 empty] | MC | Telemecanique | LC1F630 | 600, 3 | 42 | 630 | 800 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7379 | 600, 3 | 5 | 300 - 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159006.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7579 | 600, 3 | 5 | 300 - 500 | 500 | 100 | 150 | 396 | 208, 3 | 26129 | 1, 6, 7j | NA
SE159007.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | LLL36400 | 600, 3 | 50 | 400 | - | 100 | 75 | 192 | 240, 3 | 6455 | 1, 6, 7s | NA
[5 empty] | MC | Telemecanique | LC1F265 | 600, 3 | 10 | 265 | 175 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F5371 | 600, 3 | 5 | 132 - 220 | 200 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159007.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F5571 | 600, 3 | 5 | 132 - 220 | 200 | 100 | 75 | 192 | 240, 3 | 6455 | 1, 6, 7s | NA
SE159008.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | LLL36600 | 600, 3 | 50 | 600 | - | 100 | 100 | 248 | 240, 3 | 6455 | 1, 6, 7i | NA
[5 empty] | MC | Telemecanique | LC1F330 | 600, 3 | 18 | 330 | 250 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7375 | 600, 3 | 5 | 200 - 330 | 300 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159008.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7575 | 600, 3 | 5 | 200 - 330 | 300 | 100 | 100 | 248 | 240, 3 | 6455 | 1, 6, 7i | NA
SE159009.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | MJL36600 | 600, 3 | 25 | 600 | - | 65 | 125 | 312 | 240, 3 | 7377 | 1, 6, 7f | NA
[5 empty] | MC | Telemecanique | LC1F400 | 600, 3 | 18 | 400 | 300 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7375 | 600, 3 | 5 | 200 - 330 | 300 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159009.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7575 | 600, 3 | 5 | 200 - 330 | 300 | 65 | 125 | 312 | 240, 3 | 7377 | 1, 6, 7f | NA
SE159010.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | MJL36600 | 600, 3 | 25 | 600 | - | 65 | 150 | 360 | 240, 3 | 26129 | 1, 6, 7j | NA
[5 empty] | MC | Telemecanique | LC1F500 | 600, 3 | 30 | 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7379 | 600, 3 | 5 | 300 - 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159010.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7579 | 600, 3 | 5 | 300 - 500 | 500 | 65 | 150 | 360 | 240, 3 | 26129 | 1, 6, 7j | NA
SE159011.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | MJL36800 | 600, 3 | 25 | 800 | - | 65 | 200 | 480 | 240, 3 | 26129 | 1, 6, 7j | NA
[5 empty] | MC | Telemecanique | LC1F500 | 600, 3 | 30 | 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7379 | 600, 3 | 5 | 300 - 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159011.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7579 | 600, 3 | 5 | 300 - 500 | 500 | 65 | 200 | 480 | 240, 3 | 26129 | 1, 6, 7j | NA
SE159012.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | PLL34060 | 480, 3 | 100 | 600 | - | 100 | 125 | 312 | 240, 3 | 7377 | 1, 6, 7f | NA
[5 empty] | MC | Telemecanique | LC1F400 | 600, 3 | 18 | 400 | 300 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7375 | 600, 3 | 5 | 200 - 330 | 300 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159012.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7575 | 600, 3 | 5 | 200 - 330 | 300 | 100 | 125 | 312 | 240, 3 | 7377 | 1, 6, 7f | NA
SE159013.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | PLL34060 | 480, 3 | 100 | 600 | - | 100 | 150 | 360 | 240, 3 | 26129 | 1, 6, 7j | NA
[5 empty] | MC | Telemecanique | LC1F500 | 600, 3 | 30 | 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7379 | 600, 3 | 5 | 300 - 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159013.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7579 | 600, 3 | 5 | 300 - 500 | 500 | 100 | 150 | 360 | 240, 3 | 26129 | 1, 6, 7j | NA
SE159014.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | PLL34080 | 480, 3 | 100 | 800 | - | 100 | 200 | 480 | 240, 3 | 26129 | 1, 6, 7j | NA
[5 empty] | MC | Telemecanique | LC1F500 | 600, 3 | 30 | 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7379 | 600, 3 | 5 | 300 - 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159014.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7579 | 600, 3 | 5 | 300 - 500 | 500 | 100 | 200 | 480 | 240, 3 | 26129 | 1, 6, 7j | NA
SE159015.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | LLL36400 | 600, 3 | 50 | 400 | - | 100 | 150 | 180 | 480, 3 | 6455 | 1, 6, 7s | NA
[5 empty] | MC | Telemecanique | LC1F265 | 600, 3 | 10 | 265 | 175 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F5371 | 600, 3 | 5 | 132 - 220 | 200 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159015.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F5571 | 600, 3 | 5 | 132 - 220 | 200 | 100 | 150 | 180 | 480, 3 | 6455 | 1, 6, 7s | NA
SE159016.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | LLL36600 | 600, 3 | 50 | 600 | - | 100 | 200 | 240 | 480, 3 | 6455 | 1, 6, 7i | NA
[5 empty] | MC | Telemecanique | LC1F330 | 600, 3 | 18 | 330 | 250 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7375 | 600, 3 | 5 | 200 - 330 | 300 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159016.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7575 | 600, 3 | 5 | 200 - 330 | 300 | 100 | 200 | 240 | 480, 3 | 6455 | 1, 6, 7i | NA
SE159017.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | LLL36600 | 600, 3 | 50 | 600 | - | 100 | 250 | 302 | 480, 3 | 7377 | 1, 6, 7f | NA
[5 empty] | MC | Telemecanique | LC1F400 | 600, 3 | 18 | 400 | 300 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7379 | 600, 3 | 5 | 300 - 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159017.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7579 | 600, 3 | 5 | 300 - 500 | 500 | 100 | 250 | 302 | 480, 3 | 7377 | 1, 6, 7f | NA
SE159018.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | MJL36600 | 600, 3 | 25 | 600 | - | 65 | 300 | 361 | 480, 3 | 26129 | 1, 6, 7j | NA
[5 empty] | MC | Telemecanique | LC1F500 | 600, 3 | 30 | 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7379 | 600, 3 | 5 | 300 - 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159018.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7579 | 600, 3 | 5 | 300 - 500 | 500 | 65 | 300 | 361 | 480, 3 | 26129 | 1, 6, 7j | NA
SE159019.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | MJL36600 | 600, 3 | 25 | 600 | - | 65 | 350 | 414 | 480, 3 | 26129 | 1, 6, 7j | NA
[5 empty] | MC | Telemecanique | LC1F500 | 600, 3 | 30 | 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7379 | 600, 3 | 5 | 300 - 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159019.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7579 | 600, 3 | 5 | 300 - 500 | 500 | 65 | 350 | 414 | 480, 3 | 26129 | 1, 6, 7j | NA
SE159020.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | PLL34060 | 480, 3 | 100 | 600 | - | 100 | 300 | 361 | 480, 3 | 26129 | 1, 6, 7j | NA
[5 empty] | MC | Telemecanique | LC1F500 | 600, 3 | 30 | 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7379 | 600, 3 | 5 | 300 - 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159020.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7579 | 600, 3 | 5 | 300 - 500 | 500 | 100 | 300 | 361 | 480, 3 | 26129 | 1, 6, 7j | NA
SE159021.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | PLL34060 | 480, 3 | 100 | 600 | - | 100 | 350 | 414 | 480, 3 | 26129 | 1, 6, 7j | NA
[5 empty] | MC | Telemecanique | LC1F500 | 600, 3 | 30 | 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7379 | 600, 3 | 5 | 300 - 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159021.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7579 | 600, 3 | 5 | 300 - 500 | 500 | 100 | 350 | 414 | 480, 3 | 26129 | 1, 6, 7j | NA
SE159022.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | LLL36600 | 600, 3 | 50 | 600 | - | 100 | 300 | 361 | 480, 3 | 26129 | 1, 6, 7j | NA
[5 empty] | MC | Telemecanique | LC1F500 | 600, 3 | 30 | 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7379 | 600, 3 | 5 | 300 - 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159022.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7579 | 600, 3 | 5 | 300 - 500 | 500 | 100 | 300 | 361 | 480, 3 | 26129 | 1, 6, 7j | NA
SE159023.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | LLL36600 | 600, 3 | 50 | 600 | - | 100 | 350 | 414 | 480, 3 | 26129 | 1, 6, 7j | NA
[5 empty] | MC | Telemecanique | LC1F500 | 600, 3 | 30 | 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7379 | 600, 3 | 5 | 300 - 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159023.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7579 | 600, 3 | 5 | 300 - 500 | 500 | 100 | 350 | 414 | 480, 3 | 26129 | 1, 6, 7j | NA
SE159024.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | MJL36800 | 600, 3 | 25 | 800 | - | 65 | 400 | 477 | 480, 3 | 26129 | 1, 6, 7j | NA
[5 empty] | MC | Telemecanique | LC1F630 | 600, 3 | 42 | 630 | 800 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7379 | 600, 3 | 5 | 300 - 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159024.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7579 | 600, 3 | 5 | 300 - 500 | 500 | 65 | 400 | 477 | 480, 3 | 26129 | 1, 6, 7j | NA
SE159025.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | PLL34080 | 480, 3 | 100 | 800 | - | 100 | 400 | 477 | 480, 3 | 26129 | 1, 6, 7j | NA
[5 empty] | MC | Telemecanique | LC1F630 | 600, 3 | 42 | 630 | 800 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7379 | 600, 3 | 5 | 300 - 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159025.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7579 | 600, 3 | 5 | 300 - 500 | 500 | 100 | 400 | 477 | 480, 3 | 26129 | 1, 6, 7j | NA
SE159026.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | LLL36400 | 600, 3 | 50 | 400 | - | 50 | 150 | 144 | 600, 3 | 6455 | 1, 6, 7s | NA
[5 empty] | MC | Telemecanique | LC1F265 | 600, 3 | 10 | 265 | 175 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F5371 | 600, 3 | 5 | 132 - 220 | 200 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159026.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F5571 | 600, 3 | 5 | 132 - 220 | 200 | 50 | 150 | 144 | 600, 3 | 6455 | 1, 6, 7s | NA
SE159027.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | LLL36400 | 600, 3 | 50 | 400 | - | 50 | 200 | 192 | 600, 3 | 6455 | 1, 6, 7i | NA
[5 empty] | MC | Telemecanique | LC1F330 | 600, 3 | 18 | 330 | 250 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F5371 | 600, 3 | 5 | 132 - 220 | 200 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159027.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F5571 | 600, 3 | 5 | 132 - 220 | 200 | 50 | 200 | 192 | 600, 3 | 6455 | 1, 6, 7i | NA
SE159028.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | LLL36600 | 600, 3 | 50 | 600 | - | 50 | 250 | 242 | 600, 3 | 7377 | 1, 6, 7f | NA
[5 empty] | MC | Telemecanique | LC1F400 | 600, 3 | 18 | 400 | 300 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7375 | 600, 3 | 5 | 200 - 330 | 300 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159028.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7575 | 600, 3 | 5 | 200 - 330 | 300 | 50 | 250 | 242 | 600, 3 | 7377 | 1, 6, 7f | NA
SE159029.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | LLL36600 | 600, 3 | 50 | 600 | - | 50 | 300 | 289 | 600, 3 | 26129 | 1, 6, 7j | NA
[5 empty] | MC | Telemecanique | LC1F500 | 600, 3 | 30 | 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7375 | 600, 3 | 5 | 200 - 330 | 300 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159029.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7575 | 600, 3 | 5 | 200 - 330 | 300 | 50 | 300 | 289 | 600, 3 | 26129 | 1, 6, 7j | NA
SE159030.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | MJL36600 | 600, 3 | 25 | 600 | - | 25 | 350 | 336 | 600, 3 | 26129 | 1, 6, 7j | NA
[5 empty] | MC | Telemecanique | LC1F500 | 600, 3 | 30 | 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7379 | 600, 3 | 5 | 300 - 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159030.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7579 | 600, 3 | 5 | 300 - 500 | 500 | 25 | 350 | 336 | 600, 3 | 26129 | 1, 6, 7j | NA
SE159031.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | MJL36600 | 600, 3 | 25 | 600 | - | 25 | 400 | 382 | 600, 3 | 26129 | 1, 6, 7j | NA
[5 empty] | MC | Telemecanique | LC1F500 | 600, 3 | 30 | 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7379 | 600, 3 | 5 | 300 - 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159031.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7579 | 600, 3 | 5 | 300 - 500 | 500 | 25 | 400 | 382 | 600, 3 | 26129 | 1, 6, 7j | NA
SE159032.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | MJL36600 | 600, 3 | 25 | 600 | - | 25 | 450 | 412 | 600, 3 | 26129 | 1, 6, 7j | NA
[5 empty] | MC | Telemecanique | LC1F500 | 600, 3 | 30 | 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7379 | 600, 3 | 5 | 300 - 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159032.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7579 | 600, 3 | 5 | 300 - 500 | 500 | 25 | 450 | 412 | 600, 3 | 26129 | 1, 6, 7j | NA
SE159033.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | MJL36800 | 600, 3 | 25 | 800 | - | 25 | 500 | 472 | 600, 3 | 26129 | 1, 6, 7j | NA
[5 empty] | MC | Telemecanique | LC1F630 | 600, 3 | 42 | 630 | 800 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7379 | 600, 3 | 5 | 300 - 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159033.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7579 | 600, 3 | 5 | 300 - 500 | 500 | 25 | 500 | 472 | 600, 3 | 26129 | 1, 6, 7j | NA
SE159034.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | PKL36060 | 600, 3 | 50 | 600 | - | 50 | 350 | 336 | 600, 3 | 26129 | 1, 6, 7j | NA
[5 empty] | MC | Telemecanique | LC1F500 | 600, 3 | 30 | 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7379 | 600, 3 | 5 | 300 - 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159034.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7579 | 600, 3 | 5 | 300 - 500 | 500 | 50 | 350 | 336 | 600, 3 | 26129 | 1, 6, 7j | NA
SE159035.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | PKL36060 | 600, 3 | 50 | 600 | - | 50 | 400 | 382 | 600, 3 | 26129 | 1, 6, 7j | NA
[5 empty] | MC | Telemecanique | LC1F500 | 600, 3 | 30 | 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7379 | 600, 3 | 5 | 300 - 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159035.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7579 | 600, 3 | 5 | 300 - 500 | 500 | 50 | 400 | 382 | 600, 3 | 26129 | 1, 6, 7j | NA
SE159036.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | PKL36060 | 600, 3 | 50 | 600 | - | 50 | 450 | 412 | 600, 3 | 26129 | 1, 6, 7j | NA
[5 empty] | MC | Telemecanique | LC1F500 | 600, 3 | 30 | 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7379 | 600, 3 | 5 | 300 - 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159036.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7579 | 600, 3 | 5 | 300 - 500 | 500 | 50 | 450 | 412 | 600, 3 | 26129 | 1, 6, 7j | NA
SE159037.01 | E40610 | 2000-01-07 | 12.15 | C | CB | Square D | PKL36080 | 600, 3 | 50 | 800 | - | 50 | 500 | 472 | 600, 3 | 26129 | 1, 6, 7j | NA
[5 empty] | MC | Telemecanique | LC1F630 | 600, 3 | 42 | 630 | 800 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
[5 empty] | OLR | Telemecanique | LR9F7379 | 600, 3 | 5 | 300 - 500 | 500 | 100 |  |  | 208, 3 | 4620 | 1, 6, 7a | NA
SE159037.02 | E40610 | 2000-01-07 | 12.15 | C | OLR | Telemecanique | LR9F7579 | 600, 3 | 5 | 300 - 500 | 500 | 50 | 500 | 472 | 600, 3 | 26129 | 1, 6, 7j | NA