## C.O.A.
These conditions will match existing UL file Conditions. |  | revised: 2019-05-31
Conditions of Acceptability For Combination Motor Controllers:
Unless specified otherwise in the individual Recognitions, consideration is to be given to the following Conditions of Acceptability when these
components are employed as a combination motor controller in the end-use equipment: Specific Conditions of Use - Number refers to specific
condition number as defined below and number in parenthesis identifies specific information applicable to the combination motor controller.
C.O. A #:
(1) = All specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic in. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
(2) = When specified, motor controller & overload relay shall be installed to maintain the specified distance, in inches, from the overcurrent protective device, and other components shall not be installed in this area.
(3) = When specified, the overload relay heater table shall be provided with the equipment.
(4) = Unless otherwise specified in note 7, all connections between components are made using insulated wire having an ampacity of 125% of the rated motor current & connected to the terminals supplied with the individual components.
(5) = The need for cautionary markings applicable to high-fault short circuit current ratings shall be considered in the end-product application. (Type D & E Combination Motor Controllers).
(6) = Use wire ties evenly spaced apart to secure conductors in place.
(7) = See Table 7 for minimum internal wiring between load side of short circuit protective device & line side of starter.
(8) = "***" refer to digest to complete contactor Catalog number for coil voltage and Form modifications.
(9) = "@" refer to Square D Digest to complete Reversing starter contactor Catalog number for Vertical or Horizontal Types.
(10) = "*" refer to digest to complete overload Catalog number for control voltage and communications options.
(11) 208V tests are made with 200V currents to cover bothe voltage ratings.
Table 7 - Minimum Internal Power Wiring
Wiring from load side of short circuit protective device to line side of starter (all copper stranded w/ 105 C. insulation).
Wire Code | Wire Size
7a | 12 AWG
7b | 8 AWG
7c | 2 AWG
7d | 1 AWG
7e | 250 MCM
7f | 300 MCM
7g | (2) 250 MCM
7h | 2/0 AWG
7i | 4/0 AWG
7j | (2) 4/0 AWG
7k | 10 AWG
7l | 6 AWG
7m | 4 AWG
7n | 3 AWG
7p | 1/0 AWG
7q | (2) 3/0 AWG
7r | (2) 2/0 AWG
7s | 3/0 AWG

## Melting Alloy
Template for Submission of Combination Motor Controller
(NOTE: The bracketed alphanumeric in each column heading and in example entries, such as [B1], corresponds to a section of the short circuit database submittal guideline document which provides further information concerning the expected content and format for entering data into the spreadsheet cells)
Database Identification Number | Listed Combination Motor Controller Information | [7 empty] | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Enclosure Volume, cubic inches | Conditions of Use | [B10] Schematic | [B11] Other References
| Listing Report Information |  |  |  |  | Enclosure or Unit Dimensions
| UL File Number | Report Issue Date | Volume / Section | Model Number or Product Style/ Designation | Product Description on Page/Figure/Ill. | Enclosure or Unit Height, inches | Width, inches | Depth, inches |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating
Non- reversing
SE194001 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 208 | 3 | 25 | 2.5 | 0.5 | 1832 | 1,3,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194002 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 25 | 2.5 | 0.5 | 1832 | 1,3,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194003 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 25 | 4.8 | 1 | 1832 | 1,3,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194004 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 25 | 6.9 | 1.5 | 1832 | 1,3,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194005 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 208 | 3 | 25 | 7.8 | 2 | 1832 | 1,3,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194006 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 208 | 3 | 25 | 11 | 3 | 1832 | 1,3,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194007 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 208 | 3 | 25 | 17.5 | 5 | 1832 | 1,3,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194008 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 25.3 | 7.5 | 1832 | 1,3,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194009 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 32.2 | 10 | 1832 | 1,3,5,6,7b,8 and 11
[10 empty] | STR | Square D | 8536SDO1*** | 208 | 3 | 100kA | 32.2 | 10
SE194010 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 48.3 | 15 | 2747 | 1,3,5,6,7c,8 and 11
[10 empty] | STR | Square D | 8536SEO1*** | 208 | 3 | 100kA | 78.2 | 25
SE194011 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 208 | 3 | 25 | 62.1 | 20 | 2747 | 1,3,5,6,7c,8 and 11
[10 empty] | STR | Square D | 8536SEO1*** | 208 | 3 | 100kA | 78.2 | 25
SE194012 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 208 | 3 | 25 | 78.2 | 25 | 2747 | 1,3,5,6,7c,8 and 11
[10 empty] | STR | Square D | 8536SEO1*** | 208 | 3 | 100kA | 78.2 | 25
SE194013 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 240 | 3 | 25 | 80 | 30 | 2747 | 1,3,5,6,7c and 8
[10 empty] | STR | Square D | 8536SEO1*** | 240 | 3 | 100kA | 80 | 30
SE194014 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 |  | 480 | 3 | 18 | 77 | 60 | 2747 | 1,3,5,6,7c and 8
[10 empty] | STR | Square D | 8536SEO1*** | 480 | 3 | 100kA | 77 | 60
SE194015 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 | - | 208 | 3 | 25 | 78.2 | 25 | 2747 | 1,3,5,6,7c,8 and 11
[10 empty] | STR | Square D | 8536SEO1*** | 208 | 3 | 100kA | 78.2 | 25
SE194016 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 240 | 3 | 25 | 2.2 | 0.5 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 240 | 3 | 100kA | 22 | 7.5
SE194017 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 3.2 | 0.75 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 240 | 3 | 100kA | 22 | 7.5
SE194018 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 4.2 | 1 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 240 | 3 | 100kA | 22 | 7.5
SE194019 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 6 | 1.5 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 240 | 3 | 100kA | 22 | 7.5
SE194020 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 6.8 | 2 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 240 | 3 | 100kA | 22 | 7.5
SE194021 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 240 | 3 | 25 | 15.2 | 5 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 240 | 3 | 100kA | 22 | 7.5
SE194022 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 240 | 3 | 25 | 22 | 7.5 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 240 | 3 | 100kA | 22 | 7.5
SE194023 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 240 | 3 | 25 | 28 | 10 | 1832 | 1,3,5,6,7b and 8
[10 empty] | STR | Square D | 8536SDO1*** | 240 | 3 | 100kA | 42 | 15
SE194024 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 240 | 3 | 25 | 42 | 15 | 1832 | 1,3,5,6,7b and 8
[10 empty] | STR | Square D | 8536SDO1*** | 240 | 3 | 100kA | 42 | 15
SE194025 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 240 | 3 | 25 | 54 | 20 | 2747 | 1,3,5,6,7c and 8
[10 empty] | STR | Square D | 8536SEO1*** | 240 | 3 | 100kA | 80 | 30
SE194026 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 240 | 3 | 25 | 68 | 25 | 2747 | 1,3,5,6,7c and 8
[10 empty] | STR | Square D | 8536SEO1*** | 240 | 3 | 100kA | 80 | 30
SE194027 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 | - | 240 | 3 | 25 | 80 | 30 | 2747 | 1,3,5,6,7c and 8
[10 empty] | STR | Square D | 8536SEO1*** | 240 | 3 | 100kA | 80 | 30
SE194028 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T002D | 600 | 3 | - | 2 | - | 480 | 3 | 18 | 1.1 | 0.5 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 480 | 3 | 100kA | 14 | 10
SE194029 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T002D | 600 | 3 | - | 2 | - | 480 | 3 | 18 | 1.6 | 0.75 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 480 | 3 | 100kA | 14 | 10
SE194030 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 480 | 3 | 18 | 2.1 | 1 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 480 | 3 | 100kA | 14 | 10
SE194031 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 480 | 3 | 18 | 3 | 1.5 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 480 | 3 | 100kA | 14 | 10
SE194032 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 480 | 3 | 18 | 3.4 | 2 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 480 | 3 | 100kA | 14 | 10
SE194033 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 480 | 3 | 18 | 4.8 | 3 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 480 | 3 | 100kA | 14 | 10
SE194034 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 480 | 3 | 18 | 7.6 | 5 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 480 | 3 | 100kA | 14 | 10
SE194035 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 480 | 3 | 18 | 11 | 7.5 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 480 | 3 | 100kA | 14 | 10
SE194036 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 480 | 3 | 18 | 14 | 10 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 480 | 3 | 100kA | 14 | 10
SE194037 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 480 | 3 | 18 | 21 | 15 | 1832 | 1,3,5,6,7b and 8
[10 empty] | STR | Square D | 8536SDO1*** | 480 | 3 | 100kA | 34 | 25
SE194038 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 480 | 3 | 18 | 27 | 20 | 1832 | 1,3,5,6,7b and 8
[10 empty] | STR | Square D | 8536SDO1*** | 480 | 3 | 100kA | 34 | 25
SE194039 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 |  | 480 | 3 | 18 | 34 | 25 | 1832 | 1,3,5,6,7b and 8
[10 empty] | STR | Square D | 8536SDO1*** | 480 | 3 | 100kA | 34 | 25
SE194040 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 |  | 480 | 3 | 18 | 40 | 30 | 2747 | 1,3,5,6,7c and 8
[10 empty] | STR | Square D | 8536SEO1*** | 480 | 3 | 100kA | 65 | 50
SE194041 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 |  | 480 | 3 | 18 | 52 | 40 | 2747 | 1,3,5,6,7c and 8
[10 empty] | STR | Square D | 8536SEO1*** | 480 | 3 | 100kA | 65 | 50
SE194042 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 |  | 480 | 3 | 18 | 65 | 50 | 2747 | 1,3,5,6,7c and 8
[10 empty] | STR | Square D | 8536SEO1*** | 480 | 3 | 100kA | 65 | 50
SE194043 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 21 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 |  | 480 | 3 | 18 | 77 | 60 | 3205 | 1,3,5,6,7d and 8
[10 empty] | STR | Square D | 8536SFO1*** | 480 | 3 | 100kA | 77 | 60
SE194044 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 208 | 3 | 100 | 2.5 | 0.5 | 1832 | 1,3,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194045 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 208 | 3 | 100 | 3.7 | 0.75 | 1832 | 1,3,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194046 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 208 | 3 | 100 | 4.8 | 1 | 1832 | 1,3,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194047 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 208 | 3 | 100 | 6.9 | 1.5 | 1832 | 1,3,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194048 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 100 | 7.8 | 2 | 1832 | 1,3,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194049 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 100 | 11 | 3 | 1832 | 1,3,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194050 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 208 | 3 | 100 | 17.5 | 5 | 1832 | 1,3,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194051 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 100 | 25.3 | 7.5 | 1832 | 1,3,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194052 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 100 | 32.2 | 10 | 1832 | 1,3,5,6,7b and 8
[10 empty] | STR | Square D | 8536SDO1*** | 208 | 3 | 100kA | 32.2 | 10
SE194053 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 100 | 48.3 | 15 | 2747 | 1,3,5,6,7c,8 and 11
[10 empty] | STR | Square D | 8536SEO1*** | 208 | 3 | 100kA | 78.2 | 25
SE194054 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 208 | 3 | 100 | 62.1 | 20 | 2747 | 1,3,5,6,7c,8 and 11
[10 empty] | STR | Square D | 8536SEO1*** | 208 | 3 | 100kA | 78.2 | 25
SE194055 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 208 | 3 | 100 | 78.2 | 25 | 2747 | 1,3,5,6,7c,8 and 11
[10 empty] | STR | Square D | 8536SEO1*** | 208 | 3 | 100kA | 78.2 | 25
SE194056 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 240 | 3 | 100 | 2.2 | 0.5 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 240 | 3 | 100kA | 22 | 7.5
SE194057 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 3.2 | 0.75 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 240 | 3 | 100kA | 22 | 7.5
SE194058 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 4.2 | 1 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 240 | 3 | 100kA | 22 | 7.5
SE194059 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 6 | 1.5 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 240 | 3 | 100kA | 22 | 7.5
SE194060 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 6.8 | 2 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 240 | 3 | 100kA | 22 | 7.5
SE194061 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 240 | 3 | 100 | 9.6 | 3 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 240 | 3 | 100kA | 22 | 7.5
SE194062 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 240 | 3 | 100 | 15.2 | 5 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 240 | 3 | 100kA | 22 | 7.5
SE194063 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 240 | 3 | 100 | 22 | 7.5 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 240 | 3 | 100kA | 22 | 7.5
SE194064 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 100 | 28 | 10 | 1832 | 1,3,5,6,7b and 8
[10 empty] | STR | Square D | 8536SDO1*** | 240 | 3 | 100kA | 42 | 15
SE194065 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 100 | 42 | 15 | 1832 | 1,3,5,6,7b and 8
[10 empty] | STR | Square D | 8536SDO1*** | 240 | 3 | 100kA | 42 | 15
SE194066 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 240 | 3 | 100 | 54 | 20 | 2747 | 1,3,5,6,7c and 8
[10 empty] | STR | Square D | 8536SEO1*** | 240 | 3 | 100kA | 80 | 30
SE194067 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 240 | 3 | 100 | 68 | 25 | 2747 | 1,3,5,6,7c and 8
[10 empty] | STR | Square D | 8536SEO1*** | 240 | 3 | 100kA | 80 | 30
SE194068 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T115J | 600 | 3 | - | 115 | - | 240 | 3 | 100 | 80 | 30 | 2747 | 1,3,5,6,7c and 8
[10 empty] | STR | Square D | 8536SEO1*** | 240 | 3 | 100kA | 80 | 30
SE194069 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T002J | 600 | 3 | - | 2 | - | 480 | 3 | 100 | 1.1 | 0.5 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 480 | 3 | 100kA | 14 | 10
SE194070 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T002J | 600 | 3 | - | 2 | - | 480 | 3 | 100 | 1.6 | 0.75 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 480 | 3 | 100kA | 14 | 10
SE194071 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 480 | 3 | 100 | 2.1 | 1 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 480 | 3 | 100kA | 14 | 10
SE194072 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 480 | 3 | 100 | 3 | 1.5 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 480 | 3 | 100kA | 14 | 10
SE194073 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 480 | 3 | 100 | 3.4 | 2 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 480 | 3 | 100kA | 14 | 10
SE194074 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 480 | 3 | 100 | 4.8 | 3 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 480 | 3 | 100kA | 14 | 10
SE194075 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 480 | 3 | 100 | 7.6 | 5 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 480 | 3 | 100kA | 14 | 10
SE194076 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 480 | 3 | 100 | 11 | 7.5 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 480 | 3 | 100kA | 14 | 10
SE194077 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 480 | 3 | 100 | 14 | 10 | 1832 | 1,3,5,6,7a and 8
[10 empty] | STR | Square D | 8536SCO3*** | 480 | 3 | 100kA | 14 | 10
SE194078 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 480 | 3 | 100 | 21 | 15 | 1832 | 1,3,5,6,7b and 8
[10 empty] | STR | Square D | 8536SDO1*** | 480 | 3 | 100kA | 34 | 25
SE194079 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 480 | 3 | 100 | 27 | 20 | 1832 | 1,3,5,6,7b and 8
[10 empty] | STR | Square D | 8536SDO1*** | 480 | 3 | 100kA | 34 | 25
SE194080 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 480 | 3 | 100 | 34 | 25 | 1832 | 1,3,5,6,7b and 8
[10 empty] | STR | Square D | 8536SDO1*** | 480 | 3 | 100kA | 34 | 25
SE194081 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 480 | 3 | 100 | 40 | 30 | 2747 | 1,3,5,6,7c and 8
[10 empty] | STR | Square D | 8536SEO1*** | 480 | 3 | 100kA | 65 | 50
SE194082 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 480 | 3 | 100 | 52 | 40 | 2747 | 1,3,5,6,7c and 8
[10 empty] | STR | Square D | 8536SEO1*** | 480 | 3 | 100kA | 65 | 50
SE194083 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 480 | 3 | 100 | 65 | 50 | 2747 | 1,3,5,6,7c and 8
[10 empty] | STR | Square D | 8536SEO1*** | 480 | 3 | 100kA | 65 | 50
SE194084 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 21 | 14 | 11 | D | ICB | Schneider | BV4T115J | 600 | 3 | - | 115 | - | 480 | 3 | 100 | 77 | 60 | 3205 | 1,3,5,6,7d and 8
[10 empty] | STR | Square D | 8536SFO1*** | 480 | 3 | 100kA | 77 | 60
Reversing
SE194201 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 208 | 3 | 25 | 2.5 | 0.5 | 2747 | 1,3,5,6,7a,8,9 and 11
[10 empty] | STR | Square D | 8736SCO@*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194202 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 25 | 2.5 | 0.5 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194203 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 25 | 4.8 | 1 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194204 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 25 | 6.9 | 1.5 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194205 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 208 | 3 | 25 | 7.8 | 2 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194206 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 208 | 3 | 25 | 11 | 3 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194207 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 208 | 3 | 25 | 17.5 | 5 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194208 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 25.3 | 7.5 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194209 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 32.2 | 10 | 2747 | 1,3,4,5,6,7b,8,9 and 10
[10 empty] | STR | Square D | 8736SDO@*** | 208 | 3 | 100kA | 32.2 | 10
SE194210 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 48.3 | 15 | 4120 | 1,3,4,5,6,7c,8,9 and 10
[10 empty] | STR | Square D | 8736SEO@*** | 208 | 3 | 100kA | 78.2 | 25
SE194211 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 208 | 3 | 25 | 62.1 | 20 | 4120 | 1,3,4,5,6,7c,8,9 and 10
[10 empty] | STR | Square D | 8736SEO@*** | 208 | 3 | 100kA | 78.2 | 25
SE194212 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 208 | 3 | 25 | 78.2 | 25 | 4120 | 1,3,4,5,6,7c,8,9 and 10
[10 empty] | STR | Square D | 8736SEO@*** | 208 | 3 | 100kA | 78.2 | 25
SE194213 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 240 | 3 | 25 | 80 | 30 | 4120 | 1,3,4,5,6,7c,8,9 and 10
[10 empty] | STR | Square D | 8736SEO@*** | 240 | 3 | 100kA | 80 | 30
SE194214 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 |  | 480 | 3 | 18 | 77 | 60 | 4120 | 1,3,4,5,6,7c,8,9 and 10
[10 empty] | STR | Square D | 8736SEO@*** | 480 | 3 | 100kA | 77 | 60
SE194215 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 | - | 208 | 3 | 25 | 78.2 | 25 | 4120 | 1,3,4,5,6,7c,8,9 and 10
[10 empty] | STR | Square D | 8736SEO@*** | 208 | 3 | 100kA | 78.2 | 25
SE194216 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 240 | 3 | 25 | 2.2 | 0.5 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 240 | 3 | 100kA | 22 | 7.5
SE194217 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 3.2 | 0.75 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 240 | 3 | 100kA | 22 | 7.5
SE194218 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 4.2 | 1 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 240 | 3 | 100kA | 22 | 7.5
SE194219 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 6 | 1.5 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 240 | 3 | 100kA | 22 | 7.5
SE194220 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 6.8 | 2 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 240 | 3 | 100kA | 22 | 7.5
SE194221 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 240 | 3 | 25 | 15.2 | 5 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 240 | 3 | 100kA | 22 | 7.5
SE194222 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 240 | 3 | 25 | 22 | 7.5 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 240 | 3 | 100kA | 22 | 7.5
SE194223 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 240 | 3 | 25 | 28 | 10 | 2747 | 1,3,4,5,6,7b,8,9 and 10
[10 empty] | STR | Square D | 8736SDO@*** | 240 | 3 | 100kA | 42 | 15
SE194224 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 240 | 3 | 25 | 42 | 15 | 2747 | 1,3,4,5,6,7c,8,9 and 10
[10 empty] | STR | Square D | 8736SDO@*** | 240 | 3 | 100kA | 42 | 15
SE194225 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 240 | 3 | 25 | 54 | 20 | 4120 | 1,3,4,5,6,7c,8,9 and 10
[10 empty] | STR | Square D | 8736SEO@*** | 240 | 3 | 100kA | 80 | 30
SE194226 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 240 | 3 | 25 | 68 | 25 | 4120 | 1,3,4,5,6,7c,8,9 and 10
[10 empty] | STR | Square D | 8736SEO@*** | 240 | 3 | 100kA | 80 | 30
SE194227 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 | - | 240 | 3 | 25 | 80 | 30 | 4120 | 1,3,4,5,6,7c,8,9 and 10
[10 empty] | STR | Square D | 8736SEO@*** | 240 | 3 | 100kA | 80 | 30
SE194228 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T002D | 600 | 3 | - | 2 | - | 480 | 3 | 18 | 1.1 | 0.5 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 480 | 3 | 100kA | 14 | 10
SE194229 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T002D | 600 | 3 | - | 2 | - | 480 | 3 | 18 | 1.6 | 0.75 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 480 | 3 | 100kA | 14 | 10
SE194230 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 480 | 3 | 18 | 2.1 | 1 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 480 | 3 | 100kA | 14 | 10
SE194231 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 480 | 3 | 18 | 3 | 1.5 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 480 | 3 | 100kA | 14 | 10
SE194232 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 480 | 3 | 18 | 3.4 | 2 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 480 | 3 | 100kA | 14 | 10
SE194233 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 480 | 3 | 18 | 4.8 | 3 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 480 | 3 | 100kA | 14 | 10
SE194234 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 480 | 3 | 18 | 7.6 | 5 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 480 | 3 | 100kA | 14 | 10
SE194235 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 480 | 3 | 18 | 11 | 7.5 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 480 | 3 | 100kA | 14 | 10
SE194236 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 480 | 3 | 18 | 14 | 10 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 480 | 3 | 100kA | 14 | 10
SE194237 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 480 | 3 | 18 | 21 | 15 | 2747 | 1,3,4,5,6,7b,8,9 and 10
[10 empty] | STR | Square D | 8736SDO@*** | 480 | 3 | 100kA | 34 | 25
SE194238 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 480 | 3 | 18 | 27 | 20 | 2747 | 1,3,4,5,6,7b,8,9 and 10
[10 empty] | STR | Square D | 8736SDO@*** | 480 | 3 | 100kA | 34 | 25
SE194239 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 |  | 480 | 3 | 18 | 34 | 25 | 2747 | 1,3,4,5,6,7b,8,9 and 10
[10 empty] | STR | Square D | 8736SDO@*** | 480 | 3 | 100kA | 34 | 25
SE194240 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 |  | 480 | 3 | 18 | 40 | 30 | 4120 | 1,3,4,5,6,7c,8,9 and 10
[10 empty] | STR | Square D | 8736SEO@*** | 480 | 3 | 100kA | 65 | 50
SE194241 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 |  | 480 | 3 | 18 | 52 | 40 | 4120 | 1,3,4,5,6,7c,8,9 and 10
[10 empty] | STR | Square D | 8736SEO@*** | 480 | 3 | 100kA | 65 | 50
SE194242 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 |  | 480 | 3 | 18 | 65 | 50 | 4120 | 1,3,4,5,6,7c,8,9 and 10
[10 empty] | STR | Square D | 8736SEO@*** | 480 | 3 | 100kA | 65 | 50
SE194243 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 33 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 |  | 480 | 3 | 18 | 77 | 60 | 5036 | 1,3,4,5,6,7d,8,9 and 10
[10 empty] | STR | Square D | 8736SFO@*** | 480 | 3 | 100kA | 77 | 60
SE194244 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 208 | 3 | 100 | 2.5 | 0.5 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194245 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 208 | 3 | 100 | 3.7 | 0.75 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194246 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 208 | 3 | 100 | 4.8 | 1 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194247 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 208 | 3 | 100 | 6.9 | 1.5 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194248 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 100 | 7.8 | 2 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194249 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 100 | 11 | 3 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194250 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 208 | 3 | 100 | 17.5 | 5 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194251 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 100 | 25.3 | 7.5 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 208 | 3 | 100kA | 25.3 | 7.5
SE194252 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 100 | 32.2 | 10 | 2747 | 1,3,4,5,6,7b,8,9 and 10
[10 empty] | STR | Square D | 8736SDO@*** | 208 | 3 | 100kA | 32.2 | 10
SE194253 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 100 | 48.3 | 15 | 4120 | 1,3,4,5,6,7c,8,9 and 10
[10 empty] | STR | Square D | 8736SEO@*** | 208 | 3 | 100kA | 78.2 | 25
SE194254 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 208 | 3 | 100 | 62.1 | 20 | 4120 | 1,3,4,5,6,7c,8,9 and 10
[10 empty] | STR | Square D | 8736SEO@*** | 208 | 3 | 100kA | 78.2 | 25
SE194255 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 208 | 3 | 100 | 78.2 | 25 | 4120 | 1,3,4,5,6,7c,8,9 and 10
[10 empty] | STR | Square D | 8736SEO@*** | 208 | 3 | 100kA | 78.2 | 25
SE194256 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 240 | 3 | 100 | 2.2 | 0.5 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 240 | 3 | 100kA | 22 | 7.5
SE194257 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 3.2 | 0.75 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 240 | 3 | 100kA | 22 | 7.5
SE194258 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 4.2 | 1 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 240 | 3 | 100kA | 22 | 7.5
SE194259 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 6 | 1.5 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 240 | 3 | 100kA | 22 | 7.5
SE194260 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 6.8 | 2 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 240 | 3 | 100kA | 22 | 7.5
SE194261 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 240 | 3 | 100 | 9.6 | 3 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 240 | 3 | 100kA | 22 | 7.5
SE194262 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 240 | 3 | 100 | 15.2 | 5 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 240 | 3 | 100kA | 22 | 7.5
SE194263 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 240 | 3 | 100 | 22 | 7.5 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 240 | 3 | 100kA | 22 | 7.5
SE194264 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 100 | 28 | 10 | 2747 | 1,3,4,5,6,7b,8,9 and 10
[10 empty] | STR | Square D | 8736SDO@*** | 240 | 3 | 100kA | 42 | 15
SE194265 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 100 | 42 | 15 | 2747 | 1,3,4,5,6,7b,8,9 and 10
[10 empty] | STR | Square D | 8736SDO@*** | 240 | 3 | 100kA | 42 | 15
SE194266 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 240 | 3 | 100 | 54 | 20 | 4120 | 1,3,4,5,6,7c,8,9 and 10
[10 empty] | STR | Square D | 8736SEO@*** | 240 | 3 | 100kA | 80 | 30
SE194267 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 240 | 3 | 100 | 68 | 25 | 4120 | 1,3,4,5,6,7c,8,9 and 10
[10 empty] | STR | Square D | 8736SEO@*** | 240 | 3 | 100kA | 80 | 30
SE194268 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 240 | 3 | 100 | 80 | 30 | 4120 | 1,3,4,5,6,7c,8,9 and 10
[10 empty] | STR | Square D | 8736SEO@*** | 240 | 3 | 100kA | 80 | 30
SE194269 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T002J | 600 | 3 | - | 2 | - | 480 | 3 | 100 | 1.1 | 0.5 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 480 | 3 | 100kA | 14 | 10
SE194270 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T002J | 600 | 3 | - | 2 | - | 480 | 3 | 100 | 1.6 | 0.75 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 480 | 3 | 100kA | 14 | 10
SE194271 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 480 | 3 | 100 | 2.1 | 1 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 480 | 3 | 100kA | 14 | 10
SE194272 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 480 | 3 | 100 | 3 | 1.5 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 480 | 3 | 100kA | 14 | 10
SE194273 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 480 | 3 | 100 | 3.4 | 2 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 480 | 3 | 100kA | 14 | 10
SE194274 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 480 | 3 | 100 | 4.8 | 3 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 480 | 3 | 100kA | 14 | 10
SE194275 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 480 | 3 | 100 | 7.6 | 5 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 480 | 3 | 100kA | 14 | 10
SE194276 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 480 | 3 | 100 | 11 | 7.5 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 480 | 3 | 100kA | 14 | 10
SE194277 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 480 | 3 | 100 | 14 | 10 | 2747 | 1,3,4,5,6,7a,8,9 and 10
[10 empty] | STR | Square D | 8736SCO@*** | 480 | 3 | 100kA | 14 | 10
SE194278 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 480 | 3 | 100 | 21 | 15 | 2747 | 1,3,4,5,6,7b,8,9 and 10
[10 empty] | STR | Square D | 8736SDO@*** | 480 | 3 | 100kA | 34 | 25
SE194279 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 480 | 3 | 100 | 27 | 20 | 2747 | 1,3,4,5,6,7b,8,9 and 10
[10 empty] | STR | Square D | 8736SDO@*** | 480 | 3 | 100kA | 34 | 25
SE194280 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 480 | 3 | 100 | 34 | 25 | 2747 | 1,3,4,5,6,7b,8,9 and 10
[10 empty] | STR | Square D | 8736SDO@*** | 480 | 3 | 100kA | 34 | 25
SE194281 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 480 | 3 | 100 | 40 | 30 | 4120 | 1,3,4,5,6,7c,8,9 and 10
[10 empty] | STR | Square D | 8736SEO@*** | 480 | 3 | 100kA | 65 | 50
SE194282 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 480 | 3 | 100 | 52 | 40 | 4120 | 1,3,4,5,6,7c,8,9 and 10
[10 empty] | STR | Square D | 8736SEO@*** | 480 | 3 | 100kA | 65 | 50
SE194283 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 480 | 3 | 100 | 65 | 50 | 4120 | 1,3,4,5,6,7c,8,9 and 10
[10 empty] | STR | Square D | 8736SEO@*** | 480 | 3 | 100kA | 65 | 50
SE194284 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 33 | 14 | 11 | D | ICB | Schneider | BV4T115J | 600 | 3 | - | 115 | - | 480 | 3 | 100 | 77 | 60 | 5036 | 1,3,4,5,6,7d,8,9 and 10
[10 empty] | STR | Square D | 8736SFO@*** | 480 | 3 | 100kA | 77 | 60
168

## Motor Logic
Template for Submission of Combination Motor Controller
(NOTE: The bracketed alphanumeric in each column heading and in example entries, such as [B1], corresponds to a section of the short circuit database submittal guideline document which provides further information concerning the expected content and format for entering data into the spreadsheet cells)
Database Identification Number | Listed Combination Motor Controller Information | [7 empty] | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Enclosure Volume, cubic inches | Conditions of Use | [B10] Schematic | [B11] Other References
| Listing Report Information |  |  |  |  | Enclosure or Unit Dimensions
| UL File Number | Report Issue Date | Volume / Section | Model Number or Product Style/ Designation | Product Description on Page/Figure/Ill. | Enclosure or Unit Height, inches | Width, inches | Depth, inches |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating
Non-reversing
SE191001 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 208 | 3 | 25 | 2.5 | 0.5 | 1832 | 1,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3***H308 | 208 | 3 | 100kA | 1.5 - 4.5 | 3/4
SE191002 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 25 | 3.7 | 0.75 | 1832 | 1,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3***H309 | 208 | 3 | 100kA | 3 - 9 | 2
SE191003 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 25 | 4.8 | 1 | 1832 | 1,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3***H309 | 208 | 3 | 100kA | 3 - 9 | 2
SE191004 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 25 | 6.9 | 1.5 | 1832 | 1,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3***H300 | 208 | 3 | 100kA | 6 - 18 | 5
SE191005 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 208 | 3 | 25 | 7.8 | 2 | 1832 | 1,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3***H300 | 208 | 3 | 100kA | 6 - 18 | 5
SE191006 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 208 | 3 | 25 | 11 | 3 | 1832 | 1,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3***H30 | 208 | 3 | 100kA | 9 - 27 | 7 1/2
SE191007 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 208 | 3 | 25 | 17.5 | 5 | 1832 | 1,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3***H30 | 208 | 3 | 100kA | 9 - 27 | 7 1/2
SE191008 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 25.3 | 7.5 | 1832 | 1,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3***H30 | 208 | 3 | 100kA | 9 - 27 | 7 1/2
SE191009 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 32.2 | 10 | 1832 | 1,5,6,7b,8 and 11
[10 empty] | STR | Square D | 8536SDO1***H30 | 208 | 3 | 100kA | 15 - 45 | 10
SE191010 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 48.3 | 15 | 2747 | 1,5,6,7c,8 and 11
[10 empty] | STR | Square D | 8536SEO1***H30 | 208 | 3 | 100kA | 30 - 90 | 25
SE191011 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 208 | 3 | 25 | 62.1 | 20 | 2747 | 1,5,6,7c,8 and 11
[10 empty] | STR | Square D | 8536SEO1***H30 | 208 | 3 | 100kA | 30 - 90 | 25
SE191012 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 | - | 208 | 3 | 25 | 78.2 | 25 | 2747 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SEO1***H30 | 208 | 3 | 100kA | 30 - 90 | 25
SE191013 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 240 | 3 | 25 | 2.2 | 0.5 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H308 | 240 | 3 | 100kA | 1.5 - 4.5 | 1
SE191014 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 3.2 | 0.75 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H308 | 240 | 3 | 100kA | 1.5 - 4.5 | 1
SE191015 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 4.2 | 1 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H309 | 240 | 3 | 100kA | 3 - 9 | 2
SE191016 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 6 | 1.5 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H309 | 240 | 3 | 100kA | 3 - 9 | 2
SE191017 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 6.8 | 2 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H300 | 240 | 3 | 100kA | 6 - 18 | 5
SE191018 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 240 | 3 | 25 | 9.6 | 3 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H30 | 240 | 3 | 100kA | 9 - 27 | 7 1/2
SE191019 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 240 | 3 | 25 | 15.2 | 5 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H30 | 240 | 3 | 100kA | 9 - 27 | 7 1/2
SE191020 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 240 | 3 | 25 | 22 | 7.5 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H30 | 240 | 3 | 100kA | 9 - 27 | 7 1/2
SE191021 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 240 | 3 | 25 | 28 | 10 | 1832 | 1,5,6,7b and 8.
[10 empty] | STR | Square D | 8536SDO1***H30 | 240 | 3 | 100kA | 15 - 45 | 15
SE191022 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 240 | 3 | 25 | 42 | 15 | 1832 | 1,5,6,7b and 8.
[10 empty] | STR | Square D | 8536SDO1***H30 | 240 | 3 | 100kA | 15 - 45 | 15
SE191023 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 240 | 3 | 25 | 54 | 20 | 2747 | 1,5,6,7c and 8.
[10 empty] | STR | Square D | 8536SEO1***H30 | 240 | 3 | 100kA | 30 - 90 | 30
SE191024 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 240 | 3 | 25 | 68 | 25 | 2747 | 1,5,6,7c and 8.
[10 empty] | STR | Square D | 8536SEO1***H30 | 240 | 3 | 100kA | 30 - 90 | 30
SE191025 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 | - | 240 | 3 | 25 | 80 | 30 | 2747 | 1,5,6,7c and 8.
[10 empty] | STR | Square D | 8536SEO1***H30 | 240 | 3 | 100kA | 30 - 90 | 30
SE191026 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T002D | 600 | 3 | - | 2 | - | 480 | 3 | 18 | 1.1 | 0.5 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H308 | 480 | 3 | 100kA | 1.5 - 4.5 | 2
SE191027 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T002D | 600 | 3 | - | 2 | - | 480 | 3 | 18 | 1.6 | 0.75 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H308 | 480 | 3 | 100kA | 1.5 - 4.5 | 2
SE191028 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 480 | 3 | 18 | 2.1 | 1 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H308 | 480 | 3 | 100kA | 1.5 - 4.5 | 2
SE191029 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 480 | 3 | 18 | 3 | 1.5 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H308 | 480 | 3 | 100kA | 1.5 - 4.5 | 2
SE191030 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 480 | 3 | 18 | 3.4 | 2 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H308 | 480 | 3 | 100kA | 1.5 - 4.5 | 2
SE191031 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 480 | 3 | 18 | 4.8 | 3 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H309 | 480 | 3 | 100kA | 3 - 9 | 5
SE191032 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 480 | 3 | 18 | 7.6 | 5 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H300 | 480 | 3 | 100kA | 6 - 18 | 10
SE191033 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 480 | 3 | 18 | 11 | 7.5 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H30 | 480 | 3 | 100kA | 9 - 27 | 10
SE191034 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 480 | 3 | 18 | 14 | 10 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H30 | 480 | 3 | 100kA | 9 - 27 | 10
SE191035 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 480 | 3 | 18 | 21 | 15 | 1832 | 1,5,6,7b and 8.
[10 empty] | STR | Square D | 8536SDO1***H30 | 480 | 3 | 100kA | 9 - 27 | 20
SE191036 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 480 | 3 | 18 | 27 | 20 | 1832 | 1,5,6,7b and 8.
[10 empty] | STR | Square D | 8536SDO1***H30 | 480 | 3 | 100kA | 15 - 45 | 25
SE191037 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 480 | 3 | 18 | 34 | 25 | 1832 | 1,5,6,7b and 8.
[10 empty] | STR | Square D | 8536SDO1***H30 | 480 | 3 | 100kA | 15 - 45 | 25
SE191038 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 480 | 3 | 18 | 40 | 30 | 2747 | 1,5,6,7c and 8.
[10 empty] | STR | Square D | 8536SEO1***H30 | 480 | 3 | 100kA | 30 - 90 | 50
SE191039 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 480 | 3 | 18 | 52 | 40 | 2747 | 1,5,6,7c and 8.
[10 empty] | STR | Square D | 8536SEO1***H30 | 480 | 3 | 100kA | 30 - 90 | 50
SE191040 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 480 | 3 | 18 | 65 | 50 | 2747 | 1,5,6,7c and 8.
[10 empty] | STR | Square D | 8536SEO1***H30 | 480 | 3 | 100kA | 30 - 90 | 50
SE191041 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 21 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 | - | 480 | 3 | 18 | 77 | 60 | 3205 | 1,5,6,7d and 8.
[10 empty] | STR | Square D | 8536SFO1***H30 | 480 | 3 | 100kA | 30 - 90 | 60
SE191042 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 208 | 3 | 100 | 2.5 | 0.5 | 1832 | 1,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3***H308 | 208 | 3 | 100kA | 1.5 - 4.5 | 3/4
SE191043 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 208 | 3 | 100 | 3.7 | 0.75 | 1832 | 1,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3***H309 | 208 | 3 | 100kA | 3 - 9 | 2
SE191044 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 208 | 3 | 100 | 4.8 | 1 | 1832 | 1,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3***H309 | 208 | 3 | 100kA | 3 - 9 | 2
SE191045 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 208 | 3 | 100 | 6.9 | 1.5 | 1832 | 1,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3***H300 | 208 | 3 | 100kA | 6 - 18 | 5
SE191046 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 100 | 7.8 | 2 | 1832 | 1,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3***H300 | 208 | 3 | 100kA | 6 - 18 | 5
SE191047 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 100 | 11 | 3 | 1832 | 1,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3***H30 | 208 | 3 | 100kA | 9 - 27 | 7 1/2
SE191048 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 208 | 3 | 100 | 17.5 | 5 | 1832 | 1,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3***H30 | 208 | 3 | 100kA | 9 - 27 | 7 1/2
SE191049 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 100 | 25.3 | 7.5 | 1832 | 1,5,6,7a,8 and 11
[10 empty] | STR | Square D | 8536SCO3***H30 | 208 | 3 | 100kA | 9 - 27 | 7 1/2
SE191050 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 100 | 32.2 | 10 | 1832 | 1,5,6,7b,8 and 11
[10 empty] | STR | Square D | 8536SDO1***H30 | 208 | 3 | 100kA | 15 - 45 | 10
SE191051 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 100 | 48.3 | 15 | 2747 | 1,5,6,7c,8 and 11
[10 empty] | STR | Square D | 8536SEO1***H30 | 208 | 3 | 100kA | 30 - 90 | 25
SE191052 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 208 | 3 | 100 | 62.1 | 20 | 2747 | 1,5,6,7c,8 and 11
[10 empty] | STR | Square D | 8536SEO1***H30 | 208 | 3 | 100kA | 30 - 90 | 25
SE191053 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T115J | 600 | 3 | - | 115 | - | 208 | 3 | 100 | 78.2 | 25 | 2747 | 1,5,6,7c,8 and 11
[10 empty] | STR | Square D | 8536SEO1***H30 | 208 | 3 | 100kA | 30 - 90 | 25
SE191054 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 240 | 3 | 100 | 2.2 | 0.5 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H308 | 240 | 3 | 100kA | 1.5 - 4.5 | 1
SE191055 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 3.2 | 0.75 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H308 | 240 | 3 | 100kA | 1.5 - 4.5 | 1
SE191056 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 4.2 | 1 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H309 | 240 | 3 | 100kA | 3 - 9 | 2
SE191057 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 6 | 1.5 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H309 | 240 | 3 | 100kA | 3 - 9 | 2
SE191058 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 6.8 | 2 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H300 | 240 | 3 | 100kA | 6 - 18 | 5
SE191059 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 240 | 3 | 100 | 9.6 | 3 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H30 | 240 | 3 | 100kA | 9 - 27 | 7 1/2
SE191060 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 240 | 3 | 100 | 15.2 | 5 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H30 | 240 | 3 | 100kA | 9 - 27 | 7 1/2
SE191061 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 240 | 3 | 100 | 22 | 7.5 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H30 | 240 | 3 | 100kA | 9 - 27 | 7 1/2
SE191062 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 100 | 28 | 10 | 1832 | 1,5,6,7b and 8.
[10 empty] | STR | Square D | 8536SDO1***H30 | 240 | 3 | 100kA | 15 - 45 | 15
SE191063 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 100 | 42 | 15 | 1832 | 1,5,6,7b and 8.
[10 empty] | STR | Square D | 8536SDO1***H30 | 240 | 3 | 100kA | 15 - 45 | 15
SE191064 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 240 | 3 | 100 | 54 | 20 | 2747 | 1,5,6,7c and 8.
[10 empty] | STR | Square D | 8536SEO1***H30 | 240 | 3 | 100kA | 30 - 90 | 30
SE191065 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 240 | 3 | 100 | 68 | 25 | 2747 | 1,5,6,7c and 8.
[10 empty] | STR | Square D | 8536SEO1***H30 | 240 | 3 | 100kA | 30 - 90 | 30
SE191066 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T115J | 600 | 3 | - | 115 | - | 240 | 3 | 100 | 80 | 30 | 2747 | 1,5,6,7c and 8.
[10 empty] | STR | Square D | 8536SEO1***H30 | 240 | 3 | 100kA | 30 - 90 | 30
SE191067 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T002J | 600 | 3 | - | 2 | - | 480 | 3 | 100 | 1.1 | 0.5 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H308 | 480 | 3 | 100kA | 1.5 - 4.5 | 2
SE191068 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T002J | 600 | 3 | - | 2 | - | 480 | 3 | 100 | 1.6 | 0.75 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H308 | 480 | 3 | 100kA | 1.5 - 4.5 | 2
SE191069 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 480 | 3 | 100 | 2.1 | 1 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H308 | 480 | 3 | 100kA | 1.5 - 4.5 | 2
SE191070 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 480 | 3 | 100 | 3 | 1.5 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H308 | 480 | 3 | 100kA | 1.5 - 4.5 | 2
SE191071 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 480 | 3 | 100 | 3.4 | 2 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H308 | 480 | 3 | 100kA | 1.5 - 4.5 | 2
SE191072 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 480 | 3 | 100 | 4.8 | 3 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H309 | 480 | 3 | 100kA | 3 - 9 | 5
SE191073 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 480 | 3 | 100 | 7.6 | 5 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H300 | 480 | 3 | 100kA | 6 - 18 | 10
SE191074 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 480 | 3 | 100 | 11 | 7.5 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H30 | 480 | 3 | 100kA | 9 - 27 | 10
SE191075 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 480 | 3 | 100 | 14 | 10 | 1832 | 1,5,6,7a and 8.
[10 empty] | STR | Square D | 8536SCO3***H30 | 480 | 3 | 100kA | 9 - 27 | 10
SE191076 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 480 | 3 | 100 | 21 | 15 | 1832 | 1,5,6,7b and 8.
[10 empty] | STR | Square D | 8536SDO1***H30 | 480 | 3 | 100kA | 15 - 45 | 25
SE191077 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 480 | 3 | 100 | 27 | 20 | 1832 | 1,5,6,7b and 8.
[10 empty] | STR | Square D | 8536SDO1***H30 | 480 | 3 | 100kA | 15 - 45 | 25
SE191078 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 480 | 3 | 100 | 34 | 25 | 1832 | 1,5,6,7b and 8.
[10 empty] | STR | Square D | 8536SDO1***H30 | 480 | 3 | 100kA | 15 - 45 | 25
SE191079 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 480 | 3 | 100 | 40 | 30 | 2772 | 1,5,6,7c and 8.
[10 empty] | STR | Square D | 8536SEO1***H30 | 480 | 3 | 100kA | 30 - 90 | 50
SE191080 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 480 | 3 | 100 | 52 | 40 | 2747 | 1,5,6,7c and 8.
[10 empty] | STR | Square D | 8536SEO1***H30 | 480 | 3 | 100kA | 30 - 90 | 50
SE191081 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 480 | 3 | 100 | 65 | 50 | 2747 | 1,5,6,7c and 8.
[10 empty] | STR | Square D | 8536SEO1***H30 | 480 | 3 | 100kA | 30 - 90 | 50
SE191082 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T115J | 600 | 3 | - | 115 | - | 480 | 3 | 100 | 77 | 60 | 3205 | 1,5,6,7d and 8.
[10 empty] | STR | Square D | 8536SFO1***H30 | 480 | 3 | 100kA | 30 - 90 | 60
Reversing
SE191101 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 208 | 3 | 25 | 2.5 | 0.5 | 2747 | 1,5,6,7a, 8, 9 and 11.
[10 empty] | STR | Square D | 8736SCO@***H308 | 208 | 3 | 100kA | 1.5 - 4.5 | 3/4
SE191102 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 25 | 3.7 | 0.75 | 2747 | 1,5,6,7a, 8, 9 and 11.
[10 empty] | STR | Square D | 8736SCO@***H309 | 208 | 3 | 100kA | 3 - 9 | 2
SE191103 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 25 | 4.8 | 1 | 2747 | 1,5,6,7a, 8, 9 and 11.
[10 empty] | STR | Square D | 8736SCO@***H309 | 208 | 3 | 100kA | 3 - 9 | 2
SE191104 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 25 | 6.9 | 1.5 | 2747 | 1,5,6,7a, 8, 9 and 11.
[10 empty] | STR | Square D | 8736SCO@***H300 | 208 | 3 | 100kA | 6 - 18 | 5
SE191105 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 208 | 3 | 25 | 7.8 | 2 | 2747 | 1,5,6,7a, 8, 9 and 11.
[10 empty] | STR | Square D | 8736SCO@***H300 | 208 | 3 | 100kA | 6 - 18 | 5
SE191106 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 208 | 3 | 25 | 11 | 3 | 2747 | 1,5,6,7a, 8, 9 and 11.
[10 empty] | STR | Square D | 8736SCO@***H30 | 208 | 3 | 100kA | 9 - 27 | 7 1/2
SE191107 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 208 | 3 | 25 | 17.5 | 5 | 2747 | 1,5,6,7a, 8, 9 and 11.
[10 empty] | STR | Square D | 8736SCO@***H30 | 208 | 3 | 100kA | 9 - 27 | 7 1/2
SE191108 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 25.3 | 7.5 | 2747 | 1,5,6,7a, 8, 9 and 11.
[10 empty] | STR | Square D | 8736SCO@***H30 | 208 | 3 | 100kA | 9 - 27 | 7 1/2
SE191109 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 32.2 | 10 | 2747 | 1,5,6,7b, 8, 9 and 11.
[10 empty] | STR | Square D | 8736SDO@***H30 | 208 | 3 | 100kA | 15 - 45 | 10
SE191110 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 48.3 | 15 | 4120 | 1,5,6,7c, 8, 9 and 11.
[10 empty] | STR | Square D | 8736SEO@***H30 | 208 | 3 | 100kA | 30 - 90 | 25
SE191111 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 208 | 3 | 25 | 62.1 | 20 | 4120 | 1,5,6,7c, 8, 9 and 11.
[10 empty] | STR | Square D | 8736SEO@***H30 | 208 | 3 | 100kA | 30 - 90 | 25
SE191112 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 | - | 208 | 3 | 25 | 78.2 | 25 | 4120 | 1,5,6,7c, 8, 9 and 11.
[10 empty] | STR | Square D | 8736SEO@***H30 | 208 | 3 | 100kA | 30 - 90 | 25
SE191113 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 240 | 3 | 25 | 2.2 | 0.5 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H308 | 240 | 3 | 100kA | 1.5 - 4.5 | 1
SE191114 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 3.2 | 0.75 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H308 | 240 | 3 | 100kA | 1.5 - 4.5 | 1
SE191115 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 4.2 | 1 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H309 | 240 | 3 | 100kA | 3 - 9 | 2
SE191116 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 6 | 1.5 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H309 | 240 | 3 | 100kA | 3 - 9 | 2
SE191117 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 6.8 | 2 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H300 | 240 | 3 | 100kA | 6 - 18 | 5
SE191118 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 240 | 3 | 25 | 9.6 | 3 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H30 | 240 | 3 | 100kA | 9 - 27 | 7 1/2
SE191119 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 240 | 3 | 25 | 15.2 | 5 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H30 | 240 | 3 | 100kA | 9 - 27 | 7 1/2
SE191120 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 240 | 3 | 25 | 22 | 7.5 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H30 | 240 | 3 | 100kA | 9 - 27 | 7 1/2
SE191121 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 240 | 3 | 25 | 28 | 10 | 2747 | 1,5,6,7b, 8 and 9.
[10 empty] | STR | Square D | 8736SDO@***H30 | 240 | 3 | 100kA | 15 - 45 | 15
SE191122 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 240 | 3 | 25 | 42 | 15 | 2747 | 1,5,6,7b, 8 and 9.
[10 empty] | STR | Square D | 8736SDO@***H30 | 240 | 3 | 100kA | 15 - 45 | 15
SE191123 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 240 | 3 | 25 | 54 | 20 | 4120 | 1,5,6,7b, 8 and 9.
[10 empty] | STR | Square D | 8736SEO@***H30 | 240 | 3 | 100kA | 30 - 90 | 30
SE191124 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 240 | 3 | 25 | 68 | 25 | 4120 | 1,5,6,7c, 8 and 9.
[10 empty] | STR | Square D | 8736SEO@***H30 | 240 | 3 | 100kA | 30 - 90 | 30
SE191125 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 | - | 240 | 3 | 25 | 80 | 30 | 4120 | 1,5,6,7c, 8 and 9.
[10 empty] | STR | Square D | 8736SEO@***H30 | 240 | 3 | 100kA | 30 - 90 | 30
SE191126 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T002D | 600 | 3 | - | 2 | - | 480 | 3 | 18 | 1.1 | 0.5 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H308 | 480 | 3 | 100kA | 1.5 - 4.5 | 2
SE191127 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T002D | 600 | 3 | - | 2 | - | 480 | 3 | 18 | 1.6 | 0.75 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H308 | 480 | 3 | 100kA | 1.5 - 4.5 | 2
SE191128 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 480 | 3 | 18 | 2.1 | 1 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H308 | 480 | 3 | 100kA | 1.5 - 4.5 | 2
SE191129 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 480 | 3 | 18 | 3 | 1.5 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H308 | 480 | 3 | 100kA | 1.5 - 4.5 | 2
SE191130 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 480 | 3 | 18 | 3.4 | 2 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H308 | 480 | 3 | 100kA | 1.5 - 4.5 | 2
SE191131 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 480 | 3 | 18 | 4.8 | 3 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H309 | 480 | 3 | 100kA | 3 - 9 | 5
SE191132 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 480 | 3 | 18 | 7.6 | 5 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H300 | 480 | 3 | 100kA | 6 - 18 | 10
SE191133 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 480 | 3 | 18 | 11 | 7.5 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H30 | 480 | 3 | 100kA | 9 - 27 | 10
SE191134 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 480 | 3 | 18 | 14 | 10 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H30 | 480 | 3 | 100kA | 9 - 27 | 10
SE191135 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 480 | 3 | 18 | 21 | 15 | 2747 | 1,5,6,7b, 8 and 9.
[10 empty] | STR | Square D | 8736SDO@***H30 | 480 | 3 | 100kA | 9 - 27 | 20
SE191136 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 480 | 3 | 18 | 27 | 20 | 2747 | 1,5,6,7b, 8 and 9.
[10 empty] | STR | Square D | 8736SDO@***H30 | 480 | 3 | 100kA | 15 - 45 | 25
SE191137 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 480 | 3 | 18 | 34 | 25 | 2747 | 1,5,6,7b, 8 and 9.
[10 empty] | STR | Square D | 8736SDO@***H30 | 480 | 3 | 100kA | 15 - 45 | 25
SE191138 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 480 | 3 | 18 | 40 | 30 | 4120 | 1,5,6,7c, 8 and 9.
[10 empty] | STR | Square D | 8736SEO@***H30 | 480 | 3 | 100kA | 30 - 90 | 50
SE191139 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 480 | 3 | 18 | 52 | 40 | 4120 | 1,5,6,7c, 8 and 9.
[10 empty] | STR | Square D | 8736SEO@***H30 | 480 | 3 | 100kA | 30 - 90 | 50
SE191140 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 480 | 3 | 18 | 65 | 50 | 4120 | 1,5,6,7c, 8 and 9.
[10 empty] | STR | Square D | 8736SEO@***H30 | 480 | 3 | 100kA | 30 - 90 | 50
SE191141 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 33 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 | - | 480 | 3 | 18 | 77 | 60 | 5036 | 1,5,6,7d, 8 and 9.
[10 empty] | STR | Square D | 8736SFO@***H30 | 480 | 3 | 100kA | 30 - 90 | 60
SE191142 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 208 | 3 | 100 | 2.5 | 0.5 | 2747 | 1,5,6,7a, 8, 9 and 11.
[10 empty] | STR | Square D | 8736SCO@***H308 | 208 | 3 | 100kA | 1.5 - 4.5 | 3/4
SE191143 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 208 | 3 | 100 | 3.7 | 0.75 | 2747 | 1,5,6,7a, 8, 9 and 11.
[10 empty] | STR | Square D | 8736SCO@***H309 | 208 | 3 | 100kA | 3 - 9 | 2
SE191144 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 208 | 3 | 100 | 4.8 | 1 | 2747 | 1,5,6,7a, 8, 9 and 11.
[10 empty] | STR | Square D | 8736SCO@***H309 | 208 | 3 | 100kA | 3 - 9 | 2
SE191145 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 208 | 3 | 100 | 6.9 | 1.5 | 2747 | 1,5,6,7a, 8, 9 and 11.
[10 empty] | STR | Square D | 8736SCO@***H300 | 208 | 3 | 100kA | 6 - 18 | 5
SE191146 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 100 | 7.8 | 2 | 2747 | 1,5,6,7a, 8, 9 and 11.
[10 empty] | STR | Square D | 8736SCO@***H300 | 208 | 3 | 100kA | 6 - 18 | 5
SE191147 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 100 | 11 | 3 | 2747 | 1,5,6,7a, 8, 9 and 11.
[10 empty] | STR | Square D | 8736SCO@***H30 | 208 | 3 | 100kA | 9 - 27 | 7 1/2
SE191148 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 208 | 3 | 100 | 17.5 | 5 | 2747 | 1,5,6,7a, 8, 9 and 11.
[10 empty] | STR | Square D | 8736SCO@***H30 | 208 | 3 | 100kA | 9 - 27 | 7 1/2
SE191149 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 100 | 25.3 | 7.5 | 2747 | 1,5,6,7a, 8, 9 and 11.
[10 empty] | STR | Square D | 8736SCO@***H30 | 208 | 3 | 100kA | 9 - 27 | 7 1/2
SE191150 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 100 | 32.2 | 10 | 2747 | 1,5,6,7b, 8, 9 and 11.
[10 empty] | STR | Square D | 8736SDO@***H30 | 208 | 3 | 100kA | 15 - 45 | 10
SE191151 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 100 | 48.3 | 15 | 4120 | 1,5,6,7c, 8, 9 and 11.
[10 empty] | STR | Square D | 8736SEO@***H30 | 208 | 3 | 100kA | 30 - 90 | 25
SE191152 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 208 | 3 | 100 | 62.1 | 20 | 4120 | 1,5,6,7c, 8, 9 and 11.
[10 empty] | STR | Square D | 8736SEO@***H30 | 208 | 3 | 100kA | 30 - 90 | 25
SE191153 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T115J | 600 | 3 | - | 115 | - | 208 | 3 | 100 | 78.2 | 25 | 4120 | 1,5,6,7c, 8, 9 and 11.
[10 empty] | STR | Square D | 8736SEO@***H30 | 208 | 3 | 100kA | 30 - 90 | 25
SE191154 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 240 | 3 | 100 | 2.2 | 0.5 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H308 | 240 | 3 | 100kA | 1.5 - 4.5 | 1
SE191155 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 3.2 | 0.75 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H308 | 240 | 3 | 100kA | 1.5 - 4.5 | 1
SE191156 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 4.2 | 1 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H309 | 240 | 3 | 100kA | 3 - 9 | 2
SE191157 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 6 | 1.5 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H309 | 240 | 3 | 100kA | 3 - 9 | 2
SE191158 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 6.8 | 2 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H300 | 240 | 3 | 100kA | 6 - 18 | 5
SE191159 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 240 | 3 | 100 | 9.6 | 3 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H30 | 240 | 3 | 100kA | 9 - 27 | 7 1/2
SE191160 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 240 | 3 | 100 | 15.2 | 5 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H30 | 240 | 3 | 100kA | 9 - 27 | 7 1/2
SE191161 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 240 | 3 | 100 | 22 | 7.5 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H30 | 240 | 3 | 100kA | 9 - 27 | 7 1/2
SE191162 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 100 | 28 | 10 | 2747 | 1,5,6,7b, 8 and 9.
[10 empty] | STR | Square D | 8736SDO@***H30 | 240 | 3 | 100kA | 15 - 45 | 15
SE191163 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 100 | 42 | 15 | 2747 | 1,5,6,7b, 8 and 9.
[10 empty] | STR | Square D | 8736SDO@***H30 | 240 | 3 | 100kA | 15 - 45 | 15
SE191164 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 240 | 3 | 100 | 54 | 20 | 4120 | 1,5,6,7c, 8 and 9.
[10 empty] | STR | Square D | 8736SEO@***H30 | 240 | 3 | 100kA | 30 - 90 | 30
SE191165 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 240 | 3 | 100 | 68 | 25 | 4120 | 1,5,6,7c, 8 and 9.
[10 empty] | STR | Square D | 8736SEO@***H30 | 240 | 3 | 100kA | 30 - 90 | 30
SE191166 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T115J | 600 | 3 | - | 115 | - | 240 | 3 | 100 | 80 | 30 | 4120 | 1,5,6,7c, 8 and 9.
[10 empty] | STR | Square D | 8736SEO@***H30 | 240 | 3 | 100kA | 30 - 90 | 30
SE191167 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T002J | 600 | 3 | - | 2 | - | 480 | 3 | 100 | 1.1 | 0.5 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H308 | 480 | 3 | 100kA | 1.5 - 4.5 | 2
SE191168 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T002J | 600 | 3 | - | 2 | - | 480 | 3 | 100 | 1.6 | 0.75 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H308 | 480 | 3 | 100kA | 1.5 - 4.5 | 2
SE191169 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 480 | 3 | 100 | 2.1 | 1 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H308 | 480 | 3 | 100kA | 1.5 - 4.5 | 2
SE191170 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 480 | 3 | 100 | 3 | 1.5 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H308 | 480 | 3 | 100kA | 1.5 - 4.5 | 2
SE191171 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 480 | 3 | 100 | 3.4 | 2 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H308 | 480 | 3 | 100kA | 1.5 - 4.5 | 2
SE191172 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 480 | 3 | 100 | 4.8 | 3 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H309 | 480 | 3 | 100kA | 3 - 9 | 5
SE191173 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 480 | 3 | 100 | 7.6 | 5 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H300 | 480 | 3 | 100kA | 6 - 18 | 10
SE191174 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 480 | 3 | 100 | 11 | 7.5 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H30 | 480 | 3 | 100kA | 9 - 27 | 10
SE191175 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 480 | 3 | 100 | 14 | 10 | 2747 | 1,5,6,7a, 8 and 9.
[10 empty] | STR | Square D | 8736SCO@***H30 | 480 | 3 | 100kA | 9 - 27 | 10
SE191176 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 480 | 3 | 100 | 21 | 15 | 2747 | 1,5,6,7b, 8 and 9.
[10 empty] | STR | Square D | 8736SDO@***H30 | 480 | 3 | 100kA | 15 - 45 | 25
SE191177 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 480 | 3 | 100 | 27 | 20 | 2747 | 1,5,6,7b, 8 and 9.
[10 empty] | STR | Square D | 8736SDO@***H30 | 480 | 3 | 100kA | 15 - 45 | 25
SE191178 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 480 | 3 | 100 | 34 | 25 | 2747 | 1,5,6,7b, 8 and 9.
[10 empty] | STR | Square D | 8736SDO@***H30 | 480 | 3 | 100kA | 15 - 45 | 25
SE191179 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 480 | 3 | 100 | 40 | 30 | 4120 | 1,5,6,7c, 8 and 9.
[10 empty] | STR | Square D | 8736SEO@***H30 | 480 | 3 | 100kA | 30 - 90 | 50
SE191180 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 480 | 3 | 100 | 52 | 40 | 4120 | 1,5,6,7c, 8 and 9.
[10 empty] | STR | Square D | 8736SEO@***H30 | 480 | 3 | 100kA | 30 - 90 | 50
SE191181 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 480 | 3 | 100 | 65 | 50 | 4120 | 1,5,6,7c, 8 and 9.
[10 empty] | STR | Square D | 8736SEO@***H30 | 480 | 3 | 100kA | 30 - 90 | 50
SE191182 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 33 | 14 | 11 | D | ICB | Schneider | BV4T115J | 600 | 3 | - | 115 | - | 480 | 3 | 100 | 77 | 60 | 5036 | 1,5,6,7d, 8 and 9.
[10 empty] | STR | Square D | 8736SFO@***H30 | 480 | 3 | 100kA | 30 - 90 | 60
164

## TeSys T
Template for Submission of Combination Motor Controller
(NOTE: The bracketed alphanumeric in each column heading and in example entries, such as [B1], corresponds to a section of the short circuit database submittal guideline document which provides further information concerning the expected content and format for entering data into the spreadsheet cells)
Database Identification Number | Listed Combination Motor Controller Information | [7 empty] | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Enclosure Volume, cubic inches | Conditions of Use | [B10] Schematic | [B11] Other References
| Listing Report Information |  |  |  |  | Enclosure or Unit Dimensions
| UL File Number | Report Issue Date | Volume / Section | Model Number or Product Style/ Designation | Product Description on Page/Figure/Ill. | Enclosure or Unit Height, inches | Width, inches | Depth, inches |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating
Non-Reversing
SE192001 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 208 | 3 | 25 | 2.5 | 0.5 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H61* | 208 | 3 | 100kA | 0.4 - 8 | 2
SE192002 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 208 | 3 | 25 | 2.5 | 0.5 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H71* | 208 | 3 | 100kA | 0.4 - 8 | 2
SE192003 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 25 | 3.7 | 0.75 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H62* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192004 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 25 | 3.7 | 0.75 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H72* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192005 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 25 | 4.8 | 1 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H62* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192006 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 25 | 4.8 | 1 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H72* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192007 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 25 | 6.9 | 1.5 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H62* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192008 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 25 | 6.9 | 1.5 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H72* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192009 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 25 | 7.8 | 2 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H62* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192010 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 25 | 7.8 | 2 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H72* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192011 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 25 | 11 | 3 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H62* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192012 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 25 | 11 | 3 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H72* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192013 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 208 | 3 | 25 | 17.5 | 5 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H62* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192014 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 208 | 3 | 25 | 17.5 | 5 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H72* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192015 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 25.3 | 7.5 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H62* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192016 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 25.3 | 7.5 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H72* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192017 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 32.2 | 10 | 1832 | 1,5,6,7b,8, 10 and 11
[10 empty] | STR | Square D | 8536SDO1***H63* | 208 | 3 | 100kA | 5 - 100 | 10
SE192018 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 32.2 | 10 | 1832 | 1,5,6,7b,8, 10 and 11
[10 empty] | STR | Square D | 8536SDO1***H73* | 208 | 3 | 100kA | 5 - 100 | 10
SE192019 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 48.3 | 15 | 2747 | 1,5,6,7c,8, 10 and 11
[10 empty] | STR | Square D | 8536SEO1***H63* | 208 | 3 | 100kA | 5 - 100 | 25
SE192020 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 48.3 | 15 | 2747 | 1,5,6,7c,8, 10 and 11
[10 empty] | STR | Square D | 8536SEO1***H73* | 208 | 3 | 100kA | 5 - 100 | 25
SE192021 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 208 | 3 | 25 | 62.1 | 20 | 2747 | 1,5,6,7c,8, 10 and 11
[10 empty] | STR | Square D | 8536SEO1***H63* | 208 | 3 | 100kA | 5 - 100 | 25
SE192022 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 208 | 3 | 25 | 62.1 | 20 | 2747 | 1,5,6,7c,8, 10 and 11
[10 empty] | STR | Square D | 8536SEO1***H73* | 208 | 3 | 100kA | 5 - 100 | 25
SE192023 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 | - | 208 | 3 | 25 | 78.2 | 25 | 2747 | 1,5,6,7c,8, 10 and 11
[10 empty] | STR | Square D | 8536SEO1***H63* | 208 | 3 | 100kA | 5 - 100 | 25
SE192024 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 | - | 208 | 3 | 25 | 78.2 | 25 | 2747 | 1,5,6,7c,8, 10 and 11
[10 empty] | STR | Square D | 8536SEO1***H73* | 208 | 3 | 100kA | 5 - 100 | 25
SE192025 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 240 | 3 | 25 | 2.2 | 0.5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H61* | 240 | 3 | 100kA | 0.4 - 8 | 2
SE192026 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 240 | 3 | 25 | 2.2 | 0.5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H71* | 240 | 3 | 100kA | 0.4 - 8 | 2
SE192027 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 3.2 | 0.75 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H62* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192028 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 3.2 | 0.75 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H72* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192029 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 4.2 | 1 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H62* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192030 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 4.2 | 1 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H72* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192031 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 6 | 1.5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H62* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192032 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 6 | 1.5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H72* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192033 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 6.8 | 2 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H62* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192034 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 6.8 | 2 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H72* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192035 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 240 | 3 | 25 | 9.6 | 3 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H62* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192036 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 240 | 3 | 25 | 9.6 | 3 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H72* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192037 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 240 | 3 | 25 | 15.2 | 5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H62* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192038 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 240 | 3 | 25 | 15.2 | 5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H72* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192039 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 240 | 3 | 25 | 22 | 7.5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H62* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192040 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 240 | 3 | 25 | 22 | 7.5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H72* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192041 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 25 | 28 | 10 | 1832 | 1,5,6,7b,8 and 10
[10 empty] | STR | Square D | 8536SDO1***H63* | 240 | 3 | 100kA | 5 - 100 | 15
SE192042 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 25 | 28 | 10 | 1832 | 1,5,6,7b,8 and 10
[10 empty] | STR | Square D | 8536SDO1***H73* | 240 | 3 | 100kA | 5 - 100 | 15
SE192043 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 25 | 42 | 15 | 1832 | 1,5,6,7b,8 and 10
[10 empty] | STR | Square D | 8536SDO1***H63* | 240 | 3 | 100kA | 5 - 100 | 15
SE192044 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 25 | 42 | 15 | 1832 | 1,5,6,7b,8 and 10
[10 empty] | STR | Square D | 8536SDO1***H73* | 240 | 3 | 100kA | 5 - 100 | 15
SE192045 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 240 | 3 | 25 | 54 | 20 | 2747 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SEO1***H63* | 240 | 3 | 100kA | 5 - 100 | 30
SE192046 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 240 | 3 | 25 | 54 | 20 | 2747 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SEO1***H73* | 240 | 3 | 100kA | 5 - 100 | 30
SE192047 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 240 | 3 | 25 | 68 | 25 | 2747 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SEO1***H63* | 240 | 3 | 100kA | 5 - 100 | 30
SE192048 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 240 | 3 | 25 | 68 | 25 | 2747 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SEO1***H73* | 240 | 3 | 100kA | 5 - 100 | 30
SE192049 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 | - | 240 | 3 | 25 | 80 | 30 | 2747 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SEO1***H63* | 240 | 3 | 100kA | 5 - 100 | 30
SE192050 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 | - | 240 | 3 | 25 | 80 | 30 | 2747 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SEO1***H73* | 240 | 3 | 100kA | 5 - 100 | 30
SE192051 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T002D | 600 | 3 | - | 2 | - | 480 | 3 | 18 | 1.1 | 0.5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H61* | 480 | 3 | 100kA | 0.4 - 8 | 5
SE192052 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T002D | 600 | 3 | - | 2 | - | 480 | 3 | 18 | 1.1 | 0.5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H71* | 480 | 3 | 100kA | 0.4 - 8 | 5
SE192053 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T002D | 600 | 3 | - | 2 | - | 480 | 3 | 18 | 1.6 | 0.75 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H61* | 480 | 3 | 100kA | 0.4 - 8 | 5
SE192054 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T002D | 600 | 3 | - | 2 | - | 480 | 3 | 18 | 1.6 | 0.75 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H71* | 480 | 3 | 100kA | 0.4 - 8 | 5
SE192055 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 |  | 480 | 3 | 18 | 2.1 | 1 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H61* | 480 | 3 | 100kA | 0.4 - 8 | 5
SE192056 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 |  | 480 | 3 | 18 | 2.1 | 1 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H71* | 480 | 3 | 100kA | 0.4 - 8 | 5
SE192057 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 |  | 480 | 3 | 18 | 3 | 1.5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H62* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192058 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 |  | 480 | 3 | 18 | 3 | 1.5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H72* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192059 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 |  | 480 | 3 | 18 | 3.4 | 2 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H62* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192060 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 |  | 480 | 3 | 18 | 3.4 | 2 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H72* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192061 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 |  | 480 | 3 | 18 | 4.8 | 3 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H62* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192062 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 |  | 480 | 3 | 18 | 4.8 | 3 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H72* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192063 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 |  | 480 | 3 | 18 | 7.6 | 5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H62* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192064 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 |  | 480 | 3 | 18 | 7.6 | 5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H72* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192065 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 |  | 480 | 3 | 18 | 11 | 7.5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H62* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192066 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 |  | 480 | 3 | 18 | 11 | 7.5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H72* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192067 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 |  | 480 | 3 | 18 | 14 | 10 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H62* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192068 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 |  | 480 | 3 | 18 | 14 | 10 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H72* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192069 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 |  | 480 | 3 | 18 | 21 | 15 | 1832 | 1,5,6,7b,8 and 10
[10 empty] | STR | Square D | 8536SDO1***H62* | 480 | 3 | 100kA | 1.35 - 27 | 20
SE192070 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 |  | 480 | 3 | 18 | 21 | 15 | 1832 | 1,5,6,7b,8 and 10
[10 empty] | STR | Square D | 8536SDO1***H72* | 480 | 3 | 100kA | 1.35 - 27 | 20
SE192071 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 |  | 480 | 3 | 18 | 27 | 20 | 1832 | 1,5,6,7b,8 and 10
[10 empty] | STR | Square D | 8536SDO1***H63* | 480 | 3 | 100kA | 5 - 100 | 25
SE192072 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 |  | 480 | 3 | 18 | 27 | 20 | 1832 | 1,5,6,7b,8 and 10
[10 empty] | STR | Square D | 8536SDO1***H73* | 480 | 3 | 100kA | 5 - 100 | 25
SE192073 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 |  | 480 | 3 | 18 | 34 | 25 | 1832 | 1,5,6,7b,8 and 10
[10 empty] | STR | Square D | 8536SDO1***H63* | 480 | 3 | 100kA | 5 - 100 | 25
SE192074 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 |  | 480 | 3 | 18 | 34 | 25 | 1832 | 1,5,6,7b,8 and 10
[10 empty] | STR | Square D | 8536SDO1***H73* | 480 | 3 | 100kA | 5 - 100 | 25
SE192075 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 |  | 480 | 3 | 18 | 40 | 30 | 2747 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SEO1***H63* | 480 | 3 | 100kA | 5 - 100 | 50
SE192076 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 |  | 480 | 3 | 18 | 40 | 30 | 2747 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SEO1***H73* | 480 | 3 | 100kA | 5 - 100 | 50
SE192077 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 |  | 480 | 3 | 18 | 52 | 40 | 2747 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SEO1***H63* | 480 | 3 | 100kA | 5 - 100 | 50
SE192078 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 |  | 480 | 3 | 18 | 52 | 40 | 2747 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SEO1***H73* | 480 | 3 | 100kA | 5 - 100 | 50
SE192079 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 |  | 480 | 3 | 18 | 65 | 50 | 2747 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SEO1***H63* | 480 | 3 | 100kA | 5 - 100 | 50
SE192080 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 |  | 480 | 3 | 18 | 65 | 50 | 2747 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SEO1***H73* | 480 | 3 | 100kA | 5 - 100 | 50
SE192081 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 21 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 | - | 480 | 3 | 18 | 77 | 60 | 3205 | 1,5,6,7d,8 and 10
[10 empty] | STR | Square D | 8536SFO1***H63* | 480 | 3 | 100kA | 5 - 100 | 60
SE192082 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 21 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 | - | 480 | 3 | 18 | 77 | 60 | 3205 | 1,5,6,7d,8 and 10
[10 empty] | STR | Square D | 8536SFO1***H73* | 480 | 3 | 100kA | 5 - 100 | 60
SE192083 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 208 | 3 | 100 | 2.5 | 0.5 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H61* | 208 | 3 | 100kA | 0.4 - 8 | 2
SE192084 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 208 | 3 | 100 | 2.5 | 0.5 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H71* | 208 | 3 | 100kA | 0.4 - 8 | 2
SE192085 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 208 | 3 | 100 | 3.7 | 0.75 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H62* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192086 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 208 | 3 | 100 | 3.7 | 0.75 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H72* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192087 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 208 | 3 | 100 | 4.8 | 1 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H62* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192088 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 208 | 3 | 100 | 4.8 | 1 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H72* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192089 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 208 | 3 | 100 | 6.9 | 1.5 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H62* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192090 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 208 | 3 | 100 | 6.9 | 1.5 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H72* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192091 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 100 | 7.8 | 2 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H62* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192092 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 100 | 7.8 | 2 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H72* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192093 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 100 | 11 | 3 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H62* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192094 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 100 | 11 | 3 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H72* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192095 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 208 | 3 | 100 | 17.5 | 5 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H62* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192096 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 208 | 3 | 100 | 17.5 | 5 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H72* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192097 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 100 | 25.3 | 7.5 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H62* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192098 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 100 | 25.3 | 7.5 | 1832 | 1,5,6,7a,8, 10 and 11
[10 empty] | STR | Square D | 8536SCO3***H72* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192099 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 100 | 32.2 | 10 | 1832 | 1,5,6,7b,8, 10 and 11
[10 empty] | STR | Square D | 8536SDO1***H63* | 208 | 3 | 100kA | 5 - 100 | 10
SE192100 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 100 | 32.2 | 10 | 1832 | 1,5,6,7b,8, 10 and 11
[10 empty] | STR | Square D | 8536SDO1***H73* | 208 | 3 | 100kA | 5 - 100 | 10
SE192101 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 100 | 48.3 | 15 | 2747 | 1,5,6,7c,8, 10 and 11
[10 empty] | STR | Square D | 8536SEO1***H63* | 208 | 3 | 100kA | 5 - 100 | 25
SE192102 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 100 | 48.3 | 15 | 2747 | 1,5,6,7c,8, 10 and 11
[10 empty] | STR | Square D | 8536SEO1***H73* | 208 | 3 | 100kA | 5 - 100 | 25
SE192103 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 208 | 3 | 100 | 62.1 | 20 | 2747 | 1,5,6,7c,8, 10 and 11
[10 empty] | STR | Square D | 8536SEO1***H63* | 208 | 3 | 100kA | 5 - 100 | 25
SE192104 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 208 | 3 | 100 | 62.1 | 20 | 2747 | 1,5,6,7c,8, 10 and 11
[10 empty] | STR | Square D | 8536SEO1***H73* | 208 | 3 | 100kA | 5 - 100 | 25
SE192105 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T115J | 600 | 3 | - | 115 | - | 208 | 3 | 100 | 78.2 | 25 | 2747 | 1,5,6,7c,8, 10 and 11
[10 empty] | STR | Square D | 8536SEO1***H63* | 208 | 3 | 100kA | 5 - 100 | 25
SE192106 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T115J | 600 | 3 | - | 115 | - | 208 | 3 | 100 | 78.2 | 25 | 2747 | 1,5,6,7c,8, 10 and 11
[10 empty] | STR | Square D | 8536SEO1***H73* | 208 | 3 | 100kA | 5 - 100 | 25
SE192107 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 240 | 3 | 100 | 2.2 | 0.5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H61* | 240 | 3 | 100kA | 0.4 - 8 | 2
SE192108 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 240 | 3 | 100 | 2.2 | 0.5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H71* | 240 | 3 | 100kA | 0.4 - 8 | 2
SE192109 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 3.2 | 0.75 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H62* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192110 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 3.2 | 0.75 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H72* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192111 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 4.2 | 1 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H62* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192112 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 4.2 | 1 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H72* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192113 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 6 | 1.5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H62* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192114 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 6 | 1.5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H72* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192115 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 6.8 | 2 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H62* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192116 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 6.8 | 2 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H72* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192117 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 240 | 3 | 100 | 9.6 | 3 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H62* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192118 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 240 | 3 | 100 | 9.6 | 3 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H72* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192119 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 240 | 3 | 100 | 15.2 | 5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H62* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192120 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 240 | 3 | 100 | 15.2 | 5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H72* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192121 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 240 | 3 | 100 | 22 | 7.5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H62* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192122 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 240 | 3 | 100 | 22 | 7.5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H72* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192123 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 100 | 28 | 10 | 1832 | 1,5,6,7b,8 and 10
[10 empty] | STR | Square D | 8536SDO1***H63* | 240 | 3 | 100kA | 5 - 100 | 15
SE192124 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 100 | 28 | 10 | 1832 | 1,5,6,7b,8 and 10
[10 empty] | STR | Square D | 8536SDO1***H73* | 240 | 3 | 100kA | 5 - 100 | 15
SE192125 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 100 | 42 | 15 | 1832 | 1,5,6,7b,8 and 10
[10 empty] | STR | Square D | 8536SDO1***H63* | 240 | 3 | 100kA | 5 - 100 | 15
SE192126 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 100 | 42 | 15 | 1832 | 1,5,6,7b,8 and 10
[10 empty] | STR | Square D | 8536SDO1***H73* | 240 | 3 | 100kA | 5 - 100 | 15
SE192127 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 240 | 3 | 100 | 54 | 20 | 2747 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SEO1***H63* | 240 | 3 | 100kA | 5 - 100 | 30
SE192128 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 240 | 3 | 100 | 54 | 20 | 2747 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SEO1***H73* | 240 | 3 | 100kA | 5 - 100 | 30
SE192129 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 240 | 3 | 100 | 68 | 25 | 2747 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SEO1***H63* | 240 | 3 | 100kA | 5 - 100 | 30
SE192130 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 240 | 3 | 100 | 68 | 25 | 2747 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SEO1***H73* | 240 | 3 | 100kA | 5 - 100 | 30
SE192131 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T115J | 600 | 3 | - | 115 | - | 240 | 3 | 100 | 80 | 30 | 2747 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SEO1***H63* | 240 | 3 | 100kA | 5 - 100 | 30
SE192132 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T115J | 600 | 3 | - | 115 | - | 240 | 3 | 100 | 80 | 30 | 2747 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SEO1***H73* | 240 | 3 | 100kA | 5 - 100 | 30
SE192133 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 480 | 3 | 100 | 1.1 | 0.5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H61* | 480 | 3 | 100kA | 0.4 - 8 | 5
SE192134 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 480 | 3 | 100 | 1.1 | 0.5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H71* | 480 | 3 | 100kA | 0.4 - 8 | 5
SE192135 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 480 | 3 | 100 | 1.6 | 0.75 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H61* | 480 | 3 | 100kA | 0.4 - 8 | 5
SE192136 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 480 | 3 | 100 | 1.6 | 0.75 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H71* | 480 | 3 | 100kA | 0.4 - 8 | 5
SE192137 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 |  | 480 | 3 | 100 | 2.1 | 1 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H61* | 480 | 3 | 100kA | 0.4 - 8 | 5
SE192138 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 |  | 480 | 3 | 100 | 2.1 | 1 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H71* | 480 | 3 | 100kA | 0.4 - 8 | 5
SE192139 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 |  | 480 | 3 | 100 | 3 | 1.5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H62* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192140 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 |  | 480 | 3 | 100 | 3 | 1.5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H72* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192141 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 |  | 480 | 3 | 100 | 3.4 | 2 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H62* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192142 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 |  | 480 | 3 | 100 | 3.4 | 2 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H72* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192143 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 |  | 480 | 3 | 100 | 4.8 | 3 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H62* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192144 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 |  | 480 | 3 | 100 | 4.8 | 3 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H72* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192145 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 |  | 480 | 3 | 100 | 7.6 | 5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H62* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192146 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 |  | 480 | 3 | 100 | 7.6 | 5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H72* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192147 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 |  | 480 | 3 | 100 | 11 | 7.5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H62* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192148 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 |  | 480 | 3 | 100 | 11 | 7.5 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H72* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192149 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 |  | 480 | 3 | 100 | 14 | 10 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H62* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192150 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 |  | 480 | 3 | 100 | 14 | 10 | 1832 | 1,5,6,7a,8 and 10
[10 empty] | STR | Square D | 8536SCO3***H72* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192151 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 |  | 480 | 3 | 100 | 21 | 15 | 1832 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SDO1***H62* | 480 | 3 | 100kA | 1.35 - 27 | 20
SE192152 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 |  | 480 | 3 | 100 | 21 | 15 | 1832 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SDO1***H72* | 480 | 3 | 100kA | 1.35 - 27 | 20
SE192153 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 |  | 480 | 3 | 100 | 27 | 20 | 1832 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SDO1***H63* | 480 | 3 | 100kA | 5 - 100 | 25
SE192154 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 |  | 480 | 3 | 100 | 27 | 20 | 1832 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SDO1***H73* | 480 | 3 | 100kA | 5 - 100 | 25
SE192155 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 |  | 480 | 3 | 100 | 34 | 25 | 1832 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SDO1***H63* | 480 | 3 | 100kA | 5 - 100 | 25
SE192156 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 |  | 480 | 3 | 100 | 34 | 25 | 1832 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SDO1***H73* | 480 | 3 | 100kA | 5 - 100 | 25
SE192157 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 |  | 480 | 3 | 100 | 40 | 30 | 2747 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SEO1***H63* | 480 | 3 | 100kA | 5 - 100 | 50
SE192158 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 |  | 480 | 3 | 100 | 40 | 30 | 2747 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SEO1***H73* | 480 | 3 | 100kA | 5 - 100 | 50
SE192159 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 |  | 480 | 3 | 100 | 52 | 40 | 2747 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SEO1***H63* | 480 | 3 | 100kA | 5 - 100 | 50
SE192160 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 |  | 480 | 3 | 100 | 52 | 40 | 2747 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SEO1***H73* | 480 | 3 | 100kA | 5 - 100 | 50
SE192161 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 |  | 480 | 3 | 100 | 65 | 50 | 2747 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SEO1***H63* | 480 | 3 | 100kA | 5 - 100 | 50
SE192162 | E40610 | 1986-11-03 | (Vo12) (Se1) | Model 6 | Pg. 1, 1A, 2B, 3, 3A1, 3C1, 4C, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 |  | 480 | 3 | 100 | 65 | 50 | 2747 | 1,5,6,7c,8 and 10
[10 empty] | STR | Square D | 8536SEO1***H73* | 480 | 3 | 100kA | 5 - 100 | 50
Reversing
SE192201 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 208 | 3 | 25 | 2.5 | 0.5 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H61* | 208 | 3 | 100kA | 0.4 - 8 | 2
SE192202 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 208 | 3 | 25 | 2.5 | 0.5 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H71* | 208 | 3 | 100kA | 0.4 - 8 | 2
SE192203 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 25 | 3.7 | 0.75 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H62* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192204 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 25 | 3.7 | 0.75 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H72* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192205 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 25 | 4.8 | 1 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H62* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192206 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 25 | 4.8 | 1 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H72* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192207 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 25 | 6.9 | 1.5 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H62* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192208 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 25 | 6.9 | 1.5 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H72* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192209 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 25 | 7.8 | 2 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H62* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192210 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 25 | 7.8 | 2 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H72* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192211 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 25 | 11 | 3 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H62* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192212 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 25 | 11 | 3 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H72* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192213 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 208 | 3 | 25 | 17.5 | 5 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H62* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192214 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 208 | 3 | 25 | 17.5 | 5 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H72* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192215 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 25.3 | 7.5 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H62* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192216 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 25.3 | 7.5 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H72* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192217 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 32.2 | 10 | 2747 | 1,5,6,7b,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SDO@***H63* | 208 | 3 | 100kA | 5 - 100 | 10
SE192218 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 32.2 | 10 | 2747 | 1,5,6,7b,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SDO@***H73* | 208 | 3 | 100kA | 5 - 100 | 10
SE192219 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 48.3 | 15 | 4120 | 1,5,6,7c,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SEO@***H63* | 208 | 3 | 100kA | 5 - 100 | 25
SE192220 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 48.3 | 15 | 4120 | 1,5,6,7c,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SEO@***H73* | 208 | 3 | 100kA | 5 - 100 | 25
SE192221 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 208 | 3 | 25 | 62.1 | 20 | 4120 | 1,5,6,7c,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SEO@***H63* | 208 | 3 | 100kA | 5 - 100 | 25
SE192222 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 208 | 3 | 25 | 62.1 | 20 | 4120 | 1,5,6,7c,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SEO@***H73* | 208 | 3 | 100kA | 5 - 100 | 25
SE192223 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 | - | 208 | 3 | 25 | 78.2 | 25 | 4120 | 1,5,6,7c,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SEO@***H63* | 208 | 3 | 100kA | 5 - 100 | 25
SE192224 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 | - | 208 | 3 | 25 | 78.2 | 25 | 4120 | 1,5,6,7c,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SEO@***H73* | 208 | 3 | 100kA | 5 - 100 | 25
SE192225 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 240 | 3 | 25 | 2.2 | 0.5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H61* | 240 | 3 | 100kA | 0.4 - 8 | 2
SE192226 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 240 | 3 | 25 | 2.2 | 0.5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H71* | 240 | 3 | 100kA | 0.4 - 8 | 2
SE192227 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 3.2 | 0.75 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H62* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192228 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 3.2 | 0.75 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H72* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192229 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 4.2 | 1 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H62* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192230 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 4.2 | 1 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H72* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192231 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 6 | 1.5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H62* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192232 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 6 | 1.5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H72* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192233 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 6.8 | 2 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H62* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192234 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 6.8 | 2 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H72* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192235 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 240 | 3 | 25 | 9.6 | 3 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H62* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192236 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 240 | 3 | 25 | 9.6 | 3 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H72* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192237 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 240 | 3 | 25 | 15.2 | 5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H62* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192238 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 240 | 3 | 25 | 15.2 | 5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H72* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192239 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 240 | 3 | 25 | 22 | 7.5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H62* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192240 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 240 | 3 | 25 | 22 | 7.5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H72* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192241 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 25 | 28 | 10 | 2747 | 1,5,6,7b,8, 9 and 10
[10 empty] | STR | Square D | 8736SDO@***H63* | 240 | 3 | 100kA | 5 - 100 | 15
SE192242 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 25 | 28 | 10 | 2747 | 1,5,6,7b,8, 9 and 10
[10 empty] | STR | Square D | 8736SDO@***H73* | 240 | 3 | 100kA | 5 - 100 | 15
SE192243 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 25 | 42 | 15 | 2747 | 1,5,6,7b,8, 9 and 10
[10 empty] | STR | Square D | 8736SDO@***H63* | 240 | 3 | 100kA | 5 - 100 | 15
SE192244 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 25 | 42 | 15 | 2747 | 1,5,6,7b,8, 9 and 10
[10 empty] | STR | Square D | 8736SDO@***H73* | 240 | 3 | 100kA | 5 - 100 | 15
SE192245 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 240 | 3 | 25 | 54 | 20 | 4120 | 1,5,6,7c,8, 9 and 10
[10 empty] | STR | Square D | 8736SEO@***H63* | 240 | 3 | 100kA | 5 - 100 | 30
SE192246 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 240 | 3 | 25 | 54 | 20 | 4120 | 1,5,6,7c,8, 9 and 10
[10 empty] | STR | Square D | 8736SEO@***H73* | 240 | 3 | 100kA | 5 - 100 | 30
SE192247 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 240 | 3 | 25 | 68 | 25 | 4120 | 1,5,6,7c,8, 9 and 10
[10 empty] | STR | Square D | 8736SEO@***H63* | 240 | 3 | 100kA | 5 - 100 | 30
SE192248 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 240 | 3 | 25 | 68 | 25 | 4120 | 1,5,6,7c,8, 9 and 10
[10 empty] | STR | Square D | 8736SEO@***H73* | 240 | 3 | 100kA | 5 - 100 | 30
SE192249 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 | - | 240 | 3 | 25 | 80 | 30 | 4120 | 1,5,6,7c,8, 9 and 10
[10 empty] | STR | Square D | 8736SEO@***H63* | 240 | 3 | 100kA | 5 - 100 | 30
SE192250 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 | - | 240 | 3 | 25 | 80 | 30 | 4120 | 1,5,6,7c,8, 9 and 10
[10 empty] | STR | Square D | 8736SEO@***H73* | 240 | 3 | 100kA | 5 - 100 | 30
SE192251 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T002D | 600 | 3 | - | 2 | - | 480 | 3 | 18 | 1.1 | 0.5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H61* | 480 | 3 | 100kA | 0.4 - 8 | 5
SE192252 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T002D | 600 | 3 | - | 2 | - | 480 | 3 | 18 | 1.1 | 0.5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H71* | 480 | 3 | 100kA | 0.4 - 8 | 5
SE192253 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T002D | 600 | 3 | - | 2 | - | 480 | 3 | 18 | 1.6 | 0.75 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H61* | 480 | 3 | 100kA | 0.4 - 8 | 5
SE192254 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T002D | 600 | 3 | - | 2 | - | 480 | 3 | 18 | 1.6 | 0.75 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H71* | 480 | 3 | 100kA | 0.4 - 8 | 5
SE192255 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 |  | 480 | 3 | 18 | 2.1 | 1 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H61* | 480 | 3 | 100kA | 0.4 - 8 | 5
SE192256 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 |  | 480 | 3 | 18 | 2.1 | 1 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H71* | 480 | 3 | 100kA | 0.4 - 8 | 5
SE192257 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 |  | 480 | 3 | 18 | 3 | 1.5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H62* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192258 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 |  | 480 | 3 | 18 | 3 | 1.5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H72* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192259 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 |  | 480 | 3 | 18 | 3.4 | 2 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H62* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192260 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 |  | 480 | 3 | 18 | 3.4 | 2 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H72* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192261 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 |  | 480 | 3 | 18 | 4.8 | 3 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H62* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192262 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 |  | 480 | 3 | 18 | 4.8 | 3 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H72* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192263 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 |  | 480 | 3 | 18 | 7.6 | 5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H62* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192264 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 |  | 480 | 3 | 18 | 7.6 | 5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H72* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192265 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 |  | 480 | 3 | 18 | 11 | 7.5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H62* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192266 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 |  | 480 | 3 | 18 | 11 | 7.5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H72* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192267 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 |  | 480 | 3 | 18 | 14 | 10 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H62* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192268 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 |  | 480 | 3 | 18 | 14 | 10 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H72* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192269 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 |  | 480 | 3 | 18 | 21 | 15 | 2747 | 1,5,6,7b,8, 9 and 10
[10 empty] | STR | Square D | 8736SDO@***H62* | 480 | 3 | 100kA | 1.35 - 27 | 20
SE192270 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 |  | 480 | 3 | 18 | 21 | 15 | 2747 | 1,5,6,7b,8, 9 and 10
[10 empty] | STR | Square D | 8736SDO@***H72* | 480 | 3 | 100kA | 1.35 - 27 | 20
SE192271 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 |  | 480 | 3 | 18 | 27 | 20 | 2747 | 1,5,6,7b,8, 9 and 10
[10 empty] | STR | Square D | 8736SDO@***H63* | 480 | 3 | 100kA | 5 - 100 | 25
SE192272 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 |  | 480 | 3 | 18 | 27 | 20 | 2747 | 1,5,6,7b,8, 9 and 10
[10 empty] | STR | Square D | 8736SDO@***H73* | 480 | 3 | 100kA | 5 - 100 | 25
SE192273 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 |  | 480 | 3 | 18 | 34 | 25 | 2747 | 1,5,6,7b,8, 9 and 10
[10 empty] | STR | Square D | 8736SDO@***H63* | 480 | 3 | 100kA | 5 - 100 | 25
SE192274 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 |  | 480 | 3 | 18 | 34 | 25 | 2747 | 1,5,6,7b,8, 9 and 10
[10 empty] | STR | Square D | 8736SDO@***H73* | 480 | 3 | 100kA | 5 - 100 | 25
SE192275 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 |  | 480 | 3 | 18 | 40 | 30 | 4120 | 1,5,6,7c,8, 9 and 10
[10 empty] | STR | Square D | 8736SEO@***H63* | 480 | 3 | 100kA | 5 - 100 | 50
SE192276 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 |  | 480 | 3 | 18 | 40 | 30 | 4120 | 1,5,6,7c,8, 9 and 10
[10 empty] | STR | Square D | 8736SEO@***H73* | 480 | 3 | 100kA | 5 - 100 | 50
SE192277 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 |  | 480 | 3 | 18 | 52 | 40 | 4120 | 1,5,6,7c,8, 9 and 10
[10 empty] | STR | Square D | 8736SEO@***H63* | 480 | 3 | 100kA | 5 - 100 | 50
SE192278 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 |  | 480 | 3 | 18 | 52 | 40 | 4120 | 1,5,6,7c,8, 9 and 10
[10 empty] | STR | Square D | 8736SEO@***H73* | 480 | 3 | 100kA | 5 - 100 | 50
SE192279 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 |  | 480 | 3 | 18 | 65 | 50 | 4120 | 1,5,6,7c,8, 9 and 10
[10 empty] | STR | Square D | 8736SEO@***H63* | 480 | 3 | 100kA | 5 - 100 | 50
SE192280 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 |  | 480 | 3 | 18 | 65 | 50 | 4120 | 1,5,6,7c,8, 9 and 10
[10 empty] | STR | Square D | 8736SEO@***H73* | 480 | 3 | 100kA | 5 - 100 | 50
SE192281 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 33 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 | - | 480 | 3 | 18 | 77 | 60 | 5036 | 1,5,6,7d,8, 9 and 10
[10 empty] | STR | Square D | 8736SFO@***H65* | 480 | 3 | 100kA | 8-160 | 60
SE192282 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 33 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 | - | 480 | 3 | 18 | 77 | 60 | 5036 | 1,5,6,7d,8, 9 and 10
[10 empty] | STR | Square D | 8736SFO@***H75* | 480 | 3 | 100kA | 8-160 | 60
SE192283 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 208 | 3 | 100 | 2.5 | 0.5 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H61* | 208 | 3 | 100kA | 0.4 - 8 | 2
SE192284 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 208 | 3 | 100 | 2.5 | 0.5 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H71* | 208 | 3 | 100kA | 0.4 - 8 | 2
SE192285 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 208 | 3 | 100 | 3.7 | 0.75 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H62* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192286 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 208 | 3 | 100 | 3.7 | 0.75 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H72* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192287 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 208 | 3 | 100 | 4.8 | 1 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H62* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192288 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 208 | 3 | 100 | 4.8 | 1 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H72* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192289 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 208 | 3 | 100 | 6.9 | 1.5 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H62* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192290 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 208 | 3 | 100 | 6.9 | 1.5 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H72* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192291 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 100 | 7.8 | 2 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H62* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192292 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 100 | 7.8 | 2 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H72* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192293 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 100 | 11 | 3 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H62* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192294 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 100 | 11 | 3 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H72* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192295 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 208 | 3 | 100 | 17.5 | 5 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H62* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192296 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 208 | 3 | 100 | 17.5 | 5 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H72* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192297 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 100 | 25.3 | 7.5 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H62* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192298 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 100 | 25.3 | 7.5 | 2747 | 1,5,6,7a,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SCO@***H72* | 208 | 3 | 100kA | 1.35 - 27 | 7.5
SE192299 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 100 | 32.2 | 10 | 2747 | 1,5,6,7b,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SDO@***H63* | 208 | 3 | 100kA | 5 - 100 | 10
SE192300 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 100 | 32.2 | 10 | 2747 | 1,5,6,7b,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SDO@***H73* | 208 | 3 | 100kA | 5 - 100 | 10
SE192301 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 100 | 48.3 | 15 | 4120 | 1,5,6,7c,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SEO@***H63* | 208 | 3 | 100kA | 5 - 100 | 25
SE192302 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 100 | 48.3 | 15 | 4120 | 1,5,6,7c,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SEO@***H73* | 208 | 3 | 100kA | 5 - 100 | 25
SE192303 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 208 | 3 | 100 | 62.1 | 20 | 4120 | 1,5,6,7c,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SEO@***H63* | 208 | 3 | 100kA | 5 - 100 | 25
SE192304 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 208 | 3 | 100 | 62.1 | 20 | 4120 | 1,5,6,7c,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SEO@***H73* | 208 | 3 | 100kA | 5 - 100 | 25
SE192305 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T115J | 600 | 3 | - | 115 | - | 208 | 3 | 100 | 78.2 | 25 | 4120 | 1,5,6,7c,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SEO@***H63* | 208 | 3 | 100kA | 5 - 100 | 25
SE192306 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T115J | 600 | 3 | - | 115 | - | 208 | 3 | 100 | 78.2 | 25 | 4120 | 1,5,6,7c,8, 9, 10 and 11
[10 empty] | STR | Square D | 8736SEO@***H73* | 208 | 3 | 100kA | 5 - 100 | 25
SE192307 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 240 | 3 | 100 | 2.2 | 0.5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H61* | 240 | 3 | 100kA | 0.4 - 8 | 2
SE192308 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 240 | 3 | 100 | 2.2 | 0.5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H71* | 240 | 3 | 100kA | 0.4 - 8 | 2
SE192309 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 3.2 | 0.75 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H62* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192310 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 3.2 | 0.75 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H72* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192311 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 4.2 | 1 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H62* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192312 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 4.2 | 1 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H72* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192313 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 6 | 1.5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H62* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192314 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 6 | 1.5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H72* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192315 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 6.8 | 2 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H62* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192316 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 100 | 6.8 | 2 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H72* | 240 | 3 | 100kA | 1.6 - 8 | 7.5
SE192317 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 240 | 3 | 100 | 9.6 | 3 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H62* | 240 | 3 | 100kA | 1.6 - 8 | 7.5
SE192318 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 240 | 3 | 100 | 9.6 | 3 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H72* | 240 | 3 | 100kA | 1.6 - 8 | 7.5
SE192319 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 240 | 3 | 100 | 15.2 | 5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H62* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192320 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 240 | 3 | 100 | 15.2 | 5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H72* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192321 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 240 | 3 | 100 | 22 | 7.5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H62* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192322 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 240 | 3 | 100 | 22 | 7.5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H72* | 240 | 3 | 100kA | 1.35 - 27 | 7.5
SE192323 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 100 | 28 | 10 | 2747 | 1,5,6,7b,8, 9 and 10
[10 empty] | STR | Square D | 8736SDO@***H63* | 240 | 3 | 100kA | 5 - 100 | 15
SE192324 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 100 | 28 | 10 | 2747 | 1,5,6,7b,8, 9 and 10
[10 empty] | STR | Square D | 8736SDO@***H73* | 240 | 3 | 100kA | 5 - 100 | 15
SE192325 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 100 | 42 | 15 | 2747 | 1,5,6,7b,8, 9 and 10
[10 empty] | STR | Square D | 8736SDO@***H63* | 240 | 3 | 100kA | 5 - 100 | 15
SE192326 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 100 | 42 | 15 | 2747 | 1,5,6,7b,8, 9 and 10
[10 empty] | STR | Square D | 8736SDO@***H73* | 240 | 3 | 100kA | 5 - 100 | 15
SE192327 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 240 | 3 | 100 | 54 | 20 | 4120 | 1,5,6,7c,8, 9 and 10
[10 empty] | STR | Square D | 8736SEO@***H63* | 240 | 3 | 100kA | 5 - 100 | 30
SE192328 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 240 | 3 | 100 | 54 | 20 | 4120 | 1,5,6,7c,8, 9 and 10
[10 empty] | STR | Square D | 8736SEO@***H73* | 240 | 3 | 100kA | 5 - 100 | 30
SE192329 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 240 | 3 | 100 | 68 | 25 | 4120 | 1,5,6,7c,8, 9 and 10
[10 empty] | STR | Square D | 8736SEO@***H63* | 240 | 3 | 100kA | 5 - 100 | 30
SE192330 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 240 | 3 | 100 | 68 | 25 | 4120 | 1,5,6,7c,8, 9 and 10
[10 empty] | STR | Square D | 8736SEO@***H73* | 240 | 3 | 100kA | 5 - 100 | 30
SE192331 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T115J | 600 | 3 | - | 115 | - | 240 | 3 | 100 | 80 | 30 | 4120 | 1,5,6,7c,8, 9 and 10
[10 empty] | STR | Square D | 8736SEO@***H63* | 240 | 3 | 100kA | 5 - 100 | 30
SE192332 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T115J | 600 | 3 | - | 115 | - | 240 | 3 | 100 | 80 | 30 | 4120 | 1,5,6,7c,8, 9 and 10
[10 empty] | STR | Square D | 8736SEO@***H73* | 240 | 3 | 100kA | 5 - 100 | 30
SE192333 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 480 | 3 | 100 | 1.1 | 0.5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H61* | 480 | 3 | 100kA | 0.4 - 8 | 5
SE192334 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 480 | 3 | 100 | 1.1 | 0.5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H71* | 480 | 3 | 100kA | 0.4 - 8 | 5
SE192335 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 480 | 3 | 100 | 1.6 | 0.75 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H61* | 480 | 3 | 100kA | 0.4 - 8 | 5
SE192336 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 480 | 3 | 100 | 1.6 | 0.75 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H71* | 480 | 3 | 100kA | 0.4 - 8 | 5
SE192337 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 |  | 480 | 3 | 100 | 2.1 | 1 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H61* | 480 | 3 | 100kA | 0.4 - 8 | 5
SE192338 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 |  | 480 | 3 | 100 | 2.1 | 1 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H71* | 480 | 3 | 100kA | 0.4 - 8 | 5
SE192339 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 |  | 480 | 3 | 100 | 3 | 1.5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H62* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192340 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 |  | 480 | 3 | 100 | 3 | 1.5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H72* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192341 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 |  | 480 | 3 | 100 | 3.4 | 2 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H62* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192342 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 |  | 480 | 3 | 100 | 3.4 | 2 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H72* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192343 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 |  | 480 | 3 | 100 | 4.8 | 3 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H62* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192344 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 |  | 480 | 3 | 100 | 4.8 | 3 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H72* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192345 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 |  | 480 | 3 | 100 | 7.6 | 5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H62* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192346 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 |  | 480 | 3 | 100 | 7.6 | 5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H72* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192347 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 |  | 480 | 3 | 100 | 11 | 7.5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H62* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192348 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 |  | 480 | 3 | 100 | 11 | 7.5 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H72* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192349 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 |  | 480 | 3 | 100 | 14 | 10 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H62* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192350 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 |  | 480 | 3 | 100 | 14 | 10 | 2747 | 1,5,6,7a,8, 9 and 10
[10 empty] | STR | Square D | 8736SCO@***H72* | 480 | 3 | 100kA | 1.35 - 27 | 10
SE192351 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 |  | 480 | 3 | 100 | 21 | 15 | 2747 | 1,5,6,7b,8, 9 and 10
[10 empty] | STR | Square D | 8736SDO@***H62* | 480 | 3 | 100kA | 1.35 - 27 | 20
SE192352 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 |  | 480 | 3 | 100 | 21 | 15 | 2747 | 1,5,6,7b,8, 9 and 10
[10 empty] | STR | Square D | 8736SDO@***H72* | 480 | 3 | 100kA | 1.35 - 27 | 20
SE192353 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 |  | 480 | 3 | 100 | 27 | 20 | 2747 | 1,5,6,7b,8, 9 and 10
[10 empty] | STR | Square D | 8736SDO@***H63* | 480 | 3 | 100kA | 5 - 100 | 25
SE192354 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 |  | 480 | 3 | 100 | 27 | 20 | 2747 | 1,5,6,7b,8, 9 and 10
[10 empty] | STR | Square D | 8736SDO@***H73* | 480 | 3 | 100kA | 5 - 100 | 25
SE192355 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 |  | 480 | 3 | 100 | 34 | 25 | 2747 | 1,5,6,7b,8, 9 and 10
[10 empty] | STR | Square D | 8736SDO@***H63* | 480 | 3 | 100kA | 5 - 100 | 25
SE192356 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 18 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 |  | 480 | 3 | 100 | 34 | 25 | 2747 | 1,5,6,7b,8, 9 and 10
[10 empty] | STR | Square D | 8736SDO@***H73* | 480 | 3 | 100kA | 5 - 100 | 25
SE192357 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 |  | 480 | 3 | 100 | 40 | 30 | 4120 | 1,5,6,7c,8, 9 and 10
[10 empty] | STR | Square D | 8736SEO@***H63* | 480 | 3 | 100kA | 5 - 100 | 50
SE192358 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 |  | 480 | 3 | 100 | 40 | 30 | 4120 | 1,5,6,7c,8, 9 and 10
[10 empty] | STR | Square D | 8736SEO@***H73* | 480 | 3 | 100kA | 5 - 100 | 50
SE192359 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 |  | 480 | 3 | 100 | 52 | 40 | 4120 | 1,5,6,7c,8, 9 and 10
[10 empty] | STR | Square D | 8736SEO@***H63* | 480 | 3 | 100kA | 5 - 100 | 50
SE192360 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 |  | 480 | 3 | 100 | 52 | 40 | 4120 | 1,5,6,7c,8, 9 and 10
[10 empty] | STR | Square D | 8736SEO@***H73* | 480 | 3 | 100kA | 5 - 100 | 50
SE192361 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 |  | 480 | 3 | 100 | 65 | 50 | 4120 | 1,5,6,7c,8, 9 and 10
[10 empty] | STR | Square D | 8736SEO@***H63* | 480 | 3 | 100kA | 5 - 100 | 50
SE192362 | E40610 | 1986-11-03 | (Vo12) (Se2) | Model 6 | Pg. 3, fig1. | 27 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 |  | 480 | 3 | 100 | 65 | 50 | 4120 | 1,5,6,7c,8, 9 and 10
[10 empty] | STR | Square D | 8736SEO@***H73* | 480 | 3 | 100kA | 5 - 100 | 50
324

## LC1D LRD
Database Identification Number | Listed Combination Motor Controller Information | [7 empty] | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Enclosure Volume, cubic inches | Conditions of Use
| Listing Report Information |  |  |  |  | Enclosure or Unit Dimensions
| UL File Number | Report Issue Date MM-DD-YYYY | Volume / Section | Model Number or Product Style/ Designation | Product Description on Page/Figure/Ill. | Enclosure or Unit Height, inches | Width, inches | Depth, inches |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating
SE195001 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | -+R4:R36 | 208 | 3 | 25 | 2.4 | 0.5 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | LC1D09 | 208 | 3 | 85kA | 7.8 | 2
[10 empty] | OLR | Schneider | LRD07 | 208 | 3 | 65kA | 1.6 - 2.5
SE195002 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 25 | 3.5 | 0.75 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | LC1D09 | 208 | 3 | 85kA | 7.8 | 2
[10 empty] | OLR | Schneider | LRD08 | 208 | 3 | 65kA | 2.5 - 4
SE195003 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 25 | 4.6 | 1 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | LC1D09 | 208 | 3 | 85kA | 7.8 | 2
[10 empty] | OLR | Schneider | LRD10 | 208 | 3 | 65kA | 4 - 6
SE195004 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 208 | 3 | 25 | 6.6 | 1.5 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | LC1D09 | 208 | 3 | 85kA | 7.8 | 2
[10 empty] | OLR | Schneider | LRD12 | 208 | 3 | 65kA | 5.5 - 8
SE195005 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 208 | 3 | 25 | 7.5 | 2 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | LC1D09 | 208 | 3 | 85kA | 7.8 | 2
[10 empty] | OLR | Schneider | LRD12 | 208 | 3 | 65kA | 5.5 - 8
SE195006 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 208 | 3 | 25 | 10.6 | 3 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | LC1D12 | 208 | 3 | 85kA | 11 | 3
[10 empty] | OLR | Schneider | LRD16 | 208 | 3 | 65kA | 9 - 13
SE195007 | E40610 | 2000-01-07 | V12/S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 9 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 208 | 3 | 25 | 16.7 | 5 | 1373 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | LC1D18 | 208 | 3 | 85kA | 17.5 | 5
[10 empty] | OLR | Schneider | LRD21 | 208 | 3 | 65kA | 12 - 18
SE195008 | E40610 | 2000-01-07 | V12/S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 9 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 24.2 | 7.5 | 1373 | 1, 5, 6, 7k , 11
[10 empty] | MC | Schneider | LC1D32 | 208 | 3 | 85kA | 32.2 | 10
[10 empty] | OLR | Schneider | LRD32 | 208 | 3 | 65kA | 23 - 32
SE195009 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 30.8 | 10 | 915 | 1, 5, 6, 7b , 11
[10 empty] | MC | Schneider | LC1D40A | 208 | 3 | 100kA | 32.2 | 10
[10 empty] | OLR | Schneider | LRD340 | 208 | 3 | 100kA | 30 - 40
SE195010 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 208 | 3 | 25 | 46.2 | 15 | 2289 | 1, 5, 6, 7l , 11
[10 empty] | MC | Schneider | LC1D65A | 208 | 3 | 100kA | 48.3 | 20
[10 empty] | OLR | Schneider | LRD350 | 208 | 3 | 100kA | 37 - 50
SE195011 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 208 | 3 | 25 | 59.4 | 20 | 2289 | 1, 5, 6, 7l , 11
[10 empty] | MC | Schneider | LC1D80 | 208 | 3 | 100kA | 62.1 | 25
[10 empty] | OLR | Schneider | LRD365 | 208 | 3 | 100kA | 48 - 65
SE195012 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 | - | 208 | 3 | 25 | 74.8 | 25 | 2289 | 1, 5, 6, 7l , 11
[10 empty] | MC | Schneider | LC1D80 | 208 | 3 | 100kA | 78.2 | 25
[10 empty] | OLR | Schneider | LRD3363 | 208 | 3 | 100kA | 63 - 80
SE195013 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 240 | 3 | 25 | 2.2 | 0.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 240 | 3 | 85kA | 6.8 | 2
[10 empty] | OLR | Schneider | LRD07 | 240 | 3 | 65kA | 1.6 - 2.5
SE195014 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 3.2 | 0.75 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 240 | 3 | 85kA | 6.8 | 2
[10 empty] | OLR | Schneider | LRD08 | 240 | 3 | 65kA | 2.5 - 4
SE195015 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 4.2 | 1 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 240 | 3 | 85kA | 6.8 | 2
[10 empty] | OLR | Schneider | LRD10 | 240 | 3 | 65kA | 4 - 6
SE195016 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 6 | 1.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 240 | 3 | 85kA | 6.8 | 2
[10 empty] | OLR | Schneider | LRD12 | 240 | 3 | 65kA | 5.5 - 8
SE195017 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 240 | 3 | 25 | 6.8 | 2 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 240 | 3 | 85kA | 6.8 | 2
[10 empty] | OLR | Schneider | LRD12 | 240 | 3 | 65kA | 5.5 - 8
SE195018 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 240 | 3 | 25 | 9.6 | 3 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D12 | 240 | 3 | 85kA | 9.6 | 3
[10 empty] | OLR | Schneider | LRD14 | 240 | 3 | 65kA | 7 - 10
SE195019 | E40610 | 2000-01-07 | V12/S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 9 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 240 | 3 | 25 | 15.2 | 5 | 1373 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D18 | 240 | 3 | 85kA | 15.2 | 5
[10 empty] | OLR | Schneider | LRD21 | 240 | 3 | 65kA | 12 - 18
SE195020 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 240 | 3 | 25 | 22 | 7.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D25 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LRD22 | 240 | 3 | 65kA | 16 - 24
SE195021 | E40610 | 2000-01-07 | V12/S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 9 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 240 | 3 | 25 | 28 | 10 | 1373 | 1, 5, 6, 7k
[10 empty] | MC | Schneider | LC1D32 | 240 | 3 | 85kA | 28 | 10
[10 empty] | OLR | Schneider | LRD32 | 240 | 3 | 65kA | 23 - 32
SE195022 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 240 | 3 | 25 | 42 | 15 | 915 | 1, 5, 6, 7b
[10 empty] | MC | Schneider | LC1D50A | 240 | 3 | 100kA | 42 | 15
[10 empty] | OLR | Schneider | LRD350 | 240 | 3 | 100kA | 37 - 50
SE195023 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 240 | 3 | 25 | 54 | 20 | 2289 | 1, 5, 6, 7l
[10 empty] | MC | Schneider | LC1D65A | 240 | 3 | 100kA | 54 | 20
[10 empty] | OLR | Schneider | LRD365 | 240 | 3 | 100kA | 48 - 65
SE195024 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 240 | 3 | 25 | 68 | 25 | 2289 | 1, 5, 6, 7l
[10 empty] | MC | Schneider | LC1D80 | 240 | 3 | 100kA | 80 | 30
[10 empty] | OLR | Schneider | LRD3363 | 240 | 3 | 100kA | 63 - 80
SE195025 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 | - | 240 | 3 | 25 | 80 | 30 | 2289 | 1, 5, 6, 7l
[10 empty] | MC | Schneider | LC1D80 | 240 | 3 | 100kA | 80 | 30
[10 empty] | OLR | Schneider | LRD3363 | 240 | 3 | 100kA | 63 - 80
SE195026 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T002D | 600 | 3 | - | 2 | - | 480 | 3 | 18 | 1.1 | 0.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 480 | 3 | 85kA | 7.6 | 5
[10 empty] | OLR | Schneider | LRD06 | 480 | 3 | 65kA | 1 - 1.6
SE195027 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T002D | 600 | 3 | - | 2 | - | 480 | 3 | 18 | 1.6 | 0.75 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 480 | 3 | 85kA | 7.6 | 5
[10 empty] | OLR | Schneider | LRD07 | 480 | 3 | 65kA | 1.6 - 2.5
SE195028 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 480 | 3 | 18 | 2.1 | 1 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 480 | 3 | 85kA | 7.6 | 5
[10 empty] | OLR | Schneider | LRD07 | 480 | 3 | 65kA | 1.6 - 2.5
SE195029 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 480 | 3 | 18 | 3 | 1.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 480 | 3 | 85kA | 7.6 | 5
[10 empty] | OLR | Schneider | LRD08 | 480 | 3 | 65kA | 2.5 - 4
SE195030 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 480 | 3 | 18 | 3 | 1.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 480 | 3 | 85kA | 7.6 | 5
[10 empty] | OLR | Schneider | LRD07 | 480 | 3 | 65kA | 1.6 - 2.5
SE195031 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 480 | 3 | 18 | 3.4 | 2 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 480 | 3 | 85kA | 7.6 | 5
[10 empty] | OLR | Schneider | LRD08 | 480 | 3 | 65kA | 2.5 - 4
SE195032 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 480 | 3 | 18 | 4.8 | 3 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 480 | 3 | 85kA | 7.6 | 5
[10 empty] | OLR | Schneider | LRD10 | 480 | 3 | 65kA | 4 - 6
SE195033 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 480 | 3 | 18 | 7.6 | 5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 480 | 3 | 85kA | 7.6 | 5
[10 empty] | OLR | Schneider | LRD12 | 480 | 3 | 65kA | 5.5 - 8
SE195034 | E40610 | 2000-01-07 | V12/S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 9 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 480 | 3 | 18 | 11 | 7.5 | 1373 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D12 | 480 | 3 | 85kA | 11 | 7.5
[10 empty] | OLR | Schneider | LRD16 | 480 | 3 | 65kA | 9 - 13
SE195035 | E40610 | 2000-01-07 | V12/S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 9 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 480 | 3 | 18 | 14 | 10 | 1373 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D18 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LRD21 | 480 | 3 | 65kA | 12 - 18
SE195036 | E40610 | 2000-01-07 | V12/S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 9 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 480 | 3 | 18 | 21 | 15 | 1373 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D25 | 480 | 3 | 85kA | 21 | 15
[10 empty] | OLR | Schneider | LRD22 | 480 | 3 | 65kA | 16 - 24
SE195037 | E40610 | 2000-01-07 | V12/S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 9 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 480 | 3 | 18 | 27 | 20 | 1373 | 1, 5, 6, 7k
[10 empty] | MC | Schneider | LC1D32 | 480 | 3 | 85kA | 27 | 20
[10 empty] | OLR | Schneider | LRD32 | 480 | 3 | 65kA | 23 - 32
SE195038 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 480 | 3 | 18 | 34 | 25 | 915 | 1, 5, 6, 7b
[10 empty] | MC | Schneider | LC1D40A | 480 | 3 | 100kA | 40 | 30
[10 empty] | OLR | Schneider | LRD340 | 480 | 3 | 100kA | 30 - 40
SE195039 | E40610 | 2000-01-07 | V12/S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 12 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 480 | 3 | 18 | 40 | 30 | 1832 | 1, 5, 6, 7b
[10 empty] | MC | Schneider | LC1D40A | 480 | 3 | 100kA | 40 | 30
[10 empty] | OLR | Schneider | LRD340 | 480 | 3 | 100kA | 30 - 40
SE195040 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 480 | 3 | 18 | 52 | 40 | 2289 | 1, 5, 6, 7l
[10 empty] | MC | Schneider | LC1D65A | 480 | 3 | 100kA | 52 | 40
[10 empty] | OLR | Schneider | LRD365 | 480 | 3 | 100kA | 48 - 65
SE195041 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 480 | 3 | 18 | 65 | 50 | 2289 | 1, 5, 6, 7l
[10 empty] | MC | Schneider | LC1D80 | 480 | 3 | 100kA | 77 | 60
[10 empty] | OLR | Schneider | LRD3363 | 480 | 3 | 100kA | 63 - 80
SE195042 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 |  | 480 | 3 | 18 | 77 | 60 | 2289 | 1, 5, 6, 7l
[10 empty] | MC | Schneider | LC1D80 | 480 | 3 | 100kA | 77 | 60
[10 empty] | OLR | Schneider | LRD3363 | 480 | 3 | 100kA | 63 - 80
SE195043 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 208 | 3 | 65 | 2.4 | 0.5 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | LC1D09 | 208 | 3 | 85kA | 7.8 | 2
[10 empty] | OLR | Schneider | LRD07 | 208 | 3 | 65kA | 1.6 - 2.5
SE195044 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | LC1D09 | 208 | 3 | 85kA | 7.8 | 2
[10 empty] | OLR | Schneider | LRD08 | 208 | 3 | 65kA | 2.5 - 4
SE195045 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | LC1D09 | 208 | 3 | 85kA | 7.8 | 2
[10 empty] | OLR | Schneider | LRD10 | 208 | 3 | 65kA | 4 - 6
SE195046 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 65 | 6.6 | 1.5 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | LC1D09 | 208 | 3 | 85kA | 7.8 | 2
[10 empty] | OLR | Schneider | LRD12 | 208 | 3 | 65kA | 5.5 - 8
SE195047 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 65 | 7.5 | 2 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | LC1D09 | 208 | 3 | 85kA | 7.8 | 2
[10 empty] | OLR | Schneider | LRD12 | 208 | 3 | 65kA | 5.5 - 8
SE195048 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 65 | 10.6 | 3 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | LC1D12 | 208 | 3 | 85kA | 11 | 3
[10 empty] | OLR | Schneider | LRD16 | 208 | 3 | 65kA | 9 - 13
SE195049 | E40610 | 2000-01-07 | V12/S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 9 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1373 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | LC1D18 | 208 | 3 | 85kA | 17.5 | 5
[10 empty] | OLR | Schneider | LRD21 | 208 | 3 | 65kA | 12 - 18
SE195050 | E40610 | 2000-01-07 | V12/S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 9 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1373 | 1, 5, 6, 7k , 11
[10 empty] | MC | Schneider | LC1D32 | 208 | 3 | 85kA | 32.2 | 10
[10 empty] | OLR | Schneider | LRD32 | 208 | 3 | 65kA | 23 - 32
SE195051 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 65 | 30.8 | 10 | 915 | 1, 5, 6, 7b , 11
[10 empty] | MC | Schneider | LC1D40A | 208 | 3 | 100kA | 32.2 | 10
[10 empty] | OLR | Schneider | LRD340 | 208 | 3 | 100kA | 30 - 40
SE195052 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 208 | 3 | 65 | 46.2 | 15 | 2289 | 1, 5, 6, 7l , 11
[10 empty] | MC | Schneider | LC1D65A | 208 | 3 | 100kA | 48.3 | 20
[10 empty] | OLR | Schneider | LRD350 | 208 | 3 | 100kA | 37 - 50
SE195053 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 208 | 3 | 65 | 59.4 | 20 | 2289 | 1, 5, 6, 7l , 11
[10 empty] | MC | Schneider | LC1D80A | 208 | 3 | 100kA | 62.1 | 25
[10 empty] | OLR | Schneider | LRD365 | 208 | 3 | 100kA | 48 - 65
SE195054 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T115J | 600 | 3 | - | 115 | - | 208 | 3 | 65 | 74.8 | 25 | 2289 | 1, 5, 6, 7l , 11
[10 empty] | MC | Schneider | LC1D80 | 208 | 3 | 100kA | 78.2 | 25
[10 empty] | OLR | Schneider | LRD3363 | 208 | 3 | 100kA | 63 - 80
SE195055 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 240 | 3 | 65 | 2.2 | 0.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 240 | 3 | 85kA | 6.8 | 3
[10 empty] | OLR | Schneider | LRD07 | 240 | 3 | 65kA | 1.6 - 2.5
SE195056 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 65 | 3.2 | 0.75 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 240 | 3 | 85kA | 6.8 | 3
[10 empty] | OLR | Schneider | LRD08 | 240 | 3 | 65kA | 2.5 - 4
SE195057 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 65 | 4.2 | 1 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 240 | 3 | 85kA | 6.8 | 3
[10 empty] | OLR | Schneider | LRD10 | 240 | 3 | 65kA | 4 - 6
SE195058 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 65 | 6 | 1.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 240 | 3 | 85kA | 6.8 | 3
[10 empty] | OLR | Schneider | LRD12 | 240 | 3 | 65kA | 5.5 - 8
SE195059 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 240 | 3 | 65 | 6.8 | 2 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 240 | 3 | 85kA | 6.8 | 3
[10 empty] | OLR | Schneider | LRD12 | 240 | 3 | 65kA | 5.5 - 8
SE195060 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 240 | 3 | 65 | 9.6 | 3 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D12 | 240 | 3 | 85kA | 9.6 | 3
[10 empty] | OLR | Schneider | LRD14 | 240 | 3 | 65kA | 7 - 10
SE195061 | E40610 | 2000-01-07 | V12/S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 9 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 240 | 3 | 65 | 15.2 | 5 | 1373 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D18 | 240 | 3 | 85kA | 15.2 | 5
[10 empty] | OLR | Schneider | LRD21 | 240 | 3 | 65kA | 12 - 18
SE195062 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 65 | 22 | 7.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D25 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LRD22 | 240 | 3 | 65kA | 16 - 24
SE195063 | E40610 | 2000-01-07 | V12/S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 9 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 65 | 28 | 10 | 1373 | 1, 5, 6, 7k
[10 empty] | MC | Schneider | LC1D32 | 240 | 3 | 85kA | 28 | 10
[10 empty] | OLR | Schneider | LRD32 | 240 | 3 | 65kA | 23 - 32
SE195064 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 65 | 42 | 15 | 915 | 1, 5, 6, 7b
[10 empty] | MC | Schneider | LC1D50A | 240 | 3 | 100kA | 42 | 15
[10 empty] | OLR | Schneider | LRD350 | 240 | 3 | 100kA | 37 - 50
SE195065 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 240 | 3 | 65 | 54 | 20 | 2289 | 1, 5, 6, 7l
[10 empty] | MC | Schneider | LC1D65A | 240 | 3 | 100kA | 54 | 20
[10 empty] | OLR | Schneider | LRD365 | 240 | 3 | 100kA | 48 - 65
SE195066 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 240 | 3 | 65 | 68 | 25 | 2289 | 1, 5, 6, 7l
[10 empty] | MC | Schneider | LC1D80 | 240 | 3 | 100kA | 80 | 30
[10 empty] | OLR | Schneider | LRD3363 | 240 | 3 | 100kA | 63 - 80
SE195067 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T115J | 600 | 3 | - | 115 | - | 240 | 3 | 65 | 80 | 30 | 2289 | 1, 5, 6, 7l
[10 empty] | MC | Schneider | LC1D80 | 240 | 3 | 100kA | 80 | 30
[10 empty] | OLR | Schneider | LRD3363 | 240 | 3 | 100kA | 63 - 80
SE195068 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T002J | 600 | 3 | - | 2 | - | 480 | 3 | 65 | 1.1 | 0.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 480 | 3 | 85kA | 7.6 | 5
[10 empty] | OLR | Schneider | LRD06 | 480 | 3 | 65kA | 1 - 1.6
SE195069 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T002J | 600 | 3 | - | 2 | - | 480 | 3 | 65 | 1.6 | 0.75 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 480 | 3 | 85kA | 7.6 | 5
[10 empty] | OLR | Schneider | LRD07 | 480 | 3 | 65kA | 1.6 - 2.5
SE195070 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 480 | 3 | 65 | 2.1 | 1 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 480 | 3 | 85kA | 7.6 | 5
[10 empty] | OLR | Schneider | LRD07 | 480 | 3 | 65kA | 1.6 - 2.5
SE195071 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 480 | 3 | 65 | 3 | 1.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 480 | 3 | 85kA | 7.6 | 5
[10 empty] | OLR | Schneider | LRD08 | 480 | 3 | 65kA | 2.5 - 4
SE195072 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 480 | 3 | 65 | 3 | 1.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 480 | 3 | 85kA | 7.6 | 5
[10 empty] | OLR | Schneider | LRD07 | 480 | 3 | 65kA | 1.6 - 2.5
SE195073 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 480 | 3 | 65 | 3.4 | 2 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 480 | 3 | 85kA | 7.6 | 5
[10 empty] | OLR | Schneider | LRD08 | 480 | 3 | 65kA | 2.5 - 4
SE195074 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 480 | 3 | 65 | 4.8 | 3 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 480 | 3 | 85kA | 7.6 | 5
[10 empty] | OLR | Schneider | LRD10 | 480 | 3 | 65kA | 4 - 6
SE195075 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 480 | 3 | 65 | 7.6 | 5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 480 | 3 | 85kA | 7.6 | 5
[10 empty] | OLR | Schneider | LRD12 | 480 | 3 | 65kA | 5.5 - 8
SE195076 | E40610 | 2000-01-07 | V12/S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 9 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 480 | 3 | 65 | 11 | 7.5 | 1373 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D12 | 480 | 3 | 85kA | 11 | 7.5
[10 empty] | OLR | Schneider | LRD16 | 480 | 3 | 65kA | 9 - 13
SE195077 | E40610 | 2000-01-07 | V12/S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 9 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 480 | 3 | 65 | 14 | 10 | 1373 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D18 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LRD21 | 480 | 3 | 65kA | 12 - 18
SE195078 | E40610 | 2000-01-07 | V12/S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 9 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 480 | 3 | 65 | 21 | 15 | 1373 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D25 | 480 | 3 | 85kA | 21 | 15
[10 empty] | OLR | Schneider | LRD22 | 480 | 3 | 65kA | 16 - 24
SE195079 | E40610 | 2000-01-07 | V12/S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 9 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 480 | 3 | 65 | 27 | 20 | 1373 | 1, 5, 6, 7k
[10 empty] | MC | Schneider | LC1D32 | 480 | 3 | 85kA | 27 | 20
[10 empty] | OLR | Schneider | LRD32 | 480 | 3 | 65kA | 23 - 32
SE195080 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 480 | 3 | 65 | 34 | 25 | 915 | 1, 5, 6, 7b
[10 empty] | MC | Schneider | LC1D40A | 480 | 3 | 100kA | 40 | 30
[10 empty] | OLR | Schneider | LRD340 | 480 | 3 | 100kA | 30 - 40
SE195081 | E40610 | 2000-01-07 | V12/S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 480 | 3 | 65 | 40 | 30 | 1832 | 1, 5, 6, 7b
[10 empty] | MC | Schneider | LC1D40A | 480 | 3 | 100kA | 40 | 30
[10 empty] | OLR | Schneider | LRD340 | 480 | 3 | 100kA | 30 - 40
SE195082 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 480 | 3 | 65 | 52 | 40 | 2289 | 1, 5, 6, 7l
[10 empty] | MC | Schneider | LC1D65A | 480 | 3 | 100kA | 52 | 40
[10 empty] | OLR | Schneider | LRD365 | 480 | 3 | 100kA | 48 - 65
SE195083 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 480 | 3 | 65 | 65 | 50 | 2289 | 1, 5, 6, 7l
[10 empty] | MC | Schneider | LC1D80 | 480 | 3 | 100kA | 77 | 60
[10 empty] | OLR | Schneider | LRD3363 | 480 | 3 | 100kA | 63 - 80
SE195084 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T115J | 600 | 3 | - | 115 |  | 480 | 3 | 65 | 77 | 60 | 2289 | 1, 5, 6, 7l
[10 empty] | MC | Schneider | LC1D80 | 480 | 3 | 100kA | 77 | 60
[10 empty] | OLR | Schneider | LRD3363 | 480 | 3 | 100kA | 63 - 80

## TeSys N LRD
Database Identification Number | Listed Combination Motor Controller Information | [7 empty] | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Enclosure Volume, cubic inches | Conditions of Use
| Listing Report Information |  |  |  |  | Enclosure or Unit Dimensions
| UL File Number | Report Issue Date MM-DD-YYYY | Volume / Section (Vol#).(Sec#) | Model Number or Product Style/ Designation | Product Description on Page/Figure/Ill. | Enclosure or Unit Height, inches | Width, inches | Depth, inches |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating
SE196001 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 |  | 208 | 3 | 25 | 2.4 | 0.5 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | T02CN13 | 208 | 3 | 85kA | 25.3 | 7.5
[10 empty] | OLR | Schneider | LRD07L | 208 | 3 | 65kA | 1.6 - 2.5
SE196002 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 |  | 208 | 3 | 25 | 3.5 | 0.75 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | T02CN13 | 208 | 3 | 85kA | 25.3 | 7.5
[10 empty] | OLR | Schneider | LRD08L | 208 | 3 | 65kA | 2.5 - 4
SE196003 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 25 | 4.6 | 1 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | T02CN13 | 208 | 3 | 85kA | 25.3 | 7.5
[10 empty] | OLR | Schneider | LRD10L | 208 | 3 | 65kA | 4 - 6
SE196004 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 208 | 3 | 25 | 6.6 | 1.5 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | T02CN13 | 208 | 3 | 85kA | 25.3 | 7.5
[10 empty] | OLR | Schneider | LRD12L | 208 | 3 | 65kA | 5.5 - 8
SE196005 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 |  | 208 | 3 | 25 | 7.5 | 2 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | T02CN13 | 208 | 3 | 85kA | 25.3 | 7.5
[10 empty] | OLR | Schneider | LRD14L | 208 | 3 | 65kA | 7 - 10
SE196006 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 208 | 3 | 25 | 10.6 | 3 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | T02CN13 | 208 | 3 | 85kA | 25.3 | 7.5
[10 empty] | OLR | Schneider | LRD16L | 208 | 3 | 65kA | 9 - 13
SE196007 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 208 | 3 | 25 | 16.7 | 5 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | T02CN13 | 208 | 3 | 85kA | 25.3 | 7.5
[10 empty] | OLR | Schneider | LRD22L | 208 | 3 | 65kA | 16 - 24
SE196008 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 24.2 | 7.5 | 915 | 1, 5, 6, 7b , 11
[10 empty] | MC | Schneider | T02DN13 | 208 | 3 | 85kA | 32.2 | 10
[10 empty] | OLR | Schneider | LRD32L | 208 | 3 | 65kA | 23 - 32
SE196009 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 30.8 | 10 | 915 | 1, 5, 6, 7b , 11
[10 empty] | MC | Schneider | T02DN13 | 208 | 3 | 100kA | 32.2 | 10
[10 empty] | OLR | Schneider | LRD340L | 208 | 3 | 100kA | 30 - 40
SE196010 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 240 | 3 | 25 | 2.2 | 0.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LRD07L | 240 | 3 | 65kA | 1.6 - 2.5
SE196011 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 3.2 | 0.75 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LRD08L | 240 | 3 | 65kA | 2.5 - 4
SE196012 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 4.2 | 1 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LRD10L | 240 | 3 | 65kA | 4 - 6
SE196013 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 25 | 6 | 1.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LRD12L | 240 | 3 | 65kA | 5.5 - 8
SE196014 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 240 | 3 | 25 | 6.8 | 2 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LRD12L | 240 | 3 | 65kA | 5.5 - 8
SE196015 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 240 | 3 | 25 | 9.6 | 3 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LRD16L | 240 | 3 | 65kA | 9 - 13
SE196016 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 240 | 3 | 25 | 15.2 | 5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LRD21L | 240 | 3 | 65kA | 12 - 18
SE196017 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 240 | 3 | 25 | 22 | 7.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LRD22L | 240 | 3 | 65kA | 16 - 24
SE196018 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 240 | 3 | 25 | 28 | 10 | 915 | 1, 5, 6, 7b
[10 empty] | MC | Schneider | T02DN13 | 240 | 3 | 100kA | 42 | 15
[10 empty] | OLR | Schneider | LRD332L | 240 | 3 | 100kA | 23 - 32
SE196019 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 240 | 3 | 25 | 42 | 15 | 915 | 1, 5, 6, 7b
[10 empty] | MC | Schneider | T02DN13 | 240 | 3 | 100kA | 42 | 15
[10 empty] | OLR | Schneider | LRD350L | 240 | 3 | 100kA | 37 - 50
SE196020 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T002D | 600 | 3 | - | 2 | - | 480 | 3 | 18 | 1.1 | 0.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LRD06L | 480 | 3 | 65kA | 1 - 1.6
SE196021 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T002D | 600 | 3 | - | 2 | - | 480 | 3 | 18 | 1.6 | 0.75 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LRD07L | 480 | 3 | 65kA | 1.6 - 2.5
SE196022 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 480 | 3 | 18 | 2.1 | 1 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LRD07L | 480 | 3 | 65kA | 1.6 - 2.5
SE196023 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 480 | 3 | 18 | 3 | 1.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LRD08L | 480 | 3 | 65kA | 2.5 - 4
SE196024 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 480 | 3 | 18 | 3 | 1.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LRD07L | 480 | 3 | 65kA | 1.6 - 2.5
SE196025 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 480 | 3 | 18 | 3.4 | 2 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LRD08L | 480 | 3 | 65kA | 2.5 - 4
SE196026 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 480 | 3 | 18 | 4.8 | 3 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LRD10L | 480 | 3 | 65kA | 4 - 6
SE196027 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 480 | 3 | 18 | 7.6 | 5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LRD14L | 480 | 3 | 65kA | 7 - 10
SE196028 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 480 | 3 | 18 | 11 | 7.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LRD16L | 480 | 3 | 65kA | 9 - 13
SE196029 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 480 | 3 | 18 | 14 | 10 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LRD21L | 480 | 3 | 65kA | 12 - 18
SE196030 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 480 | 3 | 18 | 21 | 15 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02DN13 | 480 | 3 | 100kA | 34 | 25
[10 empty] | OLR | Schneider | LRD325L | 480 | 3 | 100kA | 15 - 25
SE196031 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 480 | 3 | 18 | 27 | 20 | 915 | 1, 5, 6, 7b
[10 empty] | MC | Schneider | T02DN13 | 480 | 3 | 100kA | 34 | 25
[10 empty] | OLR | Schneider | LRD332L | 480 | 3 | 100kA | 23 - 32
SE196032 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 480 | 3 | 18 | 34 | 25 | 915 | 1, 5, 6, 7b
[10 empty] | MC | Schneider | T02DN13 | 480 | 3 | 100kA | 34 | 25
[10 empty] | OLR | Schneider | LRD340L | 480 | 3 | 100kA | 30 - 40
SE196033 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 208 | 3 | 65 | 2.4 | 0.5 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | T02CN13 | 208 | 3 | 85kA | 25.3 | 7.5
[10 empty] | OLR | Schneider | LRD07L | 208 | 3 | 65kA | 1.6 - 2.5
SE196034 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 208 | 3 | 65 | 3.5 | 0.75 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | T02CN13 | 208 | 3 | 85kA | 25.3 | 7.5
[10 empty] | OLR | Schneider | LRD08L | 208 | 3 | 65kA | 2.5 - 4
SE196035 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 208 | 3 | 65 | 4.6 | 1 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | T02CN13 | 208 | 3 | 85kA | 25.3 | 7.5
[10 empty] | OLR | Schneider | LRD10L | 208 | 3 | 65kA | 4 - 6
SE196036 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 65 | 6.6 | 1.5 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | T02CN13 | 208 | 3 | 85kA | 25.3 | 7.5
[10 empty] | OLR | Schneider | LRD12L | 208 | 3 | 65kA | 5.5 - 8
SE196037 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 65 | 7.5 | 2 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | T02CN13 | 208 | 3 | 85kA | 25.3 | 7.5
[10 empty] | OLR | Schneider | LRD14L | 208 | 3 | 65kA | 7 - 10
SE196038 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 65 | 10.6 | 3 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | T02CN13 | 208 | 3 | 85kA | 25.3 | 7.5
[10 empty] | OLR | Schneider | LRD16L | 208 | 3 | 65kA | 9 - 13
SE196039 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | T02CN13 | 208 | 3 | 85kA | 25.3 | 7.5
[10 empty] | OLR | Schneider | LRD22L | 208 | 3 | 65kA | 16 - 24
SE196040 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 915 | 1, 5, 6, 7b , 11
[10 empty] | MC | Schneider | T02DN13 | 208 | 3 | 85kA | 32.2 | 10
[10 empty] | OLR | Schneider | LRD32L | 208 | 3 | 65kA | 23 - 32
SE196041 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 65 | 30.8 | 10 | 915 | 1, 5, 6, 7b , 11
[10 empty] | MC | Schneider | T02DN13 | 208 | 3 | 100kA | 32.2 | 10
[10 empty] | OLR | Schneider | LRD340L | 208 | 3 | 100kA | 30 - 40
SE196042 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 240 | 3 | 65 | 2.2 | 0.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LRD07L | 240 | 3 | 65kA | 1.6 - 2.5
SE196043 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 65 | 3.2 | 0.75 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LRD08L | 240 | 3 | 65kA | 2.5 - 4
SE196044 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 65 | 4.2 | 1 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LRD10L | 240 | 3 | 65kA | 4 - 6
SE196045 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 240 | 3 | 65 | 6 | 1.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LRD12L | 240 | 3 | 65kA | 5.5 - 8
SE196046 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 240 | 3 | 65 | 6.8 | 2 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LRD12L | 240 | 3 | 65kA | 5.5 - 8
SE196047 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 240 | 3 | 65 | 9.6 | 3 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LRD16L | 240 | 3 | 65kA | 9 - 13
SE196048 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 240 | 3 | 65 | 15.2 | 5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LRD21L | 240 | 3 | 65kA | 12 - 18
SE196049 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 65 | 22 | 7.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LRD22L | 240 | 3 | 65kA | 16 - 24
SE196050 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 65 | 28 | 10 | 915 | 1, 5, 6, 7b
[10 empty] | MC | Schneider | T02DN13 | 240 | 3 | 100kA | 42 | 15
[10 empty] | OLR | Schneider | LRD332L | 240 | 3 | 100kA | 23 - 32
SE196051 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 65 | 42 | 15 | 915 | 1, 5, 6, 7b
[10 empty] | MC | Schneider | T02DN13 | 240 | 3 | 100kA | 42 | 15
[10 empty] | OLR | Schneider | LRD350L | 240 | 3 | 100kA | 37 - 50
SE196052 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 480 | 3 | 65 | 21 | 15 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02DN13 | 480 | 3 | 100kA | 34 | 25
[10 empty] | OLR | Schneider | LRD325L | 480 | 3 | 100kA | 15 - 25
SE196053 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T002J | 600 | 3 | - | 2 | - | 480 | 3 | 65 | 1.1 | 0.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LRD06L | 480 | 3 | 65kA | 1 - 1.6
SE196054 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T002J | 600 | 3 | - | 2 | - | 480 | 3 | 65 | 1.6 | 0.75 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LRD07L | 480 | 3 | 65kA | 1.6 - 2.5
SE196055 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 480 | 3 | 65 | 2.1 | 1 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LRD07L | 480 | 3 | 65kA | 1.6 - 2.5
SE196056 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003J | 600 | 3 | - | 3.5 | - | 480 | 3 | 65 | 3 | 1.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LRD08L | 480 | 3 | 65kA | 2.5 - 4
SE196057 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 480 | 3 | 65 | 3.4 | 2 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LRD08L | 480 | 3 | 65kA | 2.5 - 4
SE196058 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007J | 600 | 3 | - | 7 | - | 480 | 3 | 65 | 4.8 | 3 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LRD10L | 480 | 3 | 65kA | 4 - 6
SE196059 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 480 | 3 | 65 | 7.6 | 5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LRD14L | 480 | 3 | 65kA | 7 - 10
SE196060 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 480 | 3 | 65 | 11 | 7.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LRD16L | 480 | 3 | 65kA | 9 - 13
SE196061 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 480 | 3 | 65 | 14 | 10 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LRD21L | 480 | 3 | 65kA | 12 - 18
SE196062 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 480 | 3 | 65 | 27 | 20 | 915 | 1, 5, 6, 7b
[10 empty] | MC | Schneider | T02DN13 | 480 | 3 | 100kA | 34 | 25
[10 empty] | OLR | Schneider | LRD332L | 480 | 3 | 100kA | 23 - 32
SE196063 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 480 | 3 | 65 | 34 | 25 | 915 | 1, 5, 6, 7b
[10 empty] | MC | Schneider | T02DN13 | 480 | 3 | 100kA | 34 | 25
[10 empty] | OLR | Schneider | LRD340L | 480 | 3 | 100kA | 30 - 40

## LC1D LR9D
Database Identification Number | Listed Combination Motor Controller Information | [7 empty] | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Enclosure Volume, cubic inches | Conditions of Use
| Listing Report Information |  |  |  |  | Enclosure or Unit Dimensions
| UL File Number | Report Issue Date MM-DD-YYYY | Volume / Section | Model Number or Product Style/ Designation | Product Description on Page/Figure/Ill. | Enclosure or Unit Height, inches | Width, inches | Depth, inches |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating
SE197001 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 208 | 3 | 10 | 2.4 | 0.5 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | LC1D09 | 208 | 3 | 85kA | 7.8 | 2
[10 empty] | OLR | Schneider | LR9D08 | 208 | 3 | 10kA Y | 1.6 - 8
SE197002 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 10 | 3.5 | 0.75 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | LC1D09 | 208 | 3 | 85kA | 7.8 | 2
[10 empty] | OLR | Schneider | LR9D08 | 208 | 3 | 10kA Y | 1.6 - 8
SE197003 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 208 | 3 | 10 | 4.6 | 1 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | LC1D09 | 208 | 3 | 85kA | 7.8 | 2
[10 empty] | OLR | Schneider | LR9D08 | 208 | 3 | 10kA Y | 1.6 - 8
SE197004 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 208 | 3 | 10 | 6.6 | 1.5 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | LC1D09 | 208 | 3 | 85kA | 7.8 | 2
[10 empty] | OLR | Schneider | LR9D08 | 208 | 3 | 10kA Y | 1.6 - 8
SE197005 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 208 | 3 | 10 | 7.5 | 2 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | LC1D09 | 208 | 3 | 85kA | 7.8 | 2
[10 empty] | OLR | Schneider | LR9D08 | 208 | 3 | 10kA Y | 1.6 - 8
SE197006 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 208 | 3 | 25 | 10.6 | 3 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | LC1D12 | 208 | 3 | 85kA | 11 | 3
[10 empty] | OLR | Schneider | LR9D32 | 208 | 3 | 65kA | 6.4 - 32
SE197007 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 6 9 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 208 | 3 | 25 | 16.7 | 5 | 1373 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | LC1D18 | 208 | 3 | 85kA | 17.5 | 5
[10 empty] | OLR | Schneider | LR9D32 | 208 | 3 | 65kA | 6.4 - 32
SE197008 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 6 9 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 24.2 | 7.5 | 1373 | 1, 5, 6, 7k , 11
[10 empty] | MC | Schneider | LC1D32 | 208 | 3 | 85kA | 32.2 | 10
[10 empty] | OLR | Schneider | LR9D32 | 208 | 3 | 65kA | 6.4 - 32
SE197009 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 208 | 3 | 25 | 30.8 | 10 | 915 | 1, 5, 6, 7b , 11
[10 empty] | MC | Schneider | LC1D40A | 208 | 3 | 100kA | 32.2 | 10
[10 empty] | OLR | Schneider | LR9D110S | 208 | 3 | 65kA | 22 - 110
SE197010 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 208 | 3 | 25 | 46.2 | 15 | 2289 | 1, 5, 6, 7l , 11
[10 empty] | MC | Schneider | LC1D50A | 208 | 3 | 100kA | 48.3 | 15
[10 empty] | OLR | Schneider | LR9D110S | 208 | 3 | 65kA | 22 - 110
SE197011 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 208 | 3 | 25 | 59.4 | 20 | 2289 | 1, 5, 6, 7l , 11
[10 empty] | MC | Schneider | LC1D65A | 208 | 3 | 100kA | 62.1 | 20
[10 empty] | OLR | Schneider | LR9D110S | 208 | 3 | 65kA | 22 - 110
SE197012 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 | - | 208 | 3 | 25 | 74.8 | 25 | 2289 | 1, 5, 6, 7l , 11
[10 empty] | MC | Schneider | LC1D80 | 208 | 3 | 100kA | 78.2 | 25
[10 empty] | OLR | Schneider | LR9D110S | 208 | 3 | 65kA | 22 - 110
SE197013 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 240 | 3 | 10 | 2.2 | 0.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 240 | 3 | 85kA | 6.8 | 2
[10 empty] | OLR | Schneider | LR9D08 | 240 | 3 | 10kA Y | 1.6 - 8
SE197014 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 10 | 3.2 | 0.75 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 240 | 3 | 85kA | 6.8 | 2
[10 empty] | OLR | Schneider | LR9D08 | 240 | 3 | 10kA Y | 1.6 - 8
SE197015 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 10 | 4.2 | 1 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 240 | 3 | 85kA | 6.8 | 2
[10 empty] | OLR | Schneider | LR9D08 | 240 | 3 | 10kA Y | 1.6 - 8
SE197016 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 240 | 3 | 10 | 6 | 1.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 240 | 3 | 85kA | 6.8 | 2
[10 empty] | OLR | Schneider | LR9D08 | 240 | 3 | 10kA Y | 1.6 - 8
SE197017 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 240 | 3 | 10 | 6.8 | 2 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 240 | 3 | 85kA | 6.8 | 2
[10 empty] | OLR | Schneider | LR9D08 | 240 | 3 | 10kA Y | 1.6 - 8
SE197018 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 240 | 3 | 25 | 9.6 | 3 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D12 | 240 | 3 | 85kA | 9.6 | 3
[10 empty] | OLR | Schneider | LR9D32 | 240 | 3 | 65kA | 6.4 - 32
SE197019 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 240 | 3 | 25 | 22 | 7.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D25 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LR9D32 | 240 | 3 | 65kA | 6.4 - 32
SE197020 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 6 9 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 240 | 3 | 25 | 28 | 10 | 1373 | 1, 5, 6, 7k
[10 empty] | MC | Schneider | LC1D32 | 240 | 3 | 85kA | 28 | 10
[10 empty] | OLR | Schneider | LR9D32 | 240 | 3 | 65kA | 6.4 - 32
SE197021 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 240 | 3 | 25 | 42 | 15 | 915 | 1, 5, 6, 7b
[10 empty] | MC | Schneider | LC1D50A | 240 | 3 | 100kA | 42 | 15
[10 empty] | OLR | Schneider | LR9D110S | 240 | 3 | 65kA | 22 - 110
SE197022 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 240 | 3 | 25 | 54 | 20 | 2289 | 1, 5, 6, 7l
[10 empty] | MC | Schneider | LC1D65A | 240 | 3 | 100kA | 54 | 20
[10 empty] | OLR | Schneider | LR9D110S | 240 | 3 | 65kA | 22 - 110
SE197023 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 240 | 3 | 25 | 68 | 25 | 2289 | 1, 5, 6, 7l
[10 empty] | MC | Schneider | LC1D80 | 240 | 3 | 100kA | 80 | 30
[10 empty] | OLR | Schneider | LR9D110S | 240 | 3 | 65kA | 22 - 110
SE197024 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 | - | 240 | 3 | 25 | 80 | 30 | 2289 | 1, 5, 6, 7l
[10 empty] | MC | Schneider | LC1D80 | 240 | 3 | 100kA | 80 | 30
[10 empty] | OLR | Schneider | LR9D110S | 240 | 3 | 65kA | 22 - 110
SE197025 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T002D | 600 | 3 | - | 2 | - | 480 | 3 | 10 | 1.1 | 0.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 480 | 3 | 85kA | 7.6 | 5
[10 empty] | OLR | Schneider | LR9D02 | 480 | 3 | 10kA Y | .4 - 2
SE197026 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T002D | 600 | 3 | - | 2 | - | 480 | 3 | 10 | 1.6 | 0.75 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 480 | 3 | 85kA | 7.6 | 5
[10 empty] | OLR | Schneider | LR9D02 | 480 | 3 | 10kA Y | .4 - 2
SE197027 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 480 | 3 | 10 | 2.1 | 1 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 480 | 3 | 85kA | 7.6 | 5
[10 empty] | OLR | Schneider | LR9D08 | 480 | 3 | 10kA Y | 1.6 - 8
SE197028 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 480 | 3 | 10 | 3 | 1.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 480 | 3 | 85kA | 7.6 | 5
[10 empty] | OLR | Schneider | LR9D08 | 480 | 3 | 10kA Y | 1.6 - 8
SE197029 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 | - | 480 | 3 | 10 | 3 | 1.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 480 | 3 | 85kA | 7.6 | 5
[10 empty] | OLR | Schneider | LR9D08 | 480 | 3 | 10kA Y | 1.6 - 8
SE197030 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 480 | 3 | 10 | 3.4 | 2 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 480 | 3 | 85kA | 7.6 | 5
[10 empty] | OLR | Schneider | LR9D08 | 480 | 3 | 10kA Y | 1.6 - 8
SE197031 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 | - | 480 | 3 | 10 | 4.8 | 3 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 480 | 3 | 85kA | 7.6 | 5
[10 empty] | OLR | Schneider | LR9D08 | 480 | 3 | 10kA Y | 1.6 - 8
SE197032 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 480 | 3 | 10 | 7.6 | 5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D09 | 480 | 3 | 85kA | 7.6 | 5
[10 empty] | OLR | Schneider | LR9D08 | 480 | 3 | 10kA Y | 1.6 - 8
SE197033 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 6 9 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 | - | 480 | 3 | 18 | 11 | 7.5 | 1373 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D12 | 480 | 3 | 85kA | 11 | 7.5
[10 empty] | OLR | Schneider | LR9D32 | 480 | 3 | 65kA | 6.4 - 32
SE197034 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 6 9 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 480 | 3 | 18 | 14 | 10 | 1373 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D18 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LR9D32 | 480 | 3 | 65kA | 6.4 - 32
SE197035 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 6 9 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 | - | 480 | 3 | 18 | 21 | 15 | 1373 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D25 | 480 | 3 | 85kA | 21 | 15
[10 empty] | OLR | Schneider | LR9D32 | 480 | 3 | 65kA | 6.4 - 32
SE197036 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 6 9 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 480 | 3 | 18 | 27 | 20 | 1373 | 1, 5, 6, 7k
[10 empty] | MC | Schneider | LC1D32 | 480 | 3 | 85kA | 27 | 20
[10 empty] | OLR | Schneider | LR9D32 | 480 | 3 | 65kA | 6.4 - 32
SE197037 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 480 | 3 | 18 | 34 | 25 | 915 | 1, 5, 6, 7b
[10 empty] | MC | Schneider | LC1D40A | 480 | 3 | 100kA | 40 | 30
[10 empty] | OLR | Schneider | LR9D110S | 480 | 3 | 65kA | 22 - 110
SE197038 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 12 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 | - | 480 | 3 | 18 | 40 | 30 | 1832 | 1, 5, 6, 7b
[10 empty] | MC | Schneider | LC1D40A | 480 | 3 | 100kA | 40 | 30
[10 empty] | OLR | Schneider | LR9D110S | 480 | 3 | 65kA | 22 - 110
SE197039 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 480 | 3 | 18 | 52 | 40 | 2289 | 1, 5, 6, 7l
[10 empty] | MC | Schneider | LC1D65A | 480 | 3 | 100kA | 52 | 40
[10 empty] | OLR | Schneider | LR9D110S | 480 | 3 | 65kA | 22 - 110
SE197040 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T080D | 600 | 3 | - | 80 | - | 480 | 3 | 18 | 65 | 50 | 2289 | 1, 5, 6, 7l
[10 empty] | MC | Schneider | LC1D80 | 480 | 3 | 100kA | 77 | 60
[10 empty] | OLR | Schneider | LR9D110S | 480 | 3 | 65kA | 22 - 110
SE197041 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T115D | 600 | 3 | - | 115 |  | 480 | 3 | 18 | 77 | 60 | 2289 | 1, 5, 6, 7l
[10 empty] | MC | Schneider | LC1D80 | 480 | 3 | 100kA | 77 | 60
[10 empty] | OLR | Schneider | LR9D110S | 480 | 3 | 65kA | 22 - 110
SE197042 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 208 | 3 | 65 | 10.6 | 3 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | LC1D12 | 208 | 3 | 85kA | 11 | 3
[10 empty] | OLR | Schneider | LR9D32 | 208 | 3 | 65kA | 6.4 - 32
SE197043 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 6 9 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 208 | 3 | 65 | 16.7 | 5 | 1373 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | LC1D18 | 208 | 3 | 85kA | 17.5 | 5
[10 empty] | OLR | Schneider | LR9D32 | 208 | 3 | 65kA | 6.4 - 32
SE197044 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 6 9 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 65 | 24.2 | 7.5 | 1373 | 1, 5, 6, 7k , 11
[10 empty] | MC | Schneider | LC1D32 | 208 | 3 | 85kA | 32.2 | 10
[10 empty] | OLR | Schneider | LR9D32 | 208 | 3 | 65kA | 6.4 - 32
SE197045 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 208 | 3 | 65 | 30.8 | 10 | 915 | 1, 5, 6, 7b , 11
[10 empty] | MC | Schneider | LC1D40A | 208 | 3 | 100kA | 32.2 | 10
[10 empty] | OLR | Schneider | LR9D110S | 208 | 3 | 65kA | 22 - 110
SE197046 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 208 | 3 | 65 | 46.2 | 15 | 2289 | 1, 5, 6, 7l , 11
[10 empty] | MC | Schneider | LC1D50A | 208 | 3 | 100kA | 48.3 | 15
[10 empty] | OLR | Schneider | LR9D110S | 208 | 3 | 65kA | 22 - 110
SE197047 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 208 | 3 | 65 | 59.4 | 20 | 2289 | 1, 5, 6, 7l , 11
[10 empty] | MC | Schneider | LC1D65A | 208 | 3 | 100kA | 62.1 | 20
[10 empty] | OLR | Schneider | LR9D110S | 208 | 3 | 65kA | 22 - 110
SE197048 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T115J | 600 | 3 | - | 115 | - | 208 | 3 | 65 | 74.8 | 25 | 2289 | 1, 5, 6, 7l , 11
[10 empty] | MC | Schneider | LC1D80 | 208 | 3 | 100kA | 78.2 | 25
[10 empty] | OLR | Schneider | LR9D110S | 208 | 3 | 65kA | 22 - 110
SE197049 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 240 | 3 | 65 | 9.6 | 3 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D12 | 240 | 3 | 85kA | 9.6 | 3
[10 empty] | OLR | Schneider | LR9D32 | 240 | 3 | 65kA | 6.4 - 32
SE197050 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 6 9 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 240 | 3 | 65 | 15.2 | 5 | 1373 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D18 | 240 | 3 | 85kA | 15.2 | 5
[10 empty] | OLR | Schneider | LR9D32 | 240 | 3 | 65kA | 6.4 - 32
SE197051 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 65 | 22 | 7.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D25 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LR9D32 | 240 | 3 | 65kA | 6.4 - 32
SE197052 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 6 9 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 65 | 28 | 10 | 1373 | 1, 5, 6, 7k
[10 empty] | MC | Schneider | LC1D32 | 240 | 3 | 85kA | 28 | 10
[10 empty] | OLR | Schneider | LR9D32 | 240 | 3 | 65kA | 6.4 - 32
SE197053 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 240 | 3 | 65 | 42 | 15 | 915 | 1, 5, 6, 7b
[10 empty] | MC | Schneider | LC1D50A | 240 | 3 | 100kA | 42 | 15
[10 empty] | OLR | Schneider | LR9D110S | 240 | 3 | 65kA | 22 - 110
SE197054 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 240 | 3 | 65 | 54 | 20 | 2289 | 1, 5, 6, 7l
[10 empty] | MC | Schneider | LC1D65A | 240 | 3 | 100kA | 54 | 20
[10 empty] | OLR | Schneider | LR9D110S | 240 | 3 | 65kA | 22 - 110
SE197055 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 240 | 3 | 65 | 68 | 25 | 2289 | 1, 5, 6, 7l
[10 empty] | MC | Schneider | LC1D80 | 240 | 3 | 100kA | 80 | 30
[10 empty] | OLR | Schneider | LR9D110S | 240 | 3 | 65kA | 22 - 110
SE197056 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T115J | 600 | 3 | - | 115 | - | 240 | 3 | 65 | 80 | 30 | 2289 | 1, 5, 6, 7l
[10 empty] | MC | Schneider | LC1D80 | 240 | 3 | 100kA | 80 | 30
[10 empty] | OLR | Schneider | LR9D110S | 240 | 3 | 65kA | 22 - 110
SE197057 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 6 9 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 | - | 480 | 3 | 65 | 11 | 7.5 | 1373 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D12 | 480 | 3 | 85kA | 11 | 7.5
[10 empty] | OLR | Schneider | LR9D32 | 480 | 3 | 65kA | 6.4 - 32
SE197058 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 6 9 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 480 | 3 | 65 | 14 | 10 | 1373 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D18 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LR9D32 | 480 | 3 | 65kA | 6.4 - 32
SE197059 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 6 9 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 | - | 480 | 3 | 65 | 21 | 15 | 1373 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | LC1D25 | 480 | 3 | 85kA | 21 | 15
[10 empty] | OLR | Schneider | LR9D32 | 480 | 3 | 65kA | 6.4 - 32
SE197060 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 6 9 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 480 | 3 | 65 | 27 | 20 | 1373 | 1, 5, 6, 7k
[10 empty] | MC | Schneider | LC1D32 | 480 | 3 | 85kA | 27 | 20
[10 empty] | OLR | Schneider | LR9D32 | 480 | 3 | 65kA | 6.4 - 32
SE197061 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 480 | 3 | 65 | 34 | 25 | 915 | 1, 5, 6, 7b
[10 empty] | MC | Schneider | LC1D40A | 480 | 3 | 100kA | 40 | 30
[10 empty] | OLR | Schneider | LR9D110S | 480 | 3 | 65kA | 22 - 110
SE197062 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 12 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 | - | 480 | 3 | 65 | 40 | 30 | 1832 | 1, 5, 6, 7b
[10 empty] | MC | Schneider | LC1D40A | 480 | 3 | 100kA | 40 | 30
[10 empty] | OLR | Schneider | LR9D110S | 480 | 3 | 65kA | 22 - 110
SE197063 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 480 | 3 | 65 | 52 | 40 | 2289 | 1, 5, 6, 7l
[10 empty] | MC | Schneider | LC1D65A | 480 | 3 | 100kA | 52 | 30
[10 empty] | OLR | Schneider | LR9D110S | 480 | 3 | 65kA | 22 - 110
SE197064 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T080J | 600 | 3 | - | 80 | - | 480 | 3 | 65 | 65 | 50 | 2289 | 1, 5, 6, 7l
[10 empty] | MC | Schneider | LC1D80 | 480 | 3 | 100kA | 77 | 40
[10 empty] | OLR | Schneider | LR9D110S | 480 | 3 | 65kA | 22 - 110
SE197065 | E40610 | 2000-01-07 | V12 / S15 | Model6 | Pg. 1, 1A, 2, 2A-1, 3, 3A, 4, fig1., ILL-1, ILL -2F, ILL -4 | 15 | 14 | 11 | D | ICB | Schneider | BV4T115J | 600 | 3 | - | 115 |  | 480 | 3 | 65 | 77 | 60 | 2289 | 1, 5, 6, 7l
[10 empty] | MC | Schneider | LC1D80 | 480 | 3 | 100kA | 77
[10 empty] | OLR | Schneider | LR9D110S | 480 | 3 | 65kA | 22 - 110

## TeSys N LR9D
Database Identification Number | Listed Combination Motor Controller Information | [7 empty] | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Enclosure Volume, cubic inches | Conditions of Use
| Listing Report Information |  |  |  |  | Enclosure or Unit Dimensions
| UL File Number | Report Issue Date YYYY-MM-DD | Volume / Section | Model Number or Product Style/ Designation | Product Description on Page/Figure/Ill. | Enclosure or Unit Height, inches | Width, inches | Depth, inches |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating, FLA or FLA/LRA | Hp Rating
SE198001 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 |  | 208 | 3 | 10 | 2.5 | 0.5 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | T02BN13 | 208 | 3 | 85kA | 25.3 | 7.5
[10 empty] | OLR | Schneider | LR9D08 | 208 | 3 | 10kA Y | 1.6 - 8
SE198002 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 |  | 208 | 3 | 10 | 3.7 | 0.75 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | T02BN13 | 208 | 3 | 85kA | 25.3 | 7.5
[10 empty] | OLR | Schneider | LR9D08 | 208 | 3 | 10kA Y | 1.6 - 8
SE198003 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 |  | 208 | 3 | 10 | 4.8 | 1 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | T02BN13 | 208 | 3 | 85kA | 25.3 | 7.5
[10 empty] | OLR | Schneider | LR9D08 | 208 | 3 | 10kA Y | 1.6 - 8
SE198004 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 |  | 208 | 3 | 10 | 6.9 | 1.5 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | T02BN13 | 208 | 3 | 85kA | 25.3 | 7.5
[10 empty] | OLR | Schneider | LR9D08 | 208 | 3 | 10kA Y | 1.6 - 8
SE198005 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 |  | 208 | 3 | 10 | 7.8 | 2 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | T02BN13 | 208 | 3 | 85kA | 25.3 | 7.5
[10 empty] | OLR | Schneider | LR9D08 | 208 | 3 | 10kA Y | 1.6 - 8
SE198006 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 |  | 208 | 3 | 25 | 11 | 3 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | T02BN13 | 208 | 3 | 85kA | 25.3 | 7.5
[10 empty] | OLR | Schneider | LR9D32 | 208 | 3 | 65kA | 6.4 - 32
SE198007 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 |  | 208 | 3 | 25 | 17.5 | 5 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | T02CN13 | 208 | 3 | 85kA | 25.3 | 7.5
[10 empty] | OLR | Schneider | LR9D32 | 208 | 3 | 65kA | 6.4 - 32
SE198008 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 |  | 208 | 3 | 25 | 25.3 | 7.5 | 915 | 1, 5, 6, 7b , 11
[10 empty] | MC | Schneider | T02DN13 | 208 | 3 | 85kA | 30.8 | 10
[10 empty] | OLR | Schneider | LR9D32 | 208 | 3 | 65kA | 6.4 - 32
SE198009 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 |  | 240 | 3 | 10 | 2.2 | 0.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02BN13 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LR9D08 | 240 | 3 | 10kA Y | 1.6 - 8
SE198010 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 |  | 240 | 3 | 10 | 3.2 | 0.75 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02BN13 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LR9D08 | 240 | 3 | 10kA Y | 1.6 - 8
SE198011 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 |  | 240 | 3 | 10 | 4.2 | 1 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02BN13 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LR9D08 | 240 | 3 | 10kA Y | 1.6 - 8
SE198012 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 |  | 240 | 3 | 10 | 6 | 1.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02BN13 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LR9D08 | 240 | 3 | 10kA Y | 1.6 - 8
SE198013 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 |  | 240 | 3 | 10 | 6.8 | 2 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02BN13 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LR9D08 | 240 | 3 | 10kA Y | 1.6 - 8
SE198014 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 |  | 240 | 3 | 25 | 9.6 | 3 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02BN13 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LR9D32 | 240 | 3 | 65kA | 6.4 - 32
SE198015 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 |  | 240 | 3 | 25 | 28 | 10 | 915 | 1, 5, 6, 7b , 11
[10 empty] | MC | Schneider | T02DN13 | 240 | 3 | 100kA | 42 | 15
[10 empty] | OLR | Schneider | LR9D32 | 240 | 3 | 65kA | 6.4 - 32
SE198016 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 |  | 240 | 3 | 25 | 15.2 | 5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LR9D32 | 240 | 3 | 65kA | 6.4 - 32
SE198017 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 |  | 240 | 3 | 25 | 22 | 7.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LR9D32 | 240 | 3 | 65kA | 6.4 - 32
SE198018 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T002D | 600 | 3 | - | 2 |  | 480 | 3 | 10 | 1.1 | 0.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02BN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LR9D02 | 480 | 3 | 10kA Y | .4 - 2
SE198019 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T002D | 600 | 3 | - | 2 |  | 480 | 3 | 10 | 1.6 | 0.75 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02BN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LR9D02 | 480 | 3 | 10kA Y | .4 - 2
SE198020 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 |  | 480 | 3 | 10 | 2.1 | 1 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02BN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LR9D08 | 480 | 3 | 10kA Y | 1.6 - 8
SE198021 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 |  | 480 | 3 | 10 | 3 | 1.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02BN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LR9D08 | 480 | 3 | 10kA Y | 1.6 - 8
SE198022 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T003D | 600 | 3 | - | 3.5 |  | 480 | 3 | 10 | 3 | 1.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02BN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LR9D08 | 480 | 3 | 10kA Y | 1.6 - 8
SE198023 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 |  | 480 | 3 | 10 | 3.4 | 2 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02BN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LR9D08 | 480 | 3 | 10kA Y | 1.6 - 8
SE198024 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 |  | 480 | 3 | 18 | 21 | 15 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02DN13 | 480 | 3 | 100kA | 34 | 25
[10 empty] | OLR | Schneider | LR9D32 | 480 | 3 | 65kA | 6.4 - 32
SE198025 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T007D | 600 | 3 | - | 7 |  | 480 | 3 | 10 | 4.8 | 3 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02BN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LR9D08 | 480 | 3 | 10kA Y | 1.6 - 8
SE198026 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050D | 600 | 3 | - | 50 |  | 480 | 3 | 18 | 27 | 20 | 915 | 1, 5, 6, 7b , 11
[10 empty] | MC | Schneider | T02DN13 | 480 | 3 | 100kA | 34 | 25
[10 empty] | OLR | Schneider | LR9D32 | 480 | 3 | 65kA | 6.4 - 32
SE198027 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 |  | 480 | 3 | 10 | 7.6 | 5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LR9D08 | 480 | 3 | 10kA Y | 1.6 - 8
SE198028 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013D | 600 | 3 | - | 12.5 |  | 480 | 3 | 18 | 11 | 7.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LR9D32 | 480 | 3 | 65kA | 6.4 - 32
SE198029 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T025D | 600 | 3 | - | 25 |  | 480 | 3 | 18 | 14 | 10 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LR9D32 | 480 | 3 | 65kA | 6.4 - 32
SE198030 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 |  | 208 | 3 | 65 | 11 | 3 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | T02BN13 | 208 | 3 | 85kA | 25.3 | 7.5
[10 empty] | OLR | Schneider | LR9D32 | 208 | 3 | 65kA | 6.4 - 32
SE198031 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 |  | 208 | 3 | 65 | 17.5 | 5 | 915 | 1, 5, 6, 7a , 11
[10 empty] | MC | Schneider | T02CN13 | 208 | 3 | 85kA | 25.3 | 7.5
[10 empty] | OLR | Schneider | LR9D32 | 208 | 3 | 65kA | 6.4 - 32
SE198032 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 |  | 208 | 3 | 65 | 25.3 | 7.5 | 915 | 1, 5, 6, 7b , 11
[10 empty] | MC | Schneider | T02DN13 | 208 | 3 | 85kA | 32.2 | 10
[10 empty] | OLR | Schneider | LR9D32 | 208 | 3 | 65kA | 6.4 - 32
SE198033 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 |  | 240 | 3 | 65 | 9.6 | 3 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02BN13 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LR9D32 | 240 | 3 | 65kA | 6.4 - 32
SE198034 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 |  | 240 | 3 | 65 | 28 | 10 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02DN13 | 240 | 3 | 100kA | 42 | 15
[10 empty] | OLR | Schneider | LR9D32 | 240 | 3 | 65kA | 6.4 - 32
SE198035 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 |  | 240 | 3 | 65 | 15.2 | 5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LR9D32 | 240 | 3 | 65kA | 6.4 - 32
SE198036 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 |  | 240 | 3 | 65 | 22 | 7.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 240 | 3 | 85kA | 22 | 7.5
[10 empty] | OLR | Schneider | LR9D32 | 240 | 3 | 65kA | 6.4 - 32
SE198037 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 |  | 480 | 3 | 65 | 21 | 15 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02DN13 | 480 | 3 | 100kA | 34 | 25
[10 empty] | OLR | Schneider | LR9D32 | 480 | 3 | 65kA | 6.4 - 32
SE198038 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T013J | 600 | 3 | - | 12.5 |  | 480 | 3 | 65 | 11 | 7.5 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LR9D32 | 480 | 3 | 65kA | 6.4 - 32
SE198039 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T050J | 600 | 3 | - | 50 |  | 480 | 3 | 65 | 27 | 20 | 915 | 1, 5, 6, 7b
[10 empty] | MC | Schneider | T02DN13 | 480 | 3 | 100kA | 34 | 25
[10 empty] | OLR | Schneider | LR9D32 | 480 | 3 | 65kA | 6.4 - 32
SE198040 | E40610 | 1994-08-24 | V12 / S8 | Model6 | Page 1, 2 3, Ill-2 | 6 | 14 | 11 | D | ICB | Schneider | BV4T025J | 600 | 3 | - | 25 |  | 480 | 3 | 65 | 14 | 10 | 915 | 1, 5, 6, 7a
[10 empty] | MC | Schneider | T02CN13 | 480 | 3 | 85kA | 14 | 10
[10 empty] | OLR | Schneider | LR9D32 | 480 | 3 | 65kA | 6.4 - 32

## DO NOT TEST - Design B Only (hidden)
Design B motors ONLY
Component Breaker | Component Contactor | Component Overload | Combination Phase | Combination Voltage | Maximum Combination HP | Maximum Combination NEC FLC | Combination kA (To be Tested) | Issue with Squirrel Cage Motors? Min | Issue with Squirrel Cage Motors? Max | Design B Min | Design B Max
BV4T002D | LC1D09 | LRD05 | 3 | 575 | 1/2 | 0.9 | 14 | Yes | Yes | Yes | No
BV4T002D | LC1D09 | LR9D02 | 3 | 575 | 1/2 | 0.9 | 14 | Yes | Yes | Yes | No
BV4T002D | T02CN13 | LR9D02 | 3 | 575 | 1/2 | 0.9 | 14 | Yes | Yes | Yes | No
BV4T002J | LC1D09 | LRD05 | 3 | 575 | 1/2 | 0.9 | 14 | Yes | Yes | Yes | No
BV4T002J | LC1D09 | LR9D02 | 3 | 575 | 1/2 | 0.9 | 14 | Yes | Yes | Yes | No
BV4T002J | T02CN13 | LR9D02 | 3 | 575 | 1/2 | 0.9 | 14 | Yes | Yes | Yes | No
BV4T007D | LC1D09 | LRD08 | 3 | 460 | 1.5 | 3 | 18 | Yes | Yes | Yes | No
BV4T007D | LC1D09 | LR9D08 | 3 | 460 | 1.5 | 3 | 18 | Yes | Yes | Yes | No
BV4T007D | T02CN13 | LR9D08 | 3 | 460 | 1.5 | 3 | 18 | Yes | Yes | Yes | No
BV4T007J | LC1D09 | LRD08 | 3 | 460 | 1.5 | 3 | 18 | Yes | Yes | Yes | No
BV4T007J | LC1D09 | LR9D08 | 3 | 460 | 1.5 | 3 | 18 | Yes | Yes | Yes | No
BV4T007J | T02CN13 | LR9D08 | 3 | 460 | 1.5 | 3 | 18 | Yes | Yes | Yes | No

## Working File (hidden)
TeSys BV4 Motor Circuit Protector
Ampere Rating | Adjustable Instantaneous Trip Range | Catalog Number |  |  |  |  | Interrupting Rating
|  | D Interrupting Rating | J Interrupting Rating
2 | 12 - 28 | BV4T002D | BV4T002J | 2 | 12 | 28 | 600% | 1400% |  |  |  |  | For squirrel cage motors, other than Design B energy-efficient, select adjustable trip setting not more than 800%. No bigger than 1300%.
3.5 | 21 - 49 | BV4T003D | BV4T003J | 3.5 | 21 | 49 | 600% | 1400% |  |  |  |  | For Design B energy-efficient motors, select adjustable trip setting not more than 1100%. No bigger than 1700%.
7 | 42 - 98 | BV4T007D | BV4T007J | 7 | 42 | 98 | 600% | 1400%
12.5 | 75 - 175 | BV4T012D | BV4T012J | 12.5 | 75 | 175 | 600% | 1400%
25 | 150 - 350 | BV4T025D | BV4T025J | 25 | 150 | 350 | 600% | 1400%
50 | 300 - 700 | BV4T050D | BV4T050J | 50 | 300 | 700 | 600% | 1400% | [6 empty] | GJL = 3-11x
80 | 480 - 1120 | BV4T080D | BV4T080J | 80 | 480 | 1120 | 600% | 1400% | [6 empty] | BV4 = 6-14x
115 | 690 - 1610 | BV4T115D | BV4T115J | 115 | 690 | 1610 | 600% | 1400%
|  | 240V = 25kA | 240V = 100kA
|  | 480V = 18kA | 480V = 65kA | [5 empty] | HP Ratings of Induction Type Squirrel-Cage and Wound Rotor Motors | [5 empty] | TeSys BV4 MCP | Min | Max | Issue with Squirrel Cage Motors? Min | Issue with Squirrel Cage Motors? Max | Design B Min | Design B Max
|  | 600Y = 14kA | 600Y = 25kA | [5 empty] | NEMA Size | 200 Vac | 230 Vac | 460 Vac | 575 Vac | NEC Full Load Amperes | [8 empty] | 800% | 1300% | 1100% | 1700%
[8 empty] | Can't apply with non-Design B motor |  |  |  |  | 1/2 | 0.9 | BV4T002D | 1333% | 3111% | Yes | Yes | Yes | No | 45% | 7.2 | 11.7 | 9.9 | 15.3
[12 empty] | 1/2 |  | 1.1 | BV4T002D | 1091% | 2545% | Yes | No | No | No | 55% | 8.8 | 14.3 | 12.1 | 18.7
[13 empty] | 3/4 | 1.3 | BV4T002D | 923.1% | 2154% | Yes | No | No | No | 65% | 10.4 | 16.9 | 14.3 | 22.1
[12 empty] | 3/4 |  | 1.6 | BV4T002D | 750% | 1750% | No | No | No | No | 80% | 12.8 | 20.8 | 17.6 | 27.2
[13 empty] | 1 | 1.7 | BV4T002D | 705.9% | 1647% | No | No | No | No | 85% | 13.6 | 22.1 | 18.7 | 28.9
[12 empty] | 1 |  | 2.1 | BV4T003D | 1000% | 2333% | Yes | No | No | No | 60% | 16.8 | 27.3 | 23.1 | 35.7
[11 empty] | 1/2 |  |  | 2.2 | BV4T003D | 954.5% | 2227% | Yes | No | No | No | 62.86% | 17.6 | 28.6 | 24.2 | 37.4
[13 empty] | 1.5 | 2.4 | BV4T003D | 875% | 2042% | Yes | No | No | No | 68.57% | 19.2 | 31.2 | 26.4 | 40.8
[10 empty] | 1/2 |  |  |  | 2.5 | BV4T003D | 840% | 1960% | Yes | No | No | No | 71.43% | 20 | 32.5 | 27.5 | 42.5
[13 empty] | 2 | 2.7 | BV4T003D | 777.8% | 1815% | No | No | No | No | 77.14% | 21.6 | 35.1 | 29.7 | 45.9
[8 empty] | Can't apply with non-Design B motor |  |  |  | 1.5 |  | 3 | BV4T007D | 1400% | 3267% | Yes | Yes | Yes | No | 42.86% | 24 | 39 | 33 | 51
[8 empty] | Can't apply with non-Design B motor |  |  | 3/4 |  |  | 3.2 | BV4T007D | 1312% | 3062% | Yes | Yes | Yes | No | 45.71% | 25.6 | 41.6 | 35.2 | 54.4
[12 empty] | 2 |  | 3.4 | BV4T007D | 1235% | 2882% | Yes | No | Yes | No | 48.57% | 27.2 | 44.2 | 37.4 | 57.8
[10 empty] | 3/4 |  |  |  | 3.7 | BV4T007D | 1135% | 2649% | Yes | No | Yes | No | 52.86% | 29.6 | 48.1 | 40.7 | 62.9
[13 empty] | 3 | 3.9 | BV4T007D | 1077% | 2513% | Yes | No | No | No | 55.71% | 31.2 | 50.7 | 42.9 | 66.3
[11 empty] | 1 |  |  | 4.2 | BV4T007D | 1000% | 2333% | Yes | No | No | No | 60% | 33.6 | 54.6 | 46.2 | 71.4
[10 empty] | 1 |  |  |  | 4.8 | BV4T007D | 875% | 2042% | Yes | No | No | No | 68.57% | 38.4 | 62.4 | 52.8 | 81.6
[12 empty] | 3 |  | 4.8 | BV4T007D | 875% | 2042% | Yes | No | No | No | 68.57% | 38.4 | 62.4 | 52.8 | 81.6
[11 empty] | 1.5 |  |  | 6 | BV4T007D | 700% | 1633% | No | No | No | No | 85.71% | 48 | 78 | 66 | 102
[13 empty] | 5 | 6.1 | BV4T007D | 688.5% | 1607% | No | No | No | No | 87.14% | 48.8 | 79.3 | 67.1 | 103.7
[11 empty] | 2 |  |  | 6.8 | BV4T007D | 617.6% | 1441% | No | No | No | No | 97.14% | 54.4 | 88.4 | 74.8 | 115.6
[10 empty] | 1.5 |  |  |  | 6.9 | BV4T007D | 608.7% | 1420% | No | No | No | No | 98.57% | 55.2 | 89.7 | 75.9 | 117.3
[12 empty] | 5 |  | 7.6 | BV4T012D | 986.8% | 2303% | Yes | No | No | No | 60.8% | 60.8 | 98.8 | 83.6 | 129.2
[10 empty] | 2 |  |  |  | 7.8 | BV4T012D | 961.5% | 2244% | Yes | No | No | No | 62.4% | 62.4 | 101.4 | 85.8 | 132.6
[13 empty] | 7.5 | 9 | BV4T012D | 833.3% | 1944% | Yes | No | No | No | 72% | 72 | 117 | 99 | 153
[11 empty] | 3 |  |  | 9.6 | BV4T012D | 781.2% | 1823% | No | No | No | No | 76.8% | 76.8 | 124.8 | 105.6 | 163.2
[10 empty] | 3 |  |  |  | 11 | BV4T012D | 681.8% | 1591% | No | No | No | No | 88% | 88 | 143 | 121 | 187
[12 empty] | 7.5 | 10 | 11 | BV4T012D | 681.8% | 1591% | No | No | No | No | 88% | 88 | 143 | 121 | 187
[12 empty] | 10 |  | 14 | BV4T025D | 1071% | 2500% | Yes | No | No | No | 56% | 112 | 182 | 154 | 238
[11 empty] | 5 |  |  | 15.2 | BV4T025D | 986.8% | 2303% | Yes | No | No | No | 60.8% | 121.6 | 197.6 | 167.2 | 258.4
[13 empty] | 15 | 17 | BV4T025D | 882.4% | 2059% | Yes | No | No | No | 68% | 136 | 221 | 187 | 289
[10 empty] | 5 |  |  |  | 17.5 | BV4T025D | 857.1% | 2000% | Yes | No | No | No | 70% | 140 | 227.5 | 192.5 | 297.5
[12 empty] | 15 |  | 21 | BV4T025D | 714.3% | 1667% | No | No | No | No | 84% | 168 | 273 | 231 | 357
[11 empty] | 7.5 |  | 20 | 22 | BV4T025D | 681.8% | 1591% | No | No | No | No | 88% | 176 | 286 | 242 | 374
[10 empty] | 7.5 |  |  |  | 25.3 | BV4T050D | 1186% | 2767% | Yes | No | Yes | No | 50.6% | 202.4 | 328.9 | 278.3 | 430.1
[12 empty] | 20 | 25 | 27 | BV4T050D | 1111% | 2593% | Yes | No | Yes | No | 54% | 216 | 351 | 297 | 459
[11 empty] | 10 |  |  | 28 | BV4T050D | 1071% | 2500% | Yes | No | No | No | 56% | 224 | 364 | 308 | 476
[13 empty] | 30 | 32 | BV4T050D | 937.5% | 2188% | Yes | No | No | No | 64% | 256 | 416 | 352 | 544
[10 empty] | 10 |  |  |  | 32.2 | BV4T050D | 931.7% | 2174% | Yes | No | No | No | 64.4% | 257.6 | 418.6 | 354.2 | 547.4
[12 empty] | 25 |  | 34 | BV4T050D | 882.4% | 2059% | Yes | No | No | No | 68% | 272 | 442 | 374 | 578
[12 empty] | 30 |  | 40 | BV4T050D | 750% | 1750% | No | No | No | No | 80% | 320 | 520 | 440 | 680
[13 empty] | 40 | 41 | BV4T050D | 731.7% | 1707% | No | No | No | No | 82% | 328 | 533 | 451 | 697
[11 empty] | 15 |  |  | 42 | BV4T050D | 714.3% | 1667% | No | No | No | No | 84% | 336 | 546 | 462 | 714
[10 empty] | 15 |  |  |  | 48.3 | BV4T050D | 621.1% | 1449% | No | No | No | No | 96.6% | 386.4 | 627.9 | 531.3 | 821.1
[12 empty] | 40 | 50 | 52 | BV4T080D | 923.1% | 2154% | Yes | No | No | No | 65% | 416 | 676 | 572 | 884
[11 empty] | 20 |  |  | 54 | BV4T080D | 888.9% | 2074% | Yes | No | No | No | 67.5% | 432 | 702 | 594 | 918
[6 empty] | 0.85714 | [6 empty] | 60 | 62 | BV4T080D | 774.2% | 1806% | No | No | No | No | 77.5% | 496 | 806 | 682 | 1054
[10 empty] | 20 |  |  |  | 62.1 | BV4T080D | 772.9% | 1804% | No | No | No | No | 77.62% | 496.8 | 807.3 | 683.1 | 1055.7
[12 empty] | 50 |  | 65 | BV4T080D | 738.5% | 1723% | No | No | No | No | 81.25% | 520 | 845 | 715 | 1105
[11 empty] | 25 |  |  | 68 | BV4T080D | 705.9% | 1647% | No | No | No | No | 85% | 544 | 884 | 748 | 1156
[12 empty] | 60 | 75 | 77 | BV4T080D | 623.4% | 1455% | No | No | No | No | 96.25% | 616 | 1001 | 847 | 1309
[10 empty] | 25 |  |  |  | 78.2 | BV4T080D | 613.8% | 1432% | No | No | No | No | 97.75% | 625.6 | 1016.6 | 860.2 | 1329.4
[11 empty] | 30 |  |  | 80 | BV4T080D | 600% | 1400% | No | No | No | No | 100% | 640 | 1040 | 880 | 1360
[10 empty] | 30 |  |  |  | 92 | BV4T115D | 750% | 1750% | No | No | No | No | 80% | 736 | 1196 | 1012 | 1564
[12 empty] | 75 |  | 96 | BV4T115D | 718.8% | 1677% | No | No | No | No | 83.48% | 768 | 1248 | 1056 | 1632
[13 empty] | 100 | 99 | BV4T115D | 697% | 1626% | No | No | No | No | 86.09% | 792 | 1287 | 1089 | 1683
[11 empty] | 40 |  |  | 104 | BV4T115D | 663.5% | 1548% | No | No | No | No | 90.43% | 832 | 1352 | 1144 | 1768