## Type E Combinations
Issued: 2020-12-23
Database Identification Number | [B2] Listed Combination Motor Controller Information | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Enclosure Volume, cubic inches | Conditions of Use
Listing Report Information
| UL File Number |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating. FLA or FLA/LRA | Hp Rating
E32-201 | E468300 | E | MSP | FMX | IMM32-P16A | 600Y/347 | 3 | 25 | 0.1 - 0.16 | - | 600Y/347 | 3 | 25 | 0.16 FLA / 1.6 LRA | - | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - |  | -
E32-202 | E468300 | E | MSP | FMX | IMM32-P16A | 480Y/277 | 3 | 65 | 0.1 - 0.16 | - | 480Y/277 | 3 | 65 | 0.16 FLA / 1.6 LRA | - | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - |  | -
E32-203 | E468300 | E | MSP | FMX | IMM32-P16A | 240 | 3 | 65 | 0.1 - 0.16 | - | 240 | 3 | 65 | 0.16 FLA / 1.6 LRA | - | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-204 | E468300 | E | MSP | FMX | IMM32-P16A | 200 | 3 | 65 | 0.1 - 0.16 | - | 200 | 3 | 65 | 0.16 FLA / 1.6 LRA | - | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-205 | E468300 | E | MSP | FMX | IMM32-P25A | 600Y/347 | 3 | 25 | 0.16 - 0.25 | - | 600Y/347 | 3 | 25 | 0.25 FLA / 2.5 LRA | - | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-206 | E468300 | E | MSP | FMX | IMM32-P25A | 480Y/277 | 3 | 65 | 0.16 - 0.25 | - | 480Y/277 | 3 | 65 | 0.25 FLA / 2.5 LRA | - | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-207 | E468300 | E | MSP | FMX | IMM32-P25A | 240 | 3 | 65 | 0.16 - 0.25 | - | 240 | 3 | 65 | 0.25 FLA / 2.5 LRA | - | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-208 | E468300 | E | MSP | FMX | IMM32-P25A | 200 | 3 | 65 | 0.16 - 0.25 | - | 200 | 3 | 65 | 0.25 FLA / 2.5 LRA | - | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-209 | E468300 | E | MSP | FMX | IMM32-P40A | 600Y/347 | 3 | 25 | 0.25 - 0.4 | - | 600Y/347 | 3 | 25 | 0.40 FLA / 4.0 LRA | - | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-210 | E468300 | E | MSP | FMX | IMM32-P40A | 480Y/277 | 3 | 65 | 0.25 - 0.4 | - | 480Y/277 | 3 | 65 | 0.40 FLA / 4.0 LRA | - | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-211 | E468300 | E | MSP | FMX | IMM32-P40A | 240 | 3 | 65 | 0.25 - 0.4 | - | 240 | 3 | 65 | 0.40 FLA / 4.0 LRA | - | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-212 | E468300 | E | MSP | FMX | IMM32-P40A | 200 | 3 | 65 | 0.25 - 0.4 | - | 200 | 3 | 65 | 0.40 FLA / 4.0 LRA | - | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-213 | E468300 | E | MSP | FMX | IMM32-P63A | 600Y/347 | 3 | 25 | 0.4 - 0.63 | - | 600Y/347 | 3 | 25 | 0.63 FLA / 6.3 LRA | - | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-214 | E468300 | E | MSP | FMX | IMM32-P63A | 480/277 | 3 | 65 | 0.4 - 0.63 | - | 480Y/277 | 3 | 65 | 0.63 FLA / 6.3 LRA | - | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-215 | E468300 | E | MSP | FMX | IMM32-P63A | 240 | 3 | 65 | 0.4 - 0.63 | - | 240 | 3 | 65 | 0.63 FLA / 6.3 LRA | - | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-216 | E468300 | E | MSP | FMX | IMM32-P63A | 200 | 3 | 65 | 0.4 - 0.63 | - | 200 | 3 | 65 | 0.63 FLA / 6.3 LRA | - | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-217 | E468300 | E | MSP | FMX | IMM32-1P0A | 600Y/347 | 3 | 25 | 0.63 - 1 | 1/2 | 600Y/347 | 3 | 25 | 0.9 | 1/2 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-218 | E468300 | E | MSP | FMX | IMM32-1P0A | 480Y/277 | 3 | 65 | 0.63 - 1 | - | 480Y/277 | 3 | 65 | 1.0 FLA / 10.0 LRA | - | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-219 | E468300 | E | MSP | FMX | IMM32-1P0A | 240 | 3 | 65 | 0.63 - 1 | - | 240 | 3 | 65 | 1.0 FLA / 10.0 LRA | - | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-220 | E468300 | E | MSP | FMX | IMM32-1P0A | 200 | 3 | 65 | 0.63 - 1 | - | 200 | 3 | 65 | 1.0 FLA / 10.0 LRA | - | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-221 | E468300 | E | MSP | FMX | IMM32-1P6A | 600Y/347 | 3 | 25 | 1 - 1.6 | 0.75 | 600Y/347 | 3 | 25 | 1.3 | 0.75 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-222 | E468300 | E | MSP | FMX | IMM32-1P6A | 480Y/277 | 3 | 65 | 1 - 1.6 | 3/4 | 480Y/277 | 3 | 65 | 1.6 | 3/4 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-223 | E468300 | E | MSP | FMX | IMM32-1P6A | 240 | 3 | 65 | 1 - 1.6 | - | 240 | 3 | 65 | 1.6 FLA / 16.0 LRA | - | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-224 | E468300 | E | MSP | FMX | IMM32-1P6A | 200 | 3 | 65 | 1 - 1.6 | - | 200 | 3 | 65 | 1.6 FLA / 16.0 LRA | - | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-225 | E468300 | E | MSP | FMX | IMM32-2P5A | 600Y/347 | 3 | 25 | 1.6 - 2.5 | 1-1/2 | 600Y/347 | 3 | 25 | 2.4 | 1-1/2 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-226 | E468300 | E | MSP | FMX | IMM32-2P5A | 480Y/277 | 3 | 65 | 1.6 - 2.5 | 1 | 480Y/277 | 3 | 65 | 2.1 | 1 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-227 | E468300 | E | MSP | FMX | IMM32-2P5A | 240 | 3 | 65 | 1.6 - 2.5 | 1/2 | 240 | 3 | 65 | 2.2 | 1/2 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-228 | E468300 | E | MSP | FMX | IMM32-2P5A | 200 | 3 | 65 | 1.6 - 2.5 | 1/2 | 200 | 3 | 65 | 2.5 | 1/2 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-229 | E468300 | E | MSP | FMX | IMM32-4P0A | 600Y/347 | 3 | 25 | 2.5 - 4 | 3 | 600Y/347 | 3 | 25 | 3.9 | 3 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-230 | E468300 | E | MSP | FMX | IMM32-4P0A | 480Y/277 | 3 | 65 | 2.5 - 4 | 2 | 480Y/277 | 3 | 65 | 3.4 | 2 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-231 | E468300 | E | MSP | FMX | IMM32-4P0A | 240 | 3 | 65 | 2.5 - 4 | 0.75 | 240 | 3 | 65 | 3.2 | 0.75 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-232 | E468300 | E | MSP | FMX | IMM32-4P0A | 200 | 3 | 65 | 2.5 - 4 | 3/4 | 200 | 3 | 65 | 3.7 | 3/4 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-233 | E468300 | E | MSP | FMX | IMM32-6P3A | 600Y/347 | 3 | 25 | 4 - 6.3 | 5 | 600Y/347 | 3 | 25 | 6.1 | 5 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-234 | E468300 | E | MSP | FMX | IMM32-6P3A | 480Y/277 | 3 | 65 | 4 - 6.3 | 3 | 480Y/277 | 3 | 65 | 4.8 | 3 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-235 | E468300 | E | MSP | FMX | IMM32-6P3A | 240 | 3 | 65 | 4 - 6.3 | 1-1/2 | 240 | 3 | 65 | 6 | 1-1/2 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-236 | E468300 | E | MSP | FMX | IMM32-6P3A | 200 | 3 | 65 | 4 - 6.3 | 1 | 200 | 3 | 65 | 4.8 | 1 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-237 | E468300 | E | MSP | FMX | IMM32-010A | 600Y/347 | 3 | 25 | 6.3 - 10 | 7-1/2 | 600Y/347 | 3 | 25 | 9 | 7-1/2 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-238 | E468300 | E | MSP | FMX | IMM32-010A | 480Y/277 | 3 | 65 | 6.3 - 10 | 5 | 480Y/277 | 3 | 65 | 7.6 | 5 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-239 | E468300 | E | MSP | FMX | IMM32-010A | 240 | 3 | 65 | 6.3 - 10 | 3 | 240 | 3 | 65 | 9.6 | 3 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-240 | E468300 | E | MSP | FMX | IMM32-010A | 200 | 3 | 65 | 6.3 - 10 | 2 | 200 | 3 | 65 | 7.8 | 2 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-241 | E468300 | E | MSP | FMX | IMM32-016A | 600Y/347 | 3 | 25 | 10 - 16 | 10 | 600Y/347 | 3 | 25 | 11 | 10 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-242 | E468300 | E | MSP | FMX | IMM32-016A | 480Y/277 | 3 | 65 | 10 - 16 | 10 | 480Y/277 | 3 | 65 | 14 | 10 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-243 | E468300 | E | MSP | FMX | IMM32-016A | 240 | 3 | 65 | 10 - 16 | 5 | 240 | 3 | 65 | 15.2 | 5 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-244 | E468300 | E | MSP | FMX | IMM32-016A | 200 | 3 | 65 | 10 - 16 | 3 | 200 | 3 | 65 | 11 | 3 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-245 | E468300 | E | MSP | FMX | IMM32-020A | 600Y/347 | 3 | 25 | 16 - 20 | 15 | 600Y/347 | 3 | 25 | 17 | 15 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-246 | E468300 | E | MSP | FMX | IMM32-020A | 200 | 3 | 50 | 16 - 20 | 5 | 200 | 3 | 50 | 17.5 | 5 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-247 | E468300 | E | MSP | FMX | IMM32-025A | 600Y/347 | 3 | 25 | 20 - 25 | 20 | 600Y/347 | 3 | 25 | 22 | 20 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-248 | E468300 | E | MSP | FMX | IMM32-025A | 480Y/277 | 3 | 50 | 20 - 25 | 15 | 480Y/277 | 3 | 50 | 21 | 15 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-249 | E468300 | E | MSP | FMX | IMM32-025A | 240 | 3 | 50 | 20 - 25 | 7.5 | 240 | 3 | 50 | 22 | 7.5 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-250 | E468300 | E | MSP | FMX | IMM32-025A | 200 | 3 | 50 | 20 - 25 | 7.5 | 200 | 3 | 50 | 25 | 7.5 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-251 | E468300 | E | MSP | FMX | IMM32-032A | 600Y/347 | 3 | 25 | 25 - 32 | 25 | 600Y/347 | 3 | 25 | 27 | 25 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-252 | E468300 | E | MSP | FMX | IMM32-032A | 480Y/277 | 3 | 50 | 25 - 32 | 20 | 480Y/277 | 3 | 50 | 27 | 20 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-253 | E468300 | E | MSP | FMX | IMM32-032A | 240 | 3 | 50 | 25 - 32 | 10 | 240 | 3 | 50 | 28 | 10 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-254 | E468300 | E | MSP | FMX | IMM32-032A | 200 | 3 | 50 | 25 - 32 | 10 | 200 | 3 | 50 | 32 | 10 | 121.8341 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-255 | E468300 | E | MSP | FMX | IMM32-P16A | 600Y/347 | 3 | 50 | 0.1 - 0.16 | - | 600Y/347 | 3 | 50 | 0.16 FLA / 1.6 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-256 | E468300 | E | MSP | FMX | IMM32-P16A | 480Y/277 | 3 | 100 | 0.1 - 0.16 | - | 480Y/277 | 3 | 100 | 0.16 FLA / 1.6 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-257 | E468300 | E | MSP | FMX | IMM32-P16A | 240 | 3 | 100 | 0.1 - 0.16 | - | 240 | 3 | 100 | 0.16 FLA / 1.6 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-258 | E468300 | E | MSP | FMX | IMM32-P16A | 200 | 3 | 100 | 0.1 - 0.16 | - | 200 | 3 | 100 | 0.16 FLA / 1.6 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-259 | E468300 | E | MSP | FMX | IMM32-P25A | 600Y/347 | 3 | 50 | 0.16 - 0.25 | - | 600Y/347 | 3 | 50 | 0.25 FLA / 2.5 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-260 | E468300 | E | MSP | FMX | IMM32-P25A | 480Y/277 | 3 | 100 | 0.16 - 0.25 | - | 480Y/277 | 3 | 100 | 0.25 FLA / 2.5 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-261 | E468300 | E | MSP | FMX | IMM32-P25A | 240 | 3 | 100 | 0.16 - 0.25 | - | 240 | 3 | 100 | 0.25 FLA / 2.5 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-262 | E468300 | E | MSP | FMX | IMM32-P25A | 200 | 3 | 100 | 0.16 - 0.25 | - | 200 | 3 | 100 | 0.25 FLA / 2.5 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-263 | E468300 | E | MSP | FMX | IMM32-P40A | 600Y/347 | 3 | 50 | 0.25 - 0.4 | - | 600Y/347 | 3 | 50 | 0.40 FLA / 4.0 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-264 | E468300 | E | MSP | FMX | IMM32-P40A | 480Y/277 | 3 | 100 | 0.25 - 0.4 | - | 480Y/277 | 3 | 100 | 0.40 FLA / 4.0 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-265 | E468300 | E | MSP | FMX | IMM32-P40A | 240 | 3 | 100 | 0.25 - 0.4 | - | 240 | 3 | 100 | 0.40 FLA / 4.0 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-266 | E468300 | E | MSP | FMX | IMM32-P40A | 200 | 3 | 100 | 0.25 - 0.4 | - | 200 | 3 | 100 | 0.40 FLA / 4.0 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-267 | E468300 | E | MSP | FMX | IMM32-P63A | 600Y/347 | 3 | 50 | 0.4 - 0.63 | - | 600Y/347 | 3 | 50 | 0.63 FLA / 6.3 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-268 | E468300 | E | MSP | FMX | IMM32-P63A | 480Y/277 | 3 | 100 | 0.4 - 0.63 | - | 480Y/277 | 3 | 100 | 0.63 FLA / 6.3 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-269 | E468300 | E | MSP | FMX | IMM32-P63A | 240 | 3 | 100 | 0.4 - 0.63 | - | 240 | 3 | 100 | 0.63 FLA / 6.3 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-270 | E468300 | E | MSP | FMX | IMM32-P63A | 200 | 3 | 100 | 0.4 - 0.63 | - | 200 | 3 | 100 | 0.63 FLA / 6.3 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-271 | E468300 | E | MSP | FMX | IMM32-1P0A | 600Y/347 | 3 | 50 | 0.63 - 1 | 1/2 | 600Y/347 | 3 | 50 | 0.9 | 1/2 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-272 | E468300 | E | MSP | FMX | IMM32-1P0A | 480Y/277 | 3 | 100 | 0.63 - 1 | - | 480Y/277 | 3 | 100 | 1.0 FLA / 10.0 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-273 | E468300 | E | MSP | FMX | IMM32-1P0A | 240 | 3 | 100 | 0.63 - 1 | - | 240 | 3 | 100 | 1.0 FLA / 10.0 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-274 | E468300 | E | MSP | FMX | IMM32-1P0A | 200 | 3 | 100 | 0.63 - 1 | - | 200 | 3 | 100 | 1.0 FLA / 10.0 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-275 | E468300 | E | MSP | FMX | IMM32-1P6A | 600Y/347 | 3 | 50 | 1 - 1.6 | 0.75 | 600Y/347 | 3 | 50 | 1.3 | 0.75 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-276 | E468300 | E | MSP | FMX | IMM32-1P6A | 480Y/277 | 3 | 100 | 1 - 1.6 | 3/4 | 480Y/277 | 3 | 100 | 1.6 | 3/4 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-277 | E468300 | E | MSP | FMX | IMM32-1P6A | 240 | 3 | 100 | 1 - 1.6 | - | 240 | 3 | 100 | 1.6 FLA / 16.0 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-278 | E468300 | E | MSP | FMX | IMM32-1P6A | 200 | 3 | 100 | 1 - 1.6 | - | 200 | 3 | 100 | 1.6 FLA / 16.0 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-279 | E468300 | E | MSP | FMX | IMM32-2P5A | 600Y/347 | 3 | 50 | 1.6 - 2.5 | 1-1/2 | 600Y/347 | 3 | 50 | 2.4 | 1-1/2 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-280 | E468300 | E | MSP | FMX | IMM32-2P5A | 480Y/277 | 3 | 100 | 1.6 - 2.5 | 1 | 480Y/277 | 3 | 100 | 2.1 | 1 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-281 | E468300 | E | MSP | FMX | IMM32-2P5A | 240 | 3 | 100 | 1.6 - 2.5 | 1/2 | 240 | 3 | 100 | 2.2 | 1/2 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-282 | E468300 | E | MSP | FMX | IMM32-2P5A | 200 | 3 | 100 | 1.6 - 2.5 | 1/2 | 200 | 3 | 100 | 2.5 | 1/2 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-283 | E468300 | E | MSP | FMX | IMM32-4P0A | 600Y/347 | 3 | 50 | 2.5 - 4 | 3 | 600Y/347 | 3 | 50 | 3.9 | 3 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-284 | E468300 | E | MSP | FMX | IMM32-4P0A | 480Y/277 | 3 | 100 | 2.5 - 4 | 2 | 480Y/277 | 3 | 100 | 3.4 | 2 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-285 | E468300 | E | MSP | FMX | IMM32-4P0A | 240 | 3 | 100 | 2.5 - 4 | 0.75 | 240 | 3 | 100 | 3.2 | 0.75 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-286 | E468300 | E | MSP | FMX | IMM32-4P0A | 200 | 3 | 100 | 2.5 - 4 | 3/4 | 200 | 3 | 100 | 3.7 | 3/4 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-287 | E468300 | E | MSP | FMX | IMM32-6P3A | 600Y/347 | 3 | 50 | 4 - 6.3 | 5 | 600Y/347 | 3 | 50 | 6.1 | 5 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-288 | E468300 | E | MSP | FMX | IMM32-6P3A | 480Y/277 | 3 | 100 | 4 - 6.3 | 3 | 480Y/277 | 3 | 100 | 4.8 | 3 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-289 | E468300 | E | MSP | FMX | IMM32-6P3A | 240 | 3 | 100 | 4 - 6.3 | 1-1/2 | 240 | 3 | 100 | 6 | 1-1/2 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-290 | E468300 | E | MSP | FMX | IMM32-6P3A | 200 | 3 | 100 | 4 - 6.3 | 1 | 200 | 3 | 100 | 4.8 | 1 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-291 | E468300 | E | MSP | FMX | IMM32-010A | 600Y/347 | 3 | 50 | 6.3 - 10 | 7-1/2 | 600Y/347 | 3 | 50 | 9 | 7-1/2 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-292 | E468300 | E | MSP | FMX | IMM32-010A | 480Y/277 | 3 | 100 | 6.3 - 10 | 5 | 480Y/277 | 3 | 100 | 7.6 | 5 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-293 | E468300 | E | MSP | FMX | IMM32-010A | 240 | 3 | 100 | 6.3 - 10 | 3 | 240 | 3 | 100 | 9.6 | 3 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-294 | E468300 | E | MSP | FMX | IMM32-010A | 200 | 3 | 100 | 6.3 - 10 | 2 | 200 | 3 | 100 | 7.8 | 2 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-295 | E468300 | E | MSP | FMX | IMM32-016A | 600Y/347 | 3 | 50 | 10 - 16 | 10 | 600Y/347 | 3 | 50 | 11 | 10 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-296 | E468300 | E | MSP | FMX | IMM32-016A | 480Y/277 | 3 | 100 | 10 - 16 | 10 | 480Y/277 | 3 | 100 | 14 | 10 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-297 | E468300 | E | MSP | FMX | IMM32-016A | 240 | 3 | 100 | 10 - 16 | 5 | 240 | 3 | 100 | 15.2 | 5 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-298 | E468300 | E | MSP | FMX | IMM32-016A | 200 | 3 | 100 | 10 - 16 | 3 | 200 | 3 | 100 | 11 | 3 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-299 | E468300 | E | MSP | FMX | IMM32-020A | 600Y/347 | 3 | 50 | 16 - 20 | 15 | 600Y/347 | 3 | 50 | 17 | 15 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-300 | E468300 | E | MSP | FMX | IMM32-020A | 200 | 3 | 100 | 16 - 20 | 5 | 200 | 3 | 100 | 17.5 | 5 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-301 | E468300 | E | MSP | FMX | IMM32-025A | 600Y/347 | 3 | 50 | 20 - 25 | 20 | 600Y/347 | 3 | 50 | 22 | 20 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-302 | E468300 | E | MSP | FMX | IMM32-025A | 480Y/277 | 3 | 100 | 20 - 25 | 15 | 480Y/277 | 3 | 100 | 21 | 15 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-303 | E468300 | E | MSP | FMX | IMM32-025A | 240 | 3 | 100 | 20 - 25 | 7-1/2 | 240 | 3 | 100 | 22 | 7-1/2 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-304 | E468300 | E | MSP | FMX | IMM32-025A | 200 | 3 | 100 | 20 - 25 | 7-1/2 | 200 | 3 | 100 | 25 | 7-1/2 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-305 | E468300 | E | MSP | FMX | IMM32-032A | 600Y/347 | 3 | 50 | 25 - 32 | 25 | 600Y/347 | 3 | 50 | 27 | 25 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-306 | E468300 | E | MSP | FMX | IMM32-032A | 480Y/277 | 3 | 100 | 25 - 32 | 20 | 480Y/277 | 3 | 100 | 27 | 20 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-307 | E468300 | E | MSP | FMX | IMM32-032A | 240 | 3 | 100 | 25 - 32 | 10 | 240 | 3 | 100 | 28 | 10 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E32-308 | E468300 | E | MSP | FMX | IMM32-032A | 200 | 3 | 100 | 25 - 32 | 10 | 200 | 3 | 100 | 32 | 10 | 262.5734 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F |  |  |  |  | -
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
E65-417 | E468300 | E | MSP | FMX | IMM65-040A | 600Y/347 | 3 | 10 | 32 - 40 | 30 | 600Y/347 | 3 | 10 | 32 | 30 | 336.4305 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-65F | - | - | - | - | -
E65-418 | E468300 | E | MSP | FMX | IMM65-040A | 480Y/277 | 3 | 30 | 32 - 40 | 25 | 480Y/277 | 3 | 30 | 34 | 25 | 336.4305 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-65F | - | - | - | - | -
E65-419 | E468300 | E | MSP | FMX | IMM65-050A | 600Y/347 | 3 | 10 | 40 - 50 | 40 | 600Y/347 | 3 | 10 | 41 | 40 | 336.4305 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-65F | - | - | - | - | -
E65-420 | E468300 | E | MSP | FMX | IMM65-050A | 480Y/277 | 3 | 30 | 40 - 50 | 30 | 480Y/277 | 3 | 30 | 40 | 30 | 336.4305 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-65F | - | - | - | - | -
E65-421 | E468300 | E | MSP | FMX | IMM65-050A | 240 | 3 | 30 | 40 - 50 | 15 | 240 | 3 | 30 | 42 | 15 | 336.4305 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-65F | - | - | - | - | -
E65-422 | E468300 | E | MSP | FMX | IMM65-050A | 200 | 3 | 30 | 40 - 50 | 15 | 200 | 3 | 30 | 48.3 | 15 | 336.4305 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-65F | - | - | - | - | -
E65-423 | E468300 | E | MSP | FMX | IMM65-065A | 600Y/347 | 3 | 10 | 50 - 65 | 60 | 600Y/347 | 3 | 10 | 62 | 60 | 336.4305 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-65F | - | - | - | - | -
E65-424 | E468300 | E | MSP | FMX | IMM65-065A | 480Y/277 | 3 | 30 | 50 - 65 | 50 | 480Y/277 | 3 | 30 | 65 | 50 | 336.4305 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-65F | - | - | - | - | -
E65-425 | E468300 | E | MSP | FMX | IMM65-065A | 240 | 3 | 30 | 50 - 65 | 20 | 240 | 3 | 30 | 54 | 20 | 336.4305 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-65F | - | - | - | - | -
E65-426 | E468300 | E | MSP | FMX | IMM65-065A | 200 | 3 | 30 | 50 - 65 | 20 | 200 | 3 | 30 | 62.1 | 20 | 336.4305 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-65F | - | - | - | - | -
E32-001 | E468300 | E | MSP | FMX | IMM32-P16A | 600Y/347 | 3 | 25 | 0.1 - 0.16 | - | 600Y/347 | 3 | 25 | 0.16 FLA / 1.6 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - |  | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-002 | E468300 | E | MSP | FMX | IMM32-P16A | 480Y/277 | 3 | 65 | 0.1 - 0.16 | - | 480Y/277 | 3 | 65 | 0.16 FLA / 1.6 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-003 | E468300 | E | MSP | FMX | IMM32-P16A | 240 | 3 | 65 | 0.1 - 0.16 | - | 240 | 3 | 65 | 0.16 FLA / 1.6 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-004 | E468300 | E | MSP | FMX | IMM32-P16A | 200 | 3 | 65 | 0.1 - 0.16 | - | 200 | 3 | 65 | 0.16 FLA / 1.6 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-005 | E468300 | E | MSP | FMX | IMM32-P25A | 600Y/347 | 3 | 25 | 0.16 - 0.25 | - | 600Y/347 | 3 | 25 | 0.25 FLA / 2.5 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-006 | E468300 | E | MSP | FMX | IMM32-P25A | 480Y/277 | 3 | 65 | 0.16 - 0.25 | - | 480Y/277 | 3 | 65 | 0.25 FLA / 2.5 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-007 | E468300 | E | MSP | FMX | IMM32-P25A | 240 | 3 | 65 | 0.16 - 0.25 | - | 240 | 3 | 65 | 0.25 FLA / 2.5 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-008 | E468300 | E | MSP | FMX | IMM32-P25A | 200 | 3 | 65 | 0.16 - 0.25 | - | 200 | 3 | 65 | 0.25 FLA / 2.5 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-009 | E468300 | E | MSP | FMX | IMM32-P40A | 600Y/347 | 3 | 25 | 0.25 - 0.4 | - | 600Y/347 | 3 | 25 | 0.40 FLA / 4.0 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-010 | E468300 | E | MSP | FMX | IMM32-P40A | 480Y/277 | 3 | 65 | 0.25 - 0.4 | - | 480Y/277 | 3 | 65 | 0.40 FLA / 4.0 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-011 | E468300 | E | MSP | FMX | IMM32-P40A | 240 | 3 | 65 | 0.25 - 0.4 | - | 240 | 3 | 65 | 0.40 FLA / 4.0 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-012 | E468300 | E | MSP | FMX | IMM32-P40A | 200 | 3 | 65 | 0.25 - 0.4 | - | 200 | 3 | 65 | 0.40 FLA / 4.0 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-013 | E468300 | E | MSP | FMX | IMM32-P63A | 600Y/347 | 3 | 25 | 0.4 - 0.63 | - | 600Y/347 | 3 | 25 | 0.63 FLA / 6.3 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-014 | E468300 | E | MSP | FMX | IMM32-P63A | 480/277 | 3 | 65 | 0.4 - 0.63 | - | 480Y/277 | 3 | 65 | 0.63 FLA / 6.3 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-015 | E468300 | E | MSP | FMX | IMM32-P63A | 240 | 3 | 65 | 0.4 - 0.63 | - | 240 | 3 | 65 | 0.63 FLA / 6.3 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-016 | E468300 | E | MSP | FMX | IMM32-P63A | 200 | 3 | 65 | 0.4 - 0.63 | - | 200 | 3 | 65 | 0.63 FLA / 6.3 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-017 | E468300 | E | MSP | FMX | IMM32-1P0A | 600Y/347 | 3 | 25 | 0.63 - 1 | 1/2 | 600Y/347 | 3 | 25 | 0.9 | 1/2 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-018 | E468300 | E | MSP | FMX | IMM32-1P0A | 480Y/277 | 3 | 65 | 0.63 - 1 | - | 480Y/277 | 3 | 65 | 1.0 FLA / 10.0 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-019 | E468300 | E | MSP | FMX | IMM32-1P0A | 240 | 3 | 65 | 0.63 - 1 | - | 240 | 3 | 65 | 1.0 FLA / 10.0 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-020 | E468300 | E | MSP | FMX | IMM32-1P0A | 200 | 3 | 65 | 0.63 - 1 | - | 200 | 3 | 65 | 1.0 FLA / 10.0 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-021 | E468300 | E | MSP | FMX | IMM32-1P6A | 600Y/347 | 3 | 25 | 1 - 1.6 | 0.75 | 600Y/347 | 3 | 25 | 1.3 | 0.75 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-022 | E468300 | E | MSP | FMX | IMM32-1P6A | 480Y/277 | 3 | 65 | 1 - 1.6 | 3/4 | 480Y/277 | 3 | 65 | 1.6 | 3/4 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-023 | E468300 | E | MSP | FMX | IMM32-1P6A | 240 | 3 | 65 | 1 - 1.6 | - | 240 | 3 | 65 | 1.6 FLA / 16.0 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-024 | E468300 | E | MSP | FMX | IMM32-1P6A | 200 | 3 | 65 | 1 - 1.6 | - | 200 | 3 | 65 | 1.6 FLA / 16.0 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-025 | E468300 | E | MSP | FMX | IMM32-2P5A | 600Y/347 | 3 | 25 | 1.6 - 2.5 | 1-1/2 | 600Y/347 | 3 | 25 | 2.4 | 1-1/2 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-026 | E468300 | E | MSP | FMX | IMM32-2P5A | 480Y/277 | 3 | 65 | 1.6 - 2.5 | 1 | 480Y/277 | 3 | 65 | 2.1 | 1 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-027 | E468300 | E | MSP | FMX | IMM32-2P5A | 240 | 3 | 65 | 1.6 - 2.5 | 1/2 | 240 | 3 | 65 | 2.2 | 1/2 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-028 | E468300 | E | MSP | FMX | IMM32-2P5A | 200 | 3 | 65 | 1.6 - 2.5 | 1/2 | 200 | 3 | 65 | 2.5 | 1/2 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-029 | E468300 | E | MSP | FMX | IMM32-4P0A | 600Y/347 | 3 | 25 | 2.5 - 4 | 3 | 600Y/347 | 3 | 25 | 3.9 | 3 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-030 | E468300 | E | MSP | FMX | IMM32-4P0A | 480Y/277 | 3 | 65 | 2.5 - 4 | 2 | 480Y/277 | 3 | 65 | 3.4 | 2 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-031 | E468300 | E | MSP | FMX | IMM32-4P0A | 240 | 3 | 65 | 2.5 - 4 | 0.75 | 240 | 3 | 65 | 3.2 | 0.75 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-032 | E468300 | E | MSP | FMX | IMM32-4P0A | 200 | 3 | 65 | 2.5 - 4 | 3/4 | 200 | 3 | 65 | 3.7 | 3/4 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-033 | E468300 | E | MSP | FMX | IMM32-6P3A | 600Y/347 | 3 | 25 | 4 - 6.3 | 5 | 600Y/347 | 3 | 25 | 6.1 | 5 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-034 | E468300 | E | MSP | FMX | IMM32-6P3A | 480Y/277 | 3 | 65 | 4 - 6.3 | 3 | 480Y/277 | 3 | 65 | 4.8 | 3 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-035 | E468300 | E | MSP | FMX | IMM32-6P3A | 240 | 3 | 65 | 4 - 6.3 | 1-1/2 | 240 | 3 | 65 | 6 | 1-1/2 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-036 | E468300 | E | MSP | FMX | IMM32-6P3A | 200 | 3 | 65 | 4 - 6.3 | 1 | 200 | 3 | 65 | 4.8 | 1 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-037 | E468300 | E | MSP | FMX | IMM32-010A | 600Y/347 | 3 | 25 | 6.3 - 10 | 7-1/2 | 600Y/347 | 3 | 25 | 9 | 7-1/2 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-12S | 600 | 3 | 5 | 11 | 10
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-038 | E468300 | E | MSP | FMX | IMM32-010A | 480Y/277 | 3 | 65 | 6.3 - 10 | 5 | 480Y/277 | 3 | 65 | 7.6 | 5 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-12S | 480 | 3 | 5 | 11 | 7-1/2
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-039 | E468300 | E | MSP | FMX | IMM32-010A | 240 | 3 | 65 | 6.3 - 10 | 3 | 240 | 3 | 65 | 9.6 | 3 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-12S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-040 | E468300 | E | MSP | FMX | IMM32-010A | 200 | 3 | 65 | 6.3 - 10 | 2 | 200 | 3 | 65 | 7.8 | 2 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-12S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-041 | E468300 | E | MSP | FMX | IMM32-016A | 600Y/347 | 3 | 25 | 10 - 16 | 10 | 600Y/347 | 3 | 25 | 11 | 10 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-18S | 600 | 3 | 5 | 17 | 15
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-042 | E468300 | E | MSP | FMX | IMM32-016A | 480Y/277 | 3 | 65 | 10 - 16 | 10 | 480Y/277 | 3 | 65 | 14 | 10 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-18S | 480 | 3 | 5 | 14 | 10
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-043 | E468300 | E | MSP | FMX | IMM32-016A | 240 | 3 | 65 | 10 - 16 | 5 | 240 | 3 | 65 | 15.2 | 5 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-18S | 240 | 3 | 5 | 15.2 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-044 | E468300 | E | MSP | FMX | IMM32-016A | 200 | 3 | 65 | 10 - 16 | 3 | 200 | 3 | 65 | 11 | 3 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-18S | 200 | 3 | 5 | 17.5 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-045 | E468300 | E | MSP | FMX | IMM32-020A | 600Y/347 | 3 | 25 | 16 - 20 | 15 | 600Y/347 | 3 | 25 | 17 | 15 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-25S | 600 | 3 | 5 | 17 | 15
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-046 | E468300 | E | MSP | FMX | IMM32-020A | 200 | 3 | 50 | 16 - 20 | 5 | 200 | 3 | 50 | 17.5 | 5 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-25S | 200 | 3 | 5 | 25.3 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-047 | E468300 | E | MSP | FMX | IMM32-025A | 600Y/347 | 3 | 25 | 20 - 25 | 20 | 600Y/347 | 3 | 25 | 22 | 20 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-32S | 600 | 3 | 5 | 27 | 25
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-048 | E468300 | E | MSP | FMX | IMM32-025A | 480Y/277 | 3 | 50 | 20 - 25 | 15 | 480Y/277 | 3 | 50 | 21 | 15 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-32S | 480 | 3 | 5 | 27 | 20
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-049 | E468300 | E | MSP | FMX | IMM32-025A | 240 | 3 | 50 | 20 - 25 | 7.5 | 240 | 3 | 50 | 22 | 7.5 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-32S | 240 | 3 | 5 | 28 | 10
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-050 | E468300 | E | MSP | FMX | IMM32-025A | 200 | 3 | 50 | 20 - 25 | 7.5 | 200 | 3 | 50 | 25 | 7.5 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-32S | 200 | 3 | 5 | 32.2 | 10
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-051 | E468300 | E | MSP | FMX | IMM32-P16A | 600Y/347 | 3 | 50 | 0.1 - 0.16 | - | 600Y/347 | 3 | 50 | 0.16 FLA / 1.6 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-052 | E468300 | E | MSP | FMX | IMM32-P16A | 480Y/277 | 3 | 100 | 0.1 - 0.16 | - | 480Y/277 | 3 | 100 | 0.16 FLA / 1.6 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-053 | E468300 | E | MSP | FMX | IMM32-P16A | 240 | 3 | 100 | 0.1 - 0.16 | - | 240 | 3 | 100 | 0.16 FLA / 1.6 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-054 | E468300 | E | MSP | FMX | IMM32-P16A | 200 | 3 | 100 | 0.1 - 0.16 | - | 200 | 3 | 100 | 0.16 FLA / 1.6 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-055 | E468300 | E | MSP | FMX | IMM32-P25A | 600Y/347 | 3 | 50 | 0.16 - 0.25 | - | 600Y/347 | 3 | 50 | 0.25 FLA / 2.5 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-056 | E468300 | E | MSP | FMX | IMM32-P25A | 480Y/277 | 3 | 100 | 0.16 - 0.25 | - | 480Y/277 | 3 | 100 | 0.25 FLA / 2.5 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-057 | E468300 | E | MSP | FMX | IMM32-P25A | 240 | 3 | 100 | 0.16 - 0.25 | - | 240 | 3 | 100 | 0.25 FLA / 2.5 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-058 | E468300 | E | MSP | FMX | IMM32-P25A | 200 | 3 | 100 | 0.16 - 0.25 | - | 200 | 3 | 100 | 0.25 FLA / 2.5 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-059 | E468300 | E | MSP | FMX | IMM32-P40A | 600Y/347 | 3 | 50 | 0.25 - 0.4 | - | 600Y/347 | 3 | 50 | 0.40 FLA / 4.0 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-060 | E468300 | E | MSP | FMX | IMM32-P40A | 480Y/277 | 3 | 100 | 0.25 - 0.4 | - | 480Y/277 | 3 | 100 | 0.40 FLA / 4.0 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-061 | E468300 | E | MSP | FMX | IMM32-P40A | 240 | 3 | 100 | 0.25 - 0.4 | - | 240 | 3 | 100 | 0.40 FLA / 4.0 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-062 | E468300 | E | MSP | FMX | IMM32-P40A | 200 | 3 | 100 | 0.25 - 0.4 | - | 200 | 3 | 100 | 0.40 FLA / 4.0 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-063 | E468300 | E | MSP | FMX | IMM32-P63A | 600Y/347 | 3 | 50 | 0.4 - 0.63 | - | 600Y/347 | 3 | 50 | 0.63 FLA / 6.3 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-064 | E468300 | E | MSP | FMX | IMM32-P63A | 480Y/277 | 3 | 100 | 0.4 - 0.63 | - | 480Y/277 | 3 | 100 | 0.63 FLA / 6.3 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-065 | E468300 | E | MSP | FMX | IMM32-P63A | 240 | 3 | 100 | 0.4 - 0.63 | - | 240 | 3 | 100 | 0.63 FLA / 6.3 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-066 | E468300 | E | MSP | FMX | IMM32-P63A | 200 | 3 | 100 | 0.4 - 0.63 | - | 200 | 3 | 100 | 0.63 FLA / 6.3 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-067 | E468300 | E | MSP | FMX | IMM32-1P0A | 600Y/347 | 3 | 50 | 0.63 - 1 | 1/2 | 600Y/347 | 3 | 50 | 0.9 | 1/2 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-068 | E468300 | E | MSP | FMX | IMM32-1P0A | 480Y/277 | 3 | 100 | 0.63 - 1 | - | 480Y/277 | 3 | 100 | 1.0 FLA / 10.0 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-069 | E468300 | E | MSP | FMX | IMM32-1P0A | 240 | 3 | 100 | 0.63 - 1 | - | 240 | 3 | 100 | 1.0 FLA / 10.0 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-070 | E468300 | E | MSP | FMX | IMM32-1P0A | 200 | 3 | 100 | 0.63 - 1 | - | 200 | 3 | 100 | 1.0 FLA / 10.0 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-071 | E468300 | E | MSP | FMX | IMM32-1P6A | 600Y/347 | 3 | 50 | 1 - 1.6 | 0.75 | 600Y/347 | 3 | 50 | 1.3 | 0.75 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-072 | E468300 | E | MSP | FMX | IMM32-1P6A | 480Y/277 | 3 | 100 | 1 - 1.6 | 3/4 | 480Y/277 | 3 | 100 | 1.6 | 3/4 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-073 | E468300 | E | MSP | FMX | IMM32-1P6A | 240 | 3 | 100 | 1 - 1.6 | - | 240 | 3 | 100 | 1.6 FLA / 16.0 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-074 | E468300 | E | MSP | FMX | IMM32-1P6A | 200 | 3 | 100 | 1 - 1.6 | - | 200 | 3 | 100 | 1.6 FLA / 16.0 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-075 | E468300 | E | MSP | FMX | IMM32-2P5A | 600Y/347 | 3 | 50 | 1.6 - 2.5 | 1-1/2 | 600Y/347 | 3 | 50 | 2.4 | 1-1/2 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-076 | E468300 | E | MSP | FMX | IMM32-2P5A | 480Y/277 | 3 | 100 | 1.6 - 2.5 | 1 | 480Y/277 | 3 | 100 | 2.1 | 1 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-077 | E468300 | E | MSP | FMX | IMM32-2P5A | 240 | 3 | 100 | 1.6 - 2.5 | 1/2 | 240 | 3 | 100 | 2.2 | 1/2 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-078 | E468300 | E | MSP | FMX | IMM32-2P5A | 200 | 3 | 100 | 1.6 - 2.5 | 1/2 | 200 | 3 | 100 | 2.5 | 1/2 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-079 | E468300 | E | MSP | FMX | IMM32-4P0A | 600Y/347 | 3 | 50 | 2.5 - 4 | 3 | 600Y/347 | 3 | 50 | 3.9 | 3 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-080 | E468300 | E | MSP | FMX | IMM32-4P0A | 480Y/277 | 3 | 100 | 2.5 - 4 | 2 | 480Y/277 | 3 | 100 | 3.4 | 2 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-081 | E468300 | E | MSP | FMX | IMM32-4P0A | 240 | 3 | 100 | 2.5 - 4 | 0.75 | 240 | 3 | 100 | 3.2 | 0.75 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-082 | E468300 | E | MSP | FMX | IMM32-4P0A | 200 | 3 | 100 | 2.5 - 4 | 3/4 | 200 | 3 | 100 | 3.7 | 3/4 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-083 | E468300 | E | MSP | FMX | IMM32-6P3A | 600Y/347 | 3 | 50 | 4 - 6.3 | 5 | 600Y/347 | 3 | 50 | 6.1 | 5 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-084 | E468300 | E | MSP | FMX | IMM32-6P3A | 480Y/277 | 3 | 100 | 4 - 6.3 | 3 | 480Y/277 | 3 | 100 | 4.8 | 3 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-085 | E468300 | E | MSP | FMX | IMM32-6P3A | 240 | 3 | 100 | 4 - 6.3 | 1-1/2 | 240 | 3 | 100 | 6 | 1-1/2 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-086 | E468300 | E | MSP | FMX | IMM32-6P3A | 200 | 3 | 100 | 4 - 6.3 | 1 | 200 | 3 | 100 | 4.8 | 1 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-087 | E468300 | E | MSP | FMX | IMM32-010A | 600Y/347 | 3 | 50 | 6.3 - 10 | 7-1/2 | 600Y/347 | 3 | 50 | 9 | 7-1/2 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-088 | E468300 | E | MSP | FMX | IMM32-010A | 480Y/277 | 3 | 100 | 6.3 - 10 | 5 | 480Y/277 | 3 | 100 | 7.6 | 5 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-089 | E468300 | E | MSP | FMX | IMM32-010A | 240 | 3 | 100 | 6.3 - 10 | 3 | 240 | 3 | 100 | 9.6 | 3 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-090 | E468300 | E | MSP | FMX | IMM32-010A | 200 | 3 | 100 | 6.3 - 10 | 2 | 200 | 3 | 100 | 7.8 | 2 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-091 | E468300 | E | MSP | FMX | IMM32-016A | 600Y/347 | 3 | 50 | 10 - 16 | 10 | 600Y/347 | 3 | 50 | 11 | 10 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-18S | 600 | 3 | 5 | 17 | 15
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-092 | E468300 | E | MSP | FMX | IMM32-016A | 480Y/277 | 3 | 100 | 10 - 16 | 10 | 480Y/277 | 3 | 100 | 14 | 10 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-18S | 480 | 3 | 5 | 14 | 10
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-093 | E468300 | E | MSP | FMX | IMM32-016A | 240 | 3 | 100 | 10 - 16 | 5 | 240 | 3 | 100 | 15.2 | 5 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-18S | 240 | 3 | 5 | 15.2 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-094 | E468300 | E | MSP | FMX | IMM32-016A | 200 | 3 | 100 | 10 - 16 | 3 | 200 | 3 | 100 | 11 | 3 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-18S | 200 | 3 | 5 | 17.5 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-095 | E468300 | E | MSP | FMX | IMM32-020A | 600Y/347 | 3 | 50 | 16 - 20 | 15 | 600Y/347 | 3 | 50 | 17 | 15 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-25S | 600 | 3 | 5 | 17 | 15
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-096 | E468300 | E | MSP | FMX | IMM32-020A | 200 | 3 | 100 | 16 - 20 | 5 | 200 | 3 | 100 | 17.5 | 5 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-25S | 200 | 3 | 5 | 25.3 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-097 | E468300 | E | MSP | FMX | IMM32-025A | 600Y/347 | 3 | 50 | 20 - 25 | 20 | 600Y/347 | 3 | 50 | 22 | 20 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-32S | 600 | 3 | 5 | 27 | 25
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-098 | E468300 | E | MSP | FMX | IMM32-025A | 480Y/277 | 3 | 100 | 20 - 25 | 15 | 480Y/277 | 3 | 100 | 21 | 15 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-32S | 480 | 3 | 5 | 27 | 20
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-099 | E468300 | E | MSP | FMX | IMM32-025A | 240 | 3 | 100 | 20 - 25 | 7-1/2 | 240 | 3 | 100 | 22 | 7-1/2 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-32S | 240 | 3 | 5 | 28 | 10
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
E32-100 | E468300 | E | MSP | FMX | IMM32-025A | 200 | 3 | 100 | 20 - 25 | 7-1/2 | 200 | 3 | 100 | 25 | 7-1/2 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM-32F
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-32S | 200 | 3 | 5 | 32.2 | 10
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
CofA:
|  | 1 | All of the specified individual components of the combination motor controller have been installed in an enclosure having a specified internal volume in cubic feet. Additional testing in the combination motor controller is not required when installed in an enclosure having the same or larger volume.
|  | 5 | The need for cautionary markings applicable to high-fault short-circuit current ratings; Type D and Type E combination motor controllers shall be considered in the end-product application.
|  | 6 | Device may be used at indicated currents, but overload tripping may occur if used continually above the overload FLA rating.
Note on P539: Fuoco, James: Given combination at 480, 1 HP, this FLA (2.1 A) is correct, per UL508 Table 45.2

## Type F Combinations
Issued: 2020-12-23
Database Identification Number | [B2] Listed Combination Motor Controller Information | Construction Type | Component Description | [7 empty] | Combination Motor Controller Ratings |  |  |  |  | Enclosure Volume, cubic inches | Conditions of Use
Listing Report Information
| UL File Number |  | Component Type Abbreviation | Manufacturer Name | Complete Part Number | Voltage, V | Number of Phases | SCCR, kA | Full Load Current, A | Hp Rating | Voltage, V | Number of Phases | SCCR, kA | Current Rating. FLA or FLA/LRA | Hp Rating
F32-001 | E468300 | F | MSP | FMX | IMM32-P16A | 600Y/347 | 3 | 25 | 0.1 - 0.16 | - | 600Y/347 | 3 | 25 | 0.16 FLA / 1.6 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-002 | E468300 | F | MSP | FMX | IMM32-P16A | 480Y/277 | 3 | 65 | 0.1 - 0.16 | - | 480Y/277 | 3 | 65 | 0.16 FLA / 1.6 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-003 | E468300 | F | MSP | FMX | IMM32-P16A | 240 | 3 | 65 | 0.1 - 0.16 | - | 240 | 3 | 65 | 0.16 FLA / 1.6 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-004 | E468300 | F | MSP | FMX | IMM32-P16A | 200 | 3 | 65 | 0.1 - 0.16 | - | 200 | 3 | 65 | 0.16 FLA / 1.6 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-005 | E468300 | F | MSP | FMX | IMM32-P25A | 600Y/347 | 3 | 25 | 0.16 - 0.25 | - | 600Y/347 | 3 | 25 | 0.25 FLA / 2.5 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-006 | E468300 | F | MSP | FMX | IMM32-P25A | 480Y/277 | 3 | 65 | 0.16 - 0.25 | - | 480Y/277 | 3 | 65 | 0.25 FLA / 2.5 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-007 | E468300 | F | MSP | FMX | IMM32-P25A | 240 | 3 | 65 | 0.16 - 0.25 | - | 240 | 3 | 65 | 0.25 FLA / 2.5 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-008 | E468300 | F | MSP | FMX | IMM32-P25A | 200 | 3 | 65 | 0.16 - 0.25 | - | 200 | 3 | 65 | 0.25 FLA / 2.5 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-009 | E468300 | F | MSP | FMX | IMM32-P40A | 600Y/347 | 3 | 25 | 0.25 - 0.4 | - | 600Y/347 | 3 | 25 | 0.40 FLA / 4.0 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-010 | E468300 | F | MSP | FMX | IMM32-P40A | 480Y/277 | 3 | 65 | 0.25 - 0.4 | - | 480Y/277 | 3 | 65 | 0.40 FLA / 4.0 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-011 | E468300 | F | MSP | FMX | IMM32-P40A | 240 | 3 | 50 | 0.25 - 0.4 | - | 240 | 3 | 65 | 0.40 FLA / 4.0 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-012 | E468300 | F | MSP | FMX | IMM32-P40A | 200 | 3 | 50 | 0.25 - 0.4 | - | 200 | 3 | 65 | 0.40 FLA / 4.0 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-013 | E468300 | F | MSP | FMX | IMM32-P63A | 600Y/347 | 3 | 25 | 0.4 - 0.63 | - | 600Y/347 | 3 | 25 | 0.63 FLA / 6.3 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-014 | E468300 | F | MSP | FMX | IMM32-P63A | 480/277 | 3 | 65 | 0.4 - 0.63 | - | 480Y/277 | 3 | 65 | 0.63 FLA / 6.3 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-015 | E468300 | F | MSP | FMX | IMM32-P63A | 240 | 3 | 65 | 0.4 - 0.63 | - | 240 | 3 | 65 | 0.63 FLA / 6.3 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-016 | E468300 | F | MSP | FMX | IMM32-P63A | 200 | 3 | 65 | 0.4 - 0.63 | - | 200 | 3 | 65 | 0.63 FLA / 6.3 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-017 | E468300 | F | MSP | FMX | IMM32-1P0A | 600Y/347 | 3 | 25 | 0.63 - 1 | 1/2 | 600Y/347 | 3 | 25 | 0.9 | 1/2 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-018 | E468300 | F | MSP | FMX | IMM32-1P0A | 480Y/277 | 3 | 65 | 0.63 - 1 | - | 480Y/277 | 3 | 65 | 1.0 FLA / 10.0 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-019 | E468300 | F | MSP | FMX | IMM32-1P0A | 240 | 3 | 65 | 0.63 - 1 | - | 240 | 3 | 65 | 1.0 FLA / 10.0 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-020 | E468300 | F | MSP | FMX | IMM32-1P0A | 200 | 3 | 65 | 0.63 - 1 | - | 200 | 3 | 65 | 1.0 FLA / 10.0 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-021 | E468300 | F | MSP | FMX | IMM32-1P6A | 600Y/347 | 3 | 25 | 1 - 1.6 | 0.75 | 600Y/347 | 3 | 25 | 1.3 | 0.75 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-022 | E468300 | F | MSP | FMX | IMM32-1P6A | 480Y/277 | 3 | 65 | 1 - 1.6 | 3/4 | 480Y/277 | 3 | 65 | 1.6 | 3/4 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-023 | E468300 | F | MSP | FMX | IMM32-1P6A | 240 | 3 | 65 | 1 - 1.6 | - | 240 | 3 | 65 | 1.6 FLA / 16.0 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-024 | E468300 | F | MSP | FMX | IMM32-1P6A | 200 | 3 | 65 | 1 - 1.6 | - | 200 | 3 | 65 | 1.6 FLA / 16.0 LRA | - | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-025 | E468300 | F | MSP | FMX | IMM32-2P5A | 600Y/347 | 3 | 25 | 1.6 - 2.5 | 1-1/2 | 600Y/347 | 3 | 25 | 2.4 | 1-1/2 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-026 | E468300 | F | MSP | FMX | IMM32-2P5A | 480Y/277 | 3 | 65 | 1.6 - 2.5 | 1 | 480Y/277 | 3 | 65 | 2.1 | 1 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-027 | E468300 | F | MSP | FMX | IMM32-2P5A | 240 | 3 | 65 | 1.6 - 2.5 | 1/2 | 240 | 3 | 65 | 2.2 | 1/2 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-028 | E468300 | F | MSP | FMX | IMM32-2P5A | 200 | 3 | 65 | 1.6 - 2.5 | 1/2 | 200 | 3 | 65 | 2.5 | 1/2 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-029 | E468300 | F | MSP | FMX | IMM32-4P0A | 600Y/347 | 3 | 25 | 2.4 - 4 | 3 | 600Y/347 | 3 | 25 | 3.9 | 3 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-030 | E468300 | F | MSP | FMX | IMM32-4P0A | 480Y/277 | 3 | 65 | 2.4 - 4 | 2 | 480Y/277 | 3 | 65 | 3.4 | 2 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-031 | E468300 | F | MSP | FMX | IMM32-4P0A | 240 | 3 | 65 | 2.4 - 4 | 0.75 | 240 | 3 | 65 | 3.2 | 0.75 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-032 | E468300 | F | MSP | FMX | IMM32-4P0A | 200 | 3 | 65 | 2.4 - 4 | 3/4 | 200 | 3 | 65 | 3.7 | 3/4 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-033 | E468300 | F | MSP | FMX | IMM32-6P3A | 600Y/347 | 3 | 25 | 4 - 6.3 | 5 | 600Y/347 | 3 | 25 | 6.1 | 5 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-034 | E468300 | F | MSP | FMX | IMM32-6P3A | 480Y/277 | 3 | 65 | 4 - 6.3 | 3 | 480Y/277 | 3 | 65 | 4.8 | 3 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-035 | E468300 | F | MSP | FMX | IMM32-6P3A | 240 | 3 | 65 | 4 - 6.3 | 1-1/2 | 240 | 3 | 65 | 6 | 1-1/2 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-036 | E468300 | F | MSP | FMX | IMM32-6P3A | 200 | 3 | 65 | 4 - 6.3 | 1 | 200 | 3 | 65 | 4.8 | 1 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-037 | E468300 | F | MSP | FMX | IMM32-010A | 600Y/347 | 3 | 25 | 6.3 - 10 | 7-1/2 | 600Y/347 | 3 | 25 | 9 | 7-1/2 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-18S | 600 | 3 | 5 | 11 | 10
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-038 | E468300 | F | MSP | FMX | IMM32-010A | 480Y/277 | 3 | 50 | 6.3 - 10 | 5 | 480Y/277 | 3 | 65 | 7.6 | 5 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-18S | 480 | 3 | 5 | 11 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-039 | E468300 | F | MSP | FMX | IMM32-010A | 240 | 3 | 65 | 6.3 - 10 | 3 | 240 | 3 | 65 | 9.6 | 3 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-18S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-040 | E468300 | F | MSP | FMX | IMM32-010A | 200 | 3 | 65 | 6.3 - 10 | 2 | 200 | 3 | 65 | 7.8 | 2 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-18S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-041 | E468300 | F | MSP | FMX | IMM32-016A | 600Y/347 | 3 | 25 | 10 - 16 | 10 | 600Y/347 | 3 | 25 | 11 | 10 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-18S | 600 | 3 | 5 | 17 | 15
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-042 | E468300 | F | MSP | FMX | IMM32-016A | 480Y/277 | 3 | 65 | 10 - 16 | 10 | 480Y/277 | 3 | 65 | 14 | 10 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-18S | 480 | 3 | 5 | 14 | 10
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-043 | E468300 | F | MSP | FMX | IMM32-016A | 240 | 3 | 65 | 10 - 16 | 5 | 240 | 3 | 65 | 15.2 | 5 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-18S | 240 | 3 | 5 | 15.2 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-044 | E468300 | F | MSP | FMX | IMM32-016A | 200 | 3 | 65 | 10 - 16 | 3 | 200 | 3 | 65 | 11 | 3 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-18S | 200 | 3 | 5 | 17.5 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-045 | E468300 | F | MSP | FMX | IMM32-020A | 600Y/347 | 3 | 25 | 16 - 20 | 15 | 600Y/347 | 3 | 25 | 17 | 15 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-25S | 600 | 3 | 5 | 17 | 15
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-046 | E468300 | F | MSP | FMX | IMM32-020A | 200 | 3 | 50 | 16 - 20 | 5 | 200 | 3 | 50 | 17.5 | 5 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-25S | 200 | 3 | 5 | 25.3 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-047 | E468300 | F | MSP | FMX | IMM32-025A | 600Y/347 | 3 | 25 | 20 - 25 | 20 | 600Y/347 | 3 | 25 | 22 | 20 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-32S | 600 | 3 | 5 | 27 | 25
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-048 | E468300 | F | MSP | FMX | IMM32-025A | 480Y/277 | 3 | 50 | 20 - 25 | 15 | 480Y/277 | 3 | 50 | 21 | 15 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-32S | 480 | 3 | 5 | 27 | 20
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-049 | E468300 | F | MSP | FMX | IMM32-025A | 240 | 3 | 50 | 20 - 25 | 7.5 | 240 | 3 | 50 | 22 | 7.5 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-32S | 240 | 3 | 5 | 28 | 10
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-050 | E468300 | F | MSP | FMX | IMM32-025A | 200 | 3 | 50 | 20 - 25 | 7.5 | 200 | 3 | 50 | 25 | 7.5 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-32S | 200 | 3 | 5 | 32.2 | 10
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-051 | E468300 | F | MSP | FMX | IMM32-032A | 600Y/347 | 3 | 25 | 25 - 32 | 25 | 600Y/347 | 3 | 25 | 27 | 25 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-40S | 600 | 3 | 5 | 27 | 25
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-052 | E468300 | F | MSP | FMX | IMM32-032A | 480Y/277 | 3 | 50 | 25 - 32 | 20 | 480Y/277 | 3 | 50 | 27 | 20 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-40S | 480 | 3 | 5 | 40 | 30
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-053 | E468300 | F | MSP | FMX | IMM32-032A | 240 | 3 | 50 | 25 - 32 | 10 | 240 | 3 | 50 | 28 | 10 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-40S | 240 | 3 | 5 | 42 | 15
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-054 | E468300 | F | MSP | FMX | IMM32-032A | 200 | 3 | 50 | 25 - 32 | 10 | 200 | 3 | 50 | 32.2 | 10 | 262.5734 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-40S | 200 | 3 | 5 | 32.2 | 10
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-055 | E468300 | F | MSP | FMX | IMM32-P16A | 600Y/347 | 3 | 50 | 0.1 - 0.16 | - | 600Y/347 | 3 | 50 | 0.16 FLA / 1.6 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-056 | E468300 | F | MSP | FMX | IMM32-P16A | 480Y/277 | 3 | 100 | 0.1 - 0.16 | - | 480Y/277 | 3 | 100 | 0.16 FLA / 1.6 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-057 | E468300 | F | MSP | FMX | IMM32-P16A | 240 | 3 | 100 | 0.1 - 0.16 | - | 240 | 3 | 100 | 0.16 FLA / 1.6 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-058 | E468300 | F | MSP | FMX | IMM32-P16A | 200 | 3 | 100 | 0.1 - 0.16 | - | 200 | 3 | 100 | 0.16 FLA / 1.6 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-059 | E468300 | F | MSP | FMX | IMM32-P25A | 600Y/347 | 3 | 50 | 0.16 - 0.25 | - | 600Y/347 | 3 | 50 | 0.25 FLA / 2.5 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-060 | E468300 | F | MSP | FMX | IMM32-P25A | 480Y/277 | 3 | 100 | 0.16 - 0.25 | - | 480Y/277 | 3 | 100 | 0.25 FLA / 2.5 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-061 | E468300 | F | MSP | FMX | IMM32-P25A | 240 | 3 | 100 | 0.16 - 0.25 | - | 240 | 3 | 100 | 0.25 FLA / 2.5 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-062 | E468300 | F | MSP | FMX | IMM32-P25A | 200 | 3 | 100 | 0.16 - 0.25 | - | 200 | 3 | 100 | 0.25 FLA / 2.5 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-063 | E468300 | F | MSP | FMX | IMM32-P40A | 600Y/347 | 3 | 50 | 0.25 - 0.4 | - | 600Y/347 | 3 | 50 | 0.40 FLA / 4.0 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-064 | E468300 | F | MSP | FMX | IMM32-P40A | 480Y/277 | 3 | 100 | 0.25 - 0.4 | - | 480Y/277 | 3 | 100 | 0.40 FLA / 4.0 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-065 | E468300 | F | MSP | FMX | IMM32-P40A | 240 | 3 | 100 | 0.25 - 0.4 | - | 240 | 3 | 100 | 0.40 FLA / 4.0 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-066 | E468300 | F | MSP | FMX | IMM32-P40A | 200 | 3 | 100 | 0.25 - 0.4 | - | 200 | 3 | 100 | 0.40 FLA / 4.0 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-067 | E468300 | F | MSP | FMX | IMM32-P63A | 600Y/347 | 3 | 50 | 0.4 - 0.63 | - | 600Y/347 | 3 | 50 | 0.63 FLA / 6.3 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-068 | E468300 | F | MSP | FMX | IMM32-P63A | 480Y/277 | 3 | 100 | 0.4 - 0.63 | - | 480Y/277 | 3 | 100 | 0.63 FLA / 6.3 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-069 | E468300 | F | MSP | FMX | IMM32-P63A | 240 | 3 | 100 | 0.4 - 0.63 | - | 240 | 3 | 100 | 0.63 FLA / 6.3 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-070 | E468300 | F | MSP | FMX | IMM32-P63A | 200 | 3 | 100 | 0.4 - 0.63 | - | 200 | 3 | 100 | 0.63 FLA / 6.3 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-071 | E468300 | F | MSP | FMX | IMM32-1P0A | 600Y/347 | 3 | 50 | 0.63 - 1 | 1/2 | 600Y/347 | 3 | 50 | 0.9 | 1/2 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-072 | E468300 | F | MSP | FMX | IMM32-1P0A | 480Y/277 | 3 | 100 | 0.63 - 1 | - | 480Y/277 | 3 | 100 | 1.0 FLA / 10.0 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-073 | E468300 | F | MSP | FMX | IMM32-1P0A | 240 | 3 | 100 | 0.63 - 1 | - | 240 | 3 | 100 | 1.0 FLA / 10.0 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-074 | E468300 | F | MSP | FMX | IMM32-1P0A | 200 | 3 | 100 | 0.63 - 1 | - | 200 | 3 | 100 | 1.0 FLA / 10.0 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-075 | E468300 | F | MSP | FMX | IMM32-1P6A | 600Y/347 | 3 | 50 | 1 - 1.6 | 0.75 | 600Y/347 | 3 | 50 | 1.3 | 0.75 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-076 | E468300 | F | MSP | FMX | IMM32-1P6A | 480Y/277 | 3 | 100 | 1 - 1.6 | 3/4 | 480Y/277 | 3 | 100 | 1.6 | 3/4 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-077 | E468300 | F | MSP | FMX | IMM32-1P6A | 240 | 3 | 100 | 1 - 1.6 | - | 240 | 3 | 100 | 1.6 FLA / 16.0 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-078 | E468300 | F | MSP | FMX | IMM32-1P6A | 200 | 3 | 100 | 1 - 1.6 | - | 200 | 3 | 100 | 1.6 FLA / 16.0 LRA | - | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-079 | E468300 | F | MSP | FMX | IMM32-2P5A | 600Y/347 | 3 | 50 | 1.6 - 2.5 | 1-1/2 | 600Y/347 | 3 | 50 | 2.4 | 1-1/2 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-080 | E468300 | F | MSP | FMX | IMM32-2P5A | 480Y/277 | 3 | 100 | 1.6 - 2.5 | 1 | 480Y/277 | 3 | 100 | 2.1 | 1 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-081 | E468300 | F | MSP | FMX | IMM32-2P5A | 240 | 3 | 100 | 1.6 - 2.5 | 1/2 | 240 | 3 | 100 | 2.2 | 1/2 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-082 | E468300 | F | MSP | FMX | IMM32-2P5A | 200 | 3 | 100 | 1.6 - 2.5 | 1/2 | 200 | 3 | 100 | 2.5 | 1/2 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-083 | E468300 | F | MSP | FMX | IMM32-4P0A | 600Y/347 | 3 | 50 | 2.4 - 4 | 3 | 600Y/347 | 3 | 50 | 3.9 | 3 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-084 | E468300 | F | MSP | FMX | IMM32-4P0A | 480Y/277 | 3 | 100 | 2.4 - 4 | 2 | 480Y/277 | 3 | 100 | 3.4 | 2 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-085 | E468300 | F | MSP | FMX | IMM32-4P0A | 240 | 3 | 100 | 2.4 - 4 | 0.75 | 240 | 3 | 100 | 3.2 | 0.75 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-086 | E468300 | F | MSP | FMX | IMM32-4P0A | 200 | 3 | 100 | 2.4 - 4 | 3/4 | 200 | 3 | 100 | 3.7 | 3/4 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-087 | E468300 | F | MSP | FMX | IMM32-6P3A | 600Y/347 | 3 | 50 | 4 - 6.3 | 5 | 600Y/347 | 3 | 50 | 6.1 | 5 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-088 | E468300 | F | MSP | FMX | IMM32-6P3A | 480Y/277 | 3 | 100 | 4 - 6.3 | 3 | 480Y/277 | 3 | 100 | 4.8 | 3 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-089 | E468300 | F | MSP | FMX | IMM32-6P3A | 240 | 3 | 100 | 4 - 6.3 | 1-1/2 | 240 | 3 | 100 | 6 | 1-1/2 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-090 | E468300 | F | MSP | FMX | IMM32-6P3A | 200 | 3 | 100 | 4 - 6.3 | 1 | 200 | 3 | 100 | 4.8 | 1 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-091 | E468300 | F | MSP | FMX | IMM32-010A | 600Y/347 | 3 | 50 | 6.3 - 10 | 7-1/2 | 600Y/347 | 3 | 50 | 9 | 7-1/2 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 600 | 3 | 5 | 9 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-092 | E468300 | F | MSP | FMX | IMM32-010A | 480Y/277 | 3 | 100 | 6.3 - 10 | 5 | 480Y/277 | 3 | 100 | 7.6 | 5 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 480 | 3 | 5 | 7.6 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-093 | E468300 | F | MSP | FMX | IMM32-010A | 240 | 3 | 100 | 6.3 - 10 | 3 | 240 | 3 | 100 | 9.6 | 3 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 240 | 3 | 5 | 9.6 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-094 | E468300 | F | MSP | FMX | IMM32-010A | 200 | 3 | 100 | 6.3 - 10 | 2 | 200 | 3 | 100 | 7.8 | 2 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-09S | 200 | 3 | 5 | 11 | 3
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-095 | E468300 | F | MSP | FMX | IMM32-016A | 600Y/347 | 3 | 50 | 10 - 16 | 10 | 600Y/347 | 3 | 50 | 11 | 10 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-18S | 600 | 3 | 5 | 17 | 15
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-096 | E468300 | F | MSP | FMX | IMM32-016A | 480Y/277 | 3 | 100 | 10 - 16 | 10 | 480Y/277 | 3 | 100 | 14 | 10 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-18S | 480 | 3 | 5 | 14 | 10
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-097 | E468300 | F | MSP | FMX | IMM32-016A | 240 | 3 | 100 | 10 - 16 | 5 | 240 | 3 | 100 | 15.2 | 5 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-18S | 240 | 3 | 5 | 15.2 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-098 | E468300 | F | MSP | FMX | IMM32-016A | 200 | 3 | 100 | 10 - 16 | 3 | 200 | 3 | 100 | 11 | 3 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-18S | 200 | 3 | 5 | 17.5 | 5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-099 | E468300 | F | MSP | FMX | IMM32-020A | 600Y/347 | 3 | 50 | 16 - 20 | 15 | 600Y/347 | 3 | 50 | 17 | 15 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-25S | 600 | 3 | 5 | 17 | 15
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-100 | E468300 | F | MSP | FMX | IMM32-020A | 200 | 3 | 100 | 16 - 20 | 5 | 200 | 3 | 100 | 17.5 | 5 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-25S | 200 | 3 | 5 | 25.3 | 7.5
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-101 | E468300 | F | MSP | FMX | IMM32-025A | 600Y/347 | 3 | 50 | 20 - 25 | 20 | 600Y/347 | 3 | 50 | 22 | 20 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-32S | 600 | 3 | 5 | 27 | 25
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-102 | E468300 | F | MSP | FMX | IMM32-025A | 480Y/277 | 3 | 100 | 20 - 25 | 15 | 480Y/277 | 3 | 100 | 21 | 15 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-32S | 480 | 3 | 5 | 27 | 20
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-103 | E468300 | F | MSP | FMX | IMM32-025A | 240 | 3 | 100 | 20 - 25 | 7-1/2 | 240 | 3 | 100 | 22 | 7-1/2 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-32S | 240 | 3 | 5 | 28 | 10
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-104 | E468300 | F | MSP | FMX | IMM32-025A | 200 | 3 | 100 | 20 - 25 | 7-1/2 | 200 | 3 | 100 | 25 | 7-1/2 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-32S | 200 | 3 | 5 | 32.2 | 10
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-105 | E468300 | F | MSP | FMX | IMM32-032A | 600Y/347 | 3 | 50 | 25 - 32 | 25 | 600Y/347 | 3 | 50 | 27 | 25 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-40S | 600 | 3 | 5 | 27 | 25
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-106 | E468300 | F | MSP | FMX | IMM32-032A | 480Y/277 | 3 | 100 | 25 - 32 | 20 | 480Y/277 | 3 | 100 | 27 | 20 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-40S | 480 | 3 | 5 | 40 | 30
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-107 | E468300 | F | MSP | FMX | IMM32-032A | 240 | 3 | 100 | 25 - 32 | 10 | 240 | 3 | 100 | 28 | 10 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-40S | 240 | 3 | 5 | 42 | 15
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F32-108 | E468300 | F | MSP | FMX | IMM32-032A | 200 | 3 | 100 | 25 - 32 | 10 | 200 | 3 | 100 | 32 | 10 | 516.2617 | 1 ; 5
|  |  | ACC (Current Limiter) | FMX | IMA-CURLIM
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-32F | - | - | - | - | -
|  |  | MC | FMX | IC330-40S | 200 | 3 | 5 | 32.2 | 10
|  |  | ACC (Adapter) | FMX | IMA-LNKADP | - | - | - | - | -
F65-109 | E468300 | F | MSP | FMX | IMM65-040A | 600Y/347 | 3 | 10 | 32 - 40 | 30 | 600Y/347 | 3 | 10 | 32 | 30 | 696.9533 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-65F | - | - | - | - | -
|  |  | MC | FMX | IC330-50S | 600 | 3 | 10 | 41 | 40
F65-110 | E468300 | F | MSP | FMX | IMM65-040A | 480Y/277 | 3 | 30 | 32 - 40 | 25 | 480Y/277 | 3 | 30 | 34 | 25 | 696.9533 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-65F | - | - | - | - | -
|  |  | MC | FMX | IC330-50S | 480 | 3 | 10 | 52 | 40
F65-112 | E468300 | F | MSP | FMX | IMM65-050A | 600Y/347 | 3 | 10 | 40 - 50 | 40 | 600Y/347 | 3 | 10 | 41 | 40 | 696.9533 | 1 ; 5 ; 6
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-65F | - | - | - | - | -
|  |  | MC | FMX | IC330-65S | 600 | 3 | 10 | 52 | 50
F65-113 | E468300 | F | MSP | FMX | IMM65-050A | 480Y/277 | 3 | 30 | 40 - 50 | 30 | 480Y/277 | 3 | 30 | 40 | 30 | 696.9533 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-65F | - | - | - | - | -
|  |  | MC | FMX | IC330-65S | 480 | 3 | 10 | 65 | 50
F65-114 | E468300 | F | MSP | FMX | IMM65-050A | 240 | 3 | 30 | 40 - 50 | 15 | 240 | 3 | 30 | 42 | 15 | 696.9533 | 1 ; 5 ; 6
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-65F | - | - | - | - | -
|  |  | MC | FMX | IC330-65S | 240 | 3 | 10 | 54 | 20
F65-115 | E468300 | F | MSP | FMX | IMM65-050A | 200 | 3 | 30 | 40 - 50 | 15 | 200 | 3 | 30 | 48.3 | 15 | 696.9533 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-65F | - | - | - | - | -
|  |  | MC | FMX | IC330-65S | 200 | 3 | 10 | 62.1 | 20
F65-116 | E468300 | F | MSP | FMX | IMM65-065A | 600Y/347 | 3 | 10 | 50 - 65 | 60 | 600Y/347 | 3 | 10 | 62 | 60 | 696.9533 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-65F | - | - | - | - | -
|  |  | MC | FMX | IC330-80S | 600 | 3 | 10 | 62 | 60
F65-117 | E468300 | F | MSP | FMX | IMM65-065A | 480Y/277 | 3 | 30 | 50 - 65 | 50 | 480Y/277 | 3 | 30 | 65 | 50 | 696.9533 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-65F | - | - | - | - | -
|  |  | MC | FMX | IC330-80S | 480 | 3 | 10 | 65 | 50
F65-118 | E468300 | F | MSP | FMX | IMM65-065A | 240 | 3 | 30 | 50 - 65 | 20 | 240 | 3 | 30 | 54 | 20 | 696.9533 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-65F | - | - | - | - | -
|  |  | MC | FMX | IC330-80S | 240 | 3 | 10 | 68 | 25
F65-119 | E468300 | F | MSP | FMX | IMM65-065A | 200 | 3 | 30 | 50 - 65 | 20 | 200 | 3 | 30 | 62.1 | 20 | 696.9533 | 1 ; 5
|  |  | ACC (Signaling Block) | FMX | IMA-ALARM-S02 | - | - | - | - | -
|  |  | ACC (Line Side Terminal) | FMX | IMA-TYPEE-65F | - | - | - | - | -
|  |  | MC | FMX | IC330-80S | 200 | 3 | 10 | 62.1 | 20
Note on I171: Fuoco, James: Revised per page 3 of Vol 1 Sec 1